## Summary
Quality Verification Substation (QVS) Audits Completed since January 1, 2020 with HFTD substation locations
Audit | Completed | HFTD Substations Included in Audit
2019 Bakersfield HQ Substation Maintenance Audit | 2020-04-15 | 1
2020 Substation Cancelled Tag Field Audit | 2020-09-20 | 1
2020 McMaude HQ Substation Maintenance Audit | 2020-11-24 | 10
2020 Eureka HQ Substation Maintenance Audit | 2020-11-30 | 4
2020 Fresno HQ Substation Maintenance Audit | 2021-01-04 | 3
Audit | HFTD | Substation | Non-Conformances
2019 Bakersfield HQ Substation Maintenance Audit |  |  | 1
| Tier 2 |  | 1
|  | Poso Mtn. Sub | 1
2020 Eureka HQ Substation Maintenance Audit |  |  | 6
| Tier 2 |  | 3
|  | Fruitland | 1
|  | Maple Creek | 2
| Tier 2 / 3A |  | 3
|  | Hoopa | 2
|  | Russ Ranch | 1
2020 Fresno HQ Substation Maintenance Audit |  |  | 13
| Tier 2 |  | 10
|  | Auberry | 5
|  | Hass | 5
| Tier 3 |  | 3
|  | San Joaquin #2 PH | 3
2020 McMaude HQ Substation Maintenance Audit |  |  | 130
| Tier 2 |  | 75
|  | Bolinas Sub | 17
|  | Cotati Sub | 10
|  | Ft Ross Sub | 10
|  | Oakmont N Sub | 6
|  | Rincon Sub | 9
|  | Stafford Sub | 19
|  | Tocaloma Sub | 4
| Tier 2 / 3A |  | 43
|  | Ignacio Sub | 43
| Tier 3 |  | 12
|  | Monte Rio Sub | 5
|  | Oakmont S Sub | 7
2020 Substation Cancelled Tag Field Audit |  |  | 1
| Tier 2 |  | 1
|  | Sobrante Sub | 1
Grand Total |  |  | 151

## HFTD Summary Detail
Summary Detail - HFTD Only
Audit | Substation | Record Nonconformances | Risk Rank | Priority | CAP | HFTD
2019 Bakersfield HQ Substation Maintenance Audit | Poso Mtn. Sub | Target Plate Incorrect (2200/3ABC) |  | B | 118407265 | Tier 2
2020 Substation Cancelled Tag Field Audit | Sobrante Sub | Lower 115kv gate not grounded |  | A | 119088455 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Bolinas Sub | Barrier chain missing | L | E | 119804838 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Bolinas Sub | Eye wash solution expired | L | E | 119804838 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Bolinas Sub | LTC hazard sticker missing | M | E | 119804838 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Bolinas Sub | Spoil in yard | L | E | 119804838 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Bolinas Sub | 1/1 ARSW Maint form filled incorrectly | L | E | 119777269 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Bolinas Sub | 11 ARSW Maint form filled incorrectly | L | E | 119777269 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Bolinas Sub | 1101/1 ARSW Maint form filled incorrectly | L | E | 119777269 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Bolinas Sub | 1101/3 ARSW Maint form filled incorrectly | L | E | 119777269 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Bolinas Sub | 1101/5 ARSW Maint form filled incorrectly | L | E | 119777269 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Bolinas Sub | 13 ARSW Maint form filled incorrectly | L | E | 119777269 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Bolinas Sub | 15 ARSW Maint form filled incorrectly | L | E | 119777269 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Bolinas Sub | 31 ARSW Maint form filled incorrectly | L | E | 119777269 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Bolinas Sub | 32 BRKR Mech svc form filled incorrectly | L | E | 119777269 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Bolinas Sub | 32 BRKR Mech svc form filled incorrectly | L | E | 119777269 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Bolinas Sub | 33 ARSW Maint form filled incorrectly | L | E | 119777269 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Bolinas Sub | 35 ARSW Maint form filled incorrectly | L | E | 119777269 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Bolinas Sub | 75 ARSW Maint form filled incorrectly | L | E | 119777269 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Cotati Sub | Battery charger not properly labeled | L | E | 119711529 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Cotati Sub | JB13 and JB15 damaged | M | B | 119711529 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Cotati Sub | Missing fuse inventory list | L | E | 119711529 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Cotati Sub | Missing PCB stickers on REG (6) | M | E | 119711529 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Cotati Sub | Old REGs still in station | M | E | 119711529 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Cotati Sub | Signage Missing | M | E | 119711529 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Cotati Sub | SW 23 bus side B phase not fully closed | M | B | 119711529 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Cotati Sub | Third party fence | M | B | 119711529 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Cotati Sub | MOAS 77 form filled out incorrectly | L | E | 119709775 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Cotati Sub | MOAS 77 form filled out incorrectly | L | E | 119709775 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Ft Ross Sub | First aid plan needs update | M | E | 119837260 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Ft Ross Sub | Left over material in yard | L | E | 119837260 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Ft Ross Sub | Pedestrian gate ground strap missing | M | B | 119837260 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Ft Ross Sub | Signage Missing | M | E | 119837260 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Ft Ross Sub | SPCC not signed | M | E | 119837260 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Ft Ross Sub | Wood pole needs guy wire guard | M | B | 119837260 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Ft Ross Sub | Wood pole needs reflective stripes | M | B | 119837260 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Ft Ross Sub | 1121 BRKR Mech Svc form has blank(s) | L | E | 119837260 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Ft Ross Sub | 35 ARSW Maint form filled incorrectly | L | E | 119837260 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Ft Ross Sub | Reg1 LTC Thru Neutral not in APM | L | E | 119837260 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Oakmont N Sub | Battery fan inop | M | B | 119806256 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Oakmont N Sub | Eyewash expired | L | E | 119806256 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Oakmont N Sub | Gate bonding strap broken | M | B | 119806256 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Oakmont N Sub | No NFPA sign on door | M | B | 119806256 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Oakmont N Sub | Signage | M | E | 119806256 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Oakmont N Sub | Update SPCC | M | E | 119806256 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Rincon Sub | Empty nitrogen bottle | M | B | 119645732 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Rincon Sub | Gate ground | M | B | 119645732 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Rincon Sub | Nitrogen bottle turned off | M | B | 119645732 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Rincon Sub | Signage | M | E | 119645732 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Rincon Sub | 1101 new install form field blank | L | E | 119645732 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Rincon Sub | 1102 new install form field blank | L | E | 119645732 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Rincon Sub | Bk2 LTC form multiple blanks and scribbles | L | E | 119645732 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Rincon Sub | MOAS 315 form filled out incorrectly | L | E | 119645732 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Rincon Sub | MOAS 325 form filled out incorrectly | L | E | 119645732 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Stafford Sub | Animal abatement | L | E | 119778359 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Stafford Sub | BK 1 oil weep | M | B | 119778359 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Stafford Sub | BK 1 support insulator broken | M | E | 119778359 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Stafford Sub | Eye wash solution expired | L | E | 119778359 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Stafford Sub | Fence needs repair | M | B | 119778359 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Stafford Sub | Fuses frayed | M | E | 119778359 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Stafford Sub | Ground touching insulated fence | M | E | 119778359 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Stafford Sub | Live line tool non-compliant | M | B | 119778359 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Stafford Sub | Signage | M | E | 119778359 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Stafford Sub | Third party fence | M | B | 119778359 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Stafford Sub | Update SPCC Plan | M | E | 119778359 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Stafford Sub | 1101 exercise box not checked | L | E | 119679886 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Stafford Sub | 1101 mech svc form field not checked | L | E | 119679886 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Stafford Sub | 1102 mech svc form not checked | L | E | 119679886 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Stafford Sub | 1102 mech svc form not reviewed (signed) | L | E | 119679886 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Stafford Sub | 6022 mech svc form missing fields | L | E | 119679886 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Stafford Sub | Bk1 TASA sample date incorrect in SAP | L | E | 119679886 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Stafford Sub | Bk2 LTC 50k insp missing fields | L | E | 119679886 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Stafford Sub | Bk2 TASA sample date incorrect in SAP | L | E | 119679886 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Tocaloma Sub | BK 1 A/B/C TRANS minor rust (3) | L | E | 119777665 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Tocaloma Sub | BK 1 A/B/C TRANS oil weep (3) | M | B | 119777665 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Tocaloma Sub | Signage | M | E | 119777665 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Tocaloma Sub | Update SPCC Plan | M | E | 119777665 | Tier 2
2020 Eureka HQ Substation Maintenance Audit | Fruitland | 1142 BRKR MECH missing paperwork | M | E | 119933393 | Tier 2
2020 Eureka HQ Substation Maintenance Audit | Maple Creek | 42 BRKR MECH SRV form filled incorrectly | L | E | 119954402 | Tier 2
2020 Eureka HQ Substation Maintenance Audit | Maple Creek | 42 BRKR MECH SRV not signed/rev’d | L | E | 119954402 | Tier 2
2020 Fresno HQ Substation Maintenance Audit | Auberry | Station phone not working | L | E | 119960515 | Tier 2
2020 Fresno HQ Substation Maintenance Audit | Auberry | Station improper logging entries | L | E | 119960515 | Tier 2
2020 Fresno HQ Substation Maintenance Audit | Auberry | SPCC binder out of date | L | E | 119960515 | Tier 2
2020 Fresno HQ Substation Maintenance Audit | Auberry | 1102 BRKR maint warning label faded | L | E | 119960515 | Tier 2
2020 Fresno HQ Substation Maintenance Audit | Auberry | Junction box 12 outlet box exposed | L | E | 119960515 | Tier 2
2020 Fresno HQ Substation Maintenance Audit | Hass | Bank 2 Missing B Phase label on bank | L | E | 119837856 | Tier 2
2020 Fresno HQ Substation Maintenance Audit | Hass | Bank 2 Missing PCB sticker | L | E | 119837856 | Tier 2
2020 Fresno HQ Substation Maintenance Audit | Hass | 213 Air Switch double ground on switch platform | L | E | 119837856 | Tier 2
2020 Fresno HQ Substation Maintenance Audit | Hass | Left over materials in yard | L | E | 119837856 | Tier 2
2020 Fresno HQ Substation Maintenance Audit | Hass | Wood poles missing VIS strips | M | E | 119837856 | Tier 2
2020 McMaude HQ Substation Maintenance Audit | Ignacio Sub | ARSW 113 platform too high | L | E | 119872716 | Tier 2 / 3A
2020 McMaude HQ Substation Maintenance Audit | Ignacio Sub | ARSW 115 platform too high | L | E | 119872716 | Tier 2 / 3A
2020 McMaude HQ Substation Maintenance Audit | Ignacio Sub | ARSW 151 platform too high | L | E | 119872716 | Tier 2 / 3A
2020 McMaude HQ Substation Maintenance Audit | Ignacio Sub | ARSW 153 platform too high | L | E | 119872716 | Tier 2 / 3A
2020 McMaude HQ Substation Maintenance Audit | Ignacio Sub | ARSW 155 platform too high | L | E | 119872716 | Tier 2 / 3A
2020 McMaude HQ Substation Maintenance Audit | Ignacio Sub | ARSW 193 platform too high | L | E | 119872716 | Tier 2 / 3A
2020 McMaude HQ Substation Maintenance Audit | Ignacio Sub | ARSW 195 platform too high | L | E | 119872716 | Tier 2 / 3A
2020 McMaude HQ Substation Maintenance Audit | Ignacio Sub | ARSW 381 platform too high | L | E | 119872716 | Tier 2 / 3A
2020 McMaude HQ Substation Maintenance Audit | Ignacio Sub | ARSW 383 platform too high | L | E | 119872716 | Tier 2 / 3A
2020 McMaude HQ Substation Maintenance Audit | Ignacio Sub | ARSW 391 platform too high | L | E | 119872716 | Tier 2 / 3A
2020 McMaude HQ Substation Maintenance Audit | Ignacio Sub | ARSW 393 platform too high | L | E | 119872716 | Tier 2 / 3A
2020 McMaude HQ Substation Maintenance Audit | Ignacio Sub | Battery charger charging current not listed | M | E | 119872716 | Tier 2 / 3A
2020 McMaude HQ Substation Maintenance Audit | Ignacio Sub | BK3 fan inop | M | B | 119872716 | Tier 2 / 3A
2020 McMaude HQ Substation Maintenance Audit | Ignacio Sub | BK4A needs new entry sticker | M | E | 119872716 | Tier 2 / 3A
2020 McMaude HQ Substation Maintenance Audit | Ignacio Sub | BK4B fan inop | M | B | 119872716 | Tier 2 / 3A
2020 McMaude HQ Substation Maintenance Audit | Ignacio Sub | BK4B needs new entry sticker | M | E | 119872716 | Tier 2 / 3A
2020 McMaude HQ Substation Maintenance Audit | Ignacio Sub | BK4C fan inop | M | B | 119872716 | Tier 2 / 3A
2020 McMaude HQ Substation Maintenance Audit | Ignacio Sub | BK4C needs new entry sticker | M | E | 119872716 | Tier 2 / 3A
2020 McMaude HQ Substation Maintenance Audit | Ignacio Sub | BK4C negative pressure | M | B | 119872716 | Tier 2 / 3A
2020 McMaude HQ Substation Maintenance Audit | Ignacio Sub | BK4SP needs new entry sticker | M | E | 119872716 | Tier 2 / 3A
2020 McMaude HQ Substation Maintenance Audit | Ignacio Sub | BK5 empty N2 | M | B | 119872716 | Tier 2 / 3A
2020 McMaude HQ Substation Maintenance Audit | Ignacio Sub | BK6 annunciator cut out since 2013 | M | B | 119872716 | Tier 2 / 3A
2020 McMaude HQ Substation Maintenance Audit | Ignacio Sub | BK6 change desiccant | M | B | 119872716 | Tier 2 / 3A
2020 McMaude HQ Substation Maintenance Audit | Ignacio Sub | BRKR 142 missing conduit cover | M | B | 119872716 | Tier 2 / 3A
2020 McMaude HQ Substation Maintenance Audit | Ignacio Sub | Eye wash expired (3 locations) | L | E | 119872716 | Tier 2 / 3A
2020 McMaude HQ Substation Maintenance Audit | Ignacio Sub | First aid plan needs updating | M | E | 119872716 | Tier 2 / 3A
2020 McMaude HQ Substation Maintenance Audit | Ignacio Sub | Fuses weathered | M | E | 119872716 | Tier 2 / 3A
2020 McMaude HQ Substation Maintenance Audit | Ignacio Sub | Materials left in yard | M | B | 119872716 | Tier 2 / 3A
2020 McMaude HQ Substation Maintenance Audit | Ignacio Sub | Multiple case grounds missing | M | B | 119872716 | Tier 2 / 3A
2020 McMaude HQ Substation Maintenance Audit | Ignacio Sub | Purple binder missing | M | E | 119872716 | Tier 2 / 3A
2020 McMaude HQ Substation Maintenance Audit | Ignacio Sub | Signage on SPCC pond | M | E | 119872716 | Tier 2 / 3A
2020 McMaude HQ Substation Maintenance Audit | Ignacio Sub | Unable to locate spare fuses/list | M | E | 119872716 | Tier 2 / 3A
2020 McMaude HQ Substation Maintenance Audit | Ignacio Sub | Vent fan inop | M | B | 119872716 | Tier 2 / 3A
2020 McMaude HQ Substation Maintenance Audit | Ignacio Sub | Yard lighting multiple lights out | M | B | 119872716 | Tier 2 / 3A
2020 McMaude HQ Substation Maintenance Audit | Ignacio Sub | 12 BRKR Mech Svc form filled incorrectly | L | E | 119870595 | Tier 2 / 3A
2020 McMaude HQ Substation Maintenance Audit | Ignacio Sub | 172 BRKR Mech Svc form filled incorrectly | L | E | 119870595 | Tier 2 / 3A
2020 McMaude HQ Substation Maintenance Audit | Ignacio Sub | 202 BRKR Mech Svc form filled incorrectly | L | E | 119870595 | Tier 2 / 3A
2020 McMaude HQ Substation Maintenance Audit | Ignacio Sub | 22 BRKR Mech Svc form filled incorrectly | L | E | 119870595 | Tier 2 / 3A
2020 McMaude HQ Substation Maintenance Audit | Ignacio Sub | 232 BRKR Mech Svc form filled incorrectly | L | E | 119870595 | Tier 2 / 3A
2020 McMaude HQ Substation Maintenance Audit | Ignacio Sub | 252 BRKR Mech Svc form filled incorrectly | L | E | 119870595 | Tier 2 / 3A
2020 McMaude HQ Substation Maintenance Audit | Ignacio Sub | 52 BRKR Mech Svc form filled incorrectly | L | E | 119870595 | Tier 2 / 3A
2020 McMaude HQ Substation Maintenance Audit | Ignacio Sub | BK 4A TDA date incorrect | L | E | 119870595 | Tier 2 / 3A
2020 McMaude HQ Substation Maintenance Audit | Ignacio Sub | BK 4sp TDA date incorrect | L | E | 119870595 | Tier 2 / 3A
2020 Eureka HQ Substation Maintenance Audit | Hoopa | 1101 BRKR MECH form filled incorrectly | L | E | 119933731 | Tier 2 / 3A
2020 Eureka HQ Substation Maintenance Audit | Hoopa | Battery resistance test form filled incorrectly | L | E | 119933731 | Tier 2 / 3A
2020 Eureka HQ Substation Maintenance Audit | Russ Ranch | BK 1 TXFR TDA sample taken / not rec’d by lab | M | E | 119954548 | Tier 2 / 3A
2020 McMaude HQ Substation Maintenance Audit | Monte Rio Sub | Bk1 Oil Filtration inop | M | E | 119837067 | Tier 3
2020 McMaude HQ Substation Maintenance Audit | Monte Rio Sub | Guy wire guards needed | M | E | 119837067 | Tier 3
2020 McMaude HQ Substation Maintenance Audit | Monte Rio Sub | NFPH sign needed on battery shed | M | B | 119837067 | Tier 3
2020 McMaude HQ Substation Maintenance Audit | Monte Rio Sub | No spare fuse list | M | E | 119837067 | Tier 3
2020 McMaude HQ Substation Maintenance Audit | Monte Rio Sub | SPCC pond signage/pond dirty | L | E | 119837067 | Tier 3
2020 McMaude HQ Substation Maintenance Audit | Oakmont S Sub | Battery charging current not listed | L | E | 119807583 | Tier 3
2020 McMaude HQ Substation Maintenance Audit | Oakmont S Sub | Battery fan inop | M | B | 119807583 | Tier 3
2020 McMaude HQ Substation Maintenance Audit | Oakmont S Sub | Eyewash expired | L | E | 119807583 | Tier 3
2020 McMaude HQ Substation Maintenance Audit | Oakmont S Sub | Gate bonding strap broken | M | B | 119807583 | Tier 3
2020 McMaude HQ Substation Maintenance Audit | Oakmont S Sub | Signage | M | E | 119807583 | Tier 3
2020 McMaude HQ Substation Maintenance Audit | Oakmont S Sub | Update SPCC | M | E | 119807583 | Tier 3
2020 McMaude HQ Substation Maintenance Audit | Oakmont S Sub | Wood stairs need replacement | M | E | 119807583 | Tier 3
2020 Fresno HQ Substation Maintenance Audit | San Joaquin #2 PH | SPCC binder outdated | L | E | 119959353 | Tier 3
2020 Fresno HQ Substation Maintenance Audit | San Joaquin #2 PH | Missing fuse inventory list | L | E | 119959353 | Tier 3
2020 Fresno HQ Substation Maintenance Audit | San Joaquin #2 PH | Missing fence signs | L | E | 119959353 | Tier 3