## Summary
2020 Contractor Inspection TRANSMISSION Audit HFTD Non-Conformances
HFTD Non-Conformances by Tier
Tier | Non-Conformances
Tier 2 | 57
Tier 3 | 106
Audit | HFTD | Transmission Location | Non-Conformances
2020 Transmission Contractor Inspection
Tier 2
|  | 40584652 | 2
|  | 40585890 | 2
|  | 40603063 | 1
|  | 40617175 | 5
|  | 40649835 | 4
|  | 40658346 | 2
|  | 40663624 | 1
|  | 40740278 | 1
|  | 40753897 | 1
|  | 40761222 | 1
|  | 40768968 | 5
|  | 40818965 | 1
|  | 40821462 | 6
|  | 40870904 | 3
|  | 40871845 | 1
|  | 40872358 | 4
|  | 40906368 | 4
|  | 40906381 | 2
|  | 40906403 | 2
|  | 40906798 | 1
|  | 40910974 | 1
|  | 44191483 | 2
|  | 44191489 | 2
|  | 44744773 | 3
Tier 3
|  | 40580810 | 2
|  | 40581575 | 1
|  | 40587443 | 5
|  | 40592879 | 2
|  | 40596226 | 2
|  | 40597132 | 3
|  | 40609137 | 3
|  | 40616054 | 1
|  | 40616080 | 2
|  | 40616083 | 1
|  | 40650023 | 2
|  | 40654450 | 2
|  | 40657124 | 2
|  | 40658939 | 2
|  | 40664610 | 1
|  | 40756577 | 3
|  | 40761580 | 1
|  | 40769510 | 1
|  | 40769806 | 1
|  | 40770960 | 2
|  | 40808410 | 1
|  | 40809073 | 7
|  | 40809998 | 2
|  | 40810149 | 3
|  | 40811447 | 1
|  | 40812089 | 1
|  | 40812433 | 5
|  | 40817796 | 19
|  | 40821788 | 7
|  | 40862144 | 1
|  | 41196118 | 1
|  | 42578835 | 2
|  | 42578836 | 2
|  | 42578837 | 1
|  | 42578838 | 1
|  | 42578839 | 6
|  | 44203631 | 1
|  | 44645377 | 2
|  | 44811427 | 1
|  | 44877340 | 1
|  | 44904217 | 1
|  | 44928866 | 1

## HFTD Summary Detail
Summary Detail - HFTD Only
Audit | Transmission Location | Non-Conformance Description | N/C Type | Risk Rank | HFTD
2020 Transmission Contractor Inspection | 40870904 | CI photos do not include zoom image of hot & cold end of each insulator string. | Record | Low | Tier 2
2020 Transmission Contractor Inspection | 42578839 | Contract Inspector attached photos of structure 004/043C; this is structure 004/043B. | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40906403 | CTI used same photos from hot end as cold end | Record | Low | Tier 2
2020 Transmission Contractor Inspection | 40649835 | CTI used same photos of hot end as cold end | Record | Low | Tier 2
2020 Transmission Contractor Inspection | 40821462 | Hot and cold end photos not one photo per string, not zoomed in on hot/cold ends. The inspector included pictures of the distribution crossarm under the cold end photos. | Record | Low | Tier 2
2020 Transmission Contractor Inspection | 42578835 | HOT-END PHOTOS: Contract Inspector uploaded 2 photos of structure 003/041C; this is structure 003/041/B. COLD-END PHOTOS: Contract Inspector uploaded 1 photo of structure 003/041B & 1 photo of structure 003/0041C; this is structure 003/041B. | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40770960 | The inspector did not include pictures zoomed in on the hot and cold ends of insulator strings. Hot and cold end photos not one photo per string. | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40872358 | The inspector did not include pictures zoomed in on the hot and cold ends of insulator strings. Hot and cold end photos not one photo per string. Photos attached are of top section of pole, including 10-20 feet of pole below the distribution underbuild. | Record | Low | Tier 2
2020 Transmission Contractor Inspection | 40768968 | View of Clamp (hot end) one photo per string, View of point of attachment hardware (cold end) one photo per string | Record | Low | Tier 2
2020 Transmission Contractor Inspection | 40584652 | Photo non-conformance; description not available | Record | Low | Tier 2
2020 Transmission Contractor Inspection | 40617175 | Photo non-conformance; description not available | Record | Low | Tier 2
2020 Transmission Contractor Inspection | 40810149 | Photo non-conformance; description not available | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40817796 | Photo non-conformance; description not available | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40753897 | 1 Photo missing on cold end on V-string | Record | Low | Tier 2
2020 Transmission Contractor Inspection | 40809073 | CI photos do not include zoom image of hot & cold end of each insulator string. | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40812433 | CI photos do not include zoom image of hot & cold end of each insulator string. | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40756577 | Has 12 of 16 photos of hot and cold end. Photos are not close ups of hot and cold ends, they are more of a general picture of the complete insulator string. | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40821788 | Photos are dark and not close ups. | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40587443 | The inspector did not include pictures zoomed in on the hot and cold ends of insulator strings. Hot and cold end photos not one photo per string. | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40597132 | The inspector did not include pictures zoomed in on the hot and cold ends of insulator strings. Hot and cold end photos not one photo per string. | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40769806 | The inspector did not include pictures zoomed in on the hot and cold ends of insulator strings. Hot and cold end photos not one photo per string. | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 44877340 | The inspector did not include pictures zoomed in on the hot and cold ends of insulator strings. Hot and cold end photos not one photo per string. | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40581575 | Photo non-conformance; description not available | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40658939 | Photo non-conformance; description not available | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 44928866 | Photo non-conformance; description not available | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 42578839 | Contract Inspector did not record the presence of 2 anchors. | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40817796 | Asset record non-conformance; description not available | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40871845 | Anchor rod moderate corrosion @ ground line. | Field | Low | Tier 2
2020 Transmission Contractor Inspection | 40821462 | Storm guy anchor west of pole showing rust. The inspector did not report the storm guy anchors. | Field | Low | Tier 2
2020 Transmission Contractor Inspection | 40817796 | Asset record non-conformance; description not available | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40603063 | Birds or squirrels have started eating the two inside skirts of the top insulator. | Field | Low | Tier 2
2020 Transmission Contractor Inspection | 40809073 | 2 nuts on quadrant clamp not tight per visual with binoculars from ground. Host side , bottom phase , back direction. | Field | Low | Tier 3
2020 Transmission Contractor Inspection | 40809073 | 2 nuts on quadrant clamp not tight per visual with binoculars from ground. Host side , bottom phase , back direction. | Field | Low | Tier 3
2020 Transmission Contractor Inspection | 40812433 | 'C' hook & eye show moderate rust. | Field | Low | Tier 3
2020 Transmission Contractor Inspection | 40870904 | 'C' hook & eye show moderate rust. | Field | Low | Tier 2
2020 Transmission Contractor Inspection | 40811447 | Insulator has heavy corona damage to insulator | Field | Medium | Tier 3
2020 Transmission Contractor Inspection | 40596226 | Tag created, inspector documented | Field | Low | Tier 3
2020 Transmission Contractor Inspection | 40587443 | The bells are a little dirty. | Field | Low | Tier 3
2020 Transmission Contractor Inspection | 40761222 | Field non-conformance; insulator issue | Field | Low | Tier 2
2020 Transmission Contractor Inspection | 40906381 | Noted by CTI with existing LC 119097093 | Field | Low | Tier 2
2020 Transmission Contractor Inspection | 40906368 | Wire is bird caged pretty bad on all 6 splices the issue was noted by contract inspector | Field | Medium | Tier 2
2020 Transmission Contractor Inspection | 40587443 | Field non-conformance; conductor issue | Field | Low | Tier 3
2020 Transmission Contractor Inspection | 40597132 | Field non-conformance; conductor issue | Field | Low | Tier 3
2020 Transmission Contractor Inspection | 40658939 | Field non-conformance; conductor issue | Field | Low | Tier 3
2020 Transmission Contractor Inspection | 42578839 | Contract Inspector did not record the presence of 2 down guys. | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40817796 | Asset record non-conformance; description not available | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40821462 | Both storm guys are loose. The inspector did not report the storm guys. | Field | Low | Tier 2
2020 Transmission Contractor Inspection | 40906381 | Guy is sectionalized, but not bonded noted by CTI with existing LC 119097018 | Field | Low | Tier 2
2020 Transmission Contractor Inspection | 40657124 | Contractor recoded tower as 005/042, tower is 006/042 | Field | Low | Tier 3
2020 Transmission Contractor Inspection | 40809073 | LC exists for foundation debris at location. | Field | Low | Tier 3
2020 Transmission Contractor Inspection | 44203631 | Low pole step | Field | Low | Tier 3
2020 Transmission Contractor Inspection | 40768968 | Old pole butt not removed. | Field | Low | Tier 2
2020 Transmission Contractor Inspection | 44645377 | The structure only has one high-voltage sign. This was not documented by the inspector And in looking at his photos the high-voltage sign was not here when he was doing the inspection | Field | Low | Tier 3
2020 Transmission Contractor Inspection | 40770960 | Vis strips damaged/missing. Replaced by QVS. | Field | Low | Tier 3
2020 Transmission Contractor Inspection | 40609137 | Field non-conformance; description not available | Field | Low | Tier 3
2020 Transmission Contractor Inspection | 40809998 | Field non-conformance; description not available | Field | Low | Tier 3
2020 Transmission Contractor Inspection | 40768968 | @ center phase splices @ 15’ ahead & 150’ ahead for a total of 2 splices. | Record | Low | Tier 2
2020 Transmission Contractor Inspection | 40817796 | Asset record non-conformance; description not available | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40821462 | 6 Corona rings. | Record | Low | Tier 2
2020 Transmission Contractor Inspection | 40872358 | Corona rings present on 2 suspension insulators. The inspector did not report. | Record | Low | Tier 2
2020 Transmission Contractor Inspection | 40617175 | Asset record non-conformance; description not available | Record | Low | Tier 2
2020 Transmission Contractor Inspection | 40740278 | Asset record non-conformance; description not available | Record | Low | Tier 2
2020 Transmission Contractor Inspection | 40817796 | Asset record non-conformance; description not available | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40817796 | Asset record non-conformance; description not available | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40817796 | Asset record non-conformance; description not available | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40872358 | 2 suspension 1 post. 3 Pt. 2 post insulators on distribution. The inspector reported 6. | Record | Low | Tier 2
2020 Transmission Contractor Inspection | 40808410 | 3 pin insulators. | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40821462 | 6 DE insulators, 1 post | Record | Low | Tier 2
2020 Transmission Contractor Inspection | 44904217 | CI reported 1insulator string & 3 is correct. | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40649835 | Contract Inspector recorded 1 insulator string. This is a 3-phase, double-dead end. Therefore, there are 6 insulator strings. | Record | Low | Tier 2
2020 Transmission Contractor Inspection | 40585890 | Contract Inspector recorded 1 insulator string; the correct number is 3 insulator strings. | Record | Low | Tier 2
2020 Transmission Contractor Inspection | 40769510 | Contract Inspector recorded 2 insulator strings | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40809998 | Contract Inspector recorded 2 insulator strings | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 42578835 | Contract Inspector recorded 2 insulator strings | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 42578836 | Contract Inspector recorded 2 insulator strings | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 42578837 | Contract Inspector recorded 2 insulator strings | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 42578838 | Contract Inspector recorded 2 insulator strings | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 42578839 | Contract Inspector recorded 2 insulator strings | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40663624 | Inspector did not count correctly 3 insulators not 1 | Record | Low | Tier 2
2020 Transmission Contractor Inspection | 40664610 | Only counted 1, Called Center phase jumper support insulators idle | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 44191483 | Only documented one string but had photos of the Tri-kit pole top | Record | Low | Tier 2
2020 Transmission Contractor Inspection | 44645377 | The inspector documented one string of bells, there are three insulators for the tri-kit he had the appropriate photos | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40906798 | The inspector only documented one string of bells but had the photos of all of them | Record | Low | Tier 2
2020 Transmission Contractor Inspection | 44191489 | The inspector only noted one string but had the appropriate photo of a tri-kit | Record | Low | Tier 2
2020 Transmission Contractor Inspection | 40910974 | The inspector only recorded one string of bells but took appropriate photos of the steel tower with six strings of bells | Record | Low | Tier 2
2020 Transmission Contractor Inspection | 44744773 | The inspector or recorded one string of bells there are three insulators on a T1 kit | Record | Low | Tier 2
2020 Transmission Contractor Inspection | 40587443 | Asset record non-conformance; description not available | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40609137 | Asset record non-conformance; description not available | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40616080 | Asset record non-conformance; description not available | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40650023 | Asset record non-conformance; description not available | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40658346 | Asset record non-conformance; description not available | Record | Low | Tier 2
2020 Transmission Contractor Inspection | 40810149 | Asset record non-conformance; description not available | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40817796 | Asset record non-conformance; description not available | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40821788 | Asset record non-conformance; description not available | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40906368 | Asset record non-conformance; description not available | Record | Low | Tier 2
2020 Transmission Contractor Inspection | 40906403 | Asset record non-conformance; description not available | Record | Low | Tier 2
2020 Transmission Contractor Inspection | 44811427 | Asset record non-conformance; description not available | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 41196118 | No external ground was present. | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40817796 | Asset record non-conformance; description not available | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40821462 | 3 jumpers on pole. | Record | Low | Tier 2
2020 Transmission Contractor Inspection | 40587443 | 6 jumpers on tower. | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 42578839 | Contract Inspector did not identify the presence of the 1 jumper at this location. | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40649835 | Contract Inspector did not record the presence of any jumpers. This is a 3-phase, double-dead end. Therefore, there are 3 jumpers present. | Record | Low | Tier 2
2020 Transmission Contractor Inspection | 40616054 | Contract Inspector did not record the presence of the 1 jumper at this location. | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40810149 | Middle phase jumper is too short placing strain on the SW Insulator and shoe causing tension on fired wedge connection. | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40809073 | No jumpers reported. | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40650023 | Asset record non-conformance; description not available | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40817796 | Asset record non-conformance; description not available | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40817796 | Asset record non-conformance; description not available | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40617175 | Asset record non-conformance; description not available | Record | Low | Tier 2
2020 Transmission Contractor Inspection | 40817796 | Asset record non-conformance; description not available | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40768968 | @ center phase splices @ 15’ back , 15’ ahead , 150’ ahead for a total of 3 splices. | Record | Low | Tier 2
2020 Transmission Contractor Inspection | 40872358 | 3 Splices in span to the south. The inspector did not report splices. | Record | Low | Tier 2
2020 Transmission Contractor Inspection | 40592879 | 6 splices North span | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40818965 | 6 splices SE, 1 splice per conductor | Record | Low | Tier 2
2020 Transmission Contractor Inspection | 42578839 | Contract Inspector did not record splice (approximately 20’ to the south towards structure 004/044). | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 42578836 | Contract Inspector did not record splice (approximately 50’ to the south towards structure 003/042). | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40617175 | Asset record non-conformance; description not available | Record | Low | Tier 2
2020 Transmission Contractor Inspection | 40817796 | Asset record non-conformance; description not available | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40821788 | Asset record non-conformance; description not available | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40617175 | Asset record non-conformance; description not available | Record | Low | Tier 2
2020 Transmission Contractor Inspection | 40817796 | Asset record non-conformance; description not available | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 44191483 | The inspector is inspecting the wrong locations, he took photos and inspected pole 1/31 for this location 1/32. He has three poles in this area that are in our audit and all of them are off by one pole to the North he is inspecting the wrong poles for what he is documenting. The other poles are 2/33 & 2/35 | Record | Low | Tier 2
2020 Transmission Contractor Inspection | 44744773 | The inspector is inspecting the wrong locations, he took photos and inspected pole 1/32 for this location 2/33 he has three poles in this area that are in our audit and all three of them are off by one pole to the north. He is inspecting the wrong poles for what he is documenting. The other poles are 1/32 and 2/35 | Record | Low | Tier 2
2020 Transmission Contractor Inspection | 44191489 | The inspector is inspecting the wrong locations, he took photos and inspected pole 2/34 for this location 2/35. He has three poles in this area that are in our audit and all three of them are off by one pole to the north. He is inspecting the wrong poles for what he is documenting. The other poles are 1/32 and 2/33 | Record | Low | Tier 2
2020 Transmission Contractor Inspection | 40597132 | Asset record non-conformance; description not available | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40817796 | Asset record non-conformance; description not available | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40812433 | CI reported finish as weathered , actual is galvanized. | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40809073 | Recorded as weathered, actual is galvanized. | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40654450 | Asset record non-conformance; description not available | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40756577 | Asset record non-conformance; description not available | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40821788 | Asset record non-conformance; description not available | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40817796 | Asset record non-conformance; description not available | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 44744773 | Asset record non-conformance; description not available | Record | Low | Tier 2
2020 Transmission Contractor Inspection | 40584652 | Both ends of arm show deterioration. | Field | Low | Tier 2
2020 Transmission Contractor Inspection | 40870904 | 'C' hook & eye show moderate rust. | Field | Low | Tier 2
2020 Transmission Contractor Inspection | 40906368 | CTI noted and reported existing LC,s 1- for pole damage 117243251 and 1- for woodpeckers 119118786 | Field | Medium | Tier 2
2020 Transmission Contractor Inspection | 40906368 | CTI noted and reported existing LC,s 1- for pole damage 117243251 and 1- for woodpeckers 119118786 | Field | Medium | Tier 2
2020 Transmission Contractor Inspection | 40768968 | Old pole butt not removed. | Field | Low | Tier 2
2020 Transmission Contractor Inspection | 40609137 | Bottom and Middle phase of the MORAGA-SAN LEANDRO #1 have damaged secondary members | Field | Medium | Tier 3
2020 Transmission Contractor Inspection | 40812433 | 'C' hook & eye show moderate rust. | Field | Low | Tier 3
2020 Transmission Contractor Inspection | 40821788 | Needs re-painted | Field | Low | Tier 3
2020 Transmission Contractor Inspection | 40580810 | Two bolts missing at the base of the tower | Field | Medium | Tier 3
2020 Transmission Contractor Inspection | 40654450 | Field non-conformance; description not available | Field | Low | Tier 3
2020 Transmission Contractor Inspection | 40657124 | Field non-conformance; description not available | Field | Low | Tier 3
2020 Transmission Contractor Inspection | 40596226 | Inspector created tag | Field | Low | Tier 3
2020 Transmission Contractor Inspection | 40809073 | LC exists for mastic. | Field | Low | Tier 3
2020 Transmission Contractor Inspection | 40812433 | LC exists for mastic. | Field | Low | Tier 3
2020 Transmission Contractor Inspection | 40580810 | Minor cracking and breaking up of mastic | Field | Low | Tier 3
2020 Transmission Contractor Inspection | 40756577 | Small cracks in foundations need sealed | Field | Low | Tier 3
2020 Transmission Contractor Inspection | 40821788 | Field non-conformance; description not available | Field | Medium | Tier 3
2020 Transmission Contractor Inspection | 40821788 | Field non-conformance; description not available | Field | Medium | Tier 3
2020 Transmission Contractor Inspection | 40761580 | Asset record non-conformance; description not available | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40817796 | Asset record non-conformance; description not available | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40812089 | Inspector did not identify vegetation | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40585890 | Vegetation exists on, and next to, this right-of-way in both directions. | Record | Low | Tier 2
2020 Transmission Contractor Inspection | 40649835 | Vegetation exists on, and next to, this right-of-way in both directions. | Record | Low | Tier 2
2020 Transmission Contractor Inspection | 40592879 | Vegetation exists | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40616080 | Vegetation exists | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40616083 | Vegetation exists | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40658346 | Vegetation exists | Record | Low | Tier 2
2020 Transmission Contractor Inspection | 40817796 | Vegetation exists | Record | Low | Tier 3
2020 Transmission Contractor Inspection | 40862144 | Vegetation exists | Record | Low | Tier 3