## Summary
2020 QVD Division Audit HFTD Non-Conformances
HFTD Non-Conformances by Tier
Tier | Non-Conformances
Tier 2 | 181
Tier 3 | 93
Audit | HFTD | Notification # (Work Order) | Non-Conformances
Distribution T200 Audit
Tier 2
|  | 110142456 | 1
|  | 110873801 | 2
|  | 111531721 | 1
|  | 112009632 | 1
|  | 114131338 | 3
|  | 114950500 | 1
|  | 116686972 | 1
|  | 116691457 | 1
|  | 116692310 | 2
|  | 116707396 | 1
|  | 116709728 | 4
|  | 116731139 | 1
|  | 116734616 | 3
|  | 116749362 | 1
|  | 116789560 | 1
|  | 116818542 | 2
|  | 116870657 | 3
|  | 116871967 | 1
|  | 116961307 | 1
|  | 116967977 | 1
|  | 116985405 | 2
|  | 116987369 | 2
|  | 117001069 | 1
|  | 117015931 | 1
|  | 117016283 | 5
|  | 117025986 | 1
|  | 117032781 | 3
|  | 117039088 | 1
|  | 117044328 | 2
|  | 117074442 | 4
|  | 117086258 | 1
|  | 117097751 | 1
|  | 117113380 | 1
|  | 117116158 | 2
|  | 117151648 | 2
|  | 117159411 | 3
|  | 117159698 | 4
|  | 117185991 | 1
|  | 117190032 | 2
|  | 117196341 | 1
|  | 117212115 | 2
|  | 117234815 | 1
|  | 117241589 | 3
|  | 117269408 | 1
|  | 117375545 | 1
|  | 117490976 | 2
|  | 117496181 | 2
|  | 118141852 | 3
|  | 118146823 | 5
|  | 118235886 | 1
|  | 118264827 | 1
|  | 118283932 | 4
|  | 118409190 | 3
|  | 118524057 | 5
|  | 118526127 | 4
|  | 118527806 | 5
|  | 118548313 | 4
|  | 118553923 | 2
|  | 118562240 | 3
|  | 118585834 | 1
|  | 118591579 | 3
|  | 118591756 | 3
|  | 118600932 | 10
|  | 118603430 | 3
|  | 118685770 | 5
|  | 118710214 | 4
|  | 118721438 | 3
|  | 118767009 | 1
|  | 118767425 | 2
|  | 118774961 | 3
|  | 118778045 | 1
|  | 118781056 | 2
|  | 118782726 | 3
|  | 118795232 | 1
|  | 118797380 | 2
|  | 118913052 | 1
|  | 118937136 | 2
|  | 118938223 | 2
|  | 118939668 | 4
|  | 118963997 | 1
Tier 3
|  | 109252430 | 2
|  | 110283014 | 2
|  | 110678401 | 1
|  | 116744254 | 1
|  | 116822038 | 1
|  | 116825414 | 2
|  | 116883058 | 1
|  | 117060526 | 1
|  | 117069349 | 4
|  | 117096368 | 4
|  | 117099314 | 5
|  | 117138051 | 2
|  | 117189723 | 1
|  | 117239817 | 4
|  | 117247506 | 3
|  | 117290399 | 2
|  | 117293698 | 1
|  | 117293950 | 1
|  | 117320011 | 1
|  | 117376311 | 2
|  | 117751840 | 3
|  | 118457548 | 2
|  | 118483969 | 2
|  | 118536406 | 1
|  | 118539668 | 1
|  | 118585430 | 4
|  | 118605808 | 5
|  | 118650713 | 5
|  | 118681659 | 1
|  | 118709308 | 15
|  | 118719932 | 2
|  | 118754428 | 2
|  | 118777634 | 1
|  | 118780727 | 1
|  | 118914553 | 1
|  | 118929021 | 4
|  | 118946081 | 2

## HFTD Summary Detail
Summary Detail - HFTD Only
Audit | Notification # (Work Order) | Location ID (SAP Equipment #) | Non-Conformance Description | N/C Type | Risk Rank | HFTD
Distribution T200 Audit | 118767009 | 100018211 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 2
Distribution T200 Audit | 112009632 | 103675771 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 2
Distribution T200 Audit | 117241589 | 101513117 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 2
Distribution T200 Audit | 117190032 | 101517982 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 2
Distribution T200 Audit | 118782726 | 100394976 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 2
Distribution T200 Audit | 117196341 | 100374434 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 2
Distribution T200 Audit | 116987369 | 100371779 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 2
Distribution T200 Audit | 114131338 | 101067581 | EC/ER Notification is missing required information or completed incorrectly. (Specify in notes) | Record | Low | Tier 2
Distribution T200 Audit | 111531721 | 101076384 | CCSC is missing from job package in SAP. All completed CCSC forms shall remain on file with the completed job. | Record | Low | Tier 2
Distribution T200 Audit | 116967977 | 103893362 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 2
Distribution T200 Audit | 118141852 | 101649732 | As-Built not red lined correctly and/or partially completed work in field not identified on As-Built. | Record | Low | Tier 2
Distribution T200 Audit | 118141852 | 101649732 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 2
Distribution T200 Audit | 118585834 | 100389297 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 2
Distribution T200 Audit | 116789560 | 101466204 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 2
Distribution T200 Audit | 118264827 | 100675340 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Medium | Tier 2
Distribution T200 Audit | 118963997 | 101526541 | CCSC is missing from job package in SAP. All completed CCSC forms shall remain on file with the completed job. | Record | Low | Tier 2
Distribution T200 Audit | 117097751 | 101553713 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 2
Distribution T200 Audit | 117269408 | 101524881 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 2
Distribution T200 Audit | 117015931 | 101483576 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 2
Distribution T200 Audit | 117025986 | 102316155 | EC/ER Notification is missing required information or completed incorrectly. (Specify in notes) | Record | Low | Tier 2
Distribution T200 Audit | 117151648 | 103909873 | EC/ER Notification is missing required information or completed incorrectly. (Specify in notes) | Record | Low | Tier 2
Distribution T200 Audit | 118591579 | 100525524 | CCSC is missing from job package in SAP. All completed CCSC forms shall remain on file with the completed job. | Record | Medium | Tier 2
Distribution T200 Audit | 118938223 | 101401677 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 2
Distribution T200 Audit | 116749362 | 100762620 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Medium | Tier 2
Distribution T200 Audit | 118603430 | 101033912 | Supervisor Work Verification was not completed correctly (Example: Used wrong form. Specify in comments) | Record | Low | Tier 2
Distribution T200 Audit | 118591756 | 103132459 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 2
Distribution T200 Audit | 118591756 | 103132459 | EC/ER Notification is missing required information or completed incorrectly. (Specify in comments) | Record | Low | Tier 2
Distribution T200 Audit | 118409190 | 100219134 | CCSC is missing from job package in SAP. All completed CCSC forms shall remain on file with the completed job. | Record | Low | Tier 2
Distribution T200 Audit | 116734616 | 100216310 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 2
Distribution T200 Audit | 118600932 | 100475538 | EC/ER Notification is missing required information or completed incorrectly. (Specify in notes) | Record | Low | Tier 2
Distribution T200 Audit | 118600932 | 100475538 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 2
Distribution T200 Audit | 117001069 | 101953624 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 2
Distribution T200 Audit | 117032781 | 101988249 | EC/ER Notification is missing required information or completed incorrectly. (Specify in comments) | Record | Low | Tier 2
Distribution T200 Audit | 117032781 | 101988249 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 2
Distribution T200 Audit | 116871967 | 101894452 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 2
Distribution T200 Audit | 110142456 | 101923683 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 2
Distribution T200 Audit | 116870657 | 101894482 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 2
Distribution T200 Audit | 117234815 | 101910042 | CCSC is missing from job package in SAP. All completed CCSC forms shall remain on file with the completed job. | Record | Medium | Tier 2
Distribution T200 Audit | 117116158 | 103455052 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Medium | Tier 2
Distribution T200 Audit | 118562240 | 102035474 | EC/ER Notification is missing required information or completed incorrectly. (Specify in comments) | Record | Low | Tier 2
Distribution T200 Audit | 118562240 | 102035474 | CCSC is missing from job package in SAP. All completed CCSC forms shall remain on file with the completed job. | Record | Low | Tier 2
Distribution T200 Audit | 118774961 | 101957850 | Equipment Serial #, manufacturer, and/or date manufactured missing. | Record | Low | Tier 2
Distribution T200 Audit | 118774961 | 101957850 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 2
Distribution T200 Audit | 118527806 | 100296330 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Medium | Tier 2
Distribution T200 Audit | 116731139 | 100620508 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Medium | Tier 2
Distribution T200 Audit | 110873801 | 101982641 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 2
Distribution T200 Audit | 110873801 | 101982641 | EC/ER Notification is missing required information or completed incorrectly. (Specify in comments) | Record | Low | Tier 2
Distribution T200 Audit | 117185991 | 102210389 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 2
Distribution T200 Audit | 118710214 | 102032624 | Job not redlined properly. (Provide details as to what job called for vs. what was done in field) | Record | Low | Tier 2
Distribution T200 Audit | 118710214 | 102032624 | Form 48 missing from job package when new pole/anchor was installed. | Record | Low | Tier 2
Distribution T200 Audit | 116707396 | 101879834 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 2
Distribution T200 Audit | 117016283 | 101894204 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Medium | Tier 2
Distribution T200 Audit | 117159411 | 101891953 | CCSC is missing from job package in SAP. All completed CCSC forms shall remain on file with the completed job. | Record | Low | Tier 2
Distribution T200 Audit | 118795232 | 101659726 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 2
Distribution T200 Audit | 116686972 | 101000714 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 2
Distribution T200 Audit | 116691457 | 101000970 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 2
Distribution T200 Audit | 118797380 | 41733276 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 2
Distribution T200 Audit | 116709728 | 102344957 | EC/ER Notification is missing required information or completed incorrectly. (Specify in comments) | Record | Low | Tier 2
Distribution T200 Audit | 116709728 | 102344957 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 2
Distribution T200 Audit | 118526127 | 102259128 | Job not redlined properly. (Provide details as to what job called for vs. what was done in field) | Record | Medium | Tier 2
Distribution T200 Audit | 118526127 | 102259128 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 2
Distribution T200 Audit | 118913052 | 100905934 | Job not redlined properly. (Provide details as to what job called for vs. what was done in field) | Record | Low | Tier 2
Distribution T200 Audit | 118553923 | 107262739 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 2
Distribution T200 Audit | 117074442 | 101770541 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 2
Distribution T200 Audit | 118939668 | 101770541 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 2
Distribution T200 Audit | 116692310 | 101777862 | EC/ER Notification is missing required information or completed incorrectly. (Specify in comments) | Record | Low | Tier 2
Distribution T200 Audit | 117159698 | 102229497 | EC/ER Notification is missing required information or completed incorrectly. (Specify in comments) | Record | Low | Tier 2
Distribution T200 Audit | 117159698 | 102229497 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 2
Distribution T200 Audit | 118685770 | 102262134 | CCSC is missing from job package in SAP. All completed CCSC forms shall remain on file with the completed job. | Record | Medium | Tier 2
Distribution T200 Audit | 117044328 | 102219450 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 2
Distribution T200 Audit | 118548313 | 101342091 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 2
Distribution T200 Audit | 118146823 | 102029286 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 2
Distribution T200 Audit | 118146823 | 102029286 | EC/ER Notification is missing required information or completed incorrectly. (Specify in comments) | Record | Low | Tier 2
Distribution T200 Audit | 117212115 | 101508672 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 2
Distribution T200 Audit | 117241589 | 101513117 | The guy marker is incorrectly installed or not securely attached to the guy wire/cable and/or anchor rod. | Field | Low | Tier 2
Distribution T200 Audit | 117241589 | 101513117 | The anchor rod/anchor head/guy preform is buried. Top of anchor head must be above ground with the preform grip exposed at attachment. | Field | Low | Tier 2
Distribution T200 Audit | 117190032 | 101517982 | Broken or slack guy wire. | Field | Low | Tier 2
Distribution T200 Audit | 118782726 | 100394976 | Tap Clamps have not been installed as required. | Field | Low | Tier 2
Distribution T200 Audit | 118782726 | 100394976 | Construction material, scraps, and/or debris left at job site. | Field | Low | Tier 2
Distribution T200 Audit | 116987369 | 100371779 | The guy marker is incorrectly installed or not securely attached to the guy wire/cable and/or anchor rod. | Field | Low | Tier 2
Distribution T200 Audit | 114131338 | 101067581 | Broken or slack guy wire. | Field | Medium | Tier 2
Distribution T200 Audit | 114131338 | 101067581 | The "High Voltage" sign(s) is damaged, illegible, or obstructed from view. | Field | Medium | Tier 2
Distribution T200 Audit | 116961307 | 101287761 | Conductors improperly installed with copper pressed above aluminum. | Field | Low | Tier 2
Distribution T200 Audit | 118141852 | 101649732 | The pole is set deeper than normal and preservative wrap is not installed. | Field | Low | Tier 2
Distribution T200 Audit | 118778045 | 101491643 | Tap Clamps have not been installed as required. | Field | Low | Tier 2
Distribution T200 Audit | 116985405 | 100652608 | The required press/dies and/or number of crimps for compression connectors not used. (Specify in comments) | Field | Low | Tier 2
Distribution T200 Audit | 116985405 | 100652608 | The "High Voltage" sign(s) is damaged, illegible, or obstructed from view. | Field | Medium | Tier 2
Distribution T200 Audit | 117375545 | 101061938 | The anchor rod/anchor head/guy preform is buried. Top of anchor head must be above ground with the preform grip exposed at attachment. | Field | Low | Tier 2
Distribution T200 Audit | 118937136 | 101039079 | U-shaped PVC molding is fastened at intervals greater than 18" below the 10ft. level (Construction call) | Field | Low | Tier 2
Distribution T200 Audit | 118937136 | 101039079 | Construction material, scraps, and/or debris left at job site. | Field | Low | Tier 2
Distribution T200 Audit | 117151648 | 103909873 | Plastic tape is used instead of the required plastic cable tie to secure the conductors of a triplex service drop at the point of attachment. (Note: Moisture entrapment). | Field | Low | Tier 2
Distribution T200 Audit | 117039088 | 103830484 | Basketing or bird-caging of conductor at compression splice of #4 & #2 ACSR conductor. | Field | Zero Tolerance | Tier 2
Distribution T200 Audit | 118591579 | 100525524 | The down guy/span guy/tree guy has a strain on the guy caused by vegetation. Note: The attachment of any distribution equipment to trees is not allowed. This includes wires, cables, transformers or other types of facilities. (See bulletin: TD-2999B-004) | Field | Medium | Tier 2
Distribution T200 Audit | 118591579 | 100525524 | Poor workmanship. Describe specific concerns. | Field | Medium | Tier 2
Distribution T200 Audit | 118938223 | 101401677 | The bushing mounted transformer cutouts are incorrectly installed during construction. Bushing mounted cutouts are no longer approved for new or rebuilt construction. | Field | Medium | Tier 2
Distribution T200 Audit | 117086258 | 100681612 | The "High Voltage" sign(s) is damaged, illegible, or obstructed from view. | Field | Medium | Tier 2
Distribution T200 Audit | 117490976 | 103972488 | The required press/dies and/or number of crimps for compression connectors not used. (Specify in comments) | Field | Low | Tier 2
Distribution T200 Audit | 117490976 | 103972488 | The bonding is not installed on the primary crossarm and/or brackets as required. (As Noted) | Field | Low | Tier 2
Distribution T200 Audit | 118603430 | 101033912 | The pole is set deeper than normal and preservative wrap is not installed. | Field | Low | Tier 2
Distribution T200 Audit | 118603430 | 101033912 | The service drop has less than the minimum radial clearance of 2 feet from the Telephone Company drop at a location greater than 15 feet from the point of attachment. | Field | Medium | Tier 2
Distribution T200 Audit | 117496181 | Missing in SAP | The vertical clearance between the grounded or ungrounded control cabinet and the communication level above is less than the required 48 inches. | Field | Medium | Tier 2
Distribution T200 Audit | 117496181 | Missing in SAP | The pole is set deeper than normal and preservative wrap is not installed. | Field | Low | Tier 2
Distribution T200 Audit | 118591756 | 103132459 | Proper connectors have not been installed on the primary or secondary as noted. | Field | Low | Tier 2
Distribution T200 Audit | 118409190 | 100219134 | The required cover-ups/perch deterrents are not installed/not properly installed for Raptor Protection | Field | Medium | Tier 2
Distribution T200 Audit | 118409190 | 100219134 | The "High Voltage" sign(s) are not installed on the pole as required. | Field | Medium | Tier 2
Distribution T200 Audit | 116734616 | 100216310 | Composite crossarm dead-ended and not pulling into the pole | Field | Low | Tier 2
Distribution T200 Audit | 116734616 | 100216310 | Missing or incorrect hardware (As Noted). Examples: round washer, Teco plate, 4" x 4" washer…. | Field | Low | Tier 2
Distribution T200 Audit | 118600932 | 100475538 | The pole is not set to the required depth. (Pole should be submitted to the estimating group to determine if it meets the pole calc. specifications at its current depth) | Field | Low | Tier 2
Distribution T200 Audit | 118600932 | 100475538 | Tie pad with preform tie is not installed as required. | Field | Low | Tier 2
Distribution T200 Audit | 118600932 | 100475538 | Missing or incorrect hardware (As Noted). Examples: round washer, Teco plate, 4" x 4" washer…. | Field | Low | Tier 2
Distribution T200 Audit | 118600932 | 100475538 | A guy/anchor is missing/not installed where it is needed (as noted). | Field | Medium | Tier 2
Distribution T200 Audit | 118600932 | 100475538 | The required press/dies and/or number of crimps for compression connectors not used. (Specify in comments) | Field | Low | Tier 2
Distribution T200 Audit | 118600932 | 100475538 | The service hot leg connections to underarm bus wire are not taped/sealed | Field | Medium | Tier 2
Distribution T200 Audit | 118600932 | 100475538 | The anchor guy attachment is not as close as practical to the strain. | Field | Low | Tier 2
Distribution T200 Audit | 118600932 | 100475538 | Composite crossarm dead-ended and not pulling into the pole | Field | Low | Tier 2
Distribution T200 Audit | 118721438 | 100469536 | Missing or incorrect hardware (As Noted). Examples: round washer, Teco plate, 4" x 4" washer…. | Field | Low | Tier 2
Distribution T200 Audit | 118721438 | 100469536 | Armor rod is not installed on the Al/ACSR primary conductors that have tie wires or clamps supporting them on post/pin insulators. (Note: Armor rod is not required with the use of formed ties only). | Field | Low | Tier 2
Distribution T200 Audit | 118721438 | 100469536 | The pole is not set to the required depth. (Pole should be submitted to the estimating group to determine if it meets the pole calc. specifications at its current depth) | Field | Low | Tier 2
Distribution T200 Audit | 117032781 | 101988249 | The "High Voltage" sign(s) are not installed on the pole as required. | Field | Medium | Tier 2
Distribution T200 Audit | 116870657 | 101894482 | The anchor rod/anchor head/guy preform is buried. Top of anchor head must be above ground with the preform grip exposed at attachment. | Field | Low | Tier 2
Distribution T200 Audit | 116870657 | 101894482 | The "High Voltage" sign(s) is damaged, illegible, or obstructed from view. | Field | Medium | Tier 2
Distribution T200 Audit | 117116158 | 103455052 | The "High Voltage" sign(s) is damaged, illegible, or obstructed from view. | Field | Medium | Tier 2
Distribution T200 Audit | 114950500 | NA | The pole is set deeper than normal and preservative wrap is not installed. | Field | Low | Tier 2
Distribution T200 Audit | 118562240 | 102035474 | Broken or slack guy wire. | Field | Low | Tier 2
Distribution T200 Audit | 118774961 | 101957850 | A single pole step is missing or is incorrectly installed on an equipment pole for storing of fuse holders after cutouts are opened. | Field | Low | Tier 2
Distribution T200 Audit | 118527806 | 100296330 | Exposed ground from ground level up to 8 ft. | Field | Medium | Tier 2
Distribution T200 Audit | 118527806 | 100296330 | The end of the guy wire/cable strands extend out beyond the beginning of the bight of the preform grip. | Field | Low | Tier 2
Distribution T200 Audit | 118527806 | 100296330 | A guy marker is missing on an anchor guy. | Field | Medium | Tier 2
Distribution T200 Audit | 118527806 | 100296330 | Unapproved material/hardware/equipment used and/or left in service at the work location. (Specify in comments and add reference(s). I.e. re-used steel crossarms, 9" steel brackets, etc. Hardware obtained from The Home Depot or Lowe's is not approved) | Field | Medium | Tier 2
Distribution T200 Audit | 118781056 | 100317515 | The pole is leaning into the strain >10% of height above ground. | Field | High | Tier 2
Distribution T200 Audit | 118781056 | 100317515 | Broken or slack guy wire. | Field | High | Tier 2
Distribution T200 Audit | 118710214 | 102032624 | A guy/anchor is missing/not installed where it is needed (as noted). | Field | Medium | Tier 2
Distribution T200 Audit | 118710214 | 102032624 | A guy hook fixture is installed to attach an anchor guy with more than 7,500 lbs. of strain. A guy pole plate and thimble assembly is required. (2-bolt fixture) (Wrong Guy Hardware Used) | Field | Low | Tier 2
Distribution T200 Audit | 118235886 | 101689864 | Angle washers are not installed on steel pins on a wood crossarm supporting conductors in angle construction. Angle washers not installed top and bottom of ALL insulator pins of the composite arm. | Field | Low | Tier 2
Distribution T200 Audit | 117113380 | 101702608 | The required press/dies and/or number of crimps for compression connectors not used. (Specify in comments) | Field | Medium | Tier 2
Distribution T200 Audit | 118283932 | 101936553 | 60 inches of air separation between phases for Raptor protection not met by either crossarm framing or coverups | Field | Medium | Tier 2
Distribution T200 Audit | 118283932 | 101936553 | Tie pad with preform tie is not installed as required. | Field | Medium | Tier 2
Distribution T200 Audit | 118283932 | 101936553 | The bonding is not installed on the primary crossarm and/or brackets as required. (As Noted) | Field | Low | Tier 2
Distribution T200 Audit | 118283932 | 101936553 | Angle washers are not installed on steel pins on a wood crossarm supporting conductors in angle construction. Angle washers not installed top and bottom of ALL insulator pins of the composite arm. | Field | Low | Tier 2
Distribution T200 Audit | 116818542 | 101933648 | The "High Voltage" sign(s) are not installed on the pole as required. | Field | Medium | Tier 2
Distribution T200 Audit | 116818542 | 101933648 | Non-ceramic insulator not used with insulated jumper and tie. | Field | Low | Tier 2
Distribution T200 Audit | 117016283 | 101894204 | The service drop has a vertical clearance less than the required 16 feet over commercial property accessible to vehicles. | Field | Medium | Tier 2
Distribution T200 Audit | 117016283 | 101894204 | Service wire conductors are broken or damaged. | Field | Low | Tier 2
Distribution T200 Audit | 117016283 | 101894204 | The anchor rod/anchor head/guy preform is buried. Top of anchor head must be above ground with the preform grip exposed at attachment. | Field | Low | Tier 2
Distribution T200 Audit | 117016283 | 101894204 | The "High Voltage" sign(s) are not installed on the pole as required. | Field | Medium | Tier 2
Distribution T200 Audit | 117159411 | 101891953 | Broken or slack guy wire. | Field | Low | Tier 2
Distribution T200 Audit | 117159411 | 101891953 | Non-ceramic insulator not used with insulated jumper and tie. | Field | Low | Tier 2
Distribution T200 Audit | 118797380 | 41733276 | The service drop has a vertical clearance less than 18 feet over the center portion of the street. (Note: The center portion of street is measured from a point 12 feet or more from the curb line or outermost traveled portion of the road). | Field | Low | Tier 2
Distribution T200 Audit | 116709728 | 102344957 | The "High Voltage" sign(s) are not installed on the on both sides of the primary crossarm. (Note: crossarm construction requires two "High Voltage" signs). | Field | Low | Tier 2
Distribution T200 Audit | 116709728 | 102344957 | The first pole step is less than 8' 6" above the ground or any other accessible structure. (Specify in comments) | Field | Low | Tier 2
Distribution T200 Audit | 118526127 | 102259128 | The pole is not set to the required depth. (Pole should be submitted to the estimating group to determine if it meets the pole calc. specifications at its current depth) | Field | Medium | Tier 2
Distribution T200 Audit | 118526127 | 102259128 | Broken or slack guy wire. | Field | Medium | Tier 2
Distribution T200 Audit | 118553923 | 107262739 | No operating number is installed on the underground equipment - Potential operating delay or error. (Specify in comments) | Field | Low | Tier 2
Distribution T200 Audit | 117074442 | 101770541 | The "High Voltage" sign(s) are not installed on the on both sides of the primary crossarm. (Note: crossarm construction requires two "High Voltage" signs). | Field | Low | Tier 2
Distribution T200 Audit | 117074442 | 101770541 | Proper connectors have not been installed on the primary or secondary as noted. | Field | Medium | Tier 2
Distribution T200 Audit | 117074442 | 101770541 | The required insulated jumpers are not installed for Raptor protection | Field | Medium | Tier 2
Distribution T200 Audit | 118939668 | 101770541 | Animal guards/bushing covers not installed on transformer primary bushings. (Installed after June 2002) | Field | Medium | Tier 2
Distribution T200 Audit | 118939668 | 101770541 | Construction material, scraps, and/or debris left at job site. | Field | Low | Tier 2
Distribution T200 Audit | 118939668 | 101770541 | Poor workmanship. Describe specific concerns. | Field | Medium | Tier 2
Distribution T200 Audit | 118767425 | 101742061 | Wrong date nail installed on new pole. (Outdated Date Nail Installed) | Field | Low | Tier 2
Distribution T200 Audit | 118767425 | 101742061 | Construction material, scraps, and/or debris left at job site. | Field | Low | Tier 2
Distribution T200 Audit | 116692310 | 101777862 | The required cover-ups/perch deterrents are not installed/not properly installed for Raptor Protection | Field | Medium | Tier 2
Distribution T200 Audit | 117159698 | 102229497 | Connector/splice has not been installed per standard (Wire has not been prepared, placement, etc.) | Field | Low | Tier 2
Distribution T200 Audit | 117159698 | 102229497 | Vibration dampers were not installed where required. | Field | Medium | Tier 2
Distribution T200 Audit | 118685770 | 102262134 | The "High Voltage" sign(s) is damaged, illegible, or obstructed from view. | Field | Medium | Tier 2
Distribution T200 Audit | 118685770 | 102262134 | Visibility strips not installed or work was not completed to bring location up to current visibility strip standard. (all must be the same color - yellow) | Field | Low | Tier 2
Distribution T200 Audit | 118685770 | 102262134 | Connector/splice has not been installed per standard (Wire has not been prepared, placement, etc.) | Field | Low | Tier 2
Distribution T200 Audit | 118685770 | 102262134 | Poor workmanship. Describe specific concerns. | Field | Low | Tier 2
Distribution T200 Audit | 117044328 | 102219450 | The end of the guy wire/cable strands extend out beyond the beginning of the bight of the preform grip. | Field | Low | Tier 2
Distribution T200 Audit | 118524057 | 101341920 | Missing or incorrect hardware (As Noted). Examples: round washer, Teco plate, 4" x 4" washer…. | Field | Low | Tier 2
Distribution T200 Audit | 118524057 | 101341920 | The underarm bus molding is not adequately attached to the bottom of the crossarm throughout its run. | Field | Low | Tier 2
Distribution T200 Audit | 118524057 | 101341920 | Poor workmanship. Describe specific concerns. | Field | Medium | Tier 2
Distribution T200 Audit | 118524057 | 101341920 | Proper connectors have not been installed on the primary or secondary as noted. | Field | High | Tier 2
Distribution T200 Audit | 118524057 | 101341920 | The streetlight vertical run conductors are exposed. | Field | Low | Tier 2
Distribution T200 Audit | 118548313 | 101342091 | Exposed ground above 8 ft. but below communication. | Field | Medium | Tier 2
Distribution T200 Audit | 118548313 | 101342091 | The anchor rod/anchor head/guy preform is buried. Top of anchor head must be above ground with the preform grip exposed at attachment. | Field | Low | Tier 2
Distribution T200 Audit | 118548313 | 101342091 | The first pole step is less than 8' 6" above the ground or any other accessible structure. (Specify in comments) | Field | Medium | Tier 2
Distribution T200 Audit | 118146823 | 102029286 | Proper connectors have not been installed on the primary or secondary as noted. | Field | Low | Tier 2
Distribution T200 Audit | 118146823 | 102029286 | The pole is set deeper than normal and preservative wrap is not installed. | Field | Low | Tier 2
Distribution T200 Audit | 118146823 | 102029286 | Poor workmanship. Describe specific concerns. | Field | Low | Tier 2
Distribution T200 Audit | 117212115 | 101508672 | Not built to OH construction standards and not covered by an existing call. (Note specific reference drawing and details.) | Field | High | Tier 2
Distribution T200 Audit | 118929021 | 101270036 | CCSC is missing from job package in SAP. All completed CCSC forms shall remain on file with the completed job. | Record | Low | Tier 3
Distribution T200 Audit | 117290399 | 101417673 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 3
Distribution T200 Audit | 117293950 | 101391839 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 3
Distribution T200 Audit | 117293698 | 101391721 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 3
Distribution T200 Audit | 118539668 | 101023008 | EC/ER Notification is missing required information or completed incorrectly. (Specify in notes) | Record | Low | Tier 3
Distribution T200 Audit | 117320011 | 101410991 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 3
Distribution T200 Audit | 116825414 | 101049436 | EC/ER Notification is missing required information or completed incorrectly. (Specify in notes) | Record | Low | Tier 3
Distribution T200 Audit | 118457548 | 107709438 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 3
Distribution T200 Audit | 118457548 | 107709438 | EC/ER Notification is missing required information or completed incorrectly. (Specify in comments) | Record | Low | Tier 3
Distribution T200 Audit | 118483969 | 107903173 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 3
Distribution T200 Audit | 118483969 | 107903173 | EC/ER Notification is missing required information or completed incorrectly. (Specify in comments) | Record | Low | Tier 3
Distribution T200 Audit | 116744254 | 100080714 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 3
Distribution T200 Audit | 117060526 | 100518167 | CCSC is missing from job package in SAP. All completed CCSC forms shall remain on file with the completed job. | Record | Medium | Tier 3
Distribution T200 Audit | 118536406 | 100098908 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 3
Distribution T200 Audit | 118777634 | 101676525 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 3
Distribution T200 Audit | 118650713 | 103497294 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Medium | Tier 3
Distribution T200 Audit | 118914553 | 101688039 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 3
Distribution T200 Audit | 118709308 | 103831873 | Required job documentation has not been uploaded to SAP. | Record | Low | Tier 3
Distribution T200 Audit | 118709308 | 103831873 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 3
Distribution T200 Audit | 118754428 | 102253792 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 3
Distribution T200 Audit | 117138051 | 102260032 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 3
Distribution T200 Audit | 118605808 | 42458537 | Document has an item scratched out and not initialed and/or dated. | Record | Low | Tier 3
Distribution T200 Audit | 118605808 | 42458537 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 3
Distribution T200 Audit | 117247506 | 102242409 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Medium | Tier 3
Distribution T200 Audit | 118946081 | 101683136 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 3
Distribution T200 Audit | 117376311 | 101796616 | CCSC is missing from job package in SAP. All completed CCSC forms shall remain on file with the completed job. | Record | Medium | Tier 3
Distribution T200 Audit | 118719932 | 102256882 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Medium | Tier 3
Distribution T200 Audit | 117096368 | 102229892 | As-Built not red lined correctly and/or partially completed work in field not identified on As-Built. | Record | Medium | Tier 3
Distribution T200 Audit | 117096368 | 102229892 | EC/ER Notification is missing required information or completed incorrectly. (Specify in comments) | Record | Low | Tier 3
Distribution T200 Audit | 117096368 | 102229892 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 3
Distribution T200 Audit | 117069349 | 102230071 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 3
Distribution T200 Audit | 117099314 | 102229877 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 3
Distribution T200 Audit | 110678401 | 102263362 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 3
Distribution T200 Audit | 109252430 | 102260920 | EC/ER Notification is missing required information or completed incorrectly. (Specify in comments) | Record | Low | Tier 3
Distribution T200 Audit | 109252430 | 102260920 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 3
Distribution T200 Audit | 117239817 | 102252368 | CCSC is missing from job package in SAP. All completed CCSC forms shall remain on file with the completed job. | Record | Low | Tier 3
Distribution T200 Audit | 110283014 | 102263835 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Medium | Tier 3
Distribution T200 Audit | 118585430 | 101362287 | Required job documentation has not been uploaded to SAP. | Record | Low | Tier 3
Distribution T200 Audit | 118585430 | 101362287 | CCSC form is incorrectly filled out. (Missing header info, shaded sections incorrect, not signed off, etc.) | Record | Low | Tier 3
Distribution T200 Audit | 118929021 | 101270036 | Seperation/distance from cutout(s) to another object less than minimum required. | Field | Medium | Tier 3
Distribution T200 Audit | 118929021 | 101270036 | The bonding is not installed on the primary crossarm and/or brackets as required. (As Noted) | Field | Medium | Tier 3
Distribution T200 Audit | 118929021 | 101270036 | Non-exempt equipment installed in the High Fire Threat District (HFTD). Specify in comments | Field | High | Tier 3
Distribution T200 Audit | 117290399 | 101417673 | The required press/dies and/or number of crimps for compression connectors not used. (Specify in comments) | Field | Low | Tier 3
Distribution T200 Audit | 116822038 | 101260929 | The bonding is not installed on the primary crossarm and/or brackets as required. (As Noted) | Field | Medium | Tier 3
Distribution T200 Audit | 116825414 | 101049436 | The bonding is not installed on the primary crossarm and/or brackets as required. (As Noted) | Field | Medium | Tier 3
Distribution T200 Audit | 116883058 | 100608839 | The guy wire/cable is grounded above the guy strain insulator/bob by vegetation. | Field | Medium | Tier 3
Distribution T200 Audit | 117751840 | 103973525 | The bonding is not installed on the primary crossarm and/or brackets as required. (As Noted) | Field | Medium | Tier 3
Distribution T200 Audit | 117751840 | 103973525 | The pole is set deeper than normal and preservative wrap is not installed. | Field | Low | Tier 3
Distribution T200 Audit | 117751840 | 103973525 | Angle washers are not installed on steel pins on a wood crossarm supporting conductors in angle construction. Angle washers not installed top and bottom of ALL insulator pins of the composite arm. | Field | Low | Tier 3
Distribution T200 Audit | 117189723 | 101688250 | Missing or incorrect hardware (As Noted). Examples: round washer, Teco plate, 4" x 4" washer…. | Field | Low | Tier 3
Distribution T200 Audit | 118780727 | 101934141 | The "High Voltage" sign(s) is damaged, illegible, or obstructed from view. | Field | Medium | Tier 3
Distribution T200 Audit | 118681659 | 100311530 | The primary/secondary conductors are slack and not properly sagged. | Field | Medium | Tier 3
Distribution T200 Audit | 118650713 | 103497294 | Three yellow visibility strips are not installed on the pole exposed to vehicular traffic without a curb. | Field | Low | Tier 3
Distribution T200 Audit | 118650713 | 103497294 | Construction material, scraps, and/or debris left at job site. | Field | Low | Tier 3
Distribution T200 Audit | 118650713 | 103497294 | A pole ground has been installed without a Ground Pole Tag or an ER notification identifying the location as not having been verified below grade. | Field | Medium | Tier 3
Distribution T200 Audit | 118650713 | 103497294 | Proof Positive Copper Protected Ground Wire (PPC-PGW) was not installed properly. (Specify in comments; Galvanized Staple with Drive Stop Protective Pad, spacing: just above finished grade to at least 8' max 18", above 8' max. 30"; Strap and self-tapping screw underside of the arm 18” intervals; etc.) | Field | Medium | Tier 3
Distribution T200 Audit | 118709308 | 103831873 | A pole ground has been installed without a Ground Pole Tag or an ER notification identifying the location as not having been verified below grade. | Field | Low | Tier 3
Distribution T200 Audit | 118709308 | 103831873 | Line splices are installed less than 2 ft. (10' for Transmission) from conductor support on maintenance or reconstruction work. (Note: Potential cause of conductor failure). | Field | Low | Tier 3
Distribution T200 Audit | 118709308 | 103831873 | Composite crossarm not installed per standard (dead-ended and not pulling into the pole, guy fixture not utilized, wrong type of arm used, etc.) | Field | Low | Tier 3
Distribution T200 Audit | 118709308 | 103831873 | A cable protector is not installed on the primary/secondary riser. (Note: Potential cause of cable failure). | Field | Low | Tier 3
Distribution T200 Audit | 118709308 | 103831873 | The guy marker is incorrectly installed or not securely attached to the guy wire/cable and/or anchor rod. | Field | Low | Tier 3
Distribution T200 Audit | 118709308 | 103831873 | The AWAC is not adequately guyed. | Field | Low | Tier 3
Distribution T200 Audit | 118709308 | 103831873 | A 1/2" lag bolt is not installed to support the 0-750 volt riser cables in the cable grips. This is an OH call. | Field | Low | Tier 3
Distribution T200 Audit | 118709308 | 103831873 | The AWAC has been dead-ended with improper dead-end attachments, as noted. | Field | Low | Tier 3
Distribution T200 Audit | 118709308 | 103831873 | The required press/dies and/or number of crimps for compression connectors not used. (Specify in comments) | Field | Medium | Tier 3
Distribution T200 Audit | 118709308 | 103831873 | The pole is not set to the required depth. (Pole should be submitted to the estimating group to determine if it meets the pole calc. specifications at its current depth) | Field | Low | Tier 3
Distribution T200 Audit | 118709308 | 103831873 | Pole steps are not installed per standards. (Specify in comments) | Field | Low | Tier 3
Distribution T200 Audit | 118709308 | 103831873 | Missing or incorrect hardware (As Noted). Examples: round washer, Teco plate, 4" x 4" washer…. | Field | Low | Tier 3
Distribution T200 Audit | 118709308 | 103831873 | Broken or slack guy wire. | Field | Low | Tier 3
Distribution T200 Audit | 118754428 | 102253792 | The bonding is not installed on the primary crossarm and/or brackets as required. (As Noted) | Field | Low | Tier 3
Distribution T200 Audit | 117138051 | 102260032 | Broken or slack guy wire. | Field | Low | Tier 3
Distribution T200 Audit | 118605808 | 42458537 | The anchor rod/anchor head/guy preform is buried. Top of anchor head must be above ground with the preform grip exposed at attachment. | Field | Low | Tier 3
Distribution T200 Audit | 118605808 | 42458537 | The radial clearance between the guy wire and the supply conductor or communications cable is less than required. Communications........3” 0-750V......................3” 751-7,500V............6” 7,501-20,000V.........9” 20,001-35,000V........12” 35,000-75,000V........18" 75,000-150,000V.......27" | Field | Medium | Tier 3
Distribution T200 Audit | 118605808 | 42458537 | Connector/splice has not been installed per standard (Wire has not been prepared, placement, etc.) | Field | Low | Tier 3
Distribution T200 Audit | 117247506 | 102242409 | Broken or slack guy wire. | Field | Low | Tier 3
Distribution T200 Audit | 117247506 | 102242409 | Connector/splice has not been installed per standard (Wire has not been prepared, placement, etc.) | Field | Low | Tier 3
Distribution T200 Audit | 118946081 | 101683136 | Construction material, scraps, and/or debris left at job site. | Field | Low | Tier 3
Distribution T200 Audit | 117376311 | 101796616 | The down guy/span guy/tree guy has a strain on the guy caused by vegetation. Note: The attachment of any distribution equipment to trees is not allowed. This includes wires, cables, transformers or other types of facilities. (See bulletin: TD-2999B-004) | Field | Medium | Tier 3
Distribution T200 Audit | 118719932 | 102256882 | The required cover-ups/perch deterrents are not installed/not properly installed for Raptor Protection | Field | Medium | Tier 3
Distribution T200 Audit | 117096368 | 102229892 | The "High Voltage" sign(s) are not installed on the on both sides of the primary crossarm. (Note: crossarm construction requires two "High Voltage" signs). | Field | Low | Tier 3
Distribution T200 Audit | 117069349 | 102230071 | 60 inches of air separation between phases for Raptor protection not met by either crossarm framing or coverups | Field | Medium | Tier 3
Distribution T200 Audit | 117069349 | 102230071 | Missing or incorrect hardware (As Noted). Examples: round washer, Teco plate, 4" x 4" washer…. | Field | Low | Tier 3
Distribution T200 Audit | 117069349 | 102230071 | Tie pad with preform tie is not installed as required. | Field | Medium | Tier 3
Distribution T200 Audit | 117099314 | 102229877 | 60 inches of air separation between phases for Raptor protection not met by either crossarm framing or coverups | Field | Medium | Tier 3
Distribution T200 Audit | 117099314 | 102229877 | The guy marker has been damaged and should be replaced. | Field | Low | Tier 3
Distribution T200 Audit | 117099314 | 102229877 | Visibility strips not installed or work was not completed to bring location up to current visibility strip standard. (all must be the same color - yellow) | Field | Low | Tier 3
Distribution T200 Audit | 117099314 | 102229877 | Missing or incorrect hardware (As Noted). Examples: round washer, Teco plate, 4" x 4" washer…. | Field | Low | Tier 3
Distribution T200 Audit | 117239817 | 102252368 | The required press/dies and/or number of crimps for compression connectors not used. (Specify in comments) | Field | Medium | Tier 3
Distribution T200 Audit | 117239817 | 102252368 | Connector/splice has not been installed per standard (Wire has not been prepared, placement, etc.) | Field | High | Tier 3
Distribution T200 Audit | 117239817 | 102252368 | Poor workmanship. Describe specific concerns. | Field | Low | Tier 3
Distribution T200 Audit | 110283014 | 102263835 | Poor workmanship. Describe specific concerns. | Field | Low | Tier 3
Distribution T200 Audit | 118585430 | 101362287 | Line splices are installed less than 2 ft. (10' for Transmission) from conductor support on maintenance or reconstruction work. (Note: Potential cause of conductor failure). | Field | Low | Tier 3
Distribution T200 Audit | 118585430 | 101362287 | The underarm bus molding is not adequately attached to the bottom of the crossarm throughout its run. | Field | Low | Tier 3