## Summary
2020 Contractor Inspection DISTRIBUTION Audit HFTD Non-Conformances
HFTD Non-Conformances by Tier
Tier | Non-Conformances
Tier 2 | 85
Tier 3 | 89
Audit | HFTD | Distribution Location | Non-Conformances
2020 Distribution Contractor Inspection
Tier 2
|  | 100444772 | 3
|  | 100444804 | 2
|  | 100445132 | 4
|  | 100458552 | 1
|  | 100458553 | 3
|  | 100483713 | 2
|  | 100489239 | 1
|  | 100489651 | 1
|  | 100651008 | 1
|  | 100651107 | 1
|  | 100651444 | 1
|  | 100651532 | 1
|  | 100651538 | 1
|  | 100651867 | 3
|  | 101033280 | 1
|  | 101033818 | 1
|  | 101041348 | 14
|  | 101409500 | 1
|  | 101416273 | 1
|  | 103136785 | 4
|  | 103136787 | 4
|  | 103136788 | 6
|  | 103136789 | 5
|  | 103136790 | 2
|  | 103136791 | 2
|  | 103136792 | 2
|  | 103347473 | 4
|  | 103371944 | 1
|  | 103400478 | 2
|  | 103663608 | 2
|  | 103805046 | 4
|  | 103950974 | 4
Tier 3
|  | 100483751 | 2
|  | 100483755 | 3
|  | 100483758 | 1
|  | 100483774 | 1
|  | 100487191 | 2
|  | 100487195 | 1
|  | 100488789 | 2
|  | 100488832 | 2
|  | 100488842 | 2
|  | 100488843 | 1
|  | 100488846 | 1
|  | 100492326 | 1
|  | 100497995 | 1
|  | 100497998 | 1
|  | 100498059 | 1
|  | 100500535 | 3
|  | 100500540 | 3
|  | 100505236 | 1
|  | 101013437 | 3
|  | 101016524 | 2
|  | 101037568 | 1
|  | 101038221 | 3
|  | 101039954 | 1
|  | 101052070 | 1
|  | 101058469 | 2
|  | 101064838 | 1
|  | 101066133 | 2
|  | 101372273 | 1
|  | 101372295 | 1
|  | 101389224 | 2
|  | 101401777 | 1
|  | 101403116 | 2
|  | 101412770 | 1
|  | 101422443 | 1
|  | 101673935 | 1
|  | 101676026 | 1
|  | 101676049 | 2
|  | 101801656 | 4
|  | 101802042 | 1
|  | 101802362 | 1
|  | 101803491 | 2
|  | 101900028 | 2
|  | 101900052 | 2
|  | 101900059 | 1
|  | 101919324 | 2
|  | 102318714 | 1
|  | 103118024 | 1
|  | 103160842 | 2
|  | 103344505 | 2
|  | 103636031 | 2
|  | 103752721 | 1
|  | 103774806 | 1
|  | 103778221 | 1
|  | 103855478 | 1
|  | 103857149 | 1
|  | 103892763 | 2
|  | 103944830 | 1

## HFTD Summary Detail
Summary Detail - HFTD Only
Audit | Distribution Location | Non-Conformance Description | N/C Type | Risk Rank | HFTD
2020 Distribution Contractor Inspection | 101058469 | 3 splices in one phase. One in the other . 4 total | Record | Low | Tier 3
2020 Distribution Contractor Inspection | 103805046 | 7 to the south 4 to the north (3 on one phase to the south) | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 103136785 | Actual GPS coordinates are: 37.83868 -121.725382 | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 100444772 | Anchor is buried | Field | Low | Tier 2
2020 Distribution Contractor Inspection | 100651532 | Both anchors are buried. | Field | Low | Tier 2
2020 Distribution Contractor Inspection | 103636031 | Buddy pole present. | Record | Low | Tier 3
2020 Distribution Contractor Inspection | 100488842 | Center phase not connected, idle for two spans to end of line | Field | Low | Tier 3
2020 Distribution Contractor Inspection | 100488832 | CI identified primary splices when there is no load side primary | Record | Low | Tier 3
2020 Distribution Contractor Inspection | 100489651 | Ci missed two splices | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 103136788 | CI reported guy present, down guy belongs to communications. | Field | Low | Tier 2
2020 Distribution Contractor Inspection | 100483751 | Communications company mounted in PG&E pole space | Record | Low | Tier 3
2020 Distribution Contractor Inspection | 101422443 | Contract Inspector did not record any splices; there is 1 automatic splice in the north-phase, approximately 130 feet to the west. | Record | Low | Tier 3
2020 Distribution Contractor Inspection | 101389224 | Contract Inspector did not record any splices; there is 1 automatic splice in the north-phase, approximately 15 feet to the East. | Record | Low | Tier 3
2020 Distribution Contractor Inspection | 101416273 | Contract Inspector did not record any splices; there is 1 automatic splice in the north-phase, approximately 65 feet to the west, & 1 automatic splice in the south-phase, approximately 75 feet to the west. | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 101412770 | Contract Inspector did not record any splices; there is 1 automatic splice in the north-phase, approximately 85 feet to the west. | Record | Low | Tier 3
2020 Distribution Contractor Inspection | 103663608 | Contract Inspector did not record any splices; there is 1 automatic splice in the south-phase, approximately 65 feet to the northwest, & 1 automatic splice in the north-phase, approximately 110 feet to the northwest. | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 101401777 | Contract Inspector did not record any splices; there is 1 compression splice in the center-phase, approximately 70 feet to the northwest | Record | Low | Tier 3
2020 Distribution Contractor Inspection | 101403116 | Contract Inspector did not record any splices; there is 1 compression splice in the east-phase, approximately 135 feet to the south. | Record | Low | Tier 3
2020 Distribution Contractor Inspection | 103400478 | Damaged high sign | Field | Low | Tier 2
2020 Distribution Contractor Inspection | 103136785 | Dampers present. | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 103136787 | Dampers present. | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 103136789 | Dampers present. | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 103136790 | Dampers present. | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 103136791 | Dampers present. | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 103136792 | Dampers present. | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 103347473 | Dampers present. | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 100651538 | Dead tree is laying on service mid span causing strain. | Field | Low | Tier 2
2020 Distribution Contractor Inspection | 103160842 | Did not capture splices. | Record | Low | Tier 3
2020 Distribution Contractor Inspection | 100488843 | Flying bells installed on the load side of pole and an automatic splice in load side span near next pole | Record | Low | Tier 3
2020 Distribution Contractor Inspection | 100500540 | Four splices on the load side of pole, two on each conductor | Record | Low | Tier 3
2020 Distribution Contractor Inspection | 100492326 | Guy is slack; vegetation still needs clearing; dig out anchor | Field | Low | Tier 3
2020 Distribution Contractor Inspection | 101919324 | Inspector did not identify 1 splice | Record | Low | Tier 3
2020 Distribution Contractor Inspection | 101900028 | Inspector did not identify vibration dampners | Record | Low | Tier 3
2020 Distribution Contractor Inspection | 100500535 | Inspector did not report three slices total; two splices on the road side (PN) and one splice on the field side | Record | Low | Tier 3
2020 Distribution Contractor Inspection | 103892763 | Missed spam guy supporting AWAC | Field | Low | Tier 3
2020 Distribution Contractor Inspection | 101372273 | Missing # of splices per conductor. | Record | Low | Tier 3
2020 Distribution Contractor Inspection | 100458553 | No PCB sticker on TX. | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 100487191 | One overview pic is of the wrong pole. | Record | Low | Tier 3
2020 Distribution Contractor Inspection | 100458553 | One splice in one string is present and not recorded. | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 100483713 | One splice on load side PN | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 103805046 | Pole is mapped as a four way pole when in the field it is actually a three way pole | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 103136788 | Pole mapped as solely owned, there is communications attached. | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 103347473 | Pole mapped in the middle of the dam, Actual GPS coordinates are 37.836412 -121.72601 | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 103805046 | Secondary guy grounded above insulator | Field | Low | Tier 2
2020 Distribution Contractor Inspection | 100488832 | Service connections exposed at the pole | Field | Medium | Tier 3
2020 Distribution Contractor Inspection | 101052070 | Service has insufficient clearance over metal roof on which man can walk. | Field | Low | Tier 3
2020 Distribution Contractor Inspection | 100651867 | Splice in primary. | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 103774806 | Splices were not captured. | Record | Low | Tier 3
2020 Distribution Contractor Inspection | 103160842 | Stub pole present supporting primary span guy and communications. | Record | Low | Tier 3
2020 Distribution Contractor Inspection | 101013437 | Stub present | Record | Low | Tier 3
2020 Distribution Contractor Inspection | 100445132 | The CI noted 6 total 2 in one span; There are 10 splices in the load span with 4 automatic splices in the center. | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 103855478 | The pole is a guy pole. | Record | Low | Tier 3
2020 Distribution Contractor Inspection | 103136789 | The pole is mapped as solely owned, there is communications attached. | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 103136790 | The pole is mapped as solely owned, there is communications attached. | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 103136791 | The pole is mapped as solely owned, there is communications attached. | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 103136792 | The pole is mapped as solely owned, there is communications attached. Pole is located on opposite side of the road. Actual GPS is: 37.844946 -121.720927 | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 103857149 | There are 3 splices and 1 on each string. | Record | Low | Tier 3
2020 Distribution Contractor Inspection | 101016524 | There are two splices present and not recorded. | Record | Low | Tier 3
2020 Distribution Contractor Inspection | 100651444 | This location has three splices in the primary. CI said no splices present. | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 100651107 | TX is a 10 KVA installed in 1983. | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 100445132 | Broken strand on center phase | Field | Medium | Tier 2
2020 Distribution Contractor Inspection | 100458552 | Inspector chose "no vegetation" and there is vegetation present | Field | Low | Tier 2
2020 Distribution Contractor Inspection | 100651008 | Anchor rod broken, damaged, corroded, covered by vegetation/overgrown, soil-eroded, graded, or buried | Field | Low | Tier 2
2020 Distribution Contractor Inspection | 101033280 | One cut out has either lost its oil or is no longer exempt and would now require pole clearing. Cutouts should be replaced. | Field | Low | Tier 2
2020 Distribution Contractor Inspection | 101409500 | Contract Inspector did not record the presence of vegetation in de-energized/idle span (with open flying-bells) to the west; the vegetation is growing through and above the de-energized/idle primary conductors in this de-energized/idle span. This de-energized/idle span has been identified per Idle-Facilities Notification # 119049018; this Idle-Facilities Notification has documented the current condition of the vegetation growing through the primary conductors in the same span as the flying bells with open jumpers in accordance with the Electric Distribution Preventive Maintenance Manual (EDPM) Overhead Inspection Job Aid TD-2305-M-JA02, Rev. 7., Pg. 48 of 113. *NOTE: I emailed Electric Engineering Estimator Sean Chiapas (sacm@pge.com) on 10/27/2020 at 12:51 pm to reiterate vegetation is in contact with de-energized primary conductor in HFTD Tier 2 and that the 1 set of flying-bells may not be adequate to ensure this span remains de-energized; if this 1 set of flying-bells leaks, then energized primary conduc | Field | Low | Tier 2
2020 Distribution Contractor Inspection | 103136785 | The three phase transformer located adjacent to reservoir spillway is idle. Meter has been removed. x | Field | Medium | Tier 2
2020 Distribution Contractor Inspection | 103136787 | Ground and ground rod are exposed at base of pole. Made safe by covering with rocks for temporary fix. | Field | Medium | Tier 2
2020 Distribution Contractor Inspection | 103136787 | Guy marker damaged/loose. High Voltage sign is damaged/loose. Vis strips lost reflective qualities and loose. | Field | Low | Tier 2
2020 Distribution Contractor Inspection | 103136788 | Ground wire exposed. Repaired by QVS. | Field | Low | Tier 2
2020 Distribution Contractor Inspection | 103136788 | Pole step at 8’3” removed by QVS. | Field | Low | Tier 2
2020 Distribution Contractor Inspection | 103136789 | The ground wire is exposed at the base of pole. | Field | Low | Tier 2
2020 Distribution Contractor Inspection | 103136789 | Inspector chose "yes vegetation" and there is no vegetation present | Field | Low | Tier 2
2020 Distribution Contractor Inspection | 103950974 | Transformer shows signs of leaking, seeping, or weeping oil | Field | Medium | Tier 2
2020 Distribution Contractor Inspection | 103950974 | Bird guard bushing cover not secure | Field | Low | Tier 2
2020 Distribution Contractor Inspection | 101676026 | Secondary conductors have strain caused by tree/vegetation | Field | Medium | Tier 3
2020 Distribution Contractor Inspection | 100483755 | Grounds exposed, broken, damaged, disconnected, unsecured, or missing | Field | Low | Tier 3
2020 Distribution Contractor Inspection | 100483774 | 12kV recorded in a 21kV system | Field | Low | Tier 3
2020 Distribution Contractor Inspection | 100488789 | Pole steps below 8.5’ | Field | Low | Tier 3
2020 Distribution Contractor Inspection | 100488846 | Pole steps below 8.5’ of accessible structure | Field | Low | Tier 3
2020 Distribution Contractor Inspection | 100497995 | Anchor covered by vegetation and buried. | Field | Low | Tier 3
2020 Distribution Contractor Inspection | 100497998 | Damaged visibility strips | Field | Low | Tier 3
2020 Distribution Contractor Inspection | 101013437 | Necessary guys missing or loose | Field | Low | Tier 3
2020 Distribution Contractor Inspection | 101013437 | Grounds exposed, broken, damaged, disconnected, unsecured, or missing | Field | Low | Tier 3
2020 Distribution Contractor Inspection | 101038221 | Guy wire broken, damaged, clearance issues, corroded, covered by vegetation, overgrown, strain or abrasion, Anchor rod broken, damaged, corroded, covered by vegetation/overgrown, soil-eroded, graded, or buried | Field | Low | Tier 3
2020 Distribution Contractor Inspection | 101038221 | Hand or preform tie wire broken, damaged, burnt, loose, showing signs of wearing, missing, or missing armor rod | Field | Low | Tier 3
2020 Distribution Contractor Inspection | 101038221 | Chance clamps installed on 2 ACSR with out tap guard on one serving more than two transformers. | Field | Low | Tier 3
2020 Distribution Contractor Inspection | 101039954 | Primary or secondary conductor has diminished clearance mid span or uneven conductor sag | Field | Low | Tier 3
2020 Distribution Contractor Inspection | 101066133 | Anchor rod broken, damaged, corroded, covered by vegetation/overgrown, soil-eroded, graded, or buried | Field | Low | Tier 3
2020 Distribution Contractor Inspection | 101403116 | Contract Inspector did not record buried anchor. However, Contract Inspector did update EC # 116864513 to replace this pole due to woodpecker damage, damaged crossarms, and damaged insulators. | Field | Low | Tier 3
2020 Distribution Contractor Inspection | 101673935 | Bushing insulator cover is missing on one phase and is damaged on the other phase. | Field | Medium | Tier 3
2020 Distribution Contractor Inspection | 101676049 | Visibility strips missing, broken, or no longer reflective, Pole steps incorrectly installed (below 8' 6") on the pole? | Field | Low | Tier 3
2020 Distribution Contractor Inspection | 101801656 | Hand or preform tie wire broken, damaged, burnt, loose, showing signs of wearing, missing, or missing armor rod | Field | Medium | Tier 3
2020 Distribution Contractor Inspection | 101801656 | Field non-conformance; hardware framing issue | Field | Low | Tier 3
2020 Distribution Contractor Inspection | 101802362 | High sign missing or broken | Field | Low | Tier 3
2020 Distribution Contractor Inspection | 101803491 | Pole steps incorrectly installed (below 8' 6") on the pole? | Field | Low | Tier 3
2020 Distribution Contractor Inspection | 101900052 | Guy is not permanently secured, cable tie | Field | Low | Tier 3
2020 Distribution Contractor Inspection | 101919324 | High sign missing or broken, Visibility strips missing, broken, or no longer reflective | Field | Low | Tier 3
2020 Distribution Contractor Inspection | 103778221 | There is a pole number on this pole, records say it is not there | Field | Low | Tier 3
2020 Distribution Contractor Inspection | 103944830 | Guy marker not secure | Field | Low | Tier 3
2020 Distribution Contractor Inspection | 100444772 | Asset Record non-conformance; transformer record incorrect | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 100444772 | 4kV recorded as 2Kv | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 100444804 |  | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 100444804 | 12kV recorded as 5kV | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 100445132 |  | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 100445132 | Voltage is listed as 5kV, line voltage is 12kV | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 100458553 | Transformer pole has cutout jumper connections. | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 100483713 | 21kV recorded as 12kV | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 100489239 | Pole bar code number does not match records | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 100651867 | Insul links installed in primary. | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 100651867 | Inspector pictures are of the wrong location 2 poles away. | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 101033818 | Connections are present but are not high risk. | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 100483751 | Asset Record non-conformance; primary connection record incorrect | Record | Low | Tier 3
2020 Distribution Contractor Inspection | 100483755 | Asset Record non-conformance; primary connection record incorrect | Record | Low | Tier 3
2020 Distribution Contractor Inspection | 100483755 | Line voltage marked 12kV instead of 21kV | Record | Low | Tier 3
2020 Distribution Contractor Inspection | 100483758 | 21kV recorded as 12kV | Record | Low | Tier 3
2020 Distribution Contractor Inspection | 100487191 | Asset Record non-conformance; primary connection record incorrect | Record | Low | Tier 3
2020 Distribution Contractor Inspection | 100487195 | Asset Record non-conformance; primary connection record incorrect | Record | Low | Tier 3
2020 Distribution Contractor Inspection | 100488789 | Asset Record non-conformance; primary connection record incorrect | Record | Low | Tier 3
2020 Distribution Contractor Inspection | 100488842 | Asset Record non-conformance; primary connection record incorrect | Record | Low | Tier 3
2020 Distribution Contractor Inspection | 100498059 | Asset Record non-conformance; primary connection record incorrect | Record | Low | Tier 3
2020 Distribution Contractor Inspection | 100500535 | Asset Record non-conformance; primary connection record incorrect | Record | Low | Tier 3
2020 Distribution Contractor Inspection | 100500535 | 21kV is recorded as 12kV | Record | Low | Tier 3
2020 Distribution Contractor Inspection | 100500540 | Asset Record non-conformance; primary connection record incorrect | Record | Low | Tier 3
2020 Distribution Contractor Inspection | 100500540 | 21kV reorder as 12kV | Record | Low | Tier 3
2020 Distribution Contractor Inspection | 100505236 | Asset Record non-conformance; primary connection record incorrect | Record | Low | Tier 3
2020 Distribution Contractor Inspection | 101037568 | Asset record non-conformance; support structure record incorrect | Record | Low | Tier 3
2020 Distribution Contractor Inspection | 101041348 | Asset record non-conformance; 3rd party non-utility infraction record incorrect | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 101041348 | Asset record non-conformance; 3rd party non-utility infraction record incorrect | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 101041348 | Asset record non-conformance; mapping record incorrect | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 101041348 | Asset record non-conformance; work performed record incorrect | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 101041348 | Asset record non-conformance; transmission record incorrect | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 101041348 | Asset record non-conformance; idle facility record incorrect | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 101041348 | Asset record non-conformance; bird issue record incorrect | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 103400478 | Inspector did not identify existing connectors | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 103663608 | Contract Inspector uploaded photos of SAP ID # 103663115 (which is 1 pole to the northwest of the correct location). | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 103805046 | Three way pole with connections | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 101041348 | Asset record non-conformance; additional asset record incorrect | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 101041348 | Asset Record non-conformance; primary connection record incorrect | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 101041348 | Asset Record non-conformance; splicer record incorrect | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 101041348 | Asset record non-conformance; transmission record incorrect | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 101041348 | Asset record non-conformance; transmission record incorrect | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 101041348 | Asset record non-conformance; transmission record incorrect | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 101041348 | Asset record non-conformance; vibration damper record incorrect | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 101066133 | Asset Record non-conformance; primary connection record incorrect | Record | Low | Tier 3
2020 Distribution Contractor Inspection | 101372295 | Asset Record non-conformance; primary connection record incorrect | Record | Low | Tier 3
2020 Distribution Contractor Inspection | 101676049 | Asset Record non-conformance; primary connection record incorrect | Record | Low | Tier 3
2020 Distribution Contractor Inspection | 101801656 | Asset Record non-conformance; primary connection record incorrect | Record | Low | Tier 3
2020 Distribution Contractor Inspection | 101801656 | Asset Record non-conformance; splicer record incorrect | Record | Low | Tier 3
2020 Distribution Contractor Inspection | 101802042 | Asset Record non-conformance; primary connection record incorrect | Record | Low | Tier 3
2020 Distribution Contractor Inspection | 101803491 | Asset Record non-conformance; primary connection record incorrect | Record | Low | Tier 3
2020 Distribution Contractor Inspection | 103136785 | Asset Record non-conformance; primary connection record incorrect | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 103136787 | Asset Record non-conformance; primary connection record incorrect | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 101016524 | Two connections | Record | Low | Tier 3
2020 Distribution Contractor Inspection | 103136788 | Asset Record non-conformance; primary connection record incorrect | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 101058469 | Connectors were present for transformer. Not over a highway. | Record | Low | Tier 3
2020 Distribution Contractor Inspection | 101064838 | Connections for the transformer were present | Record | Low | Tier 3
2020 Distribution Contractor Inspection | 103136788 | Asset record non-conformance; vibration damper record incorrect | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 103136789 | Asset Record non-conformance; primary connection record incorrect | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 101389224 | Contract Inspector did not record any primary connectors; there are 2 transformer chance-clamps. *NOTE: these connectors are NOT installed on the conductor that crosses over major roadways. | Record | Low | Tier 3
2020 Distribution Contractor Inspection | 103344505 | Asset Record non-conformance; splicer record incorrect | Record | Low | Tier 3
2020 Distribution Contractor Inspection | 103347473 | Asset Record non-conformance; primary connection record incorrect | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 103347473 | asset record non-conformance; description not available | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 103371944 | Asset record non-conformance; vibration damper record incorrect | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 103636031 | Asset Record non-conformance; primary connection record incorrect | Record | Low | Tier 3
2020 Distribution Contractor Inspection | 101900028 | Inspector did not identify compression connectors on jumpers for double dead end | Record | Low | Tier 3
2020 Distribution Contractor Inspection | 101900052 | Inspector did not identify connectors | Record | Low | Tier 3
2020 Distribution Contractor Inspection | 101900059 | Inspector did not identify the connectors | Record | Low | Tier 3
2020 Distribution Contractor Inspection | 102318714 | Connections were present with no issues. | Record | Low | Tier 3
2020 Distribution Contractor Inspection | 103118024 | Connections on riser to switch | Record | Low | Tier 3
2020 Distribution Contractor Inspection | 103344505 | Connections were present. | Record | Low | Tier 3
2020 Distribution Contractor Inspection | 103892763 | Asset Record non-conformance; primary connection record incorrect | Record | Low | Tier 3
2020 Distribution Contractor Inspection | 103950974 | Asset Record non-conformance; primary connection record incorrect | Record | Low | Tier 2
2020 Distribution Contractor Inspection | 103752721 | Primary connections on transformer were not recorded. | Record | Low | Tier 3
2020 Distribution Contractor Inspection | 103950974 | Asset Record non-conformance; splicer record incorrect | Record | Low | Tier 2