## Table 1
#VALUE!
Table 1: Customers Notified and De-energized1
| Total Customers Notified | Total Customers De-energized | Total Customers Cancelled | MBL Program Customers De-energized | Counties De-energized | Tribes De-energized | Circuits Transmission De-energized | Circuits Unique Distribution Circuits in Any Version of Scope | Circuits Distribution Circuits De-energized | Damage/Hazard Count | CFI De-energized
| 583 | 583 | 0 | 26 | 1 | 0 | 4 | 2 | 2 | 0 damages 0 hazards | 33
1 The information, times, and figures referenced in this report are based on the best available information available at the time of this report’s submission. The information, times, and figures herein are subject to revision based on further analysis and validation.

## Table 2
#VALUE!
Table 2: 2025 PSPS Risk-Benefit Consequence Modelling Considerations
| Consequence Type | Wildfire Consequence Considerations | PSPS Consequence Considerations
| Safety | Calculated based on maximum population impacts derived from Technosylva wildfire simulation models and a fatality ratio based on National Fire Protection Association (NFPA) data. | Calculated from an estimate of Equivalent Fatalities (EF) per Million Customer Minutes Interrupted (MMCI). The EF/MMCI ratio is estimated from previous PG&E PSPS outages and other large external outage events.1
| Reliability | N/A | Calculated directly from the potential number of customers impacted and outage duration based on customer minutes interrupted.
| Financial | Calculated based on maximum building impacts derived from Technosylva wildfire simulation models and a cost per structure burned previously evaluated in 2020 RAMP Report.2 | Calculated based on two financial estimates, 1) distribution of a lump sum cost of execution across all relevant circuits and 2) an estimated proxy cost per customer in scope per PSPS.3
1 Previous PG&E PSPS include 2019-2021 events, and other large external outage events include the 2003 Northeast Blackout in New York City, 2011 Southwest Blackout in San Diego, 2012 Derecho Windstorms, 2012 Superstorm Sandy, 2017 Hurricane Irma, 2021 Blackout event.
2 See A.20-06-012.
3 The assumptions used in these calculations, including the proxy cost per customer per PSPS, are subject to be updated and are not intended to prejudge or create precedent with regard to the development of more precise values of resiliency or cost of PSPS metrics being considered in other ongoing proceedings at the California Public Utilities Commission, such as the Risk-Based Decision-Making Rulemaking [R.20.07.013] and the Microgrid and Resiliency Strategies.

## Table 3
#VALUE!
Table 3: Notification Descriptions
| Type of Notification | Recipients | Description
| PRIORITY NOTIFICATION: 48-72 hours in advance of anticipated de-energization | Public Safety Partners and CBOs,1 transmission-level customers, and municipal utilities | On January 20, 2025, PG&E’s Meteorology Team noted a potential PSPS and updated the weather forecast on pge.com/weather to “elevated” in certain parts of the service area. At this time, local PG&E representatives called each County Office of Emergency Services (OES) in PG&E’s electrical service area and select cities to inform them that PG&E is monitoring an increased potential of PSPS outages. As mentioned in Section 1.1, PG&E’s EOC was still active from a previous PSPS. During this time, PG&E submitted a PSPS Notification Form to Cal OES and sent an e-mail to the CPUC notifying them that PG&E was monitoring for a potential PSPS.
| WATCH NOTIFICATION: 24-48 hours in advance of anticipated de-energization | Public Safety Partners, CBOs, and All Customers (including MBL Program customers and SIV Program customers), transmission-level customers, and municipal utilities | During this time, the following was completed: • PG&E submitted a PSPS Notification Form to Cal OES. • PG&E sent notifications to other Public Safety Partners, transmission level customers, municipal utilities, and all customers via call, text message, and e-mail; these notifications included the following information: o Estimated window of the de-energization time. o When the adverse weather is anticipated to pass. o ETOR. o For Public Safety Partners only: Links to the PSPS Portal. o For Customers only: Potentially impacted addresses, links to PSPS Updates webpage with CRC information, and resources for AFN customers, including but not limited to information on the MBL Program, language support, and the Portable Battery Program. o For transmission-level customers only: Transmission Substation Name and Line name serving substation. • PG&E sent notifications to MBL Program customers, including tenants of master metered accounts, and SIV Program customers every hour until the customer confirmed receipt of the notification. Customer notifications were provided in English, with information on how to get PSPS information in translated languages. Customers with their language preference selected in their PG&E accounts received in-language (translated) notifications. Public Safety Partner notifications were provided in English.
| WARNING NOTIFICATION: 1-4 hours in advance of anticipated de-energization, if possible | Public Safety Partners, CBOs, and All Customers (including MBL Program customers, SIV Program customers), transmission level customers, and municipal utilities | During this time, the following was completed: • PG&E submitted a PSPS Notification Form to Cal OES and sent an e-mail to the CPUC notifying them that PG&E has made the decision to de-energize. • PG&E sent notifications to other Public Safety Partners, transmission-level customers, and customers; these notifications included the same key PSPS timing information and resource links as the “Watch Notification.” • PG&E sent notifications to MBL Program customers, including tenants of master metered accounts, and SIV Program customers every hour until the customer confirmed receipt of the notification. • PG&E takes effort to provide an additional call to transmission-level customers within 30 minutes of de-energization when possible in order to provide transmission-level customers with sufficient time to properly ramp down any processes and shut down equipment. Customer notifications were provided in English, with information on how to receive PSPS information in translated languages. Customers with their language preference selected in their PG&E accounts received in-language (translated) notifications. Public Safety Partner notifications were provided in English.
| POWER OFF NOTIFICATION: When de-energization is initiated | Public Safety Partners, CBOs, and All Customers (including MBL Program customers and SIV Program customers), transmission-level customers,3 and municipal utilities | When shut off was initiated, the following was completed: • PG&E submitted a PSPS State Notification Form to Cal OES and sent an e-mail to the CPUC to notify them that de-energization has been initiated. • Agency Representatives of PG&E conducted a live call and/or sent an e-mail, as appropriate, to County OES representatives that were within the potential PSPS scope area and select cities to inform them that customers within their jurisdiction were beginning to be de-energized. • PG&E Grid Control Center (GCC) conducted live agent calls to impacted transmission-level customers. • PG&E sent notifications to other Public Safety Partners, municipal utilities, transmission level customers and customers via call, text messages, and e-mail, which included: o Impacted addresses (for customers only). o De-energization time. o When the adverse weather is anticipated to pass. o For Customers Only: Links to the PSPS Updates webpage with CRC information, and resources for AFN customers, including but not limited to information on the MBL Program, Meals on Wheels, language support, and the Portable Battery Program. Customer notifications were provided in English, with information on how to receive PSPS information in translated languages. Customers with their language preference selected in their PG&E accounts received in-language (translated) notifications. Public Safety Partner notifications were provided in English.
| WEATHER “ALL-CLEAR”/ETOR UPDATE NOTIFICATION: Immediately before re-energization begins | Public Safety Partners, CBOs, and All Customers (including MBL Program customers and SIV Program customers), transmission-level customers, and municipal utilities | After the weather event had passed and the area was deemed safe to begin patrols and restoration, PG&E completed the following: • Submitted a PSPS State Notification Form to Cal OES and sent an e-mail to the CPUC notifying them that PG&E is initiating re-energization patrols. • Sent notifications to other Public Safety Partners, transmission level customers3 , municipal utilities and customers via call, text message and e-mail; these notifications included the ETOR. • Sent “PSPS update” notifications to customers if their ETOR changed; two ways that an ETOR may change include: o New field or meteorology conditions. o Damage was found during patrols and repair is needed. Customer notifications were provided in English, with information on how to get PSPS information in translated languages. Customers with their language preference selected in their PG&E accounts received in-language (translated) notifications. Public Safety Partner notifications were provided in English.
| RESTORATION NOTIFICATION: When re-energization is complete | Public Safety Partners, CBOs, and All Customers (including MBL Program customers and SIV Program customers), transmission level customers, and municipal utilities | GCC conducted live agent calls to notify impacted transmission-level customers of restoration. Once customers, including MBL Program customers and SIV Program customers, were restored, they received notifications via call, text, and e-mail. This was done using an automated process that issued customer notifications every 15 minutes upon restoration of service. Customer notifications were provided in English, with information on how to receive PSPS information in translated languages. Customers with their language preference selected in their PG&E accounts received in-language (translated) notifications. Once all customers were restored, PG&E submitted the final PSPS State Notification Form to Cal OES, sent an e-mail to the CPUC confirming restoration of PSPS outages and reclassification of customers if applicable, and sent a notification to Public Safety Partners via call, text, and e-mail. Public Safety Partner notifications were provided in English.
1 Phase 3 D.21-06-034, Appendix A, page A9, Section G. MBL Program and AFN Communities, No. 4, Each electric investor-owned utility must provide proactive notification and impacted zip code information to paratransit agencies that may serve all the known transit- or paratransit-dependent persons that may need access to a CRC during a PSPS.
2 Transmission-level customers receive a GCC live call before de-energization and prior to re-energization.
3 Transmission lines serving impacted Transmission-level Customers and Municipal Utilities may cut across multiple Fire Index Areas (FIAs) and will only be notified when all those FIAs that the line cuts across have been given the All-Clear.

## Table 4
#VALUE!
Table 4: Customer Notification Timeline Summary
| Event Order | Minimum Timeline1 | Notification Sent to: | Approximate Time Sent (PST) | Message | Notes | Who made the Notification
| Pre-De-energization (Prior) | 72-48 hours | Local Governments and CCAs,* Public Safety Partners** | Not sent | Priority | Priority notifications were not sent. See Section 5.2 and 5.5 for more information. | Failed
| Pre-De-energization (Prior) | 48-24 hours | Local Governments and CCAs* | 2025-01-21 15:29 | Watch |  | PG&E
| Pre-De-energization (Prior) | 48-24 hours | Public Safety Partners** | 2025-01-21 15:52 | Watch |  | PG&E
| Pre-De-energization (Prior) | 48-24 hours | All Customers*** | 2025-01-21 15:49 | Watch |  | PG&E
| Pre-De-energization (Prior) | 48-24 hours | All Customers*** | 2025-01-21 15:59 | Watch |  | SCE
| Pre-De-energization (Prior) | 24-12 hours2 | Local Governments and CCAs* | 2025-01-22 06:45 | Watch |  | PG&E
| Pre-De-energization (Prior) | 24-12 hours3 | Public Safety Partners** | 2025-01-22 07:40 | Watch |  | PG&E
| Pre-De-energization (Prior) | 24-12 hours4 | All Customers*** | 2025-01-22 07:38 | Watch |  | PG&E
| Pre-De-energization (Prior) | 24-12 hours5 | All Customers*** | 2025-01-22 08:15 | Watch |  | SCE
| Pre-De-energization (Prior) | 4-1 hours | Local Governments and CCAs* | 2025-01-22 14:35 | Warning |  | PG&E
| Pre-De-energization (Prior) | 4-1 hours | Public Safety Partners** | 2025-01-22 15:00 | Warning |  | PG&E
| Pre-De-energization (Prior) | 4-1 hours | Public Safety Partners** | 2025-01-22 18:20 | Warning |  | PG&E
| Pre-De-energization (Prior) | 4-1 hours | All Customers*** | 2025-01-22 14:48 | Warning |  | PG&E
| Pre-De-energization (Prior) | 4-1 hours | All Customers*** | 2025-01-22 14:47 | Warning |  | SCE
| Pre-De-energization (Prior) | 4-1 hours | All Customers*** | 2025-01-22 18:17 | Warning |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Public Safety Partners** | 2025-01-22 18:01 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Public Safety Partners** | 2025-01-22 18:45 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Public Safety Partners** | 2025-01-22 22:16 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | All Customers*** | 2025-01-22 17:55 | Power Off |  | SCE
| Initiation (During) | When De-energization is initiated (Power Off) | All Customers*** | 2025-01-22 18:01 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | All Customers*** | 2025-01-22 18:45 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | All Customers*** | 2025-01-22 22:16 | Power Off |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Local Governments and CCAs* | 2025-01-24 08:58 | Inspecting/Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-01-24 08:47 | Inspecting/Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-01-24 08:33 | Inspecting/Weather All-Clear |  | SCE
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-01-24 08:47 | Inspecting/Weather All-Clear |  | PG&E
| Restoration (After) | After re-energization was completed | Local Governments and CCAs* | 2025-01-24 11:05 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-01-24 10:16 | Restore | First initial Restoration Notification sent. | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-01-24 10:47 | Restore | First initial Restoration Notification sent. | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-01-24 10:16 | Restore | First initial Restoration Notification sent. | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-01-24 10:47 | Restore | First initial Restoration Notification sent. | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-01-24 16:12 | Restore |  | SCE
*A subset of Public Safety Partners, including cities, counties, and community choice aggregators.
**A subset of Public Safety Partners, including water, wastewater, and communication service providers.
***All Customers, including MBL Program customers and SIV Program customers.
1 D.19-05-042, Appendix A, Timing of Notification.
2 While not a CPUC requirement, PG&E provides an additional 24-12 hour notification to Local Governments, Public Safety Partners and Customers.

## Table 5
#VALUE!
Table 5: Notifications to Customers where Positive or Affirmative Notification was Attempted1
| Designation | Total Number of customers | Notification Attempts Made2 | Timing of Attempts3 | Who made the Notification Attempt | Successful Positive Notification4
| MBL5 | 26 | 419 | Daily | PG&E | 26
| MBL behind a master meter6 | 0 | 0 | N/A | PG&E | 0
| SIV | 14 | 191 | Daily | PG&E | 14
1 Counts of Notification Attempts Made will not reflect the actual total of customers notified as both MBL Program and SIV Program customers can appear in both subset groups.
2 Count of Attempts Made includes doorbell rings and Live Agent phone calls.
3 Initial start time notification was sent.
4 PG&E tracks positive confirmation from MBL/SIV customers via text, phone call, email, doorbell rings, live agent phone calls or door hanger at all stages of notifications. If we receive confirmation at any stage or a door hanger was left, that is considered a successful positive notification. See PG&E’s quarterly AFN reporting and PG&E Pre-Season reports for more information.
5 Residential tenants of master-metered customers can also qualify for MBL quantities. The MBL category for the purposes of Table 5 does not include MBL Program customers who are master meter tenants.
6 PG&E has additional processes in place to ensure MBL Program customers are notified. Master meter tenants are contacted directly to be considered a positive notification. Contacting the property or building manager does not count as a positive notification.

## Table 6
#VALUE!
Table 6: Notification Failure Causes
| Notifications Sent to | Notification Failure Description | Number of Entities or Customer Account | Explanation of Failure
| Public Safety Partners excluding CFI1 | Entities who did not receive 48-to 72-hour priority notification | 1 | Priority Notifications were not sent. See above and Section 5.2 for explanation.
| Public Safety Partners excluding CFI1 | Entities who did not receive 1–4-hour imminent notification | 0 | No failures.
| Public Safety Partners excluding CFI1 | Entities who did not receive any notifications before de-energization | 0 | No failures.
| Public Safety Partners excluding CFI1 | Entities who were not notified immediately before re-energization | 0 | No failures.
| Public Safety Partners excluding CFI1 | Entities who did not receive cancellation notification within two hours of the decision to cancel | 0 | No failures.
| CFI2 | Facilities who did not receive 48-to 72-hour priority notification | 33 | Priority Notifications were not sent. See above and Section 5.2 for explanation.
| CFI2 | Facilities who did not receive 1–4-hour imminent notification | 0 | No failures.
| CFI2 | Facilities who did not receive any notifications before de-energization | 0 | No failures.
| CFI2 | Facilities who were not notified at de-energization initiation | 0 | No failures.
| CFI2 | Facilities who were not notified immediately before re-energization | 0 | No failures.
| CFI2 | Facilities who were not notified when re-energization is complete | 0 | No failures.
| CFI2 | Facilities who did not receive cancellation notification within two hours of the decision to cancel | 0 | No failures.
| All other affected customers | Customers who did not receive 24–48-hour advance notifications | 0 | No failures.
| All other affected customers | Customers who did not receive 1–4-hour imminent notifications | 0 | No failures.
| All other affected customers | Customers who did not receive any notifications before de-energization | 0 | No failures.
| All other affected customers | Customers who were not notified at de-energization initiation | 0 | No failures.
| All other affected customers | Customers who were not notified immediately before re-energization | 0 | No failures.
| All other affected customers | Customers who were not notified when re-energization is complete | 0 | No failures.
| All other affected customers | Customers who did not receive cancellation notification within two hours of the decision to cancel | 0 | No failures.
1 Only includes cities, counties, and CCAs.
2 Includes Public Safety Partners who are CFI customers.

## Table 7
#VALUE!
Table 7: PSPS Portal Time & Date for Map Sharing
| Date | Time PDF and GIS Maps Shared (PST)
| 2025-01-21 | 15:33
| 2025-01-22 | 6:47
| 2025-01-22 | 13:44

## Table 8
#VALUE!
Table 8: PSPS Notifications Submitted to Cal OES
| Date | Time PDF and GIS Maps Shared (PST)
| 2025-01-21 | 15:13
| 2025-01-22 | 6:38
| 2025-01-22 | 11:36
| 2025-01-22 | 14:21
| 2025-01-22 | 17:32
| 2025-01-23 | 6:16
| 2025-01-23 | 14:06
| 2025-01-24 | 6:47
| 2025-01-24 | 8:29
| 2025-01-24 | 11:45

## Table 9
#VALUE!
Table 9: PSPS Notifications Submitted to CPUC
| Date | Time PDF and GIS Maps Shared (PST)
| 2025-01-21 | 15:20
| 2025-01-22 | 14:26
| 2025-01-22 | 17:54
| 2025-01-24 | 8:39
| 2025-01-24 | 11:09

## Table 10
#VALUE!
Table 10: Generators Available for CFI Customers
| Generator Type | Number of Units | Individual Size (MW) | Run Time (Hrs.)1 | Description
| Diesel Generator | 13 | 0.032 | 37.6 | 13 units on reserve in Sacramento.
| Diesel Generator | 3 | 0.056 | 50 | 3 units on reserve in Sacramento.
| Diesel Generator | 5 | 0.065 | 31 | 5 units on reserve in San Leandro.
| Diesel Generator | 3 | 0.07 | 31 | 3 units on reserve in Sacramento.
| Diesel Generator | 35 | 0.1 | 25.3 | 35 units on reserve in Sacramento.
| Diesel Generator | 5 | 0.125 | 25 | 3 units on reserve in Sacramento and 2 units on reserve in San Leandro.
| Diesel Generator | 9 | 0.15 | 30.3 | 9 units on reserve in Sacramento.
| Diesel Generator | 13 | 0.2 | 22.9 | 5 units on reserve in Sacramento and 8 units on reserve in San Leandro.
| Diesel Generator | 5 | 0.275 | 26 | 5 units on reserve in Sacramento.
| Diesel Generator | 4 | 0.5 | 24.1 | 5 units on reserve in Sacramento.
| Diesel Generator | 4 | 0.57 | 24.1 | 4 units on reserve in San Leandro.
| Diesel Generator | 4 | 1 | 35 | 4 units on reserve in Sacramento.
| Diesel Generator | 5 | 1.14 | 24 | 5 units on reserve in San Leandro.
| Diesel Generator | 7 | 1.5 | 10 | 7 units on reserve in Benecia.
| Diesel Generator | 3 | 2 | 27.7 | 3 units on reserve in Sacramento.
1 Estimated based on a 75% load. Barring mechanical failure and refueling the temporary generators have the ability to operate continuously throughout a typical PSPS.

## Table 11
#VALUE!
Table 11: CFI Customers Energized with Backup Generation
| County | Site Type | Generation Deployed (MW) | Duration of Operation (Hours) | Reason Deployed
| Kern | El Tejon School | 0.2 | 1899-12-31 15:00 | High risk to environment or public safety.
| Kern | Residential Home in Lebec | 0.056 | 1899-12-31 19:25 | High risk to environment or public safety.
| Kern | Tejon Ranch, Lebec | 0.036 | 1900-01-01 22:15 | High risk to environment or public safety.
| Kern | Tejon Ranch, Lebec | 0.2 | 1900-01-01 17:14 | High risk to environment or public safety.

## Table 12
#VALUE!
Table 12: Number and Nature of Complaints due to the January 22 – 24, 2025 PSPS
| Nature of Complaints | Number of Complaints
| Communications/Notifications Including, but not limited to complaints regarding lack of notice, excessive notices, confusing notice, false alarm notice, problems with getting up-to-date information, inaccurate information provided, not being able to get information in the prevalent languages and/or information accessibility, complaints about website, Public Safety Partner Portal, Representational State Transfer (REST)/Digital Asset Manager (DAM) sites (as applicable). | 3
| PSPS Frequency/Duration Including, but not limited to complaints regarding the frequency and/or duration of PSPS, including delays in restoring power, scope of PSPS and dynamic of weather conditions. | 6
| Safety/Health Concern Including, but not limited to complaints regarding difficulties experienced by AFN/MBL populations, traffic accidents due to non-operating traffic lights, inability to get medical help, well water or access to clean water, inability to keep property cool/warm during outage raising health concern. | 2
| General PSPS Dissatisfaction/Other Including, but not limited to complaints about being without power during PSPS and related hardships such as food loss, income loss, inability to work/attend school, plus any PSPS-related complaints that do not fall into any other category. | 7
| Outreach/Assistance Including, but not limited to complaints regarding CRCs, community crew vehicles, backup power, hotel vouchers, other assistance provided by utility to mitigate impact of PSPS. | 0

## Table 13
#VALUE!
Table 13: Count and Type of Claim(s) Received
| Description of Claims | Number of Claims
| Business Interruption / Economic Loss | 0
| Food Loss Only | 1
| Property Damage | 0

## Table 14
#VALUE!
Table 14: Weather All-Clear Times
| All-Clear Zones | Weather All-Clear Date and Time (PST)
| 651A, 651B, 448B, 445 | 2025-01-24 08:17

## Table 15
#VALUE!
Table 15: Maximum Wind Gusts Recorded January 22 – 24, 2025 in Impacted County
| County | Maximum Wind Gust (mph) | Station ID | Station Name
| Kern | 46 | PG449 | Pampa Peak Towers

## Table A-1.1
#VALUE!
Table A-1.1: Factors Considered in the Decision to Shut Off Power for Each Distribution Circuit De-energized During the January 22 – 24, 2025 PSPS
| Circuit Name | Time Place | Forecast WS MPH | Forecast Temp 2MF | Forecast Flame Length ft 8hr | Forecast Rate of Spread Chhr 8hr | Forecast RH 2M | Forecast Prob Cat | Forecast DFM 10hr | Forecast DFM 100hr | Forecast LFM Chamise New | Forecast CFPD | Agency NOAA Yes No | Agency RFW Yes No | Agency GACC Yes No | Agency WS MPH | Agency WG MPH | Observed Temp F | Observed RH % | Observed WS MPH AC | Observed WG MPH AC | Observed Temp F AC | Observed RH % AC | Observed Open PSPS Tags | Observed TX Impacts Yes No | PSPS Risk vs. Benefit PSPS Potential Risk Consequence | PSPS Risk vs. Benefit PSPS Potential Benefit
| LAMONT 1104 | TP-02 | 29 | 67 | 10.8 | 124.5 | 7.6 | 0.17 | 0.06 | 0.09 | 74 | 3.39 | No | No | Yes | 34 | 46 | 70 | 5 | 14 | 20 | 63 | 9 | Yes | No | 0.4 | 1430.8
| TEJON 1102 | TP-01 | 39 | 61 | 15.1 | 197 | 5.4 | 0.26 | 0.05 | 0.08 | 64 | 16.94 | Yes | No | Yes | 30 | 49 | 66 | 7 | 17 | 29 | 64 | 8 | Yes | No | 1.5 | 296.4

## Table A-1.2
#VALUE!
Table A-1.2: Description, Units, and Value provided for Factors Considered in the Decision to Shut Off Power for Each Distribution Circuit De-energized During the January 22 – 24, 2025 PSPS
| Forecast / Agency / Observed | Value | Name | Unit | Value Provided | Description
| Forecast | WS MPH | Sustained Wind Speed | mph | max | Sustained windspeed in miles per hour at 10 meters above ground level.
| Forecast | Temp 2MF | Temperature | degrees F | max | Temperature in Fahrenheit at 2 meters above ground level.
| Forecast | Flame Length ft 8hr | Flame Length | ft | max | Flame length in feet on fire front for first 8 hours of fire spread simulation from Technosylva.
| Forecast | Rate of Spread Chhr 8hr | Rate of Spread | chains/hr | max | Rate of fire spread in chains per hour for first 8 hours of fire spread simulation from Technosylva.
| Forecast | RH 2M | Relative Humidity | % | min | Relative Humidity in percent at 2 meters above ground level.
| Forecast | Prob Cat | Fire Potential Index (FPI) | probability outputs | max | Fire Potential Index (FPI) Model Output - Probability of a catastrophic fire if an ignition were to occur. FPI component of the CFPD model.
| Forecast | DFM 10hr | Dead Fuel Moisture Content 10 hrs | fuel moisture fraction | min | Dead Fuel Moisture in 10-hour fuel moisture class. Can be scaled to percentage by multiplying by 100.
| Forecast | DFM 100hr | Dead Fuel Moisture Content 100 hrs | fuel moisture fraction | min | Dead Fuel Moisture in 100-hour moisture class. Can be scaled to percentage by multiplying by 100.
| Forecast | LFM Chamise New | Live Fuel Moisture Content-shrub | % | min | Live Fuel Moisture Percentage of Chamise (shrub) plant species. (% of species that is comprised of water).
| Forecast | CFPD | Catastrophic Fire Probability (CFPD) | Scaled Probability | max | The product of probability of catastrophic fire (Prob Cat) and IPW - probability of ignition (Prob Ignition). This product is called the (CFPD) Catastrophic Fire Probability distribution. Scaled by 1000 to convert to an integer value.
| Agency | NOAA Yes No | National Oceanic and Atmospheric Administration | N/A | Yes/No During Event | NOAA (SPC) Fire Weather Outlook forecast.
| Agency | RFW Yes No | Red Flag Warning | N/A | Yes/No During Event | Red Flag Warning from the Federal National Weather Service.
| Agency | GACC Yes No | GACC | N/A | Yes/No During Event | GAAC High Risk issued by the Federal North or South Operations Predictive Services.
| Observed | WS MPH | Observed Sustained Wind Speed During Event | mph | max | The maximum sustained wind speed recorded by weather stations mapped to each circuit from planned de-energization time to anticipated All-Clear time.
| Observed | WG MPH | Observed Peak Wind Gust During Event | mph | max | The maximum wind gust recorded by weather stations mapped to each circuit from planned de-energization time to anticipated All- Clear time.
| Observed | Temp F | Observed Temperature During Event | degrees F | max | The maximum temperature recorded by weather stations mapped to each circuit from planned de-energization time to anticipated All-Clear time.
| Observed | RH % | Observed Relative Humidity During Event | % | min | Minimum relative humidity recorded by all weather stations mapped to each circuit from planned de-energization time to anticipated All-Clear time.
| Observed | WS MPH AC | Observed Sustained Wind Speed at All-Clear | mph | max | The maximum sustained wind speed recorded by weather stations mapped to each circuit at the All-Clear time.
| Observed | WG MPH AC | Observed Peak Wind Gust at All Clear | mph | max | The maximum wind gust recorded by weather stations mapped to each circuit at the All-Clear time.
| Observed | Temp F AC | Observed Temperature at All-Clear | degrees F | max | The maximum temperature recorded by weather stations mapped to each circuit at the All-Clear time.
| Observed | Observed RH % AC | Observed Relative Humidity at All-Clear | % | min | Minimum relative humidity recorded by all weather stations mapped to each circuit at the All-Clear time.
| Observed | Open PSPS Tags | Open PSPS Qualified Tags | N/A | Yes/No During Event | PSPS-Qualified Tags include P1 (tree represents an immediate risk) and P2 (tree is damaged or diseased and could fall into nearby power lines) tree tags and Electric Corrective tags (Priority A - emergency, B - urgent, and E/F - risk-based).
| Observed | Tx Impacts Yes No | Impacted by Transmission | N/A | Yes/No During Event | Distribution lines that would have been de-energized due to de-energization of upstream transmission lines, regardless of whether those distribution lines would have also been de-energized due to direct distribution PSPS.
| Observed | PSPS Potential Risk Consequence | PSPS Potential Risk Consequence | MAVF Score | Yes/No During Event | Measure of the adverse impact to customers due to de-energization.
| Observed | PSPS Potential Benefit | PSPS Potential Benefit | MAVF Score | Yes/No During Event | Measure of the adverse impact to customers due to a catastrophic fire.

## Table A-2.1
#VALUE!
Table A-2.1: Factors Considered in the Decision to Shut Off Power for Each Transmission Circuit De-energized During the January 22 – 24, 2025 PSPS
| Circuit Name | Time Place | Forecast WS MPH | Forecast Temp 2FM | Forecast Flame Length ft 8hr | Forecast Rate of Spread Chhr 8hr | Forecast RH 2M | Forecast Prob Cat | Forecast DFM 10hr | Forecast DFM 100hr | Forecast LFM ChamiseNew | Forecast OA | Forecast CFPT | Agency NOAA Yes No | Agency RFW Yes No | Agency GACC Yes No | Observed WS MPH | Observed WG MPH | Observed Temp F | Observed RH % | Observed WS MPH AC | Observed WG MPH AC | Observed Temp F AC | Observed RH % AC | Observed HFRA Yes No | Observed High Risk Veg Present Yes No | Observed TX Impacts Yes No | PSPS Risk vs. Benefit PSPS Potential Risk Consequence | PSPS Risk vs. Benefit PSPS Potential Benefit
| CASTAIC TAP | TP-01 | 24 | 53 | 9.9 | 127.4 | 6.4 | 0.2 | 0.05 | 0.09 | 75 | No | 0.002 | No | No | No | 30 | 49 | 66 | 7 | 9 | 17 | 53 | 9 | Yes | No | No | 0.4 | 38
| GRAPEVINE TAP | TP-01 | 37 | 56 | 13 | 184.1 | 6 | 0.2 | 0.05 | 0.09 | 71 | No | 0.26 | No | No | No | 30 | 49 | 66 | 7 | 9 | 17 | 53 | 9 | Yes | No | No | 0.4 | 51.3
| ROSE TAP | TP-01 | 30 | 66 | 12.9 | 180.5 | 5.8 | 0.15 | 0.07 | 0.1 | 73 | No | 0.01 | No | No | No | 30 | 49 | 66 | 7 | 9 | 17 | 53 | 9 | No | No | No | 0.4 | 19.6
| TEJON-LEBEC | TP-01 | 39 | 61 | 12.9 | 180.5 | 5.6 | 0.22 | 0.05 | 0.09 | 70 | 2.6 | 0.29 | No | No | No | 30 | 49 | 66 | 7 | 9 | 17 | 53 | 9 | Yes | No | No | 0.4 | 66.4

## Table A-2.2
#VALUE!
Table A-2.2: Description, Units, and Value provided for Factors Considered in the Decision to Shut Off Power for Each Transmission Circuit De-energized During the January 22 – 24, 2025 PSPS
| Forecast / Agency / Observed | Value | Name | Unit | Value Provided | Description
| Forecast | WS MPH | Sustained Wind Speed | mph | max | Sustained wind speed in miles per hour at 10 meters above ground level.
| Forecast | Temp 2MF | Temperature | degrees F | max | Temperature in Fahrenheit at 2 meters above ground level.
| Forecast | Flame Length ft 8hr | Flame Length | ft | max | Flame length in feet on fire front for first 8 hours of fire spread simulation from Technoslyva.
| Forecast | Rate of Spread Chhr 8hr | Rate of Spread | chains/hr | max | Rate of fire spread in chains per hour for first 8 hours of fire spread simulation from Technoslyva.
| Forecast | RH 2M | Relative Humidity | % | min | Relative Humidity in percent at 2 meters above ground level.
| Forecast | Prob Cat | Fire Potential Index (FPI) | probability outputs | max | FPI Model Output - Probability of a catastrophic fire if an ignition were to occur. FPI component of the CFPD model.
| Forecast | DFM 10hr | Dead Fuel Moisture Content 10 hrs (%) | fuel moisture fraction | min | Dead Fuel Moisture in 10-hour fuel moisture class. Can be scaled to percentage by multiplying by 100.
| Forecast | DFM 100hr | Dead Fuel Moisture Content 100 hrs (%) | fuel moisture fraction | min | Dead Fuel Moisture in 100-hour moisture class. Can be scaled to percentage by multiplying by 100.
| Forecast | LFM Chamise New | Live Fuel Moisture Content-shrub | % | min | Live Fuel Moisture Percentage of Chamise (shrub) plant species (% of species that are comprised of water).
| Forecast | OA | Transmission Operability Assessment (OA) | Probability | max | IPW Model Output - Probability of Ignition based on the probability of outages by cause. Ignition component of the CFPD model. IPW Model - A model that provides estimates of the probability of an ignition given an outage on an hourly basis.
| Forecast | CFPT | Catastrophic Fire Potential (CFPT) | Scaled Probability | max | The product of probability of catastrophic fire (Prob Cat) and IPW - probability of ignition (Prob Ignition). This product is called the (CFPD) Catastrophic Fire Probability distribution model. Scaled by 1000 to covert to an integer value.
| Agency | NOAA Yes No | National Oceanic and Atmospheric Administration | N/A | Yes/No During Event | NOAA (SPC) Fire Weather Outlook forecast.
| Agency | RFW Yes No | Red Flag Warning | N/A | Yes/No During Event | Red Flag Warning from the Federal National Weather Service.
| Agency | GACC Yes No | GACC | N/A | Yes/No During Event | High Risk issued by the Federal North or South Operations Predictive Services.
| Observed | WS MPH | Observed Sustained Wind Speed During Event | mph | max | The maximum sustained wind speed recorded by weather stations mapped to each circuit from de-energization time to All-Clear time.
| Observed | WG MPH | Observed Wind Gust During Event | mph | max | The maximum sustained wind gust recorded by weather stations mapped to each circuit from de-energization time to All-Clear time.
| Observed | Temp F | Observed Temperature During Event | degrees F | max | The maximum temperature recorded by weather stations mapped to each circuit from de-energization time to All-Clear time.
| Observed | RH % | Observed Relative Humidity During Event | % | min | Minimum relative humidity recorded by all weather stations mapped to each circuit from de-energization time to All-Clear time.
| Observed | WS MPH AC | Observed Sustained Wind Speed at All-Clear | mph | max | The maximum sustained wind speed recorded by weather stations mapped to each circuit at the All-Clear time.
| Observed | WG MPH AC | Observed Sustained Wind gust at All-Clear | mph | max | The maximum sustained wind gust recorded by weather stations mapped to each circuit at the All-Clear time.
| Observed | Temp F AC | Observed Temperature at All-Clear | degrees F | max | The maximum temperature recorded by weather stations mapped to each circuit at the All-Clear time.
| Observed | RH % AC | Observed Relative Humidity at All-Clear | % | min | Minimum relative humidity recorded by all weather stations mapped to each circuit at the All-Clear time.
| Observed | HFRA | High Fire Risk Area (HFRA) | N/A | Yes/No During Event | Labeled ‘Yes’ when Circuit goes through HFRA.
| Observed | High Risk Veg Present on Circuit | High Risk Vegetation Present on Circuit | N/A | Yes/No During Event | High risk vegetation present on the circuit.
| Observed | TX Impacts Yes No | Impacted by Transmission | N/A | Yes/No During Event | Distribution lines that would have been de-energized due to de-energization of upstream transmission lines, regardless of whether those distribution lines would have also been de-energized due to direct distribution PSPS.
| Observed | PSPS Potential Risk Consequence | PSPS Potential Risk Consequence | MAVF Score | Yes/No During Event | Measure of the adverse impact to customers due to de-energization.
| Observed | PSPS Potential Benefit | PSPS Potential Benefit | MAVF Score | Yes/No During Event | Measure of the adverse impact to customers due to a catastrophic fire.

## Table B-1
#VALUE!
Table B-1. Circuits De-Energized During the January 22 – 24, 2025 PSPS
| Distribution / Transmission | Circuit Name | De-Energization Date and Time (PST) | All-Clear Date and Time (PST) | Restoration Date and Time (PST) | Key Communities | HFTD Tier(s) | Total Customers | Residential Customers | Commercial / Industrial Customers | MBL Program Customers | AFN other than MBL Program Customers | Other Customers
| Distribution | LAMONT 1104 | 2025-01-22 22:12 | 2025-01-24 08:17 | 2025-01-24 10:37 | Kern | Tier 2 | 5 | 0 | 5 | 0 | 0 | 0
| Distribution | TEJON 1102 | 2025-01-22 17:37 | 2025-01-24 08:17 | 2025-01-24 10:33 | Kern | Partially Outside HFTD, Tier 2 | 573 | 473 | 89 | 26 | 177 | 11
| Transmission | CASTAIC TAP | 2025-01-22 17:43 | 2025-01-24 08:17 | 2025-01-24 10:08 | Kern | Tier 2 | 1 | 0 | 0 | 0 | 0 | 0
| Transmission | GRAPEVINE TAP | 2025-01-22 17:43 | 2025-01-24 08:17 | 2025-01-24 10:08 | Kern | Tier 2 | 1 | 0 | 0 | 0 | 0 | 0
| Transmission | ROSE TAP | 2025-01-22 17:43 | 2025-01-24 08:17 | 2025-01-24 10:08 | Kern | Outside HFTD | 1 | 0 | 0 | 0 | 0 | 0
| Transmission | TEJON-LEBEC | 2025-01-22 17:43 | 2025-01-24 08:17 | 2025-01-24 10:08 | Kern | Tier 2 | 2 | 0 | 0 | 0 | 0 | 0
| Total | [6 empty] | 583 | 473 | 94 | 26 | 177 | 11

## Table C-1
#VALUE!
Table C-1. Public Safety Partners Contacted
| Organization/Jurisdiction | Title | HFTD or HFRA Tier1 | Date/Time Contacted (PST)
| Kern County | Board Chairman | HFRA, Tier 2 | 2025-01-21 15:30
| Kern County | County Administrative Officer | HFRA, Tier 2 | 2025-01-21 15:30
| Kern County | County Clerk | HFRA, Tier 2 | 2025-01-21 15:30
| Kern County | Emergency | HFRA, Tier 2 | 2025-01-21 15:30
| Kern County | Emergency Supervisor | HFRA, Tier 2 | 2025-01-21 15:30
| Kern County | Fire Chief | HFRA, Tier 2 | 2025-01-21 15:30
| Kern County | MHOAC | HFRA, Tier 2 | 2025-01-21 15:30
| Kern County | Manager | HFRA, Tier 2 | 2025-01-21 15:30
| Kern County | Sheriff | HFRA, Tier 2 | 2025-01-21 15:30
| Kern County | Supervisor | HFRA, Tier 2 | 2025-01-21 15:30
| Kern County Communication Facility | AT&T Mobility LLC | Tier 2 | 2025-01-21 15:49
| Kern County Communication Facility | AT&T Services Inc | Tier 2 | 2025-01-21 15:49
| Kern County Communication Facility | T-Mobile West LLC | Tier 2 | 2025-01-21 15:49
| Kern County Communication Facility | Verizon | Tier 2 | 2025-01-21 15:49
| Kern County Emergency Services Facility | California Highway Patrol | Tier 2 | 2025-01-21 15:49
| Kern County Emergency Services Facility | County of Kern | Tier 2 | 2025-01-21 15:49
| Kern County Other Facility | Crown Castle USA Inc | Tier 2 | 2025-01-21 15:49
| Kern County Water and Waste Water Facility | Lebec County Water District | Tier 2 | 2025-01-21 15:49
1 Catastrophic Fire Behavior runs both in and outside of High Fire Risk Areas (HFRA). The PG&E Meteorology Team evaluates non-HFRA areas for catastrophic wildfire risk in unusual circumstances.

## Table E-1
#VALUE!
Table E-1. Community Resource Centers Provided by PG&E
| UNMATrre | County | Site Name | Address | Operating Hours (PST) | Column1 | Column2 | Total Visitors | Indoor / Outdoor | Amenities Provided
[5 empty] | Day 1 Jan-22 | Day 2 Jan-23 | Day 3 Jan-24
| 1 | Kern | Lebec Post Office | 2132 Lebec Road | 08:00 – 22:00 | 08:00 – 22:00 | 08:00 – 11:45 | 429 | Outdoor | Wi-Fi, ADA Restrooms, Bottled Water, Device Charging, Snacks, Seating, Ice and Heating.*
*Heating was added due to low temperatures, and ice was added due to extended outages.