## Table 1
#VALUE!
Table 1: PSPS Event Summary 1
| Total Customers Notified | Total Customers De-energized | Total Customers Canceled | MBL Customers De-energized | Counties De-energized | Tribes De-energized | CFI De-energized | Transmission De-energized | Unique Distribution Circuits in Scope | Distribution Circuits De-energized | Damage/ Hazard Count
| 7,440 2 | 4,583 3 | 2802 | 232 | 15 | 2 | 220 | 0 | 31 | 31 | 3 damages 1 hazard
1 The information, times, and figures referenced in this report are based on the best available information available at the time of this report’s submission. The information, times, and figures herein are subject to revision based on further analysis and validation.
2 Of the 7,440 customers who received notifications that their power may be de-energized, one customer did not receive a cancelation notice after being removed from scope, four customers remained in the final scope but were mitigated by backup generation, and 74 customers remained in the final scope but avoided a long PSPS outage. See Section 5.5 and Section 5.7 for more information.
3 Of the 4,583 customers de-energized, 24 customers did not receive any notifications regarding planned de-energization, and one customer received this notification after de-energization began. See Section 5.3 and Section 5.5 for more information.

## Table 2
#VALUE!
Table 2: 2026 PG&E’s PSPS Risk-Benefit Consequence Modeling Considerations
| Consequence Type | Wildfire Consequence Considerations | PSPS Consequence Considerations
| Safety | Calculated based on maximum population impacts derived from Technosylva wildfire simulation models and a fatality ratio based on National Fire Protection Association (NFPA) data. | Calculated from an estimate of Equivalent Fatalities (EF) per Million Customer Minutes Interrupted (MMCI). The EF/MMCI ratio is estimated from previous PG&E PSPS outages and other large external outages.1
| Reliability | None | Calculated directly from the potential number of customers impacted and outage duration based on customer minutes interrupted.
| Financial | Calculated based on maximum building impacts derived from Technosylva wildfire simulation models and a cost per structure burned previously evaluated in 2024 RAMP Report.2 | Calculated based on two financial estimates, 1) distribution of a lump sum cost of execution across all relevant circuits and 2) an estimated proxy cost per customer in scope per PSPS.3
1 Includes 2019-2021 PSPS outages, the 2003 Northeast Blackout in New York City, 2011 Southwest Blackout in San Diego, 2012 Derecho Windstorms, 2012 Superstorm Sandy, 2017 Hurricane Irma, and 2021 Blackout event.
2 A.24-05-008.
3 The assumptions used in these calculations, including the proxy cost per customer per PSPS, are subject to be updated and are not intended to prejudge or create precedent with regard to the development of more precise values of resiliency or cost of PSPS metrics being considered in other ongoing proceedings at the California Public Utilities Commission, such as the Risk-Based Decision-Making Rulemaking [R.20.07.013] and the Microgrid and Resiliency Strategies.

## Table 3
#VALUE!
Table 3: Notification Descriptions
| Type of Notification | Recipients | Description
| PRIORITY NOTIFICATION: 48-72 hours in advance of anticipated de-energization | Public Safety Partners and CBOs1 | On May 14, our Meteorology Team noted a potential PSPS and updated the weather forecast on pge.com/weather to “elevated” in certain parts of the service area. At this time, agency representatives called each County Office of Emergency Services (OES) in PG&E’s electrical service area and select Tribes and cities to inform them that PG&E was monitoring an increased potential for a PSPS. We also notified CAISO of a potential PSPS on May 13 at 19:34 PDT. Following the EOC activation, we completed the following: • Submitted a PSPS Notification Form to Cal OES and sent an e-mail to the CPUC notifying them that PG&E’s EOC has been activated and that PG&E is monitoring for a potential PSPS. • Agency representatives called potentially impacted County OES and select Tribes and cities to inform them that PG&E is monitoring a potential PSPS. • Sent notifications to other Public Safety Partners,2 via call, text and e-mail, which included: o Estimated window of the de-energization time. o When weather is anticipated to pass. o Estimated Time of Restoration (ETOR). o Links to the PSPS Portal where PSPS-specific maps and information are available.
| WATCH NOTIFICATION: 24-48 hours in advance of anticipated de-energization | Public Safety Partners, CBOs, and All Customers (including MBL and SIV customers) | During this time, we completed the following: • Submitted a PSPS Notification Form to Cal OES and sent an email to the CPUC notifying them that PG&E’s EOC has been activated and that PG&E is monitoring for potential PSPS. • Sent notifications to Public Safety Partners and customers, via call, text message and e-mail, which included: o Estimated window of the de-energization time. o When weather is anticipated to pass. o ETOR. o For Public Safety Partners Only: Links to the PSPS Portal. o For customers only: Potentially impacted addresses, links to PSPS emergency website with CRC information, and resources for AFN customers, including but not limited to information on the MBL Program, language support, and the Portable Battery Program3 (PBP). • Sent notifications to MBL customers, including tenants of master metered accounts, and SIV customers. See Section 5.3 for more information regarding MBL Program notifications. • Sent Cancellation Notifications to Public Safety Partners and customers within, two hours of being removed from scope, to inform them that their power would not be shut off. Customer notifications are provided in English, with information on how to receive PSPS information in translated languages. Customers with their language preference selected in their PG&E accounts received in-language (translated) notifications. Public Safety Partner notifications are provided in English.
| WARNING NOTIFICATION: 1-4 hours in advance of anticipated de-energization, if possible | Public Safety Partners, CBOs, and All Customers (including MBL customers, SIV customers) | During this time, we completed the following: • Submitted a PSPS Notification Form to Cal OES and sent an e-mail to the CPUC notifying them that PG&E has made the decision to de-energize. • Sent notifications to Public Safety Partners and customers which included the same key information and resources as Watch Notifications. • Sent notifications to MBL customers, including tenants of master metered accounts, and SIV customers. See Section 5.3 for more information regarding MBL Program notifications. • Sent Cancellation Notifications to Public Safety Partners and customers within two hours of being removed from scope to inform them that their power would not be shut off. Customer notifications are provided in English, with information on how to receive PSPS information in translated languages. Customers with their language preference selected in their PG&E accounts received in-language (translated) notifications. Public Safety Partner notifications are provided in English.
| POWER OFF NOTIFICATION: When de-energization is initiated | Public Safety Partners, CBOs, and All Customers (including MBL and SIV customers) | When de-energization was initiated, we completed the following: • Submitted a PSPS State Notification Form to Cal OES and sent an e-mail to the CPUC to notify them that de-energization has been initiated. • Sent notifications to Public Safety Partners and customers, via call, text messages, and e-mail, which included: o De-energization time. o When weather is anticipated to pass. o For customers only: Impacted addresses. o For customers only: Links to the PSPS emergency website with CRC information, and resources for AFN customers, including but not limited to information on the MBL Program, Meals on Wheels, language support, and the PBP. • Sent notifications to MBL customers, including tenants of master metered accounts, and SIV customers. See Section 5.3 for more information regarding MBL Program notifications. Customer notifications are provided in English, with information on how to receive PSPS information in translated languages. Customers with their language preference selected in their PG&E accounts received in-language (translated) notifications. Public Safety Partner notifications are provided in English.
| WEATHER “ALL-CLEAR”/ETOR UPDATE NOTIFICATION: Immediately before re-energization begins | Public Safety Partners, CBOs, and All Customers (including MBL and SIV customers) | After weather conditions had passed and areas were deemed safe to begin patrols and restoration, we completed the following: • Submitted a PSPS State Notification Form to Cal OES and sent an e-mail to the CPUC notifying them that PG&E is initiating re-energization patrols. • Sent notifications to other Public Safety Partners and customers, via call, text message and e-mail, which included the ETOR. • Sent “update” notifications to customers if their ETOR changed. Two ways that an ETOR may change include: o New field or meteorology conditions. o Damage found during patrols and repair was needed. Customer notifications are provided in English, with information on how to receive PSPS information in translated languages. Customers with their language preference selected in their PG&E accounts received in-language (translated) notifications. Public Safety Partner notifications are provided in English.
| RESTORATION NOTIFICATION: When re-energization is complete | Public Safety Partners, CBOs, and All Customers (including MBL and SIV customers) | Once all customers were restored, we completed the following: • Submitted the final PSPS State Notification Form to Cal OES. • Sent an e-mail to the CPUC confirming restoration of PSPS outages and reclassification of customers if applicable. • Sent a notification to Public Safety Partners via call, text, and e-mail. Once customers, including MBL and SIV customers, were restored, they received automated notifications via call, text, and e-mail. Customer notifications are provided in English, with information on how to receive PSPS information in translated languages. Customers with their language preference selected in their PG&E accounts received in-language (translated) notifications. Public Safety Partner notifications are provided in English.
1 D.21-06-034, Appendix A, page A9, Section G. MBL Program and AFN Communities, No. 4, Each electric investor-owned utility must provide proactive notification and impacted zip code information to paratransit agencies that may serve all the known transit- or paratransit-dependent persons that may need access to a CRC during a PSPS.
2 Other Public Safety Partners refers to first/emergency responders at the local, state, and federal level, water, wastewater, and communication service providers, affected CCAs, publicly owned utilities/electrical cooperatives, the CPUC, the California Governor’s Office of Emergency Services, and the CAL FIRE.
3 See PG&E’s 2026 AFN Plan for more information about the PBP Program.

## Table 4
#VALUE!
Table 4: Notification Timeline Summary
| Jurisdiction or Circuit Type | Jurisdiction or Circuit Name | Notification Requirement | Time of First Notification (PDT) | PG&E Remarks
| County | Alameda | 48-72 Hour Advance Notification (Priority) | See PG&E remark. | As explained in Table 6A: due to changes in forecasted weather, this jurisdiction entered into scope after this notification window had passed. Therefore, it was not possible for the agency entities within this jurisdiction to receive Priority Notifications.
| County | Alameda | 24-48 Hour Advance Notification (Watch) | 2026-05-15 17:28
| County | Alameda | 1-4 Hour Imminent Notification | 2026-05-17 03:45
| County | Alameda | At De-energization Initiation | 2026-05-17 13:04
| County | Alameda | Immediately Before Re-energization | 2026-05-18 08:14
| County | Alameda | When Re-energization is Complete | 2026-05-18 14:16
| County | Colusa | 48-72 Hour Advance Notification (Priority) | 2026-05-14 22:45
| County | Colusa | 24-48 Hour Advance Notification (Watch) | 2026-05-15 17:28
| County | Colusa | 1-4 Hour Imminent Notification | 2026-05-17 02:34
| County | Colusa | At De-energization Initiation | 2026-05-17 06:19
| County | Colusa | Immediately Before Re-energization | 2026-05-18 09:37
| County | Colusa | When Re-energization is Complete | 2026-05-19 11:53 | As explained in Table 6G: the agency entities in this jurisdiction received a delayed notification after restoration was complete due to delay in performing a manual categorization step. The delayed notification timestamp is reported here.
| County | Contra Costa | 48-72 Hour Advance Notification (Priority) | See PG&E remark. | As explained in Table 6A: due to changes in forecasted weather, this jurisdiction entered into scope after this notification window had passed. Therefore, it was not possible for the agency entities within this jurisdiction to receive Priority Notifications.
| County | Contra Costa | 24-48 Hour Advance Notification (Watch) | 2026-05-15 17:28
| County | Contra Costa | 1-4 Hour Imminent Notification | 2026-05-17 03:45
| County | Contra Costa | At De-energization Initiation | 2026-05-17 13:10
| County | Contra Costa | Immediately Before Re-energization | 2026-05-18 08:59
| County | Contra Costa | When Re-energization is Complete | 2026-05-18 16:02
| County | Fresno | 48-72 Hour Advance Notification (Priority) | See PG&E remark. | As explained in Table 6A: due to changes in forecasted weather, this jurisdiction entered into scope after this notification window had passed. Therefore, it was not possible for the agency entities within this jurisdiction to receive Priority Notifications.
| County | Fresno | 24-48 Hour Advance Notification (Watch) | 2026-05-15 17:28
| County | Fresno | 1-4 Hour Imminent Notification | 2026-05-17 03:45
| County | Fresno | At De-energization Initiation | 2026-05-17 13:57
| County | Fresno | Immediately Before Re-energization | 2026-05-18 07:59
| County | Fresno | When Re-energization is Complete | 2026-05-19 11:56 | As explained in Table 6G: the agency entities in this jurisdiction received a delayed notification after restoration was complete due to delay in performing a manual categorization step. The delayed notification timestamp is reported here.
| County | Glenn | 48-72 Hour Advance Notification (Priority) | 2026-05-14 22:45
| County | Glenn | 24-48 Hour Advance Notification (Watch) | 2026-05-15 17:28
| County | Glenn | 1-4 Hour Imminent Notification | 2026-05-17 02:34
| County | Glenn | At De-energization Initiation | 2026-05-17 06:22
| County | Glenn | Immediately Before Re-energization | 2026-05-18 12:08
| County | Glenn | When Re-energization is Complete | 2026-05-19 11:58 | As explained in Table 6G: the agency entities in this jurisdiction received a delayed notification after restoration was complete due to delay in performing a manual categorization step. The delayed notification timestamp is reported here.
| County | Lake | 48-72 Hour Advance Notification (Priority) | 2026-05-14 22:45
| County | Lake | 24-48 Hour Advance Notification (Watch) | 2026-05-15 17:28
| County | Lake | 1-4 Hour Imminent Notification | 2026-05-17 03:45
| County | Lake | At De-energization Initiation | 2026-05-17 13:59
| County | Lake | Immediately Before Re-energization | 2026-05-18 15:25
| County | Lake | When Re-energization is Complete | 2026-05-18 18:24
| County | Merced | 48-72 Hour Advance Notification (Priority) | See PG&E remark. | As explained in Table 6A: due to changes in forecasted weather, this jurisdiction entered into scope after this notification window had passed. Therefore, it was not possible for the agency entities within this jurisdiction to receive Priority Notifications.
| County | Merced | 24-48 Hour Advance Notification (Watch) | 2026-05-15 17:28
| County | Merced | 1-4 Hour Imminent Notification | 2026-05-17 03:45
| County | Merced | At De-energization Initiation | 2026-05-17 15:45
| County | Merced | Immediately Before Re-energization | 2026-05-18 07:58
| County | Merced | When Re-energization is Complete | 2026-05-19 11:50 | As explained in Table 6G: the agency entities in this jurisdiction received a delayed notification after restoration was complete due to delay in performing a manual categorization step. The delayed notification timestamp is reported here.
| County | Napa | 48-72 Hour Advance Notification (Priority) | 2026-05-14 22:45
| County | Napa | 24-48 Hour Advance Notification (Watch) | 2026-05-15 17:28
| County | Napa | 1-4 Hour Imminent Notification | 2026-05-17 03:45
| County | Napa | At De-energization Initiation | 2026-05-17 11:07
| County | Napa | Immediately Before Re-energization | 2026-05-18 15:25
| County | Napa | When Re-energization is Complete | 2026-05-18 16:25
| County | San Benito | 48-72 Hour Advance Notification (Priority) | See PG&E remark. | As explained in Table 6A: due to changes in forecasted weather, this jurisdiction entered into scope after this notification window had passed. Therefore, it was not possible for the agency entities within this jurisdiction to receive Priority Notifications.
| County | San Benito | 24-48 Hour Advance Notification (Watch) | 2026-05-15 17:28
| County | San Benito | 1-4 Hour Imminent Notification | 2026-05-17 03:45
| County | San Benito | At De-energization Initiation | 2026-05-17 16:41
| County | San Benito | Immediately Before Re-energization | 2026-05-18 08:02
| County | San Benito | When Re-energization is Complete | 2026-05-18 13:50
| County | San Joaquin | 48-72 Hour Advance Notification (Priority) | See PG&E remark. | As explained in Table 6A: due to changes in forecasted weather, this jurisdiction entered into scope after this notification window had passed. Therefore, it was not possible for the agency entities within this jurisdiction to receive Priority Notifications.
| County | San Joaquin | 24-48 Hour Advance Notification (Watch) | 2026-05-15 17:28
| County | San Joaquin | 1-4 Hour Imminent Notification | 2026-05-17 03:45
| County | San Joaquin | At De-energization Initiation | 2026-05-17 11:33
| County | San Joaquin | Immediately Before Re-energization | 2026-05-18 08:14
| County | San Joaquin | When Re-energization is Complete | 2026-05-19 11:55 | As explained in Table 6G: the agency entities in this jurisdiction received a delayed notification after restoration was complete due to delay in performing a manual categorization step. The delayed notification timestamp is reported here.
| County | Solano | 48-72 Hour Advance Notification (Priority) | See PG&E remark. | As explained in Table 6A: due to changes in forecasted weather, this jurisdiction entered into scope after this notification window had passed. Therefore, it was not possible for the agency entities within this jurisdiction to receive Priority Notifications.
| County | Solano | 24-48 Hour Advance Notification (Watch) | 2026-05-15 17:28
| County | Solano | 1-4 Hour Imminent Notification | 2026-05-17 03:45
| County | Solano | At De-energization Initiation | 2026-05-17 11:07
| County | Solano | Immediately Before Re-energization | 2026-05-18 15:25
| County | Solano | When Re-energization is Complete | 2026-05-18 16:28
| County | Sonoma | 48-72 Hour Advance Notification (Priority) | 2026-05-14 22:45
| County | Sonoma | 24-48 Hour Advance Notification (Watch) | 2026-05-15 17:28
| County | Sonoma | 1-4 Hour Imminent Notification | 2026-05-17 03:45
| County | Sonoma | At De-energization Initiation | 2026-05-17 13:59
| County | Sonoma | Immediately Before Re-energization | 2026-05-18 15:25
| County | Sonoma | When Re-energization is Complete | 2026-05-18 18:24
| County | Stanislaus | 48-72 Hour Advance Notification (Priority) | See PG&E remark. | As explained in Table 6A: due to changes in forecasted weather, this jurisdiction entered into scope after this notification window had passed. Therefore, it was not possible for the agency entities within this jurisdiction to receive Priority Notifications.
| County | Stanislaus | 24-48 Hour Advance Notification (Watch) | 2026-05-15 17:28
| County | Stanislaus | 1-4 Hour Imminent Notification | 2026-05-17 03:45
| County | Stanislaus | At De-energization Initiation | 2026-05-17 11:33
| County | Stanislaus | Immediately Before Re-energization | 2026-05-18 09:24
| County | Stanislaus | When Re-energization is Complete | 2026-05-18 13:13
| County | Tehama | 48-72 Hour Advance Notification (Priority) | 2026-05-14 22:45
| County | Tehama | 24-48 Hour Advance Notification (Watch) | 2026-05-15 17:28
| County | Tehama | 1-4 Hour Imminent Notification | 2026-05-17 02:34
| County | Tehama | At De-energization Initiation | 2026-05-17 06:22
| County | Tehama | Immediately Before Re-energization | 2026-05-18 10:13
| County | Tehama | When Re-energization is Complete | 2026-05-18 15:35
| County | Yolo | 48-72 Hour Advance Notification (Priority) | 2026-05-14 22:45
| County | Yolo | 24-48 Hour Advance Notification (Watch) | 2026-05-15 17:28
| County | Yolo | 1-4 Hour Imminent Notification | 2026-05-17 03:45
| County | Yolo | At De-energization Initiation | 2026-05-17 11:12
| County | Yolo | Immediately Before Re-energization | 2026-05-18 09:36
| County | Yolo | When Re-energization is Complete | 2026-05-18 20:17
| Incorporated City | Tracy | 48-72 Hour Advance Notification (Priority) | See PG&E remark. | As explained in Table 6A: due to changes in forecasted weather, this jurisdiction entered into scope after this notification window had passed. Therefore, it was not possible for the agency entities within this jurisdiction to receive Priority Notifications.
| Incorporated City | Tracy | 24-48 Hour Advance Notification (Watch) | 2026-05-15 17:28
| Incorporated City | Tracy | Cancellation Notification | 2026-05-16 14:47
| Tribe | Cortina Rancheria | 48-72 Hour Advance Notification (Priority) | 2026-05-14 22:45
| Tribe | Cortina Rancheria | 24-48 Hour Advance Notification (Watch) | 2026-05-15 17:28
| Tribe | Cortina Rancheria | 1-4 Hour Imminent Notification | 2026-05-17 03:45
| Tribe | Cortina Rancheria | At De-energization Initiation | 2026-05-17 11:16
| Tribe | Cortina Rancheria | Immediately Before Re-energization | 2026-05-18 09:38
| Tribe | Cortina Rancheria | When Re-energization is Complete | 2026-05-18 11:21
| Tribe | Grindstone Rancheria | 48-72 Hour Advance Notification (Priority) | 2026-05-14 22:45
| Tribe | Grindstone Rancheria | 24-48 Hour Advance Notification (Watch) | 2026-05-15 17:28
| Tribe | Grindstone Rancheria | 1-4 Hour Imminent Notification | 2026-05-17 02:34
| Tribe | Grindstone Rancheria | At De-energization Initiation | 2026-05-17 06:28
| Tribe | Grindstone Rancheria | Immediately Before Re-energization | 2026-05-18 12:09
| Tribe | Grindstone Rancheria | When Re-energization is Complete | 2026-05-18 16:12
| CCA | Alameda County, East Bay Community Energy | 48-72 Hour Advance Notification (Priority) | See PG&E remark. | As explained in Table 6A: due to changes in forecasted weather, this jurisdiction entered into scope after this notification window had passed. Therefore, it was not possible for the agency entities within this jurisdiction to receive Priority Notifications.
| CCA | Alameda County, East Bay Community Energy | 24-48 Hour Advance Notification (Watch) | 2026-05-15 17:28
| CCA | Alameda County, East Bay Community Energy | 1-4 Hour Imminent Notification | 2026-05-17 03:45
| CCA | Contra Costa County, MCE Clean Energy | 48-72 Hour Advance Notification (Priority) | See PG&E remark. | As explained in Table 6A: due to changes in forecasted weather, this jurisdiction entered into scope after this notification window had passed. Therefore, it was not possible for the agency entities within this jurisdiction to receive Priority Notifications.
| CCA | Contra Costa County, MCE Clean Energy | 24-48 Hour Advance Notification (Watch) | 2026-05-15 17:28
| CCA | Contra Costa County, MCE Clean Energy | 1-4 Hour Imminent Notification | 2026-05-17 03:45
| CCA | Napa County, MCE Clean Energy | 48-72 Hour Advance Notification (Priority) | 2026-05-14 22:45
| CCA | Napa County, MCE Clean Energy | 24-48 Hour Advance Notification (Watch) | 2026-05-15 17:28
| CCA | Napa County, MCE Clean Energy | 1-4 Hour Imminent Notification | 2026-05-17 03:45
| CCA | San Benito County, Monterey Bay Community Power | 48-72 Hour Advance Notification (Priority) | See PG&E remark. | As explained in Table 6A: due to changes in forecasted weather, this jurisdiction entered into scope after this notification window had passed. Therefore, it was not possible for the agency entities within this jurisdiction to receive Priority Notifications.
| CCA | San Benito County, Monterey Bay Community Power | 24-48 Hour Advance Notification (Watch) | 2026-05-15 17:28
| CCA | San Benito County, Monterey Bay Community Power | 1-4 Hour Imminent Notification | 2026-05-17 03:45
| CCA | Solano County, MCE Clean Energy | 48-72 Hour Advance Notification (Priority) | See PG&E remark. | As explained in Table 6A: due to changes in forecasted weather, this jurisdiction entered into scope after this notification window had passed. Therefore, it was not possible for the agency entities within this jurisdiction to receive Priority Notifications.
| CCA | Solano County, MCE Clean Energy | 24-48 Hour Advance Notification (Watch) | 2026-05-15 17:28
| CCA | Solano County, MCE Clean Energy | 1-4 Hour Imminent Notification | 2026-05-17 03:45
| CCA | Sonoma County, Sonoma Clean Power | 48-72 Hour Advance Notification (Priority) | 2026-05-14 22:45
| CCA | Sonoma County, Sonoma Clean Power | 24-48 Hour Advance Notification (Watch) | 2026-05-15 17:28
| CCA | Sonoma County, Sonoma Clean Power | 1-4 Hour Imminent Notification | 2026-05-17 03:45
| CCA | Yolo County, Valley Clean Energy | 48-72 Hour Advance Notification (Priority) | 2026-05-14 22:45
| CCA | Yolo County, Valley Clean Energy | 24-48 Hour Advance Notification (Watch) | 2026-05-15 17:28
| CCA | Yolo County, Valley Clean Energy | 1-4 Hour Imminent Notification | 2026-05-17 03:45
| Distribution Circuit | BRENTWOOD 2105 | 48-72 Hour Advance Notification (Priority) | See PG&E remark. | As explained in Table 6A: due to changes in forecasted weather, all CFI on this circuit entered into scope after this notification window had passed. Therefore, it was not possible for the CFI on this circuit to receive Priority Notifications.
| Distribution Circuit | BRENTWOOD 2105 | 24-48 Hour Advance Notification (Watch) | 2026-05-15 18:30
| Distribution Circuit | BRENTWOOD 2105 | 1-4 Hour Imminent Notification | 2026-05-17 03:56
| Distribution Circuit | BRENTWOOD 2105 | At De-energization Initiation | 2026-05-17 13:11
| Distribution Circuit | BRENTWOOD 2105 | Immediately Before Re-energization | 2026-05-18 09:02
| Distribution Circuit | BRENTWOOD 2105 | When Re-energization is Complete | 2026-05-18 13:38
| Distribution Circuit | CALISTOGA 1101 | 48-72 Hour Advance Notification (Priority) | 2026-05-14 23:45
| Distribution Circuit | CALISTOGA 1101 | 24-48 Hour Advance Notification (Watch) | 2026-05-15 18:30
| Distribution Circuit | CALISTOGA 1101 | 1-4 Hour Imminent Notification | 2026-05-17 03:56
| Distribution Circuit | CALISTOGA 1101 | At De-energization Initiation | 2026-05-17 13:59
| Distribution Circuit | CALISTOGA 1101 | Immediately Before Re-energization | See PG&E remark. | As explained in Table 6F: none of the customers on this circuit were notified immediately before re-energization due to a gap in coordination between the local emergency centers.
| Distribution Circuit | CALISTOGA 1101 | When Re-energization is Complete | 2026-05-18 14:15
| Distribution Circuit | CALPINE 1144 | 48-72 Hour Advance Notification (Priority) | 2026-05-14 23:45
| Distribution Circuit | CALPINE 1144 | 24-48 Hour Advance Notification (Watch) | 2026-05-15 18:30
| Distribution Circuit | CALPINE 1144 | 1-4 Hour Imminent Notification | 2026-05-17 04:16
| Distribution Circuit | CALPINE 1144 | At De-energization Initiation | 2026-05-17 14:32
| Distribution Circuit | CALPINE 1144 | Immediately Before Re-energization | 2026-05-18 15:16
| Distribution Circuit | CALPINE 1144 | When Re-energization is Complete | 2026-05-18 18:24
| Distribution Circuit | CALPINE 1146 | 48-72 Hour Advance Notification (Priority) | 2026-05-14 23:45
| Distribution Circuit | CALPINE 1146 | 24-48 Hour Advance Notification (Watch) | 2026-05-15 18:30
| Distribution Circuit | CALPINE 1146 | 1-4 Hour Imminent Notification | 2026-05-17 04:16
| Distribution Circuit | CALPINE 1146 | At De-energization Initiation | 2026-05-17 14:29
| Distribution Circuit | CALPINE 1146 | Immediately Before Re-energization | 2026-05-18 15:16
| Distribution Circuit | CALPINE 1146 | When Re-energization is Complete | 2026-05-18 18:25
| Distribution Circuit | CANTUA 1102 | 48-72 Hour Advance Notification (Priority) | See PG&E remark. | As explained in Table 6A: due to changes in forecasted weather, all CFI on this circuit entered into scope after this notification window had passed. Therefore, it was not possible for the CFI on this circuit to receive Priority Notifications.
| Distribution Circuit | CANTUA 1102 | 24-48 Hour Advance Notification (Watch) | 2026-05-15 18:30
| Distribution Circuit | CANTUA 1102 | 1-4 Hour Imminent Notification | 2026-05-17 03:58
| Distribution Circuit | CANTUA 1102 | At De-energization Initiation | 2026-05-17 13:57
| Distribution Circuit | CANTUA 1102 | Immediately Before Re-energization | 2026-05-18 08:20
| Distribution Circuit | CANTUA 1102 | When Re-energization is Complete | 2026-05-18 11:29
| Distribution Circuit | CANTUA 1102 | Cancellation Notification | 2026-05-16 15:26
| Distribution Circuit | CANTUA 1103 | 48-72 Hour Advance Notification (Priority) | See PG&E remark. | As explained in Table 6A: due to changes in forecasted weather, all CFI on this circuit entered into scope after this notification window had passed. Therefore, it was not possible for the CFI on this circuit to receive Priority Notifications.
| Distribution Circuit | CANTUA 1103 | 24-48 Hour Advance Notification (Watch) | 2026-05-15 18:30
| Distribution Circuit | CANTUA 1103 | 1-4 Hour Imminent Notification | 2026-05-17 03:56
| Distribution Circuit | CANTUA 1103 | At De-energization Initiation | 2026-05-17 14:14
| Distribution Circuit | CANTUA 1103 | Immediately Before Re-energization | 2026-05-18 08:20
| Distribution Circuit | CANTUA 1103 | When Re-energization is Complete | 2026-05-18 10:49
| Distribution Circuit | CARBONA 1101 | 48-72 Hour Advance Notification (Priority) | See PG&E remark. | As explained in Table 6A: due to changes in forecasted weather, all CFI on this circuit entered into scope after this notification window had passed. Therefore, it was not possible for the CFI on this circuit to receive Priority Notifications.
| Distribution Circuit | CARBONA 1101 | 24-48 Hour Advance Notification (Watch) | 2026-05-15 18:30
| Distribution Circuit | CARBONA 1101 | 1-4 Hour Imminent Notification | 2026-05-17 03:56
| Distribution Circuit | CARBONA 1101 | At De-energization Initiation | 2026-05-17 12:00
| Distribution Circuit | CARBONA 1101 | Immediately Before Re-energization | 2026-05-18 08:14
| Distribution Circuit | CARBONA 1101 | When Re-energization is Complete | 2026-05-18 09:39
| Distribution Circuit | CARBONA 1101 | Cancellation Notification | 2026-05-16 15:26
| Distribution Circuit | CAYETANO 2109 | 48-72 Hour Advance Notification (Priority) | See PG&E remark. | As explained in Table 6A: due to changes in forecasted weather, all CFI on this circuit entered into scope after this notification window had passed. Therefore, it was not possible for the CFI on this circuit to receive Priority Notifications.
| Distribution Circuit | CAYETANO 2109 | 24-48 Hour Advance Notification (Watch) | 2026-05-15 18:30
| Distribution Circuit | CAYETANO 2109 | 1-4 Hour Imminent Notification | 2026-05-17 03:56
| Distribution Circuit | CAYETANO 2109 | At De-energization Initiation | 2026-05-17 13:09
| Distribution Circuit | CAYETANO 2109 | Immediately Before Re-energization | 2026-05-18 13:58
| Distribution Circuit | CAYETANO 2109 | When Re-energization is Complete | 2026-05-18 14:16
| Distribution Circuit | COALINGA NO 2 1105 | 48-72 Hour Advance Notification (Priority) | See PG&E remark. | As explained in Table 6A: due to changes in forecasted weather, all CFI on this circuit entered into scope after this notification window had passed. Therefore, it was not possible for the CFI on this circuit to receive Priority Notifications.
| Distribution Circuit | COALINGA NO 2 1105 | 24-48 Hour Advance Notification (Watch) | 2026-05-15 18:30
| Distribution Circuit | COALINGA NO 2 1105 | 1-4 Hour Imminent Notification | 2026-05-17 03:56
| Distribution Circuit | COALINGA NO 2 1105 | At De-energization Initiation | 2026-05-17 14:21
| Distribution Circuit | COALINGA NO 2 1105 | Immediately Before Re-energization | 2026-05-18 08:20
| Distribution Circuit | COALINGA NO 2 1105 | When Re-energization is Complete | 2026-05-18 10:23
| Distribution Circuit | COALINGA NO 2 1105 | Cancellation Notification | 2026-05-16 23:57
| Distribution Circuit | COALINGA NO 2 1107 | 48-72 Hour Advance Notification (Priority) | See PG&E remark. | None of the customers in scope or de-energized on this circuit were CFI, so none of them required Priority notifications.
| Distribution Circuit | COALINGA NO 2 1107 | 24-48 Hour Advance Notification (Watch) | 2026-05-15 18:30
| Distribution Circuit | COALINGA NO 2 1107 | 1-4 Hour Imminent Notification | 2026-05-17 03:58
| Distribution Circuit | COALINGA NO 2 1107 | At De-energization Initiation | 2026-05-17 14:07
| Distribution Circuit | COALINGA NO 2 1107 | Immediately Before Re-energization | 2026-05-18 08:20
| Distribution Circuit | COALINGA NO 2 1107 | When Re-energization is Complete | 2026-05-18 10:40
| Distribution Circuit | CORNING 1101 | 48-72 Hour Advance Notification (Priority) | 2026-05-14 23:45
| Distribution Circuit | CORNING 1101 | 24-48 Hour Advance Notification (Watch) | 2026-05-15 18:30
| Distribution Circuit | CORNING 1101 | 1-4 Hour Imminent Notification | 2026-05-17 03:56
| Distribution Circuit | CORNING 1101 | At De-energization Initiation | 2026-05-17 10:34
| Distribution Circuit | CORNING 1101 | Immediately Before Re-energization | 2026-05-18 10:27
| Distribution Circuit | CORNING 1101 | When Re-energization is Complete | 2026-05-18 11:22
| Distribution Circuit | CORNING 1102 | 48-72 Hour Advance Notification (Priority) | 2026-05-14 23:45
| Distribution Circuit | CORNING 1102 | 24-48 Hour Advance Notification (Watch) | 2026-05-15 18:30
| Distribution Circuit | CORNING 1102 | 1-4 Hour Imminent Notification | 2026-05-17 03:56
| Distribution Circuit | CORNING 1102 | At De-energization Initiation | 2026-05-17 10:35
| Distribution Circuit | CORNING 1102 | Immediately Before Re-energization | 2026-05-18 10:13
| Distribution Circuit | CORNING 1102 | When Re-energization is Complete | 2026-05-18 11:36
| Distribution Circuit | CORTINA 1101 | 48-72 Hour Advance Notification (Priority) | 2026-05-14 23:45
| Distribution Circuit | CORTINA 1101 | 24-48 Hour Advance Notification (Watch) | 2026-05-15 18:30
| Distribution Circuit | CORTINA 1101 | 1-4 Hour Imminent Notification | 2026-05-17 03:56
| Distribution Circuit | CORTINA 1101 | At De-energization Initiation | 2026-05-17 11:16
| Distribution Circuit | CORTINA 1101 | Immediately Before Re-energization | 2026-05-18 09:38
| Distribution Circuit | CORTINA 1101 | When Re-energization is Complete | 2026-05-18 11:18
| Distribution Circuit | DUNNIGAN 1103 | 48-72 Hour Advance Notification (Priority) | See PG&E remark. | None of the customers in scope or de-energized on this circuit were CFI, so none of them required Priority notifications.
| Distribution Circuit | DUNNIGAN 1103 | 24-48 Hour Advance Notification (Watch) | 2026-05-15 18:30
| Distribution Circuit | DUNNIGAN 1103 | 1-4 Hour Imminent Notification | 2026-05-17 03:57
| Distribution Circuit | DUNNIGAN 1103 | At De-energization Initiation | 2026-05-17 11:09
| Distribution Circuit | DUNNIGAN 1103 | Immediately Before Re-energization | 2026-05-18 09:37
| Distribution Circuit | DUNNIGAN 1103 | When Re-energization is Complete | 2026-05-18 10:59
| Distribution Circuit | ELK CREEK 1101 | 48-72 Hour Advance Notification (Priority) | 2026-05-14 23:45
| Distribution Circuit | ELK CREEK 1101 | 24-48 Hour Advance Notification (Watch) | 2026-05-15 18:30
| Distribution Circuit | ELK CREEK 1101 | 1-4 Hour Imminent Notification | 2026-05-17 02:49
| Distribution Circuit | ELK CREEK 1101 | At De-energization Initiation | 2026-05-17 06:29
| Distribution Circuit | ELK CREEK 1101 | Immediately Before Re-energization | 2026-05-18 12:09
| Distribution Circuit | ELK CREEK 1101 | When Re-energization is Complete | 2026-05-18 13:37
| Distribution Circuit | GLENN 1101 | 48-72 Hour Advance Notification (Priority) | 2026-05-14 23:45
| Distribution Circuit | GLENN 1101 | 24-48 Hour Advance Notification (Watch) | 2026-05-15 18:30
| Distribution Circuit | GLENN 1101 | 1-4 Hour Imminent Notification | 2026-05-17 02:49
| Distribution Circuit | GLENN 1101 | At De-energization Initiation | 2026-05-17 06:23
| Distribution Circuit | GLENN 1101 | Immediately Before Re-energization | 2026-05-18 12:08
| Distribution Circuit | GLENN 1101 | When Re-energization is Complete | 2026-05-18 14:26
| Distribution Circuit | GUSTINE 1102 | 48-72 Hour Advance Notification (Priority) | See PG&E remark. | None of the customers in scope or de-energized on this circuit were CFI, so none of them required Priority notifications.
| Distribution Circuit | GUSTINE 1102 | 24-48 Hour Advance Notification (Watch) | 2026-05-15 18:30
| Distribution Circuit | GUSTINE 1102 | 1-4 Hour Imminent Notification | 2026-05-17 03:57
| Distribution Circuit | GUSTINE 1102 | At De-energization Initiation | 2026-05-17 15:45
| Distribution Circuit | GUSTINE 1102 | Immediately Before Re-energization | 2026-05-18 07:58
| Distribution Circuit | GUSTINE 1102 | When Re-energization is Complete | 2026-05-18 12:03
| Distribution Circuit | HAMMONDS 1102 | 48-72 Hour Advance Notification (Priority) | See PG&E remark. | As explained in Table 6A: due to changes in forecasted weather, all CFI on this circuit entered into scope after this notification window had passed. Therefore, it was not possible for the CFI on this circuit to receive Priority Notifications.
| Distribution Circuit | HAMMONDS 1102 | 24-48 Hour Advance Notification (Watch) | 2026-05-15 18:30
| Distribution Circuit | HAMMONDS 1102 | 1-4 Hour Imminent Notification | 2026-05-17 03:56
| Distribution Circuit | HAMMONDS 1102 | At De-energization Initiation | 2026-05-17 16:28
| Distribution Circuit | HAMMONDS 1102 | Immediately Before Re-energization | 2026-05-18 07:59
| Distribution Circuit | HAMMONDS 1102 | When Re-energization is Complete | 2026-05-18 12:16
| Distribution Circuit | HERDLYN 1102 | 48-72 Hour Advance Notification (Priority) | See PG&E remark. | None of the customers in scope or de-energized on this circuit were CFI, so none of them required Priority notifications.
| Distribution Circuit | HERDLYN 1102 | 24-48 Hour Advance Notification (Watch) | 2026-05-15 18:30
| Distribution Circuit | HERDLYN 1102 | 1-4 Hour Imminent Notification | 2026-05-17 03:57
| Distribution Circuit | HERDLYN 1102 | At De-energization Initiation | 2026-05-17 13:09
| Distribution Circuit | HERDLYN 1102 | Immediately Before Re-energization | 2026-05-18 13:00
| Distribution Circuit | HERDLYN 1102 | When Re-energization is Complete | 2026-05-18 13:38
| Distribution Circuit | LOGAN CREEK 2102 | 48-72 Hour Advance Notification (Priority) | 2026-05-14 23:45
| Distribution Circuit | LOGAN CREEK 2102 | 24-48 Hour Advance Notification (Watch) | 2026-05-15 18:30
| Distribution Circuit | LOGAN CREEK 2102 | 1-4 Hour Imminent Notification | 2026-05-17 02:49
| Distribution Circuit | LOGAN CREEK 2102 | At De-energization Initiation | 2026-05-17 06:36
| Distribution Circuit | LOGAN CREEK 2102 | Immediately Before Re-energization | 2026-05-18 12:10
| Distribution Circuit | LOGAN CREEK 2102 | When Re-energization is Complete | 2026-05-18 13:27
| Distribution Circuit | MADISON 2101 | 48-72 Hour Advance Notification (Priority) | 2026-05-14 23:45
| Distribution Circuit | MADISON 2101 | 24-48 Hour Advance Notification (Watch) | 2026-05-15 18:30
| Distribution Circuit | MADISON 2101 | 1-4 Hour Imminent Notification | 2026-05-17 03:56
| Distribution Circuit | MADISON 2101 | At De-energization Initiation | 2026-05-17 11:12
| Distribution Circuit | MADISON 2101 | Immediately Before Re-energization | 2026-05-18 09:35
| Distribution Circuit | MADISON 2101 | When Re-energization is Complete | 2026-05-18 11:04
| Distribution Circuit | MAXWELL 1102 | 48-72 Hour Advance Notification (Priority) | 2026-05-14 23:45
| Distribution Circuit | MAXWELL 1102 | 24-48 Hour Advance Notification (Watch) | 2026-05-15 18:30
| Distribution Circuit | MAXWELL 1102 | 1-4 Hour Imminent Notification | 2026-05-17 02:49
| Distribution Circuit | MAXWELL 1102 | At De-energization Initiation | 2026-05-17 06:19
| Distribution Circuit | MAXWELL 1102 | Immediately Before Re-energization | 2026-05-18 12:12
| Distribution Circuit | MAXWELL 1102 | When Re-energization is Complete | 2026-05-18 15:37
| Distribution Circuit | MAXWELL 1105 | 48-72 Hour Advance Notification (Priority) | 2026-05-14 23:45
| Distribution Circuit | MAXWELL 1105 | 24-48 Hour Advance Notification (Watch) | 2026-05-15 18:30
| Distribution Circuit | MAXWELL 1105 | 1-4 Hour Imminent Notification | 2026-05-17 02:49
| Distribution Circuit | MAXWELL 1105 | At De-energization Initiation | 2026-05-17 06:23
| Distribution Circuit | MAXWELL 1105 | Immediately Before Re-energization | 2026-05-18 12:13
| Distribution Circuit | MAXWELL 1105 | When Re-energization is Complete | 2026-05-18 16:34
| Distribution Circuit | MONTICELLO 1101 | 48-72 Hour Advance Notification (Priority) | 2026-05-14 23:45
| Distribution Circuit | MONTICELLO 1101 | 24-48 Hour Advance Notification (Watch) | 2026-05-15 18:30
| Distribution Circuit | MONTICELLO 1101 | 1-4 Hour Imminent Notification | 2026-05-17 04:16
| Distribution Circuit | MONTICELLO 1101 | At De-energization Initiation | 2026-05-17 11:12
| Distribution Circuit | MONTICELLO 1101 | Immediately Before Re-energization | 2026-05-18 11:51
| Distribution Circuit | MONTICELLO 1101 | When Re-energization is Complete | 2026-05-18 20:17
| Distribution Circuit | NORTH DUBLIN 2103 | 48-72 Hour Advance Notification (Priority) | See PG&E remark. | As explained in Table 6A: due to changes in forecasted weather, all CFI on this circuit entered into scope after this notification window had passed. Therefore, it was not possible for the CFI on this circuit to receive Priority Notifications.
| Distribution Circuit | NORTH DUBLIN 2103 | 24-48 Hour Advance Notification (Watch) | 2026-05-15 18:30
| Distribution Circuit | NORTH DUBLIN 2103 | 1-4 Hour Imminent Notification | 2026-05-17 03:56
| Distribution Circuit | NORTH DUBLIN 2103 | At De-energization Initiation | 2026-05-17 13:14
| Distribution Circuit | NORTH DUBLIN 2103 | Immediately Before Re-energization | 2026-05-18 13:37
| Distribution Circuit | NORTH DUBLIN 2103 | When Re-energization is Complete | 2026-05-18 15:16
| Distribution Circuit | PANOCHE 1103 | 48-72 Hour Advance Notification (Priority) | See PG&E remark. | As explained in Table 6A: due to changes in forecasted weather, all CFI on this circuit entered into scope after this notification window had passed. Therefore, it was not possible for the CFI on this circuit to receive Priority Notifications.
| Distribution Circuit | PANOCHE 1103 | 24-48 Hour Advance Notification (Watch) | 2026-05-15 18:30
| Distribution Circuit | PANOCHE 1103 | 1-4 Hour Imminent Notification | 2026-05-17 03:56
| Distribution Circuit | PANOCHE 1103 | At De-energization Initiation | 2026-05-17 16:41
| Distribution Circuit | PANOCHE 1103 | Immediately Before Re-energization | 2026-05-18 08:02
| Distribution Circuit | PANOCHE 1103 | When Re-energization is Complete | 2026-05-18 10:08
| Distribution Circuit | SANTA NELLA 1103 | 48-72 Hour Advance Notification (Priority) | See PG&E remark. | As explained in Table 6A: due to changes in forecasted weather, all CFI on this circuit entered into scope after this notification window had passed. Therefore, it was not possible for the CFI on this circuit to receive Priority Notifications.
| Distribution Circuit | SANTA NELLA 1103 | 24-48 Hour Advance Notification (Watch) | 2026-05-15 18:30
| Distribution Circuit | SANTA NELLA 1103 | 1-4 Hour Imminent Notification | 2026-05-17 03:56
| Distribution Circuit | SANTA NELLA 1103 | At De-energization Initiation | 2026-05-17 16:07
| Distribution Circuit | SANTA NELLA 1103 | Immediately Before Re-energization | 2026-05-18 07:59
| Distribution Circuit | SANTA NELLA 1103 | When Re-energization is Complete | 2026-05-18 09:11
| Distribution Circuit | SANTA NELLA 1104 | 48-72 Hour Advance Notification (Priority) | See PG&E remark. | As explained in Table 6A: due to changes in forecasted weather, all CFI on this circuit entered into scope after this notification window had passed. Therefore, it was not possible for the CFI on this circuit to receive Priority Notifications.
| Distribution Circuit | SANTA NELLA 1104 | 24-48 Hour Advance Notification (Watch) | 2026-05-15 18:30
| Distribution Circuit | SANTA NELLA 1104 | 1-4 Hour Imminent Notification | 2026-05-17 03:56
| Distribution Circuit | SANTA NELLA 1104 | At De-energization Initiation | 2026-05-17 15:55
| Distribution Circuit | SANTA NELLA 1104 | Immediately Before Re-energization | 2026-05-18 07:58
| Distribution Circuit | SANTA NELLA 1104 | When Re-energization is Complete | 2026-05-18 09:38
| Distribution Circuit | VACAVILLE 1108 | 48-72 Hour Advance Notification (Priority) | See PG&E remark. | As explained in Table 6A: due to changes in forecasted weather, all CFI on this circuit entered into scope after this notification window had passed. Therefore, it was not possible for the CFI on this circuit to receive Priority Notifications.
| Distribution Circuit | VACAVILLE 1108 | 24-48 Hour Advance Notification (Watch) | 2026-05-15 18:30
| Distribution Circuit | VACAVILLE 1108 | 1-4 Hour Imminent Notification | 2026-05-17 03:56
| Distribution Circuit | VACAVILLE 1108 | At De-energization Initiation | 2026-05-17 11:07
| Distribution Circuit | VACAVILLE 1108 | Immediately Before Re-energization | 2026-05-18 15:16
| Distribution Circuit | VACAVILLE 1108 | When Re-energization is Complete | 2026-05-18 16:25
| Distribution Circuit | WESTLEY 1101 | 48-72 Hour Advance Notification (Priority) | See PG&E remark. | As explained in Table 6A: due to changes in forecasted weather, all CFI on this circuit entered into scope after this notification window had passed. Therefore, it was not possible for the CFI on this circuit to receive Priority Notifications.
| Distribution Circuit | WESTLEY 1101 | 24-48 Hour Advance Notification (Watch) | 2026-05-15 18:30
| Distribution Circuit | WESTLEY 1101 | 1-4 Hour Imminent Notification | 2026-05-17 03:56
| Distribution Circuit | WESTLEY 1101 | At De-energization Initiation | 2026-05-17 11:33
| Distribution Circuit | WESTLEY 1101 | Immediately Before Re-energization | 2026-05-18 09:27
| Distribution Circuit | WESTLEY 1101 | When Re-energization is Complete | 2026-05-18 10:22
| Distribution Circuit | WESTLEY 1103 | 48-72 Hour Advance Notification (Priority) | See PG&E remark. | As explained in Table 6A: due to changes in forecasted weather, all CFI on this circuit entered into scope after this notification window had passed. Therefore, it was not possible for the CFI on this circuit to receive Priority Notifications.
| Distribution Circuit | WESTLEY 1103 | 24-48 Hour Advance Notification (Watch) | 2026-05-15 18:30
| Distribution Circuit | WESTLEY 1103 | 1-4 Hour Imminent Notification | 2026-05-17 03:56
| Distribution Circuit | WESTLEY 1103 | At De-energization Initiation | 2026-05-17 11:33
| Distribution Circuit | WESTLEY 1103 | Immediately Before Re-energization | 2026-05-18 09:27
| Distribution Circuit | WESTLEY 1103 | When Re-energization is Complete | 2026-05-18 12:34

## Table 5
#VALUE!
Table 5: Positive Notification
| Designation | Total Number of customers | Number of Notification Attempts Made1 | Timing of Attempts | Who made the Notification Attempt | Successful Positive Notification
| MBL in scope2 | 298 | 298 | Daily | PG&E | 298
| SIV | 103 | 102 | Daily | PG&E | 100
1 Count of “Notification Attempts Made” includes doorbell rings and Live Agent phone calls.
2 Residential tenants of master-metered customers can also qualify for MBL quantities. The MBL category for the purposes of Table 5 includes MBL customers who are master meter tenants.

## Table 6
#VALUE!
Table 6: Breakdown of Notification Failure
| Notifications Sent to | Notification Failure Description | Number of Entities or Customer Account | Explanation of Failure
| Public Safety Partners excluding CFI1 | Entities who did not receive 48-to 72-hour priority notification | 64 | See Table 6A for explanations.
|  | Entities who did not receive 24-48 hour advance notification | 0 | No failures.
|  | Entities who did not receive 1-4-hour imminent notification | 0 | No failures.
|  | Entities who did not receive any notifications before de-energization | 0 | No failures.
|  | Entities who were not notified at de-energization initiation | 5 | See Table 6E for explanations.
|  | Entities who were not notified immediately before re-energization | 5 | See Table 6F for explanations.
|  | Entities who were not notified when re-energization is complete | 37 | See Table 6G for explanations.
|  | Entities who did not receive cancellation notification within two hours of the decision to cancel | 0 | No failures.
| CFI2 | Facilities who did not receive 48-72-hour priority notification | 124 | See Table 6A for explanations.
|  | Facilities who did not receive 24-48 hour advance notification | 4 | See Table 6B for explanations.
|  | Facilities who did not receive 1-4-hour imminent notification | 2 | See Table 6C for explanations.
|  | Facilities who did not receive any notifications before de-energization | 0 | No failures.
|  | Facilities who were not notified at de-energization initiation | 6 | See Table 6E for explanations.
|  | Facilities who were not notified immediately before re-energization | 9 | See Table 6F for explanations.
|  | Facilities who were not notified when re-energization is complete | 3 | See Table 6G for explanations.
|  | Facilities who did not receive cancellation notification within two hours of the decision to cancel | 0 | No failures.
| All other affected customers | Customers who did not receive 24-48-hour advance notifications | 107 | See Table 6B for explanations.
|  | Customers who did not receive 1-4-hour imminent notifications | 35 | See Table 6C for explanations.
|  | Customers who did not receive any notifications before de-energization | 25 | See Table 6D for explanations.
|  | Customers who were not notified at de-energization initiation | 111 | See Table 6E for explanations.
|  | Customers who were not notified immediately before re-energization | 34 | See Table 6F for explanations.
|  | Customers who were not notified when re-energization is complete | 45 | See Table 6G for explanations.
|  | Customers who did not receive cancellation notification within two hours of the decision to cancel | 1 | See Table 6H for explanations.
1 Only includes Tribes, cities, counties, and CCAs.
2 Includes Public Safety Partners who are CFI customers.

## Table 6A
#VALUE!
Table 6A: Explanation of Failures for Agency Entities and CFI Who Did Not Receive 48-to 72-Hour Priority Notification
| Total (Agency Entities) | Total (CFI) | Explanation
| 64 | 124 | Due to changes in forecasted weather, these agency entities and critical facilities entered into scope after this notification window had passed. Therefore, it was not possible for these agencies and customers to receive Priority Notifications.*
*PG&E does not consider these to be notification failures as the agencies and customers were not within scope during the applicable notification timeframe due to weather factors outside of PG&E’s control. (See D.19-05-042, D.21-06-034.)

## Table 6B
#VALUE!
Table 6B: Explanation of Failures for CFI and Other Affected Customers Who Did Not Receive 24-to 48-Hour Watch Notification
| Total (CFI) | Total (Other Customers) | Explanation
| 4 | 80 | Due to operational feedback, these critical facilities and other customers entered into scope after this notification window had passed.
| 0 | 27 | These customers did not receive 24-48 hour Watch Notification because our system indicated there was no valid contact information provided to PG&E.* We are still investigating to validate this information, and we will report our findings in the 2026 PSPS Post-Season Report.
*If it is confirmed that no valid contact information was provided, PG&E does not consider these to be notification failures as we operated within the discretionary parameters prescribed in the CPUC’s PSPS guidelines for utilities. (See D.19-05-042, D.21-06-034.)

## Table 6C
#VALUE!
Table 6C: Explanation of Failures for CFI and Other Affected Customers Who Did Not Receive 1-4-Hour Imminent Notifications
| Total (CFI) | Total (Other Customers) | Explanation
| 2 | 10 | These critical facilities and other customers were all COL who did not receive 1-4 Hour Imminent Notification because they were not included in the notification files due to human error.
| 0 | 25 | These customers did not receive 1-4 hour Imminent Notification because our system indicated there was no valid contact information provided to PG&E.* We are still investigating to validate this information, and we will report our findings in the 2026 PSPS Post-Season Report.
*If it is confirmed that no valid contact information was provided, PG&E does not consider these to be notification failures as we operated within the discretionary parameters prescribed in the CPUC’s PSPS guidelines for utilities. (See D.19-05-042, D.21-06-034.)

## Table 6D
#VALUE!
Table 6D: Explanation of Failures for All Other Affected Customers Who Did Not Receive Any Notifications Before De-Energization
| Total | Explanation
| 25 | These customers did not receive any notification before de-energization because our system indicated there was no valid contact information provided to PG&E.* We are still investigating to validate this information, and we will report our findings in the 2026 PSPS Post-Season Report.
*If it is confirmed that no valid contact information was provided, PG&E does not consider these to be notification failures as we operated within the discretionary parameters prescribed in the CPUC’s PSPS guidelines for utilities. (See D.19-05-042, D.21-06-034.)

## Table 6E
#VALUE!
Table 6E: Explanation of Failures for Agency Entities, CFI, and All Other Affected Customers Who Did Not Receive Power Off Notification
| Total (Agency Entities) | Total (CFI) | Total (Other Customers) | Explanation
| 5 | 0 | 0 | These agency entities did not receive any notifications at or after de-energization initiation. This occurred because our system used for automatically generating in-outage notifications intentionally suppressed notifications to these agency entities. This suppression occurred due to a system logic error where suppression from past events was incorrectly applied to this PSPS. We will be correcting this logic in our systems to prevent a recurrence.
| 0 | 4 | 84 | These critical facilities and other customers received a notification at de-energization initiation, however their notification was delayed due to human error – the manual step to trigger these notifications was delayed.
| 0 | 2 | 2 | These critical facilities and other customers did not receive any notifications at or after de-energization initiation due to incorrect information in our data systems. As a result, the system did not recognize the customer as impacted by PSPS and therefore did not generate the notifications.
| 0 | 0 | 25 | These customers did not receive any notifications at or after de-energization initiation because our system indicated there was no valid contact information provided to PG&E.* We are still investigating to validate this information, and we will report our findings in the 2026 PSPS Post-Season Report.
*If it is confirmed that no valid contact information was provided, PG&E does not consider these to be notification failures as we operated within the discretionary parameters prescribed in the CPUC’s PSPS guidelines for utilities. (See D.19-05-042, D.21-06-034.)

## Table 6F
#VALUE!
Table 6F: Explanation of Failures for Agency Entities, CFI, and All Other Affected Customers Not Notified Immediately Before Re-energization
| Total (Agency Entities) | Total (CFI) | Total (Other Customers) | Explanation
| 5 | 0 | 0 | These agency entities did not receive any notifications at or after de-energization initiation. This occurred because our system used for automatically generating in-outage notifications intentionally suppressed notifications to these agency entities. This suppression occurred due to a system logic error where suppression from past events was incorrectly applied to this PSPS. We will be correcting this logic in our systems to prevent a recurrence.
| 0 | 7 | 7 | These critical facilities and other customers were not notified immediately before re-energization due to a gap in coordination between the local emergency centers that manage the outages – the manual step to trigger these notifications was either not performed for these outages, or was performed late, leaving insufficient time to notify customers before the end of the outage.
| 0 | 2 | 2 | These critical facilities and other customers did not receive any notifications at or after de-energization initiation due to incorrect information in our data systems. As a result, the system did not recognize the customer as impacted by PSPS and therefore did not generate the notifications.
| 0 | 0 | 25 | These customers did not receive any notifications at or after de-energization initiation because our system indicated there was no valid contact information provided to PG&E.* We are still investigating to validate this information, and we will report our findings in the 2026 PSPS Post-Season Report.
*If it is confirmed that no valid contact information was provided, PG&E does not consider these to be notification failures as we operated within the discretionary parameters prescribed in the CPUC’s PSPS guidelines for utilities. (See D.19-05-042, D.21-06-034.)

## Table 6G
#VALUE!
Table 6G: Explanation of Failures for CFI and All Other Affected Customers Who Did Not Receive Restore Notification
| Total (Agency Entities) | Total (CFI) | Total (Other Customers) | Explanation
| 32 | 0 | 0 | These agency entities received a delayed notification after restoration was complete in their jurisdictions. These delays occurred because a manual categorization step was delayed in their jurisdictions. Our automatic in-outage notification system generates Restore Notifications for agencies when all customers within their jurisdiction are either restored from PSPS or their remaining outage duration is re-categorized to non-PSPS.1
| 5 | 0 | 0 | These agency entities did not receive any notifications at or after de-energization initiation. This occurred because our system used for automatically generating in-outage notifications intentionally suppressed notifications to these agency entities. This suppression occurred due to a system logic error where suppression from past events was incorrectly applied to this PSPS. We will be correcting this logic in our systems to prevent a recurrence.
| 0 | 1 | 18 | These critical facilities and other customers received a Restore notification after re-energization was complete, however it was delayed. During the patrol and restoration process, crews found damage caused by a third-party vehicle which prevented these customers from being restored. To reflect the new cause for delayed restoration, the outage categorization for these customers was manually changed from PSPS cause code into a non-PSPS cause code, which resulted in these customers receiving delayed PSPS Restore Notifications.
| 0 | 2 | 2 | These critical facilities and other customers did not receive any notifications at or after de-energization initiation due to incorrect information in our data systems. As a result, the system did not recognize the customer as impacted by PSPS and therefore did not generate the notifications.
| 0 | 0 | 25 | These customers did not receive any notifications at or after de-energization initiation because our system indicated there was no valid contact information provided to PG&E.* We are still investigating to validate this information, and we will report our findings in the 2026 PSPS Post-Season Report.
*If it is confirmed that no valid contact information was provided, PG&E does not consider these to be notification failures as we operated within the discretionary parameters prescribed in the CPUC’s PSPS guidelines for utilities. (See D.19-05-042, D.21-06-034.)
1 These agencies contained COL customers which require special patrol and restoration procedures involving elements outside of PG&E’s control – although PG&E can patrol and ensure the safety of our own facilities prior to restoration, COL customers must perform their own patrol and confirm with PG&E that their lines are safe to re-energize prior to re-energization.

## Table 6H
#VALUE!
Table 6H: Explanation of Failures for All Other Affected Customers Who Did Not Receive Cancelation Notification
| Total | Explanation
| 1 | This customer stopped service prior to their removal from scope so they could not be notified of cancellation.*
*PG&E does not consider these to be notification failures as we operated within the discretionary parameters prescribed in the CPUC’s PSPS guidelines for utilities. (See D.19-05-042, D.21-06-034.)

## Table 7
#VALUE!
Table 7: Explanations of False Positive Communications
| Total (Agency Entities) | Total (CFI) | Total (Other Customers) | Explanation
| 2 | 0 | 0 | These agency entities were incorrectly notified of active PSPS de-energization for their jurisdiction because a data issue caused a de-energized streetlight to be incorrectly assigned to their city. This issue only impacted agency entities and did not result in any false communications to customers. These agency entities were notified of active PSPS impact but their jurisdiction did not experience an actual PSPS outage. Once this issue was identified, PG&E took action to prevent further PSPS notifications from being sent to these agency entities. We also sent emails and made live calls to correct our false positive communications – these were sent 2.3 hours after the initial false positive communication.
| 0 | 1 | 3 | These critical facilities and other customers were mitigated from PSPS de-energization using PG&E-provided backup generation. However, these customers received PSPS notifications both prior to and during their avoided PSPS de-energization. These backup generation recipients were notified of PSPS but did not experience a PSPS outage. However, PG&E does not believe this is a compliance violation because the recipients of backup generation would be aware of their mitigation from PSPS and thus would not be negatively impacted by the PSPS pre-outage and in-outage notifications.
| 0 | 0 | 3 | These customers were removed from scope and notified of cancellation within two hours of their removal from scope. However, PG&E performs additional automated notification attempts for customers requiring successful positive notifications and the additional notification attempts for a prior Watch Notification extended past the time of the Cancellation Notification. Thus, the last notification received by these customers was a Watch notification informing them of planned PSPS impact, despite PG&E’s intention to notify them of cancellation. These customers’ last communication from PG&E was advising of planned PSPS impact but these customers were ultimately not de-energized for PSPS.
| 0 | 0 | 1 | This customer did not receive a notification of Cancellation, as reported in Table 6H. This customer’s last communication from PG&E was advising of planned PSPS impact but this customer was ultimately not de-energized for PSPS.*
| 9 | 7 | 170 | These critical facilities and other customers were impacted by a non-PSPS outage. However, their outage was incorrectly manually classified as PSPS in PG&E’s internal outage management platform. As a result, these customers and agency entities for their jurisdiction received PSPS template notifications including those sent at de-energization initiation for PSPS outages which inform recipients of active PSPS impact. Subsequently, these customers and agency entities received PSPS Restore Notifications approximately 1.1 hours after their false positive communication. The short duration between the false communication and this subsequent notification may mitigate the impact caused by the false positive communication. These customers and agency entities were notified of active PSPS impact but did not experience an actual PSPS outage. PG&E also took additional action to mitigate the impact of these false positive communications by making live calls to impacted agency entities to explain that their jurisdiction and not yet been de-energized and re-energized from PSPS, and that the forecasted PSPS outages would still occur later. These live calls were made 3.2 hours after the initial false positive communication.
| 0 | 0 | 74 | These customers were located outside of the area directly scoped for PSPS but were downstream of the device that would be used to isolate their circuit segment for PSPS. As a result, these customers were planned to experience PSPS impacts and thus notified prior to de-energization. They also received PSPS notifications upon de-energization initiation. However, these customers were re-energized approximately 1.3 hours after the start of their outage: the planned isolation device for their circuit segment was reenergized early, and the PSPS outage for the rest of their circuit segment was instead sustained using unplanned downstream devices. Due to the short duration of their outage, PG&E does not consider these customers to be PSPS impacts. However, this is considered false positive communications because they were informed of PSPS impact but did not experience a long PSPS outage.
| 0 | 4 | 88 | These critical facilities and other customers were not planned for PSPS impact. Prior to the start of PSPS de-energization, a non-PSPS outage occurred on their circuit because a third-party vehicle struck a pole. To keep these customers energized while this non-PSPS damage was being repaired, their circuit segment was temporarily reconfigured to energize them from a neighboring circuit. However, this neighboring circuit was in-scope for PSPS. Specifically, these customers were fed from the same portion of circuit as the 74 customers with false communications explained above. When that neighboring circuit was de-energized for PSPS, these customers also lost power and were grouped into the same outage in our internal outage management platform. That combined outage was manually categorized as PSPS, resulting in PSPS notifications upon de-energization initiation. Since these customers were not in scope for PSPS, they did not need to wait until Weather All Clear for restoration. These customers were restored approximately 1.3 hours after their outage began, at the same time as the 74 customers with false communications explained above. Due to the short duration of their outage, PG&E does not consider these customers to be PSPS impacts. However, these are considered false positive communications because they were informed of active PSPS impact but did not experience a long PSPS outage.
*PG&E does not consider these to be false communications as we operated within the discretionary parameters prescribed in the CPUC’s PSPS guidelines for utilities. (See D.19-05-042, D.21-06-034.)

## Table 8
#VALUE!
Table 8: Explanations of False Negative Communications
| Total (Agency Entities) | Total (CFI) | Total (Other Customers) | Explanation
| 9 | 0 | 0 | In the explanations of false positive communications above, we reported false positive communications to nine agency entities, seven critical facilities, and 170 other customers due to human error. We also reported that the impacted entities and customers subsequently received PSPS Restore Notifications. While those 177 customers were never truly de-energized for PSPS, the nine agency entities would later experience actual PSPS de-energization in their jurisdiction. Thus, when the PSPS Restore Notification was sent prior to the jurisdiction’s actual PSPS de-energization, this created false negative communications for those nine agency entities because this notification prematurely communicated the end of the PSPS for that jurisdiction. As reported in our explanations of false positive communications above, PG&E made live calls to impacted agency entities to explain that their jurisdiction had not yet been de-energized and re-energized from PSPS, and that the forecasted PSPS outages would still occur later. These live calls were made 3.2 hours after the initial false positive communication and 2.1 hours after the subsequent false negative communication. Critically, these corrections were communicated before the actual start of PSPS de-energization for that jurisdiction.
| 0 | 0 | 7 | These customers were de-energized for PSPS. However, due to manual actions performed in PG&E’s internal outage management platform, these customers were incorrectly and prematurely marked as restored from PSPS. They were then added to a new outage in our internal outage management platform, but that new outage was not categorized as PSPS. This generated a Restore Notification to these customers prior to the actual restoration time. Once this false negative communication was realized, PG&E took steps to mitigate the impact from this false communication. We updated the categorization of their new outage to PSPS which generated PSPS Power Off Notifications to these customers approximately 2.5 hours after the false negative communication, which informed these customers that they are still impacted by an active PSPS outage. PG&E also attempted live calls to avoid confusion caused by the premature PSPS Restore Notification.
| 0 | 2 | 13 | These critical facilities and other customers were de-energized for PSPS as part of the same outage as the 74 non-critical customers and the four critical and 88 other customers with false positive notifications in the table above. However, unlike those customers which only experienced a short outage, these 15 critical customers and other customers experienced the full length of the planned PSPS. When restoring the 166 customers with shorter outage durations, the entire outage was manually marked as restored in our internal outage management platform. A new outage identifier was then created in our platform to manage notifications to these 15 customers for the rest of their PSPS outage duration. This new outage identifier was classified as PSPS. Those actions caused these 15 customers to be prematurely marked as restored from PSPS and generated Restore Notifications to these customers prior to their actual restoration time. Because these customers were quickly added to a new PSPS outage in our internal platform, they received PSPS Power Off Notifications only a few minutes after their false negative communication, which informed these customers that they are still impacted by an active PSPS outage. PG&E took further actions to correct our false communications and to clarify any potential confusion from the overlapping PSPS Restore and PSPS Power Off Notifications, PG&E launched custom messaging to the two critical facilities and 11 of the 13 non-critical customers.

## Table 9
#VALUE!
Table 9: PSPS Portal Map Sharing (Date and Time)
| Date | Time PDF and GIS Maps Shared (PDT)
| 2026-05-14 | 22:00
| 2026-05-15 | 17:30
| 2026-05-16 | 15:00
| 2026-05-16 | 23:00

## Table 10
#VALUE!
Table 10: Notifications Submitted to Cal OES (Date and Time)
| Date | Time PDF and GIS Maps Shared (PDT)
| 2026-05-14 | 18:15
| 2026-05-14 | 19:40
| 2026-05-15 | 7:14
| 2026-05-15 | 15:18
| 2026-05-15 | 18:06
| 2026-05-16 | 6:11
| 2026-05-16 | 15:13
| 2026-05-17 | 6:16
| 2026-05-17 | 11:46
| 2026-05-17 | 15:07
| 2026-05-17 | 16:15
| 2026-05-17 | 16:36
| 2026-05-18 | 7:23
| 2026-05-18 | 15:29
| 2026-05-18 | 22:39
| 2026-05-18 | 23:08
| 2026-05-18 | 23:35

## Table 11
#VALUE!
Table 11: Notifications Submitted to CPUC (Date and Time)
| Date | Time PDF and GIS Maps Shared (PDT)
| 2026-05-14 | 18:15
| 2026-05-15 | 16:21
| 2026-05-16 | 14:12
| 2026-05-17 | 1:01
| 2026-05-17 | 6:03
| 2026-05-17 | 11:25
| 2026-05-17 | 13:25
| 2026-05-17 | 13:47
| 2026-05-17 | 15:36
| 2026-05-17 | 16:10
| 2026-05-18 | 7:20
| 2026-05-18 | 22:57

## Table 12
#VALUE!
Table 12: AFN Customer Programs and Support
| Resource/Program | Information/Quantity of Resources Provided
| Disability Disaster Access and Resource Program (DDAR)1 | Partnered with seven local ILCs across 15 counties to provide aid to 904 customers who rely on power for medical or independent living needs, including: • 4 hotel accommodations • 2 food voucher(s) • 2 generator fuel voucher(s) • 0 accessible transportation2 • 84 batteries were previously distributed in impacted counties. • 3 batteries were delivered during the activation to potentially impacted customers.
| PBP3 | 67 customers in scope were supported by batteries received through the PBP. Since July 2020, a total of approximately 28,073 battery units has been delivered through the PBP across PG&E’s service area.
| Food Bank Partnerships | Partnered with 11 local food banks that serve all impacted counties to provide boxes of food for families.
| Meals on Wheels Partnerships4 | Partnered with 15 Meals on Wheels Organizations in 10 counties to provide services to customers in scope for the de-energization.
| CA 211 Providers Network5 | Partnered with 14 CA 211 network centers across 15 counties to assist 116 customers with resources. The direct assistance resources provided during this activation included: • 24 food voucher(s) • 6 hotel accommodations • 1 water bladder • 1 generator fuel voucher(s) • 0 accessible transportation6
| Accessible Transportation Partnerships | Partnered with three organizations across six counties in preparation for the possibility of any transportation needs. However, we did not receive any transportation requests for this PSPS. Any area that was not in scope for our accessible transportation partners is deferred as AFN transportation requests to our DDAR and CA 211 Network Providers, who also provide transportation assistance.
1 For more information on the types of aid ILCs provided and how the delivery of aid was coordinated among DDAR, ILCs and the customers, see PG&E’s 2026 AFN Plan.
2 Although PG&E partners with DDAR to provide accessible transportation, we did not receive any transportation requests for this PSPS.
3 For more information on the PBP, see PG&E’s 2026 AFN Plan.
4 For more information on PG&E’s partnership with the Meals on Wheels Organizations, see PG&E’s 2026 AFN Plan.
5 For more information on PG&E’s partnership with CA 211, see PG&E’s 2026 AFN Plan.
6 Although PG&E partners with CA 211 to provide accessible transportation, we did not receive any transportation requests for this PSPS.

## Table 13
#VALUE!
Table 13: Generators Available for CFI Customers
| Number of Units | Individual Size (MW) | Run Time (Hrs.)1 | Description
| 2 | 0.032 | 37.6 | 2 units on reserve in Sacramento
| 1 | 0.036 | 37.6 | 1 unit on reserve in Sacramento
| 4 | 0.065 | 31 | 4 units on reserve in San Leandro
| 6 | 0.1 | 25.3 | 6 units on reserve in San Leandro
| 2 | 0.125 | 25 | 2 units on reserve in Sacramento
| 1 | 0.15 | 30.3 | 1 unit on reserve in Sacramento
| 6 | 0.2 | 22.9 | 6 units on reserve in San Leandro
| 2 | 230 | 22.9 | 2 units on reserve in San Leandro
| 3 | 0.275 | 26 | 3 units on reserve in Sacramento
| 4 | 0.5 | 24.1 | 4 units on reserve in Sacramento
| 2 | 0.57 | 24.1 | 2 units on reserve in San Leandro
| 7 | 1 | 35 | 7 units on reserve in Sacramento
| 15 | 1.14 | 24 | 15 units on reserve in San Leandro
| 7 | 1.5 | 10 | 7 units on reserve in Benecia
| 11 | 2 | 27.7 | 8 units on reserve in Sacramento, 3 units on reserve in San Leandro
1 Estimated based on a 75% load. Barring mechanical failure and refueling the temporary generators have the ability to operate continously throughout a typical PSPS.

## Table 14
#VALUE!
Table 14: Number and Nature of Complaints
| Nature of Complaints | Number of Complaints
| Communications/Notifications Including, but not limited to complaints regarding lack of notice, excessive notices, confusing notice, false alarm notice, problems with getting up-to-date information, inaccurate information provided, not being able to access information in the prevalent languages and/or information accessibility, complaints about website, Public Safety Partner Portal, Representational State Transfer (REST)/Digital Asset Manager (DAM) sites (as applicable). | 5
| PSPS Frequency/Duration Including, but not limited to complaints regarding the frequency and/or duration of PSPS, including delays in restoring power, scope of PSPS and dynamic of weather conditions. | 3
| Safety/Health Concern Including, but not limited to complaints regarding difficulties experienced by AFN/MBL populations, traffic accidents due to non-operating traffic lights, inability to get medical help, well water or access to clean water, inability to keep property cool/warm during outage raising health concern. | 4
| General PSPS Dissatisfaction/Other Including, but not limited to complaints about being without power during PSPS and related hardships such as food loss, income loss, inability to work/attend school, plus any PSPS-related complaints that do not fall into any other category. | 7
| Outreach/Assistance Including, but not limited to complaints regarding CRCs, community crew vehicles, backup power, hotel vouchers, and other assistance provided by utility to mitigate impact of PSPS. | 2

## Table 15
#VALUE!
Table 15: Circuits Requiring More than 24 Hours to Restore
| Circuit Name | Reason the Utility was Unable to Restore the Circuit Within 24 Hours
| None | None

## Table 16
#VALUE!
Table 16: Lessons Learned
| Issue | Discussion | Resolution
| Customer Notification | During this PSPS, certain triggers for post-de-energization notifications were not completed properly due to incorrectly categorized cause codes. This impacted our notification performance (see Section 5.5 for more information). | During this PSPS, we leveraged an enhanced dashboard to more closely monitor occurrences of incorrect cause codes to address this issue in real-time. In addition to the corrective actions discussed in Section 5.6, we are continuing to identify opportunities to mitigate reoccurrence of this in the future.

## Table 17
#VALUE!
Table 17: Maximum Wind Gusts Recorded During May 17 – 18, 2026
| County | Maximum Wind Gust (mph) | Station Name
| Alameda | 60 | Mt Allison
| Colusa | 54 | Wadleigh Road
| Contra Costa | 63 | Los Vaqueros
| Glenn | 60 | Road 65
| Fresno | 69 | Upper Providence
| Lake | 73 | Santa Fe Geothermal
| Napa | 57 | Summit Lake
| San Benito | 58 | Lone Tree Towers
| San Joaquin | 43 | SR-99-SR-26 Fremont Street
| Solano | 59 | Sky Ranch Lane
| Sonoma | 73 | Mt St Helena West
| Stanislaus | 56 | Mt Oso
| Tehama | 70 | Ponderosa Sky
| Merced | 41 | SR-99 – Le Grand Road
| Yolo | 59 | Bald Mountain Tower

## Appendix A-1.1
#VALUE!
Appendix A-1.1 - Factors Considered in the Decision to Shut Off Power for Each Distribution Circuit De-energized During the May 17 – 18, 2026 PSPS
| Circuit Name | Time Place | De-energization Date/ Time | Restoration Date/ Time | Threshold | [9 empty] | Forecast | [9 empty] | Observed | [9 empty] | Qualitative Factors
[5 empty] | WS MPH | Flame Length ft 8hr | Rate of Spread Chhr 8hr | RH % | Prob Cat | DFM 10hr | DFM 100 hr | CFPD | NVDI | Benefit to Risk Ratio | WS MPH | Flame Length ft 8hr | Rate of Spread Chhr 8hr | RH % | Prob Cat | DFM 10hr | DFM 100 hr | CFPD | NVDI | Benefit to Risk Ratio | WS MPH | Flame Length ft 8hr | Rate of Spread Chhr 8hr | RH % | Prob Cat | DFM 10hr | DFM 100 hr | CFPD | NVDI | Benefit to Risk Ratio | NOAA (Yes/ No) | RFW (Yes/ No) | Open PSPS Tags (Yes/ No) | Tx Impacts (Yes/ No)
| BRENTWOOD 2105 | TP09 | 2026-05-17 12:49:00 | 2026-05-18 13:51:00 | 19 | 10 | 30 | 30 | 0.2 | 0.09 | 0.12 | 6 | 0.36 | 1 | 23 | 11.5 | 152.2 | 7.1 | 0.211 | 0.033 | 0.064 | 2.6422 | 0.387 | 569.4554 | 42 | No observed values available | No observed values available | 11 | 0.17735 | 0.05 | No observed values available | 4.1802 | 0.197 | No observed values available | Yes | Yes | Yes | No
| CALISTOGA 1101 | TP07 | 2026-05-17 13:43:00 | 2026-05-18 13:58:00 | 19 | 10 | 30 | 30 | 0.2 | 0.09 | 0.12 | 6 | 0.36 | 1 | 21 | 12.6 | 28.7 | 10.6 | 0.139 | 0.043 | 0.072 | 4.5659 | 0.572 | 676.9267 | 54 | No observed values available | No observed values available | 15 | 0.15685 | 0.06 | No observed values available | 9.6093 | 0.296 | No observed values available | No | No | Yes | No
| CALPINE 1144 | TP06 | 2026-05-17 13:41:00 | 2026-05-18 17:59:00 | 19 | 10 | 30 | 30 | 0.2 | 0.09 | 0.12 | 6 | 0.36 | 1 | 25 | 10.1 | 48.1 | 9 | 0.152 | 0.047 | 0.07 | 1.544 | 0.549 | 318.5576 | 55 | No observed values available | No observed values available | 14 | 0.1528 | 0.06 | No observed values available | 2.2247 | 0.398 | No observed values available | No | No | Yes | No
| CALPINE 1146 | TP06 | 2026-05-17 13:54:00 | 2026-05-18 18:00:00 | 19 | 10 | 30 | 30 | 0.2 | 0.09 | 0.12 | 6 | 0.36 | 1 | 19 | 10.9 | 29.3 | 10.8 | 0.106 | 0.057 | 0.078 | 1.5716 | 0.591 | 320.3295 | 55 | No observed values available | No observed values available | 16 | 0.11178 | 0.06 | No observed values available | 2.0714 | 0.398 | No observed values available | No | No | No | No
| CANTUA 1102 | TP15 | 2026-05-17 13:45:00 | 2026-05-18 11:07:00 | 19 | 10 | 30 | 30 | 0.2 | 0.09 | 0.12 | 6 | 0.36 | 1 | 23 | 7.3 | 79.9 | 8 | 0.23 | 0.029 | 0.053 | 2.1448 | 0.316 | 5.9273 | 28 | No observed values available | No observed values available | 27 | 0.21613 | 0.04 | No observed values available | 3.2656 | 0.128 | No observed values available | Yes | Yes | No | No
| CANTUA 1103 | TP15 | 2026-05-17 13:58:00 | 2026-05-18 12:33:00 | 19 | 10 | 30 | 30 | 0.2 | 0.09 | 0.12 | 6 | 0.36 | 1 | 24 | 8.7 | 86.4 | 7.8 | 0.256 | 0.028 | 0.053 | 4.0605 | 0.301 | 49.9355 | 28 | No observed values available | No observed values available | 27 | 0.23269 | 0.04 | No observed values available | 3.4406 | 0.2 | No observed values available | Yes | Yes | Yes | No
| CARBONA 1101 | TP11 | 2026-05-17 10:54:00 | 2026-05-18 11:14:00 | 19 | 10 | 30 | 30 | 0.2 | 0.09 | 0.12 | 6 | 0.36 | 1 | 25 | 10.5 | 130.9 | 7 | 0.21 | 0.032 | 0.061 | 5.8821 | 0.342 | 153.0677 | 39 | No observed values available | No observed values available | 13 | 0.18463 | 0.05 | No observed values available | 4.3766 | 0.231 | No observed values available | Yes | Yes | Yes | No
| CAYETANO 2109 | TP10 | 2026-05-17 12:50:00 | 2026-05-18 14:04:00 | 19 | 10 | 30 | 30 | 0.2 | 0.09 | 0.12 | 6 | 0.36 | 1 | 23 | 11.2 | 135.4 | 7.5 | 0.201 | 0.034 | 0.065 | 2.2026 | 0.395 | 352.1738 | 42 | No observed values available | No observed values available | 12 | 0.15407 | 0.05 | No observed values available | 4.2478 | 0.273 | No observed values available | Yes | No | Yes | No
| COALINGA NO 2 1105 | TP15 | 2026-05-17 14:07:00 | 2026-05-18 09:59:00 | 19 | 10 | 30 | 30 | 0.2 | 0.09 | 0.12 | 6 | 0.36 | 1 | 35 | 11 | 70.9 | 7.6 | 0.252 | 0.029 | 0.052 | 3.9763 | 0.309 | 199.8807 | 28 | No observed values available | No observed values available | 19 | 0.25156 | 0.04 | No observed values available | 8.6016 | 0.204 | No observed values available | Yes | Yes | Yes | No
| COALINGA NO 2 1107 | TP15 | 2026-05-17 13:51:00 | 2026-05-18 12:09:00 | 19 | 10 | 30 | 30 | 0.2 | 0.09 | 0.12 | 6 | 0.36 | 1 | 31 | 7.9 | 97.5 | 7.4 | 0.273 | 0.028 | 0.052 | 5.5545 | 0.291 | 9.5453 | 28 | No observed values available | No observed values available | 9 | 0.25553 | 0.04 | No observed values available | 4.5331 | 0.193 | No observed values available | Yes | Yes | Yes | No
| CORNING 1101 | TP01 | 2026-05-17 10:00:00 | 2026-05-18 12:22:00 | 19 | 10 | 30 | 30 | 0.2 | 0.09 | 0.12 | 6 | 0.36 | 1 | 25 | 10.2 | 120.5 | 7.7 | 0.29 | 0.035 | 0.064 | 7.8181 | 0.525 | 41.1534 | 29 | No observed values available | No observed values available | 14 | 0.25352 | 0.05 | No observed values available | 9.9155 | 0.343 | No observed values available | Yes | Yes | Yes | No
| CORNING 1102 | TP01 | 2026-05-17 09:58:00 | 2026-05-18 13:05:00 | 19 | 10 | 30 | 30 | 0.2 | 0.09 | 0.12 | 6 | 0.36 | 1 | 26 | 9.4 | 112.4 | 7.2 | 0.268 | 0.034 | 0.061 | 6.0734 | 0.539 | 100.3179 | 38 | No observed values available | No observed values available | 14 | 0.25161 | 0.05 | No observed values available | 9.2211 | 0.35 | No observed values available | Yes | Yes | Yes | No
| CORTINA 1101 | TP03 | 2026-05-17 10:54:00 | 2026-05-18 11:05:00 | 19 | 10 | 30 | 30 | 0.2 | 0.09 | 0.12 | 6 | 0.36 | 1 | 26 | 9.8 | 108.7 | 6.8 | 0.257 | 0.032 | 0.058 | 8.1213 | 0.439 | 250.7882 | 31 | No observed values available | No observed values available | 16 | 0.22527 | 0.05 | No observed values available | 9.5313 | 0.258 | No observed values available | Yes | Yes | Yes | No
| DUNNIGAN 1103 | TP03 | 2026-05-17 10:51:00 | 2026-05-18 10:41:00 | 19 | 10 | 30 | 30 | 0.2 | 0.09 | 0.12 | 6 | 0.36 | 1 | 23 | 7.4 | 41.3 | 6.7 | 0.305 | 0.033 | 0.06 | 7.1879 | 0.451 | 207.8005 | 29 | No observed values available | No observed values available | 14 | 0.24605 | 0.05 | No observed values available | 12.2046 | 0.34 | No observed values available | Yes | Yes | Yes | No
| ELK CREEK 1101 | TP02 | 2026-05-17 06:00:00 | 2026-05-18 15:48:00 | 19 | 10 | 30 | 30 | 0.2 | 0.09 | 0.12 | 6 | 0.36 | 1 | 30 | 13.2 | 118.8 | 7 | 0.258 | 0.033 | 0.06 | 7.7154 | 0.471 | 31.7797 | 33 | No observed values available | No observed values available | 13 | 0.23135 | 0.05 | No observed values available | 9.5831 | 0.204 | No observed values available | Yes | Yes | Yes | No
| GLENN 1101 | TP02 | 2026-05-17 05:54:00 | 2026-05-18 15:00:00 | 19 | 10 | 30 | 30 | 0.2 | 0.09 | 0.12 | 6 | 0.36 | 1 | 30 | 11.5 | 158.2 | 6.7 | 0.251 | 0.034 | 0.062 | 13.2156 | 0.517 | 40.5915 | 34 | No observed values available | No observed values available | 11 | 0.21286 | 0.05 | No observed values available | 13.0177 | 0.364 | No observed values available | Yes | Yes | Yes | No
| GUSTINE 1102 | TP13 | 2026-05-17 15:27:00 | 2026-05-18 11:46:00 | 19 | 10 | 30 | 30 | 0.2 | 0.09 | 0.12 | 6 | 0.36 | 1 | 23 | 7.4 | 85.9 | 7.8 | 0.247 | 0.031 | 0.062 | 3.1889 | 0.349 | 594.6748 | 24 | No observed values available | No observed values available | 15 | 0.20521 | 0.05 | No observed values available | 4.9485 | 0.225 | No observed values available | Yes | Yes | Yes | No
| HAMMONDS 1102 | TP14 | 2026-05-17 16:07:00 | 2026-05-18 12:44:00 | 19 | 10 | 30 | 30 | 0.2 | 0.09 | 0.12 | 6 | 0.36 | 1 | 25 | 7.3 | 89.6 | 7.3 | 0.23 | 0.029 | 0.055 | 4.8139 | 0.311 | 1.4813 | 25 | No observed values available | No observed values available | 18 | 0.19841 | 0.04 | No observed values available | 6.0233 | 0.166 | No observed values available | Yes | Yes | Yes | No
| HERDLYN 1102 | TP09 | 2026-05-17 12:47:00 | 2026-05-18 13:20:00 | 19 | 10 | 30 | 30 | 0.2 | 0.09 | 0.12 | 6 | 0.36 | 1 | 26 | 10.9 | 143.9 | 7.1 | 0.19 | 0.035 | 0.072 | 2.2687 | 0.377 | 2015.7388 | 33 | No observed values available | No observed values available | 11 | 0.19019 | 0.05 | No observed values available | 6.2978 | 0.262 | No observed values available | Yes | Yes | Yes | No
| LOGAN CREEK 2102 | TP02 | 2026-05-17 05:55:00 | 2026-05-18 17:43:00 | 19 | 10 | 30 | 30 | 0.2 | 0.09 | 0.12 | 6 | 0.36 | 1 | 31 | 13 | 186.6 | 6.5 | 0.218 | 0.032 | 0.059 | 8.8515 | 0.467 | 29.5515 | 44 | No observed values available | No observed values available | 13 | 0.18874 | 0.05 | No observed values available | 10.3378 | 0.306 | No observed values available | Yes | Yes | Yes | No
| MADISON 2101 | TP04 | 2026-05-17 10:53:00 | 2026-05-18 10:47:00 | 19 | 10 | 30 | 30 | 0.2 | 0.09 | 0.12 | 6 | 0.36 | 1 | 28 | 8.4 | 84.3 | 6.8 | 0.272 | 0.032 | 0.058 | 4.4037 | 0.436 | 1956.9214 | 37 | No observed values available | No observed values available | 13 | 0.24829 | 0.05 | No observed values available | 15.307 | 0.323 | No observed values available | Yes | Yes | Yes | No
| MAXWELL 1102 | TP02 | 2026-05-17 06:00:00 | 2026-05-18 18:31:00 | 19 | 10 | 30 | 30 | 0.2 | 0.09 | 0.12 | 6 | 0.36 | 1 | 28 | 10.7 | 133.4 | 6.7 | 0.197 | 0.031 | 0.057 | 12.0913 | 0.446 | 45.7816 | 39 | No observed values available | No observed values available | 15 | 0.17292 | 0.05 | No observed values available | 13.3947 | 0.311 | No observed values available | Yes | Yes | Yes | No
| MAXWELL 1105 | TP02 | 2026-05-17 06:01:00 | 2026-05-18 18:29:00 | 19 | 10 | 30 | 30 | 0.2 | 0.09 | 0.12 | 6 | 0.36 | 1 | 29 | 12.2 | 157.1 | 6.6 | 0.227 | 0.032 | 0.059 | 9.4245 | 0.446 | 67.1201 | 44 | No observed values available | No observed values available | 13 | 0.20829 | 0.05 | No observed values available | 10.2146 | 0.34 | No observed values available | Yes | Yes | Yes | No
| MONTICELLO 1101 | TP05 | 2026-05-17 10:50:00 | 2026-05-18 19:59:00 | 19 | 10 | 30 | 30 | 0.2 | 0.09 | 0.12 | 6 | 0.36 | 1 | 23 | 8.3 | 58.3 | 8.2 | 0.146 | 0.04 | 0.071 | 2.8855 | 0.546 | 275.2552 | 28 | No observed values available | No observed values available | 16 | 0.19021 | 0.05 | No observed values available | 6.0702 | 0.355 | No observed values available | Yes | No | Yes | No
| NORTH DUBLIN 2103 | TP10 | 2026-05-17 12:51:00 | 2026-05-18 15:45:00 | 19 | 10 | 30 | 30 | 0.2 | 0.09 | 0.12 | 6 | 0.36 | 1 | 20 | 11.7 | 139.6 | 8.2 | 0.133 | 0.041 | 0.087 | 1.4645 | 0.492 | 407.5222 | 42 | No observed values available | No observed values available | 12 | 0.089189 | 0.05 | No observed values available | 1.4314 | 0.286 | No observed values available | Yes | No | Yes | No
| PANOCHE 1103 | TP14 | 2026-05-17 16:13:00 | 2026-05-18 13:30:00 | 19 | 10 | 30 | 30 | 0.2 | 0.09 | 0.12 | 6 | 0.36 | 1 | 24 | 10.5 | 71.3 | 7.8 | 0.271 | 0.03 | 0.057 | 1.646 | 0.306 | 113.5497 | 24 | No observed values available | No observed values available | 19 | 0.2242 | 0.04 | No observed values available | 2.5911 | 0.128 | No observed values available | Yes | Yes | Yes | No
| SANTA NELLA 1103 | TP13 | 2026-05-17 15:50:00 | 2026-05-18 12:46:00 | 19 | 10 | 30 | 30 | 0.2 | 0.09 | 0.12 | 6 | 0.36 | 1 | 31 | 7.4 | 86.2 | 8 | 0.22 | 0.034 | 0.066 | 3.1569 | 0.343 | 57.4074 | 24 | No observed values available | No observed values available | 15 | 0.18776 | 0.05 | No observed values available | 3.6309 | 0.203 | No observed values available | Yes | Yes | Yes | No
| SANTA NELLA 1104 | TP13 | 2026-05-17 15:38:00 | 2026-05-18 12:47:00 | 19 | 10 | 30 | 30 | 0.2 | 0.09 | 0.12 | 6 | 0.36 | 1 | 31 | 8.2 | 96.4 | 8.1 | 0.212 | 0.032 | 0.064 | 2.6761 | 0.346 | 562.6675 | 24 | No observed values available | No observed values available | 15 | 0.14644 | 0.05 | No observed values available | 2.4337 | 0.188 | No observed values available | Yes | Yes | Yes | No
| VACAVILLE 1108 | TP08 | 2026-05-17 10:51:00 | 2026-05-18 16:08:00 | 19 | 10 | 30 | 30 | 0.2 | 0.09 | 0.12 | 6 | 0.36 | 1 | 24 | 5.2 | 30.8 | 7.5 | 0.236 | 0.031 | 0.06 | 5.0204 | 0.422 | 88.1268 | 42 | No observed values available | No observed values available | 11 | 0.22326 | 0.05 | No observed values available | 24.8246 | 0.322 | No observed values available | Yes | Yes | Yes | No
| WESTLEY 1101 | TP12 | 2026-05-17 11:03:00 | 2026-05-18 20:15:00 | 19 | 10 | 30 | 30 | 0.2 | 0.09 | 0.12 | 6 | 0.36 | 1 | 24 | 9.8 | 112.3 | 6.9 | 0.196 | 0.03 | 0.059 | 6.8241 | 0.361 | 4.1168 | 36 | No observed values available | No observed values available | 16 | 0.16986 | 0.05 | No observed values available | 5.5133 | 0.253 | No observed values available | Yes | Yes | Yes | No
| WESTLEY 1103 | TP12 | 2026-05-17 11:07:00 | 2026-05-18 12:18:00 | 19 | 10 | 30 | 30 | 0.2 | 0.09 | 0.12 | 6 | 0.36 | 1 | 28 | 7.2 | 78.7 | 7.4 | 0.196 | 0.031 | 0.059 | 4.8333 | 0.374 | 23.6783 | 36 | No observed values available | No observed values available | 16 | 0.17782 | 0.05 | No observed values available | 6.4757 | 0.246 | No observed values available | Yes | Yes | Yes | No

## Appendix A-1.2
#VALUE!
Appendix A-1.2 - Description, Units, and Value provided for Factors Considered in the Decision to Shut Off Power for Each Distribution Circuit De-energized During the May 17 – 18, 2026 PSPS
| Category | Value | Name | Unit | Value Provided | Description
| Threshold, Forecast, Observed | WS MPH | Sustained Wind Speeds | mph | max | Sustained windspeed in miles per hour at 10 meters above ground level. The observed values show the maximum sustained wind speed recorded by weather stations mapped to each circuit from planned de-energization time to anticipated All-Clear time.
| Threshold, Forecast, Observed | Flame Length ft 8hr | Flame Length | ft | max | Flame length in feet on fire front for first 8 hours of fire spread simulation from Technosylva. No observed value is available for this factor.
| Threshold, Forecast, Observed | Rate of Spread Chhr 8hr | Rate of Spread | chains/hr | max | Rate of fire spread in chains per hour for first 8 hours of fire spread simulation from Technosylva. No observed value is available for this factor.
| Threshold, Forecast, Observed | RH % | Relative Humidity | % | min | Relative Humidity in percent at 2 meters above ground level. For observed values, this is the minimum relative humidity recorded by all weather stations mapped to each circuit from planned de-energization time to anticipated All-Clear time.
| Threshold, Forecast, Observed | Prob Cat | Fire Potential Index (FPI) | probability outputs | max | Fire Potential Index (FPI) Model Output - Probability of a catastrophic fire if an ignition were to occur. FPI component of the CFPD model.
| Threshold, Forecast, Observed | DFM 10hr | Dead Fuel Moisture Content 10 hrs | fuel moisture fraction | min | Dead Fuel Moisture in 10-hour fuel moisture class. Can be scaled to percentage by multiplying by 100.
| Threshold, Forecast, Observed | DFM 100hr | Dead Fuel Moisture Content 100 hrs | fuel moisture fraction | min | Dead Fuel Moisture in 100-hour moisture class. Can be scaled to percentage by multiplying by 100. No observed value is available for this factor.
| Threshold, Forecast, Observed | CFPD | Catastrophic Fire Probability (CFPD) | Scaled Probability | max | The product of probability of catastrophic fire (Prob Cat) and IPW - probability of ignition (Prob Ignition). This product is called the (CFPD) Catastrophic Fire Probability distribution. Scaled by 1000 to convert to an integer value.
| Threshold, Forecast, Observed | NDVI | Normalized Difference Vegetation Index | fraction | min | Normalized Difference Vegetation Index (NDVI), is the difference between near-infrared (NIR) and red reflectance from the Earth's surface, divided by their sum.
| Threshold, Forecast, Observed | Benefit to Risk Ratio | Threshold, Forecast, Observed | fraction | max | Adverse impact to customers due to a catastrophic fire prevented by PSPS de-energization divided by adverse impact to customers due to PSPS de-energization. No observed value is available for this factor.
| Qualitative Factors | NOAA (Yes/No) | National Oceanic and Atmospheric Administration | N/A | Yes/No During Event | NOAA (SPC) Fire Weather Outlook forecast.
| Qualitative Factors | RFW (Yes/No) | Red Flag Warning | N/A | Yes/No During Event | Red Flag Warning from the Federal National Weather Service.
| Qualitative Factors | Open PSPS Tags | Open PSPS Qualified Tags | N/A | Yes/No During Event | PSPS-Qualified Tags include P1 (tree represents an immediate risk) and P2 (tree is damaged or diseased and could fall into nearby power lines) tree tags and Electric Corrective tags (Priority A - emergency, B - urgent, and E/F - risk-based).
| Qualitative Factors | Tx Impacts (Yes/No) | Impacted by Transmission | N/A | Yes/No During Event | Distribution lines that would have been de-energized due to de-energization of upstream Transmission lines, regardless of whether those Distribution lines would have also been de-energized due to direct Distribution PSPS.

## Appendix B
#VALUE!
Circuits labeled as “non-HFTD” are located outside of the CPUC High Fire-Threat District (HFTD). We use a High Fire Risk Area (HFRA) classification which PG&E utilizes in addition to HFTD to determine PSPS scope – these circuits intersected PG&E's HFRA despite not entering HFTD Tier 2 or Tier 3. Circuits with an asterisk (*) were sectionalized during the PSPS to further reduce customer impact. The de-energization date and time represents the time the first customer was de-energized on the circuit and the restoration time represents the date and time of the last customer restored on a circuit by circuit.
Appendix B - Circuits De-Energized During the May 17 – 18, 2026 PSPS
| Distribution / Transmission | Circuit Name | De-Energization Date and Time (PDT) | All-Clear Date and Time (PDT) | Restoration Date and Time (PDT) | Key Communities | HFTD Tier(s) | Total Customers1 | Residential Customers | Commercial / Industrial Customers | MBL Program Customers | AFN other than MBL Program Customers | Other Customers
| Distribution | BRENTWOOD 2105* | 2026-05-17 12:49:00 | 2026-05-18 08:38:00 | 2026-05-18 13:51:00 | CONTRA COSTA | Partially Outside HFTD, Tier 2 | 84 | 45 | 30 | 9 | 5 | 9
| Distribution | CALISTOGA 1101* | 2026-05-17 13:43:00 | 2026-05-18 13:14:00 | 2026-05-18 13:58:00 | NAPA, SONOMA | Tier 3 | 9 | 0 | 8 | 0 | 0 | 1
| Distribution | CALPINE 1144 | 2026-05-17 13:41:00 | 2026-05-18 13:14:00 | 2026-05-18 17:59:00 | SONOMA, LAKE | Tier 3, Tier 2 | 7 | 2 | 5 | 0 | 0 | 0
| Distribution | CALPINE 1146 | 2026-05-17 13:54:00 | 2026-05-18 13:14:00 | 2026-05-18 18:00:00 | LAKE | Tier 3 | 1 | 0 | 1 | 0 | 0 | 0
| Distribution | CANTUA 1102* | 2026-05-17 13:45:00 | 2026-05-18 07:12:00 | 2026-05-18 11:07:00 | FRESNO | Outside HFTD | 1 | 0 | 1 | 0 | 0 | 0
| Distribution | CANTUA 1103* | 2026-05-17 13:58:00 | 2026-05-18 07:12:00 | 2026-05-18 12:33:00 | FRESNO | Outside HFTD | 14 | 2 | 5 | 0 | 0 | 7
| Distribution | CARBONA 1101* | 2026-05-17 10:54:00 | 2026-05-18 08:38:00 | 2026-05-18 11:14:00 | ALAMEDA, SAN JOAQUIN | Outside HFTD | 175 | 98 | 42 | 8 | 12 | 35
| Distribution | CAYETANO 2109* | 2026-05-17 12:50:00 | 2026-05-18 12:33:00 | 2026-05-18 14:04:00 | CONTRA COSTA, ALAMEDA | Tier 3, Tier 2 | 174 | 129 | 35 | 11 | 11 | 10
| Distribution | COALINGA NO 2 1105* | 2026-05-17 14:07:00 | 2026-05-18 07:12:00 | 2026-05-18 09:59:00 | FRESNO | Outside HFTD | 14 | 1 | 10 | 0 | 1 | 3
| Distribution | COALINGA NO 2 1107* | 2026-05-17 13:51:00 | 2026-05-18 07:12:00 | 2026-05-18 12:09:00 | FRESNO | Outside HFTD | 51 | 8 | 27 | 0 | 0 | 16
| Distribution | CORNING 1101* | 2026-05-17 10:00:00 | 2026-05-18 09:33:00 | 2026-05-18 12:22:00 | TEHAMA | Partially Outside HFTD, Tier 2 | 804 | 745 | 57 | 83 | 408 | 2
| Distribution | CORNING 1102* | 2026-05-17 09:58:00 | 2026-05-18 09:33:00 | 2026-05-18 13:05:00 | TEHAMA | Partially Outside HFTD, Tier 2 | 274 | 221 | 44 | 14 | 75 | 9
| Distribution | CORTINA 1101* | 2026-05-17 10:54:00 | 2026-05-18 08:38:00 | 2026-05-18 11:05:00 | COLUSA | Partially Outside HFTD, Tier 2 | 18 | 7 | 10 | 0 | 2 | 1
| Distribution | DUNNIGAN 1103* | 2026-05-17 10:51:00 | 2026-05-18 08:38:00 | 2026-05-18 10:41:00 | COLUSA | Partially Outside HFTD, Tier 2 | 13 | 9 | 3 | 0 | 3 | 1
| Distribution | ELK CREEK 1101* | 2026-05-17 06:00:00 | 2026-05-18 11:34:00 | 2026-05-18 15:48:00 | COLUSA, GLENN | Partially Outside HFTD, Tier 2 | 821 | 680 | 116 | 52 | 178 | 25
| Distribution | GLENN 1101* | 2026-05-17 05:54:00 | 2026-05-18 11:34:00 | 2026-05-18 15:00:00 | GLENN, TEHAMA | Partially Outside HFTD, Tier 2 | 147 | 83 | 40 | 3 | 18 | 24
| Distribution | GUSTINE 1102* | 2026-05-17 15:27:00 | 2026-05-18 07:12:00 | 2026-05-18 11:46:00 | MERCED | Outside HFTD | 24 | 10 | 11 | 0 | 2 | 3
| Distribution | HAMMONDS 1102 | 2026-05-17 16:07:00 | 2026-05-18 07:12:00 | 2026-05-18 12:44:00 | FRESNO | Outside HFTD | 220 | 34 | 52 | 0 | 1 | 134
| Distribution | HERDLYN 1102* | 2026-05-17 12:47:00 | 2026-05-18 08:38:00 | 2026-05-18 13:20:00 | CONTRA COSTA, ALAMEDA | Outside HFTD | 30 | 15 | 7 | 0 | 6 | 8
| Distribution | LOGAN CREEK 2102* | 2026-05-17 05:55:00 | 2026-05-18 11:34:00 | 2026-05-18 17:43:00 | COLUSA, GLENN | Partially Outside HFTD, Tier 2 | 501 | 238 | 116 | 7 | 58 | 147
| Distribution | MADISON 2101* | 2026-05-17 10:53:00 | 2026-05-18 08:38:00 | 2026-05-18 10:47:00 | YOLO | Tier 2 | 11 | 0 | 11 | 0 | 0 | 0
| Distribution | MAXWELL 1102* | 2026-05-17 06:00:00 | 2026-05-18 11:34:00 | 2026-05-18 18:31:00 | COLUSA | Outside HFTD | 146 | 60 | 23 | 7 | 2 | 63
| Distribution | MAXWELL 1105* | 2026-05-17 06:01:00 | 2026-05-18 11:34:00 | 2026-05-18 18:29:00 | COLUSA | Partially Outside HFTD, Tier 2 | 151 | 68 | 39 | 1 | 11 | 44
| Distribution | MONTICELLO 1101* | 2026-05-17 10:50:00 | 2026-05-18 08:38:00 | 2026-05-18 19:59:00 | YOLO | Tier 2 | 8 | 0 | 7 | 0 | 0 | 1
| Distribution | NORTH DUBLIN 2103* | 2026-05-17 12:51:00 | 2026-05-18 12:33:00 | 2026-05-18 15:45:00 | CONTRA COSTA | Partially Outside HFTD, Tier 2 | 170 | 128 | 30 | 11 | 13 | 12
| Distribution | PANOCHE 1103* | 2026-05-17 16:13:00 | 2026-05-18 07:12:00 | 2026-05-18 13:30:00 | SAN BENITO, FRESNO | Partially Outside HFTD, Tier 2 | 202 | 96 | 87 | 6 | 12 | 19
| Distribution | SANTA NELLA 1103 | 2026-05-17 15:50:00 | 2026-05-18 07:12:00 | 2026-05-18 12:46:00 | MERCED | Outside HFTD | 107 | 62 | 40 | 3 | 20 | 5
| Distribution | SANTA NELLA 1104* | 2026-05-17 15:38:00 | 2026-05-18 07:12:00 | 2026-05-18 12:47:00 | MERCED | Outside HFTD | 26 | 0 | 20 | 0 | 0 | 6
| Distribution | VACAVILLE 1108* | 2026-05-17 10:51:00 | 2026-05-18 14:45:00 | 2026-05-18 16:08:00 | NAPA, SOLANO | Partially Outside HFTD, Tier 2 | 207 | 154 | 44 | 15 | 17 | 9
| Distribution | WESTLEY 1101* | 2026-05-17 11:03:00 | 2026-05-18 08:38:00 | 2026-05-18 20:15:00 | STANISLAUS, SAN JOAQUIN | Outside HFTD | 148 | 39 | 57 | 2 | 15 | 52
| Distribution | WESTLEY 1103* | 2026-05-17 11:07:00 | 2026-05-18 08:38:00 | 2026-05-18 12:18:00 | STANISLAUS | Outside HFTD | 25 | 3 | 20 | 0 | 0 | 2
| Total | [6 empty] | 4583 | 2937 | 998 | 232 | 870 | 648

## Appendix C
#VALUE!
Appendix C - Damages & Hazards Found Within the De-Energized Areas
| Circuit Name | County | Structure Identifier | Tier 2/3 or Non-HFTD | Damage / Hazard | Type of Damage/ | Description of Damage/Hazard
Hazard
| Monticello 1101 | Napa | 103928743 | Tier 2 | Hazard | Foreign object | Other - balloon on line
| Westley 1101 | San Joaquin | 103370873 | Non-HFTD | Damage | Wind related | Other - ground wire detached from poleand bird nest on pole
| Maxwell 1105 | Colusa | 101617522 | Non-HFTD | Damage | Wind related | Broken crossarm
| Glenn 1101 | Glenn | 100369467 | Non-HFTD | Damage | Wind related | Broken insulator

## Appendix D
#VALUE!
Appendix D - Public Safety Partners Contacted
| Jurisdiction | Agency/Organization | HFTD or HFRA Tier | Date/Time Contacted (PDT)
| Alameda County | Alameda County Fire Department, OES | Tier 2 | 2026-05-15 17:27
| Alameda County | BART | Tier 2 | 2026-05-15 17:27
| Alameda County | County Administration | Tier 2 | 2026-05-15 17:27
| Alameda County | EBMUD | Tier 2 | 2026-05-15 17:27
| Alameda County | EMS | Tier 2 | 2026-05-15 17:27
| Alameda County | Fire Department | Tier 2 | 2026-05-15 17:28
| Alameda County | Office of Education | Tier 2 | 2026-05-15 17:27
| Alameda County | Sheriff's Department | Tier 2 | 2026-05-15 17:27
| Alameda County CCA | East Bay Community Energy | Tier 2 | 2026-05-15 17:27
| Alameda County Communication Facility | AT&T Services Inc | Tier 2 | 2026-05-15 18:30
| Colusa County | Colusa County Board of Supervisors, County Administration | HFRA, Tier 2 | 2026-05-14 22:44
| Colusa County | Colusa County Sheriff Office, OES | HFRA, Tier 2 | 2026-05-14 22:44
| Colusa County | County Administration | HFRA, Tier 2 | 2026-05-14 22:44
| Colusa County | County Public Works | HFRA, Tier 2 | 2026-05-14 22:44
| Colusa County | EMS | HFRA, Tier 2 | 2026-05-14 22:45
| Colusa County | Fire Department | HFRA, Tier 2 | 2026-05-14 22:44
| Colusa County | Police Department | HFRA, Tier 2 | 2026-05-14 22:45
| Colusa County | Sheriff's Department | HFRA, Tier 2 | 2026-05-14 22:44
| Colusa County | US Forest Service Fire | HFRA, Tier 2 | 2026-05-14 22:44
| Colusa County Communication Facility | AT&T | Tier 2 | 2026-05-14 23:44
| Colusa County Communication Facility | AT&T Mobility LLC | Tier 2 | 2026-05-14 23:44
| Colusa County Communication Facility | AT&T Services Inc | Partially Outside HFTD, Tier 2 | 2026-05-14 23:44
| Colusa County Communication Facility | Citizens Telecommunications of California Inc. | Tier 2 | 2026-05-14 23:44
| Colusa County Communication Facility | Frontier Communications Corporation Dip | Partially Outside HFTD, Tier 2 | 2026-05-14 23:44
| Colusa County Communication Facility | GTE Mobile Net of California LP | Tier 2 | 2026-05-14 23:44
| Colusa County Emergency Services Facility | California Department of Forestry | Non-HFTD and Non-HFRA; within PSPS scope because downstream of HFRA. | 2026-05-14 23:44
| Colusa County Emergency Services Facility | County of Colusa | Non-HFTD and Non-HFRA; within PSPS scope because downstream of HFRA. | 2026-05-14 23:44
| Colusa County Emergency Services Facility | Indian Valley - Bear Valley Fire Protection District | Non-HFTD and Non-HFRA; within PSPS scope because downstream of HFRA. | 2026-05-14 23:44
| Colusa County Emergency Services Facility | Indian Valley Fire Protection District | Non-HFTD and Non-HFRA; within PSPS scope because downstream of HFRA. | 2026-05-14 23:45
| Colusa County Energy Sector Facility | Western Area Power Administration | Non-HFTD and Non-HFRA; upstream of HFRA but within PSPS scope because downstream of de-energization device. | 2026-05-14 23:45
| Colusa County Tribal | Cortina Rancheria | Tier 2 | 2026-05-14 22:44
| Colusa County Water And Waste Water Facility | California Department of Forestry | Non-HFTD and Non-HFRA; within PSPS scope because downstream of HFRA. | 2026-05-14 23:44
| Colusa County Water And Waste Water Facility | County of Colusa | Partially Outside HFTD, Tier 2 | 2026-05-14 23:44
| Contra Costa County | BART | HFRA, Tier 2, Tier 3 | 2026-05-15 17:28
| Contra Costa County | City of Concord Administration | HFRA, Tier 2, Tier 3 | 2026-05-15 17:28
| Contra Costa County | Contra Costa County Fire Protection District, Fire Department | HFRA, Tier 2, Tier 3 | 2026-05-15 17:27
| Contra Costa County | Contra Costa Office of Emergency Services | HFRA, Tier 2, Tier 3 | 2026-05-15 17:27
| Contra Costa County | County Administration | HFRA, Tier 2, Tier 3 | 2026-05-15 17:27
| Contra Costa County | EMS | HFRA, Tier 2, Tier 3 | 2026-05-15 17:27
| Contra Costa County | East Bay Regional Parks Fire Department | HFRA, Tier 2, Tier 3 | 2026-05-15 17:27
| Contra Costa County | OES | HFRA, Tier 2, Tier 3 | 2026-05-15 17:27
| Contra Costa County | Rodeo Hercules Fire Protection District | HFRA, Tier 2, Tier 3 | 2026-05-15 17:27
| Contra Costa County | San Ramon Valley Fire Protection District | HFRA, Tier 2, Tier 3 | 2026-05-15 17:27
| Contra Costa County CCA | MCE Clean Energy | HFRA, Tier 2, Tier 3 | 2026-05-15 17:27
| Contra Costa County Communication Facility | AT&T Mobility LLC | Partially Outside HFTD, Tier 2 | 2026-05-15 18:30
| Contra Costa County Communication Facility | AT&T Services Inc | Partially Outside HFTD, Tier 2 | 2026-05-15 18:30
| Contra Costa County Communication Facility | Comcast Fresno LLC | Tier 2 | 2026-05-15 18:30
| Contra Costa County Communication Facility | County of Contra Costa | Tier 3 | 2026-05-15 18:30
| Contra Costa County Communication Facility | GTE Mobile Net of California LP | HFRA | 2026-05-15 18:30
| Contra Costa County Communication Facility | Sprint Corporation | Tier 2 | 2026-05-15 18:30
| Contra Costa County Communication Facility | T-Mobile West LLC | Tier 2 | 2026-05-15 18:30
| Contra Costa County Communication Facility | Verizon | Tier 2 | 2026-05-15 18:30
| Contra Costa County Emergency Services Facility | San Ramon Valley Fire District | Tier 3, Tier 2 | 2026-05-15 18:30
| Contra Costa County Other Facility | Contra Costa Water District | Tier 2 | 2026-05-15 18:30
| Fresno County | City Administration | HFRA | 2026-05-15 17:27
| Fresno County | County Administration | HFRA | 2026-05-15 17:27
| Fresno County | EMS | HFRA | 2026-05-15 17:27
| Fresno County | Fire Department | HFRA | 2026-05-15 17:28
| Fresno County | Fresno County Office of Emergency Services | HFRA | 2026-05-15 17:27
| Fresno County | Sheriff's Department | HFRA | 2026-05-15 17:27
| Fresno County Communication Facility | American Tower Corporation | HFRA, Partially Outside HFRA | 2026-05-15 18:30
| Fresno County Communication Facility | AT&T Mobility LLC | Non-HFTD and Non-HFRA; upstream of HFRA but within PSPS scope because downstream of de-energization device. | 2026-05-15 18:30
| Fresno County Communication Facility | AT&T Services Inc | HFRA, Partially Outside HFRA | 2026-05-15 18:30
| Fresno County Communication Facility | California Highway Patrol | HFRA | 2026-05-15 18:30
| Fresno County Communication Facility | Frontier Communications Corporation Dip | Non-HFTD and Non-HFRA; upstream of HFRA but within PSPS scope because downstream of de-energization device. | 2026-05-15 18:30
| Fresno County Communication Facility | GTE Mobile Net of California LP | Non-HFTD and Non-HFRA; upstream of HFRA but within PSPS scope because downstream of de-energization device. | 2026-05-15 18:30
| Fresno County Communication Facility | Pinnacle Towers Inc | HFRA | 2026-05-15 18:30
| Fresno County Communication Facility | T-Mobile West LLC | Non-HFTD and Non-HFRA; upstream of HFRA but within PSPS scope because downstream of de-energization device. | 2026-05-15 18:30
| Fresno County Communication Facility | Verizon | Non-HFTD and Non-HFRA; upstream of HFRA but within PSPS scope because downstream of de-energization device. | 2026-05-15 18:30
| Glenn County | County Administration | HFRA, Tier 2 | 2026-05-14 22:44
| Glenn County | Fire Department | HFRA, Tier 2 | 2026-05-14 22:44
| Glenn County | Glenn County Sheriff's Office; Office of Emergency Services (OES) | HFRA, Tier 2 | 2026-05-14 22:44
| Glenn County | Orland Fire Department | HFRA, Tier 2 | 2026-05-14 22:44
| Glenn County Communication Facility | American Tower Corporation | Tier 2 | 2026-05-14 23:44
| Glenn County Communication Facility | AT&T Services Inc | HFRA, Partially Outside HFTD, Tier 2 | 2026-05-14 23:44
| Glenn County Communication Facility | GTE Mobile Net of California LP | HFRA, Partially Outside HFRA | 2026-05-14 23:44
| Glenn County Communication Facility | New Cingular Wireless PCS LLC | Non-HFTD and Non-HFRA; upstream of HFRA but within PSPS scope because downstream of de-energization device. | 2026-05-14 23:44
| Glenn County Communication Facility | T-Mobile West LLC | Non-HFTD and Non-HFRA; upstream of HFRA but within PSPS scope because downstream of de-energization device. | 2026-05-14 23:45
| Glenn County Communication Facility | Verizon | Tier 2 | 2026-05-14 23:44
| Glenn County Communication Facility | Verizon Services Corporation | Non-HFTD and Non-HFRA; upstream of HFRA but within PSPS scope because downstream of de-energization device. | 2026-05-14 23:44
| Glenn County Communication Facility | Verizon Wireless | Non-HFTD and Non-HFRA; upstream of HFRA but within PSPS scope because downstream of de-energization device. | 2026-05-14 23:44
| Glenn County Emergency Services Facility | County of Glenn | Tier 2 | 2026-05-14 23:44
| Glenn County Emergency Services Facility | Elk Creek Fire District | Tier 2 | 2026-05-14 23:44
| Glenn County Emergency Services Facility | Kanawha Fire Prtection District | Non-HFTD and Non-HFRA; upstream of HFRA but within PSPS scope because downstream of de-energization device. | 2026-05-14 23:44
| Glenn County Energy Sector Facility | City OF Santa Clara | HFRA | 2026-05-14 23:45
| Glenn County Other Facility | US Army Corps of Engineers | HFRA | 2026-05-14 23:44
| Glenn County Tribal | Grindstone Rancheria | HFRA | 2026-05-14 22:44
| Glenn County Water And Waste Water Facility | Elk Creek Community Service | Tier 2 | 2026-05-14 23:44
| Lake County | CAL FIRE | HFRA, Tier 2, Tier 3 | 2026-05-14 22:45
| Lake County | City Administration | HFRA, Tier 2, Tier 3 | 2026-05-14 22:44
| Lake County | City of Lakeport | HFRA, Tier 2, Tier 3 | 2026-05-14 22:45
| Lake County | County Administration | HFRA, Tier 2, Tier 3 | 2026-05-14 22:44
| Lake County | Fire Department, Lake County Fire Protection District | HFRA, Tier 2, Tier 3 | 2026-05-14 22:44
| Lake County | OES | HFRA, Tier 2, Tier 3 | 2026-05-14 22:44
| Lake County | Sheriff's Department | HFRA, Tier 2, Tier 3 | 2026-05-14 22:44
| Lake County | US Forest Service Fire | HFRA, Tier 2, Tier 3 | 2026-05-14 22:44
| Lake County Communication Facility | AT&T Mobility LLC | Tier 3, Tier 2 | 2026-05-14 23:44
| Lake County Communication Facility | AT&T Services Inc | Tier 3 | 2026-05-14 23:44
| Lake County Communication Facility | Mediacom California LLC | Tier 2 | 2026-05-14 23:44
| Merced County | CAL FIRE | HFRA | 2026-05-15 17:27
| Merced County | City Administration | HFRA | 2026-05-15 17:27
| Merced County | County Administration | HFRA | 2026-05-15 17:27
| Merced County | Fire Department | HFRA | 2026-05-15 17:28
| Merced County | Merced County OES | HFRA | 2026-05-15 17:27
| Merced County | Sheriff's Department | HFRA | 2026-05-15 17:27
| Merced County Communication Facility | AT&T Services Inc | Partially Outside HFRA, HFRA | 2026-05-15 18:30
| Merced County Communication Facility | T-Mobile West LLC | HFRA | 2026-05-15 18:30
| Merced County Communication Facility | Verizon | HFRA | 2026-05-15 18:30
| Merced County Communication Facility | Verizon Services Corporation | Non-HFTD and Non-HFRA; upstream of HFRA but within PSPS scope because downstream of de-energization device. | 2026-05-15 18:30
| Merced County Emergency Services Facility | California Department of Forestry | Non-HFTD and Non-HFRA; within PSPS scope because downstream of HFRA. | 2026-05-15 18:30
| Merced County Other Facility | Crown Castle USA Inc | HFRA | 2026-05-15 18:30
| Merced County Water And Waste Water Facility | San Luis Water District | Non-HFTD and Non-HFRA; upstream of HFRA but within PSPS scope because downstream of de-energization device. | 2026-05-16 16:50
| Napa County | CAL FIRE | Tier 3 | 2026-05-14 22:45
| Napa County | County Administration | Tier 3 | 2026-05-14 22:44
| Napa County | EMS | Tier 3 | 2026-05-14 22:45
| Napa County | EOC | Tier 3 | 2026-05-14 22:44
| Napa County | Napa Co Fire Dept/Cal Fire | Tier 3 | 2026-05-14 22:44
| Napa County | Napa County Assessor-Recorder-County Clerk Department | Tier 3 | 2026-05-14 22:44
| Napa County | OES | Tier 3 | 2026-05-14 22:44
| Napa County | Sheriff's Department | Tier 3 | 2026-05-14 22:44
| Napa County CCA | MCE Clean Energy | Tier 3 | 2026-05-14 22:44
| Napa County Communication Facility | American Tower Corporation | Tier 2 | 2026-05-15 18:30
| Napa County Communication Facility | AT&T Services Inc | Tier 2 | 2026-05-15 18:30
| San Benito County | County Administration | HFRA, Tier 2 | 2026-05-15 17:27
| San Benito County | EMS | HFRA, Tier 2 | 2026-05-15 17:27
| San Benito County | OES | HFRA, Tier 2 | 2026-05-15 17:27
| San Benito County | Sheriff's Department | HFRA, Tier 2 | 2026-05-15 17:27
| San Benito County CCA | Monterey Bay Community Power | HFRA, Tier 2 | 2026-05-15 17:27
| San Benito County Communication Facility | American Tower Corporation | HFRA | 2026-05-15 18:30
| San Benito County Communication Facility | AT&T Services Inc | Partially Outside HFTD, Tier 2 | 2026-05-15 18:30
| San Benito County Communication Facility | Pinnacles Tel Co | HFRA | 2026-05-15 18:30
| San Benito County Communication Facility | T-Mobile West Corporation | Tier 2 | 2026-05-15 18:30
| San Joaquin County | Board of Supervisors, County Administration | HFRA, Tier 2 | 2026-05-15 17:27
| San Joaquin County | Clements Fire District | HFRA, Tier 2 | 2026-05-15 17:27
| San Joaquin County | Collegeville Fire District | HFRA, Tier 2 | 2026-05-15 17:27
| San Joaquin County | County Administration | HFRA, Tier 2 | 2026-05-15 17:27
| San Joaquin County | EMS | HFRA, Tier 2 | 2026-05-15 17:27
| San Joaquin County | Farmington Fire District | HFRA, Tier 2 | 2026-05-15 17:27
| San Joaquin County | French Camp/Mountain House Fire District | HFRA, Tier 2 | 2026-05-15 17:27
| San Joaquin County | Liberty Fire District | HFRA, Tier 2 | 2026-05-15 17:27
| San Joaquin County | Linden Peters Fire District | HFRA, Tier 2 | 2026-05-15 17:27
| San Joaquin County | Mokelumne Fire District | HFRA, Tier 2 | 2026-05-15 17:27
| San Joaquin County | Montezuma Fire District | HFRA, Tier 2 | 2026-05-15 17:27
| San Joaquin County | OES, Office of Emergency Services | HFRA, Tier 2 | 2026-05-15 17:27
| San Joaquin County | Sheriff's Office | HFRA, Tier 2 | 2026-05-15 17:27
| San Joaquin County | Thornton Fire District | HFRA, Tier 2 | 2026-05-15 17:27
| San Joaquin County | Waterloo Morada Rural County Fire Protection District | HFRA, Tier 2 | 2026-05-15 17:27
| San Joaquin County | Woodbridge Fire District | HFRA, Tier 2 | 2026-05-15 17:27
| San Joaquin County Communication Facility | AT&T Services Inc | HFRA | 2026-05-15 18:30
| San Joaquin County Communication Facility | AT&T Wireless Service LLC | Non-HFTD and Non-HFRA; upstream of HFRA but within PSPS scope because downstream of de-energization device. | 2026-05-15 18:30
| San Joaquin County Communication Facility | Comcast | Non-HFTD and Non-HFRA; upstream of HFRA but within PSPS scope because downstream of de-energization device. | 2026-05-15 18:30
| San Joaquin County Communication Facility | Comcast Cable | Non-HFTD and Non-HFRA; upstream of HFRA but within PSPS scope because downstream of de-energization device. | 2026-05-15 18:30
| San Joaquin County Communication Facility | Comcast Cable Communications Management LLC | Non-HFTD and Non-HFRA; upstream of HFRA but within PSPS scope because downstream of de-energization device. | 2026-05-15 18:30
| San Joaquin County Communication Facility | Comcast of California | Non-HFTD and Non-HFRA; upstream of HFRA but within PSPS scope because downstream of de-energization device. | 2026-05-15 18:30
| San Joaquin County Communication Facility | T-Mobile West LLC | Non-HFTD and Non-HFRA; upstream of HFRA but within PSPS scope because downstream of de-energization device. | 2026-05-15 18:30
| San Joaquin County Communication Facility | Verizon | Partially Outside HFRA, HFRA | 2026-05-15 18:30
| San Joaquin County Communication Facility | Verizon Services Corporation | Non-HFTD and Non-HFRA; upstream of HFRA but within PSPS scope because downstream of de-energization device. | 2026-05-15 18:30
| San Joaquin County Other Facility | City of Tracy | Non-HFTD and Non-HFRA; upstream of HFRA but within PSPS scope because downstream of de-energization device. | 2026-05-15 18:30
| San Joaquin County Tracy | City Administration | HFRA | 2026-05-15 17:27
| San Joaquin County Tracy | Police Department | HFRA | 2026-05-15 17:27
| San Joaquin County Tracy | South San Joaquin County Fire Authority | HFRA | 2026-05-15 17:27
| San Joaquin County Water And Waste Water Facility | City of Tracy | Non-HFTD and Non-HFRA; upstream of HFRA but within PSPS scope because downstream of de-energization device. | 2026-05-15 18:30
| San Joaquin County Water And Waste Water Facility | County of San Joaquin | Non-HFTD and Non-HFRA; upstream of HFRA but within PSPS scope because downstream of de-energization device. | 2026-05-15 18:30
| Solano County | Benicia Fire Department | HFRA, Tier 2 | 2026-05-15 17:27
| Solano County | CHP Golden Gate Division Dispatch | HFRA, Tier 2 | 2026-05-15 17:28
| Solano County | County Administration | HFRA, Tier 2 | 2026-05-15 17:27
| Solano County | EMS | HFRA, Tier 2 | 2026-05-15 17:27
| Solano County | OES | HFRA, Tier 2 | 2026-05-15 17:27
| Solano County | Sheriff's Department | HFRA, Tier 2 | 2026-05-15 17:27
| Solano County | Solano County | HFRA, Tier 2 | 2026-05-15 17:27
| Solano County Communication Facility | American Tower Corp | Tier 2 | 2026-05-15 18:30
| Solano County Communication Facility | AT&T Services Inc | Partially Outside HFTD, Tier 2 | 2026-05-15 18:30
| Solano County Communication Facility | Crown Castle International | Tier 2 | 2026-05-15 18:30
| Solano County Communication Facility | Verizon | Tier 2 | 2026-05-15 18:30
| Solano County CCA | MCE Clean Energy | HFRA, Tier 2 | 2026-05-15 17:27
| Sonoma County | CAL FIRE, Fire Department | Tier 3 | 2026-05-14 22:44
| Sonoma County | County Administration | Tier 3 | 2026-05-14 22:44
| Sonoma County | Department of Health Services | Tier 3 | 2026-05-14 22:44
| Sonoma County | EMS | Tier 3 | 2026-05-14 22:44
| Sonoma County | Fire Department | Tier 3 | 2026-05-14 22:44
| Sonoma County | OES | Tier 3 | 2026-05-14 22:45
| Sonoma County | Redcom Fire Dispatch | Tier 3 | 2026-05-14 22:44
| Sonoma County | Sheriff's Department | Tier 3 | 2026-05-14 22:44
| Sonoma County CCA | Sonoma Clean Power | Tier 3 | 2026-05-14 22:44
| Sonoma County Communication Facility | T-Mobile West Corporation | Tier 3 | 2026-05-14 23:45
| Stanislaus County | County Administration | HFRA, Tier 2 | 2026-05-15 17:27
| Stanislaus County | EMS | HFRA, Tier 2 | 2026-05-15 17:27
| Stanislaus County | Emergency Management, OES | HFRA, Tier 2 | 2026-05-15 17:27
| Stanislaus County | Public Health Officer | HFRA, Tier 2 | 2026-05-15 17:28
| Stanislaus County | Sheriff's Department | HFRA, Tier 2 | 2026-05-15 17:27
| Stanislaus County Communication Facility | AT&T Wireless Service LLC | Non-HFTD and Non-HFRA; upstream of HFRA but within PSPS scope because downstream of de-energization device. | 2026-05-15 18:30
| Stanislaus County Communication Facility | Federal Bureau of Investigation | HFRA | 2026-05-15 18:30
| Stanislaus County Communication Facility | Verizon | Non-HFTD and Non-HFRA; upstream of HFRA but within PSPS scope because downstream of de-energization device. | 2026-05-15 18:30
| Stanislaus County Other Facility | T-Mobile USA Inc | Non-HFTD and Non-HFRA; upstream of HFRA but within PSPS scope because downstream of de-energization device. | 2026-05-15 18:30
| Tehama County | Tehama-Colusa Canal Authority | HFRA, Tier 2 | 2026-05-14 22:45
| Tehama County | County Administration | HFRA, Tier 2 | 2026-05-14 22:44
| Tehama County | OES and Sheriff's Office | HFRA, Tier 2 | 2026-05-14 22:44
| Tehama County Communication Facility | AT&T Services Inc | Partially Outside HFTD, Tier 2 | 2026-05-14 23:44
| Tehama County Communication Facility | Ducor Telephone Co | Tier 2 | 2026-05-14 23:44
| Tehama County Communication Facility | Ducor Telephone Corp | Tier 2 | 2026-05-14 23:44
| Tehama County Communication Facility | New Cingular Wireless PCS LLC | Tier 2 | 2026-05-14 23:44
| Tehama County Emergency Services Facility | California Department of Forestry | Tier 2 | 2026-05-14 23:44
| Tehama County Energy Sector Facility | City of Santa Clara | HFRA | 2026-05-14 23:45
| Tehama County Government - Jail Facility | California Department of Corrections | Tier 2 | 2026-05-14 23:44
| Tehama County Other Facility | Tehama County Fire Department | Tier 2 | 2026-05-14 23:45
| Tehama County Other Facility | US Army Corps of Engineers | HFRA | 2026-05-14 23:44
| Tehama County Water And Waste Water Facility | US Army Corps of Engineers | Non-HFTD and Non-HFRA; upstream of HFRA but within PSPS scope because downstream of de-energization device. | 2026-05-14 23:44
| Yolo County | County Administration | Tier 2 | 2026-05-14 22:44
| Yolo County | Fire Department | Tier 2 | 2026-05-14 22:44
| Yolo County | OES | Tier 2 | 2026-05-14 22:44
| Yolo County | Sheriff's Department | Tier 2 | 2026-05-14 22:44
| Yolo County CCA | Valley Clean Energy | Tier 2 | 2026-05-14 22:44
| Yolo County Communication Facility | AT&T Mobility LLC | Tier 2 | 2026-05-14 23:44
| Yolo County Communication Facility | California Highway Patrol | Tier 2 | 2026-05-14 23:44
| Yolo County Communication Facility | GTE Mobile Net of California LP | Tier 2 | 2026-05-14 23:44

## Appendix E
#VALUE!
Appendix E - Community Resource Centers Provided by PG&E
| # | County | Site Name | Address | Operating Hours (PDT) |  | Total Visitors | Indoor / Outdoor | Amenities Provided | Communities, Time Places, or Potential Circuits Supported
[5 empty] | Day 1 (May 17) | Day 2 (May 18)
| 1 | Alameda | Costco Wholesale Livermore | 2800 Independence Drive, Livermore, CA 94551 | 08:00 - 22:00 | 08:00 - 17:30 | 62 | Outdoor | WiFi, ADA Restroom, Bottled water, Device Charging, Snacks, Seating | TP 9, TP 10, TP 11
| 2 | Colusa | Stonyford Community Hall | 239 Market Street, Stonyford, CA 95979 | 08:00 - 22:00 | 08:00 - 17:00 | 155 | Indoor | WiFi, ADA Restroom, Bottled water, Device Charging, Cooling/Heating, Ice, Snacks, Seating | TP 2
| 3 | Glenn | Elk Creek Junior Senior High School | 3430 Co Rd 309, Elk Creek, CA 95939 | 08:00 - 21:49 | 08:00 - 17:00 | 112 | Outdoor | WiFi, ADA Restroom, Bottled water, Device Charging, Snacks, Seating | TP 2
| 4 | San Benito | Bolado Park Event Center | 9000 Airline Highway, Tres Pinos, CA 95075 | 08:00 - 22:00 | 08:00 - 16:00 | 11 | Outdoor | WiFi, ADA Restroom, Bottled water, Device Charging, Snacks, Seating | TP 13, TP 14
| 5 | Stanislaus | Grayson Elementary School | 301 Howard Road, Westley, CA 95363 | 08:00 - 22:00 | 08:00 - 16:00 | 324 | Outdoor | WiFi, ADA Restroom, Bottled water, Device Charging, Snacks, Seating | TP 11, TP 12
| 6 | Tehama | Rancho Tehama Association | 17605 Park Terrace Road, Corning, CA 96021 | 08:00 - 22:00 | 08:00 - 15:00 | 588 | Outdoor | WiFi, ADA Restroom, Bottled water, Device Charging, Snacks, Seating | TP 1