## Table 1
#VALUE!
Table 1: Customers Notified and De-energized1, 2
| Total Customers Notified | Total Customers De-energized | Total Customers Cancelled | MBL Program Customers De-energized | Counties De-energized | Tribes De-energized | Circuits Transmission De-energized | Circuits Unique Distribution Circuits in Any Version of Scope | Circuits Distribution Circuits De-energized | Damage / Hazard Count | CFI De-energized
| 18730 | 16223 | 2567 | 804 | 19 | 1 | 22 | 47 | 60 | 2 damages 1 hazard | 522
1 The information, times, and figures referenced in this report are based on the best available information available at the time of this report’s submission. The information, times, and figures herein are subject to revision based on further analysis and validation.
2 Number of customers de-energized and notified is a unique count. Customers who experienced multiple waves of de-energization are counted as included as a single customer impact.

## Table 2
#VALUE!
Table 2: 2025 PSPS Risk-Benefit Consequence Modelling Considerations
| Consequence Type | Wildfire Consequence Considerations | PSPS Consequence Considerations
| Safety | Calculated based on maximum population impacts derived from Technosylva wildfire simulation models and a fatality ratio based on National Fire Protection Association (NFPA) data. | Calculated from an estimate of Equivalent Fatalities (EF) per Million Customer Minutes Interrupted (MMCI). The EF/MMCI ratio is estimated from previous PG&E PSPS outages and other large external outage events.1
| Reliability | N/A | Calculated directly from the potential number of customers impacted and outage duration based on customer minutes interrupted.
| Financial | Calculated based on maximum building impacts derived from Technosylvia wildfire simulation models and a cost per structure burned previously evaluated in 2020 RAMP Report.2 | Calculated based on two financial estimates, 1) distribution of a lump sum cost of execution across all relevant circuits and 2) an estimated proxy cost per customer in scope per PSPS.3
1 Previous PG&E PSPS include 2019-2021 events, and other large external outage events include the 2003 Northeast Blackout in New York City, 2011 Southwest Blackout in San Diego, 2012 Derecho Windstorms, 2012 Superstorm Sandy, 2017 Hurricane Irma, 2021 Blackout event.
2 See A.20-06-012.
3 The assumptions used in these calculations, including the proxy cost per customer per PSPS, are subject to be updated and are not intended to prejudge or create precedent with regard to the development of more precise values of resiliency or cost of PSPS metrics being considered in other ongoing proceedings at the California Public Utilities Commission, such as the Risk-Based Decision-Making Rulemaking [R.20.07.013] and the Microgrid and Resiliency Strategies.

## Table 3
#VALUE!
Table 3: Notification Descriptions
| Type of Notification | Recipients | Description
| PRIORITY NOTIFICATION: 48-72 hours in advance of anticipated de-energization | Public Safety Partners and CBOs,1 transmission-level customers, and municipal utilities | On June 17, 2025, PG&E’s Meteorology Team observed that forecast models had strengthened and weather materialized faster than anticipated for a potential PSPS. As a result, weather forecast on pge.com/weather was updated to “elevated” in certain parts of the service area. Simultaneously, local PG&E representatives called each County Office of Emergency Services (OES) in PG&E’s electrical service area and select Tribes and cities to inform them that PG&E was monitoring an increased potential for a PSPS. PG&E was also in contact with local agency representatives and alerted Public Safety Partners of the potential PSPS as meteorological conditions developed. Once PSPS scope was approved and materials were established for potential de-energization, the Priority Notification window had already passed, therefore, Priority Notifications were not sent to some Public Safety Partners in the initial scope.
| WATCH NOTIFICATION: 24-48 hours in advance of anticipated de-energization | Public Safety Partners, CBOs, and All Customers (including MBL Program customers and SIV Program customers), transmission-level customers, and municipal utilities | During this time, the following was completed: • PG&E submitted a PSPS Notification Form to Cal OES and sent an email to the CPUC notifying them that PG&E’s EOC has been activated and that PG&E is monitoring for potential PSPS. • PG&E sent notifications to Public Safety Partners, transmission-level customers, municipal utilities, and all customers via call, text message and e-mail; these notifications included the following information: o Estimated window of the de-energization time. o When the adverse weather is anticipated to pass. o ETOR. o For Public Safety Partners only: Links to the PSPS Portal. o For Customers only: Potentially impacted addresses, links to PSPS Updates webpage with CRC information, and resources for AFN customers, including but not limited to information on the MBL Program, language support, and the Portable Battery Program2 (PBP). o For transmission-level customers only: Transmission Substation Name and Line name serving substation. • PG&E sent notifications to MBL Program customers, including tenants of master metered accounts, and SIV Program customers every hour until the customer confirmed receipt of the notification. Customer notifications were provided in English, with information on how to get PSPS information in translated languages. Customers with their language preference selected in their PG&E accounts received in-language (translated) notifications. Public Safety Partner notifications were provided in English.
| WARNING NOTIFICATION: 1-4 hours in advance of anticipated de-energization, if possible | Public Safety Partners, CBOs, and All Customers (including MBL Program customers, SIV Program customers), transmission-level customers, and municipal utilities | During this time, the following was completed: • PG&E submitted a PSPS Notification Form to Cal OES and sent an e-mail to the CPUC notifying them that PG&E has made the decision to de-energize. • PG&E sent notifications to other Public Safety Partners, transmission-level customers, and customers; these notifications included the same key PSPS timing information and resource links as the “Watch Notification.” • PG&E sent notifications to MBL Program customers, including tenants of master metered accounts, and SIV Program customers every hour until the customer confirmed receipt of the notification. o PG&E also sent Cancellation Notifications to Public Safety Partners and customers within two hours of being removed from scope to inform them that power would not be shut off. Customer notifications were provided in English, with information on how to receive PSPS information in translated languages. Customers with their language preference selected in their PG&E accounts received in-language (translated) notifications. Public Safety Partner notifications were provided in English.
| CANCELLATION NOTIFICATION: Within 2-hours of decision to cancel | Public Safety Partners, CBOs, All Customers (including MBL program customers, SIV customers) | When it was determined that de-energization was not needed for safety, the following was completed: • PG&E submitted a PSPS Notification Form to Cal OES and sent an e-mail to the CPUC. • PG&E sent notifications to other Public Safety Partners, customers and MBL Program customers, including tenants of master metered accounts, and SIV Program customers; these notifications included confirmation that they would no longer be de-energized, along with PG&E information resource links. Customer notifications were provided in English, with information on how to receive PSPS information in translated languages. Customers with their language preference selected in their PG&E accounts received in-language (translated) notifications. Public Safety Partner notifications were provided in English.
| POWER OFF NOTIFICATION: When de-energization is initiated | Public Safety Partners, CBOs, and All Customers (including MBL Program customers and SIV Program customers), transmission-level customers3, and municipal utilities | When shut off was initiated, the following was completed: • PG&E submitted a PSPS State Notification Form to Cal OES and sent an e-mail to the CPUC to notify them that de-energization has been initiated. • Agency Representatives of PG&E conducted a live call and/or sent an e-mail, as appropriate, to County OES representatives that were within the potential PSPS scope area and select Tribes and cities to inform them that customers within their jurisdiction were beginning to be de-energized. • PG&E Grid Control Center (GCC) conducted live agent calls to impacted transmission-level customers. • PG&E sent notifications to other Public Safety Partners municipal utilities, transmission-level customers and customers via call, text messages, and e-mail, which included: o Impacted addresses (for customers only). o De-energization time. o When the adverse weather is anticipated to pass. o For Customers Only: Links to the PSPS Updates webpage with CRC information, and resources for AFN customers, including but not limited to information on the MBL Program, Meals on Wheels, language support, and the PBP. Customer notifications were provided in English, with information on how to receive PSPS information in translated languages. Customers with their language preference selected in their PG&E accounts received in-language (translated) notifications. Public Safety Partner notifications were provided in English.
| WEATHER “ALL-CLEAR”/ETOR UPDATE NOTIFICATION: Immediately before re-energization begins | Public Safety Partners, CBOs, and All Customers (including MBL Program customers and SIV Program customers), transmission-level customers, and municipal utilities | After the weather event had passed and the area was deemed safe to begin patrols and restoration, PG&E completed the following: • Submitted a PSPS State Notification Form to Cal OES and sent an e-mail to the CPUC notifying them that PG&E is initiating re-energization patrols. • Sent notifications to other Public Safety Partners, transmission-level customers4, municipal utilities and customers via call, text message and e-mail; these notifications included the ETOR. • Sent “PSPS update” notifications to customers if their ETOR changed; two ways that an ETOR may change include: o New field or meteorology conditions. o Damage was found during patrols and repair is needed. Customer notifications were provided in English, with information on how to receive PSPS information in translated languages. Customers with their language preference selected in their PG&E accounts received in-language (translated) notifications. Public Safety Partner notifications were provided in English.
| RESTORATION NOTIFICATION: When re-energization is complete | Public Safety Partners, CBOs, and All Customers (including MBL Program customers and SIV Program customers), transmission-level customers, and municipal utilities | GCC conducted live agent calls to notify impacted transmission-level customers of restoration. Once customers, including MBL Program customers and SIV Program customers, were restored, they received notifications via call, text, and e-mail. This was done using an automated process that issued customer notifications every 15 minutes upon restoration of service. Customer notifications were provided in English, with information on how to receive PSPS information in translated languages. Customers with their language preference selected in their PG&E accounts received in-language (translated) notifications. Once all customers were restored, PG&E submitted the final PSPS State Notification Form to Cal OES, sent an e-mail to the CPUC confirming restoration of PSPS outages and reclassification of customers if applicable, and sent a notification to Public Safety Partners via call, text, and e-mail. Public Safety Partner notifications were provided in English.
1 Phase 3 D.21-06-034, Appendix A, page A9, Section G. MBL Program and AFN Communities, No. 4, Each electric investor-owned utility must provide proactive notification and impacted zip code information to paratransit agencies that may serve all the known transit- or paratransit-dependent persons that may need access to a CRC during a PSPS.
2 For more information about the PBP Program, see PG&E’s 2025 AFN Plan.
3 Transmission-level customers receive a GCC live call before de-energization and prior to re-energization.
4 Transmission lines serving impacted Transmission-level Customers and Municipal Utilities may cut across multiple FIAs and will only be notified when all those FIAs that the line cuts across have been given the All-Clear.

## Table 4
#VALUE!
Table 4: Customer Notification Timeline Summary
| Event Order | Minimum Timeline1 | Notification Sent to: | Approximate Time Sent (PDT) | Message | Notes | Who made the Notification
| Pre-De-energization (Prior) | 72-48 hours | Tribal/Local Governments and CCAs* | Not sent | Priority | Priority Notifications were not sent for initial scope See Section 5.2 and 5.5 for more information. | None
| Pre-De-energization (Prior) | 72-48 hours | Tribal/Local Governments and CCAs* | 2025-06-19 01:53 | Priority |  | PG&E
| Pre-De-energization (Prior) | 72-48 hours | Public Safety Partners** | Not sent | Priority | Priority Notifications were not sent for initial scope. See Section 5.2 and 5.5 for more information. | None
| Pre-De-energization (Prior) | 72-48 hours | Public Safety Partners** | 2025-06-19 03:01 | Priority |  | PG&E
| Pre-De-energization (Prior) | 48-24 hours | Tribal/Local Governments and CCAs* | 2025-06-17 21:03 | Watch |  | PG&E
| Pre-De-energization (Prior) | 48-24 hours | Tribal/Local Governments and CCAs* | 2025-06-18 07:16 | Watch |  | PG&E
| Pre-De-energization (Prior) | 48-24 hours | Tribal/Local Governments and CCAs* | 2025-06-18 23:27 | Watch |  | PG&E
| Pre-De-energization (Prior) | 48-24 hours | Tribal/Local Governments and CCAs* | 2025-06-19 17:28 | Watch |  | PG&E
| Pre-De-energization (Prior) | 48-24 hours | Tribal/Local Governments and CCAs* | 2025-06-20 05:44 | Watch |  | PG&E
| Pre-De-energization (Prior) | 48-24 hours | Public Safety Partners** | 2025-06-18 07:42 | Watch |  | PG&E
| Pre-De-energization (Prior) | 48-24 hours | Public Safety Partners** | 2025-06-19 18:30 | Watch |  | PG&E
| Pre-De-energization (Prior) | 48-24 hours | Public Safety Partners** | 2025-06-20 05:44 | Watch |  | PG&E
| Pre-De-energization (Prior) | 48-24 hours | All Customers*** | 2025-06-18 07:27 | Watch |  | PG&E
| Pre-De-energization (Prior) | 48-24 hours | All Customers*** | 2025-06-19 18:30 | Watch |  | PG&E
| Pre-De-energization (Prior) | 48-24 hours | All Customers*** | 2025-06-20 05:44 | Watch |  | PG&E
| Pre-De-energization (Prior) | 48-24 hours | All Customers*** | 2025-06-20 06:50 | Watch |  | SCE
| Pre-De-energization (Prior) | 24-12 hours2 | Tribal/Local Governments and CCAs* | 2025-06-20 21:16 | Watch |  | PG&E
| Pre-De-energization (Prior) | 24-12 hours2 | Public Safety Partners** | 2025-06-19 00:46 | Watch |  | PG&E
| Pre-De-energization (Prior) | 24-12 hours2 | Public Safety Partners** | 2025-06-20 21:16 | Watch |  | PG&E
| Pre-De-energization (Prior) | 24-12 hours2 | All Customers*** | 2025-06-19 00:45 | Watch |  | PG&E
| Pre-De-energization (Prior) | 24-12 hours2 | All Customers*** | 2025-06-20 21:10 | Watch |  | SCE
| Pre-De-energization (Prior) | 24-12 hours2 | All Customers*** | 2025-06-20 21:13 | Watch |  | PG&E
| Pre-De-energization (Prior) | 4-1 hours | Tribal/Local Governments and CCAs* | 2025-06-19 06:56 | Warning |  | PG&E
| Pre-De-energization (Prior) | 4-1 hours | Tribal/Local Governments and CCAs* | 2025-06-19 14:39 | Warning |  | PG&E
| Pre-De-energization (Prior) | 4-1 hours | Tribal/Local Governments and CCAs* | 2025-06-20 10:12 | Warning |  | PG&E
| Pre-De-energization (Prior) | 4-1 hours | Tribal/Local Governments and CCAs* | 2025-06-20 12:26 | Warning |  | PG&E
| Pre-De-energization (Prior) | 4-1 hours | Tribal/Local Governments and CCAs* | 2025-06-21 04:38 | Warning |  | PG&E
| Pre-De-energization (Prior) | 4-1 hours | Tribal/Local Governments and CCAs* | 2025-06-21 05:35 | Warning |  | PG&E
| Pre-De-energization (Prior) | 4-1 hours | Tribal/Local Governments and CCAs* | 2025-06-21 07:35 | Warning |  | PG&E
| Pre-De-energization (Prior) | 4-1 hours | Tribal/Local Governments and CCAs* | 2025-06-21 09:34 | Warning |  | PG&E
| Pre-De-energization (Prior) | 4-1 hours | Public Safety Partners** | 2025-06-19 07:31 | Warning |  | PG&E
| Pre-De-energization (Prior) | 4-1 hours | Public Safety Partners** | 2025-06-19 14:26 | Warning |  | PG&E
| Pre-De-energization (Prior) | 4-1 hours | Public Safety Partners** | 2025-06-20 10:13 | Warning |  | PG&E
| Pre-De-energization (Prior) | 4-1 hours | Public Safety Partners** | 2025-06-20 12:36 | Warning |  | PG&E
| Pre-De-energization (Prior) | 4-1 hours | Public Safety Partners** | 2025-06-21 04:47 | Warning |  | PG&E
| Pre-De-energization (Prior) | 4-1 hours | Public Safety Partners** | 2025-06-21 07:51 | Warning |  | PG&E
| Pre-De-energization (Prior) | 4-1 hours | Public Safety Partners** | 2025-06-21 05:42 | Warning |  | PG&E
| Pre-De-energization (Prior) | 4-1 hours | Public Safety Partners** | 2025-06-21 09:59 | Warning |  | PG&E
| Pre-De-energization (Prior) | 4-1 hours | All Customers*** | 2025-06-19 07:24 | Warning |  | PG&E
| Pre-De-energization (Prior) | 4-1 hours | All Customers*** | 2025-06-19 14:21 | Warning |  | PG&E
| Pre-De-energization (Prior) | 4-1 hours | All Customers*** | 2025-06-20 10:11 | Warning |  | PG&E
| Pre-De-energization (Prior) | 4-1 hours | All Customers*** | 2025-06-20 12:36 | Warning |  | PG&E
| Pre-De-energization (Prior) | 4-1 hours | All Customers*** | 2025-06-21 04:47 | Warning |  | PG&E
| Pre-De-energization (Prior) | 4-1 hours | All Customers*** | 2025-06-21 05:41 | Warning |  | PG&E
| Pre-De-energization (Prior) | 4-1 hours | All Customers*** | 2025-06-21 07:47 | Warning |  | PG&E
| Pre-De-energization (Prior) | 4-1 hours | All Customers*** | 2025-06-21 09:56 | Warning |  | PG&E
| Pre-De-energization (Prior) | 4-1 hours | All Customers*** | 2025-06-21 10:06 | Warning |  | SCE
| Initiation (During) | When De-energization is initiated (Power Off) | Tribal/Local Governments and CCAs* | 2025-06-19 09:08 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Tribal/Local Governments and CCAs* | 2025-06-19 09:45 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Tribal/Local Governments and CCAs* | 2025-06-19 09:48 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Tribal/Local Governments and CCAs* | 2025-06-19 09:48 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Tribal/Local Governments and CCAs* | 2025-06-19 09:56 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Tribal/Local Governments and CCAs* | 2025-06-19 09:57 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Tribal/Local Governments and CCAs* | 2025-06-19 10:19 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Tribal/Local Governments and CCAs* | 2025-06-19 10:24 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Tribal/Local Governments and CCAs* | 2025-06-19 10:28 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Tribal/Local Governments and CCAs* | 2025-06-19 13:13 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Tribal/Local Governments and CCAs* | 2025-06-19 13:14 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Tribal/Local Governments and CCAs* | 2025-06-19 14:13 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Tribal/Local Governments and CCAs* | 2025-06-19 17:35 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Tribal/Local Governments and CCAs* | 2025-06-19 18:59 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Tribal/Local Governments and CCAs* | 2025-06-20 13:51 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Tribal/Local Governments and CCAs* | 2025-06-20 13:59 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Tribal/Local Governments and CCAs* | 2025-06-20 15:46 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Tribal/Local Governments and CCAs* | 2025-06-20 15:50 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Tribal/Local Governments and CCAs* | 2025-06-20 16:34 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Tribal/Local Governments and CCAs* | 2025-06-21 05:28 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Tribal/Local Governments and CCAs* | 2025-06-21 10:39 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Tribal/Local Governments and CCAs* | 2025-06-21 10:43 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Tribal/Local Governments and CCAs* | 2025-06-21 11:07 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Tribal/Local Governments and CCAs* | 2025-06-21 14:14 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Tribal/Local Governments and CCAs* | 2025-06-21 14:22 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Tribal/Local Governments and CCAs* | 2025-06-21 15:24 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Tribal/Local Governments and CCAs* | 2025-06-21 15:31 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Tribal/Local Governments and CCAs* | 2025-06-21 17:03 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Tribal/Local Governments and CCAs* | 2025-06-21 17:13 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Public Safety Partners** | 2025-06-19 09:08 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Public Safety Partners** | 2025-06-19 09:45 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Public Safety Partners** | 2025-06-19 09:56 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Public Safety Partners** | 2025-06-19 10:19 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Public Safety Partners** | 2025-06-19 10:31 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Public Safety Partners** | 2025-06-19 10:52 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Public Safety Partners** | 2025-06-19 13:12 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Public Safety Partners** | 2025-06-19 13:25 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Public Safety Partners** | 2025-06-19 14:12 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Public Safety Partners** | 2025-06-19 14:27 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Public Safety Partners** | 2025-06-19 14:45 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Public Safety Partners** | 2025-06-19 15:11 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Public Safety Partners** | 2025-06-19 17:36 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Public Safety Partners** | 2025-06-19 18:59 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Public Safety Partners** | 2025-06-19 19:13 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Public Safety Partners** | 2025-06-19 19:24 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Public Safety Partners** | 2025-06-19 20:16 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Public Safety Partners** | 2025-06-20 05:16 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Public Safety Partners** | 2025-06-20 05:26 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Public Safety Partners** | 2025-06-20 13:52 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Public Safety Partners** | 2025-06-20 15:46 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Public Safety Partners** | 2025-06-20 16:01 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Public Safety Partners** | 2025-06-20 16:34 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Public Safety Partners** | 2025-06-20 16:44 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Public Safety Partners** | 2025-06-20 18:19 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Public Safety Partners** | 2025-06-20 19:54 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Public Safety Partners** | 2025-06-21 10:39 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Public Safety Partners** | 2025-06-21 11:07 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Public Safety Partners** | 2025-06-21 11:17 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Public Safety Partners** | 2025-06-21 12:00 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Public Safety Partners** | 2025-06-21 14:14 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Public Safety Partners** | 2025-06-21 14:33 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Public Safety Partners** | 2025-06-21 14:48 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Public Safety Partners** | 2025-06-21 15:14 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Public Safety Partners** | 2025-06-21 15:24 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Public Safety Partners** | 2025-06-21 16:48 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Public Safety Partners** | 2025-06-21 17:00 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Public Safety Partners** | 2025-06-21 17:11 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Public Safety Partners** | 2025-06-21 17:21 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Public Safety Partners** | 2025-06-21 17:33 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Public Safety Partners** | 2025-06-21 19:23 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Public Safety Partners** | 2025-06-22 07:21 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | All Customers*** | 2025-06-19 09:08 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | All Customers*** | 2025-06-19 09:45 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | All Customers*** | 2025-06-19 09:56 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | All Customers*** | 2025-06-19 10:19 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | All Customers*** | 2025-06-19 10:31 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | All Customers*** | 2025-06-19 10:52 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | All Customers*** | 2025-06-19 13:12 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | All Customers*** | 2025-06-19 13:25 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | All Customers*** | 2025-06-19 14:12 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | All Customers*** | 2025-06-19 14:27 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | All Customers*** | 2025-06-19 14:45 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | All Customers*** | 2025-06-19 15:11 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | All Customers*** | 2025-06-19 17:36 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | All Customers*** | 2025-06-19 18:59 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | All Customers*** | 2025-06-19 19:13 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | All Customers*** | 2025-06-19 19:24 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | All Customers*** | 2025-06-19 20:16 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | All Customers*** | 2025-06-20 05:16 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | All Customers*** | 2025-06-20 05:26 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | All Customers*** | 2025-06-20 13:52 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | All Customers*** | 2025-06-20 15:46 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | All Customers*** | 2025-06-20 16:01 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | All Customers*** | 2025-06-20 16:34 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | All Customers*** | 2025-06-20 16:44 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | All Customers*** | 2025-06-20 18:19 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | All Customers*** | 2025-06-20 19:54 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | All Customers*** | 2025-06-21 10:39 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | All Customers*** | 2025-06-21 11:07 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | All Customers*** | 2025-06-21 11:17 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | All Customers*** | 2025-06-21 12:00 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | All Customers*** | 2025-06-21 14:14 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | All Customers*** | 2025-06-21 14:33 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | All Customers*** | 2025-06-21 14:48 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | All Customers*** | 2025-06-21 15:14 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | All Customers*** | 2025-06-21 15:24 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | All Customers*** | 2025-06-21 16:35 | Power Off |  | SCE
| Initiation (During) | When De-energization is initiated (Power Off) | All Customers*** | 2025-06-21 16:48 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | All Customers*** | 2025-06-21 17:00 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | All Customers*** | 2025-06-21 17:11 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | All Customers*** | 2025-06-21 17:21 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | All Customers*** | 2025-06-21 17:33 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | All Customers*** | 2025-06-21 19:23 | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | All Customers*** | 2025-06-22 07:21 | Power Off |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Tribal/Local Governments and CCAs* | 2025-06-20 11:03 | Inspecting/ Weather All-Clear | First All-Clear Notification Sent | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Tribal/Local Governments and CCAs* | 2025-06-20 11:09 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Tribal/Local Governments and CCAs* | 2025-06-20 11:10 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Tribal/Local Governments and CCAs* | 2025-06-21 05:37 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Tribal/Local Governments and CCAs* | 2025-06-21 05:38 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Tribal/Local Governments and CCAs* | 2025-06-21 05:39 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Tribal/Local Governments and CCAs* | 2025-06-21 06:24 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Tribal/Local Governments and CCAs* | 2025-06-21 06:24 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Tribal/Local Governments and CCAs* | 2025-06-21 06:34 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Tribal/Local Governments and CCAs* | 2025-06-21 06:39 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Tribal/Local Governments and CCAs* | 2025-06-21 06:50 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Tribal/Local Governments and CCAs* | 2025-06-21 06:53 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Tribal/Local Governments and CCAs* | 2025-06-21 07:03 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Tribal/Local Governments and CCAs* | 2025-06-21 07:37 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Tribal/Local Governments and CCAs* | 2025-06-21 07:40 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Tribal/Local Governments and CCAs* | 2025-06-21 07:41 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Tribal/Local Governments and CCAs* | 2025-06-21 07:41 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Tribal/Local Governments and CCAs* | 2025-06-21 07:56 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Tribal/Local Governments and CCAs* | 2025-06-21 08:11 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Tribal/Local Governments and CCAs* | 2025-06-22 07:42 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Tribal/Local Governments and CCAs* | 2025-06-22 07:43 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Tribal/Local Governments and CCAs* | 2025-06-22 07:50 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Tribal/Local Governments and CCAs* | 2025-06-22 07:52 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Tribal/Local Governments and CCAs* | 2025-06-22 07:52 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Tribal/Local Governments and CCAs* | 2025-06-22 08:32 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Tribal/Local Governments and CCAs* | 2025-06-22 08:34 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Tribal/Local Governments and CCAs* | 2025-06-22 08:34 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Tribal/Local Governments and CCAs* | 2025-06-22 08:47 | Inspecting/ Weather All-Clear | Last All-Clear Notification Sent | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-20 11:03 | Inspecting/ Weather All-Clear | First All-Clear Notification Sent | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-20 12:05 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-21 05:37 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-21 05:47 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-21 06:24 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-21 06:34 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-21 06:50 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-21 07:07 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-21 07:19 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-21 07:37 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-21 07:54 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-21 08:06 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-21 08:34 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-21 09:06 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-22 07:42 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-22 07:52 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-22 08:22 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-22 08:32 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-22 08:42 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-22 09:00 | Inspecting/ Weather All-Clear | Last All-Clear Notification Sent | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-20 11:03 | Inspecting/ Weather All-Clear | First All-Clear Notification Sent | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-20 12:05 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-21 05:37 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-21 05:47 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-21 06:24 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-21 06:34 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-21 06:50 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-21 07:07 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-21 07:19 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-21 07:37 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-21 07:54 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-21 08:06 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-21 08:34 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-21 09:06 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-22 07:42 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-22 07:52 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-22 08:22 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-22 08:32 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-22 08:42 | Inspecting/ Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-22 08:57 | Inspecting/ Weather All-Clear |  | SCE
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-22 09:00 | Inspecting/ Weather All-Clear | Last All-Clear Notification Sent | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-19 09:48 | ETOR Update | First ETOR Update Notification Sent | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-19 10:00 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-19 10:20 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-19 10:32 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-19 11:07 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-19 13:18 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-19 14:02 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-19 14:17 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-19 14:34 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-19 14:49 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-19 17:39 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-20 05:16 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-20 11:12 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-20 11:25 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-20 14:01 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-20 14:17 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-20 16:07 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-20 16:35 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-20 16:45 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-20 20:04 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-21 05:53 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-21 07:21 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-21 07:43 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-21 08:04 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-21 08:22 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-21 08:35 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-21 09:02 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-21 09:13 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-21 09:27 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-21 09:59 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-21 10:01 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-21 10:11 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-21 10:31 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-21 10:41 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-21 10:51 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-21 11:02 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-21 11:15 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-21 11:26 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-21 11:36 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-21 12:11 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-21 12:32 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-21 12:44 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-21 13:24 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-21 15:14 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-21 15:27 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-21 15:39 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-21 17:15 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-21 17:25 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-21 17:35 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-21 17:46 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-22 08:12 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-22 08:25 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-22 08:39 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-22 08:52 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-22 09:05 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-22 09:19 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-22 09:31 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-22 09:50 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-22 10:01 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-22 10:20 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-22 10:31 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-22 10:42 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-22 10:52 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-22 11:02 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-22 11:15 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-22 11:44 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-22 12:09 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-22 12:24 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | Public Safety Partners** | 2025-06-22 14:19 | ETOR Update | Last ETOR Update Notification Sent | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-19 09:48 | ETOR Update | First ETOR Update Notification Sent | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-19 10:00 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-19 10:20 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-19 10:32 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-19 11:07 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-19 13:18 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-19 14:02 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-19 14:17 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-19 14:34 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-19 14:49 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-19 17:39 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-20 05:16 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-20 11:12 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-20 11:25 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-20 14:01 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-20 14:17 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-20 16:07 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-20 16:35 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-20 16:45 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-20 20:04 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-21 05:53 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-21 07:21 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-21 07:43 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-21 08:04 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-21 08:22 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-21 08:35 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-21 09:02 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-21 09:13 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-21 09:27 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-21 09:59 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-21 10:01 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-21 10:11 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-21 10:31 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-21 10:41 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-21 10:51 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-21 11:02 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-21 11:15 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-21 11:26 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-21 11:36 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-21 12:11 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-21 12:32 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-21 12:44 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-21 13:24 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-21 15:14 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-21 15:27 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-21 15:39 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-21 17:15 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-21 17:25 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-21 17:35 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-21 17:46 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-22 08:12 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-22 08:25 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-22 08:39 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-22 08:52 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-22 09:05 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-22 09:19 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-22 09:31 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-22 09:50 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-22 10:01 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-22 10:20 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-22 10:31 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-22 10:42 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-22 10:52 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-22 11:02 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-22 11:15 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-22 11:44 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-22 12:09 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-22 12:24 | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization (All-Clear) | All Customers*** | 2025-06-22 14:19 | ETOR Update | Last ETOR Update Notification Sent | PG&E
| Restoration (After) | After re-energization was completed | Tribal/Local Governments and CCAs* | 2025-06-20 13:50 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Tribal/Local Governments and CCAs* | 2025-06-20 18:09 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Tribal/Local Governments and CCAs* | 2025-06-21 08:19 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Tribal/Local Governments and CCAs* | 2025-06-21 08:45 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Tribal/Local Governments and CCAs* | 2025-06-21 09:13 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Tribal/Local Governments and CCAs* | 2025-06-21 09:36 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Tribal/Local Governments and CCAs* | 2025-06-21 09:48 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Tribal/Local Governments and CCAs* | 2025-06-21 10:02 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Tribal/Local Governments and CCAs* | 2025-06-21 10:15 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Tribal/Local Governments and CCAs* | 2025-06-21 10:51 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Tribal/Local Governments and CCAs* | 2025-06-21 11:01 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Tribal/Local Governments and CCAs* | 2025-06-21 11:07 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Tribal/Local Governments and CCAs* | 2025-06-21 11:13 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Tribal/Local Governments and CCAs* | 2025-06-21 11:16 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Tribal/Local Governments and CCAs* | 2025-06-21 11:22 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Tribal/Local Governments and CCAs* | 2025-06-21 11:23 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Tribal/Local Governments and CCAs* | 2025-06-21 11:53 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Tribal/Local Governments and CCAs* | 2025-06-21 12:22 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Tribal/Local Governments and CCAs* | 2025-06-21 12:41 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Tribal/Local Governments and CCAs* | 2025-06-21 12:45 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Tribal/Local Governments and CCAs* | 2025-06-21 13:40 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Tribal/Local Governments and CCAs* | 2025-06-21 13:50 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Tribal/Local Governments and CCAs* | 2025-06-21 14:43 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Tribal/Local Governments and CCAs* | 2025-06-22 09:31 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Tribal/Local Governments and CCAs* | 2025-06-22 10:18 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Tribal/Local Governments and CCAs* | 2025-06-22 10:38 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Tribal/Local Governments and CCAs* | 2025-06-22 11:01 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Tribal/Local Governments and CCAs* | 2025-06-22 11:27 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Tribal/Local Governments and CCAs* | 2025-06-22 11:46 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Tribal/Local Governments and CCAs* | 2025-06-22 11:47 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Tribal/Local Governments and CCAs* | 2025-06-22 12:18 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Tribal/Local Governments and CCAs* | 2025-06-22 12:27 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Tribal/Local Governments and CCAs* | 2025-06-22 12:42 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Tribal/Local Governments and CCAs* | 2025-06-22 13:20 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Tribal/Local Governments and CCAs* | 2025-06-22 14:58 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Tribal/Local Governments and CCAs* | 2025-06-22 19:50 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Tribal/Local Governments and CCAs* | 2025-06-22 19:54 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Tribal/Local Governments and CCAs* | 2025-06-23 09:26 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-19 14:19 | Restore | First initial Restoration Notification sent. | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-19 14:37 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-19 16:45 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-19 17:48 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-20 12:26 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-20 13:37 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-20 13:48 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-20 14:05 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-20 16:20 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-20 18:16 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-20 20:05 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-21 07:38 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-21 07:51 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-21 08:05 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-21 08:11 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-21 08:45 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-21 09:02 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-21 09:12 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-21 09:31 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-21 09:44 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-21 09:59 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-21 10:14 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-21 10:31 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-21 10:44 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-21 10:55 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-21 11:05 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-21 11:16 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-21 11:28 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-21 11:41 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-21 11:53 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-21 12:03 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-21 12:15 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-21 12:34 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-21 12:44 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-21 13:13 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-21 13:23 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-21 13:34 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-21 13:46 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-21 14:03 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-21 14:16 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-21 14:29 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-21 14:41 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-21 15:25 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-21 15:51 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-21 16:07 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-21 16:23 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-21 17:08 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-21 17:25 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-21 17:29 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-22 08:12 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-22 08:31 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-22 08:45 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-22 08:55 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-22 09:23 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-22 09:46 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-22 09:56 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-22 10:13 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-22 10:24 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-22 10:34 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-22 10:45 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-22 10:59 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-22 11:10 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-22 11:23 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-22 11:33 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-22 11:46 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-22 12:17 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-22 12:27 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-22 12:38 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-22 13:00 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-22 13:24 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-22 13:37 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-22 13:48 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-22 14:00 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-22 14:27 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-22 14:58 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-22 15:15 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-22 15:50 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-22 16:30 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 2025-06-22 17:03 | Restore | Last initial Restoration Notification sent. | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-19 14:19 | Restore | First Restoration Notification sent. | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-19 14:37 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-19 16:45 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-19 17:48 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-20 12:26 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-20 13:37 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-20 13:48 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-20 14:05 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-20 16:20 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-20 18:16 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-20 20:05 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-21 07:38 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-21 07:51 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-21 08:05 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-21 08:11 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-21 08:45 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-21 09:02 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-21 09:12 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-21 09:31 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-21 09:44 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-21 09:59 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-21 10:14 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-21 10:31 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-21 10:44 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-21 10:55 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-21 11:05 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-21 11:16 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-21 11:28 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-21 11:41 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-21 11:53 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-21 12:03 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-21 12:15 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-21 12:34 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-21 12:44 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-21 13:13 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-21 13:23 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-21 13:34 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-21 13:46 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-21 14:03 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-21 14:16 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-21 14:29 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-21 14:41 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-21 15:25 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-21 15:51 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-21 16:07 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-21 16:23 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-21 17:08 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-21 17:25 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-21 17:29 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-22 08:12 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-22 08:31 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-22 08:45 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-22 08:55 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-22 09:23 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-22 09:46 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-22 09:56 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-22 10:13 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-22 10:24 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-22 10:34 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-22 10:45 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-22 10:59 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-22 11:10 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-22 11:23 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-22 11:33 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-22 11:46 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-22 12:17 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-22 12:27 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-22 12:38 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-22 13:00 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-22 13:24 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-22 13:37 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-22 13:48 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-22 14:00 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-22 14:27 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-22 14:58 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-22 15:15 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-22 15:50 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-22 16:30 | Restore |  | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-22 17:03 | Restore | Last Restoration Notification sent. | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 2025-06-22 12:13 | Restore |  | SCE
| Cancellation | Within 2-hours of decision to cancel | Tribal/Local Governments and CCAs* | 2025-06-22 10:27 | Cancel |  | PG&E
| Cancellation | Within 2-hours of decision to cancel | Public Safety Partners** | 2025-06-18 22:51 | Cancel |  | PG&E
| Cancellation | Within 2-hours of decision to cancel | Public Safety Partners** | 2025-06-20 05:17 | Cancel |  | PG&E
| Cancellation | Within 2-hours of decision to cancel | Public Safety Partners** | 2025-06-20 20:33 | Cancel |  | PG&E
| Cancellation | Within 2-hours of decision to cancel | Public Safety Partners** | 2025-06-21 05:17 | Cancel |  | PG&E
| Cancellation | Within 2-hours of decision to cancel | Public Safety Partners** | 2025-06-22 10:42 | Cancel |  | PG&E
| Cancellation | Within 2-hours of decision to cancel | All Customers*** | 2025-06-18 22:51 | Cancel |  | PG&E
| Cancellation | Within 2-hours of decision to cancel | All Customers*** | 2025-06-20 05:17 | Cancel |  | PG&E
| Cancellation | Within 2-hours of decision to cancel | All Customers*** | 2025-06-20 20:33 | Cancel |  | PG&E
| Cancellation | Within 2-hours of decision to cancel | All Customers*** | 2025-06-21 05:17 | Cancel |  | PG&E
| Cancellation | Within 2-hours of decision to cancel | All Customers*** | 2025-06-22 10:42 | Cancel |  | PG&E
*A subset of Public Safety Partners, including Tribes, cities, counties, and community choice aggregators.
**A subset of Public Safety Partners, including water, wastewater, and communication service providers.
***All Customers, including MBL Program customers and SIV Program customers.
1 D.19-05-042, Appendix A, Timing of Notification
2 While not a CPUC requirement, PG&E provides an additional 24-12 hour notification to Tribal/Local Governments, Public Safety Partners and Customers.

## Table 5
#VALUE!
Table 5: Notifications to Customers where Positive or Affirmative Notification was Attempted1
| Designation | Total Number of customers | Notification Attempts Made2 | Timing of Attempts | Who made the Notification Attempt | Successful Positive Notification
| MBL3 | 978 | 18598 | Daily | PG&E | 978
| MBL Behind a Master Meter4 | 3 | 35 | Daily | PG&E | 2
| SIV | 350 | 5487 | Daily | PG&E | 349
1 Counts of Notification Attempts Made will not reflect the actual total of customers notified as both MBL Program and SIV Program customers can appear in both subset groups.
2 Count of Attempts Made includes doorbell rings and Live Agent phone calls.
3 Residential tenants of master-metered customers can also qualify for MBL quantities. The MBL category for the purposes of Table 5 does not include MBL Program customers who are master meter tenant
4 PG&E has additional processes in place to ensure MBL Program customers are notified. Master meter tenants are contacted directly to be considered a positive notification. Contacting the property or building manager does not count as a positive notification.

## Table 6
#VALUE!
Table 6: Notification Failure Causes
| Notifications Sent to | Notification Failure Description | Number of Entities or Customer Account | Explanation of Failure
| Public Safety Partners excluding CFI1 | Entities who did not receive 48-to 72-hour priority notification | 141 | Priority Notifications were not sent for initial scope. PG&E does not consider these to be notification failures as it was due to weather factors outside of PG&E’s control. See above and Section 5.2 for explanation.
| Public Safety Partners excluding CFI1 | Entities who did not receive 1–4-hour imminent notification | 3 | Due to human error, two entities were not included in the proper notification materials created prior to deploying these notifications. Therefore, these entities did not receive a 1-4 hour (Warning) Imminent Notification. One other entity did not receive this notification due to a technical failure with their contact information entry.
| Public Safety Partners excluding CFI1 | Entities who did not receive any notifications before de-energization | 1 | This entity did not receive any notifications due to a technical failure with their contact information entry.
| Public Safety Partners excluding CFI1 | Entities who were not notified immediately before re-energization | 2 | Due to a technical error, our notification automation system did not launch one of these entities’ Inspect Notifications (notification immediately before re-energization). The other entity did not receive this notification due to a technical failure with their contact information entry.
| Public Safety Partners excluding CFI1 | Entities who did not receive cancellation notification within two hours of the decision to cancel | 13 | Due to human error, these entities were not included in the proper notification materials created prior to deploying these notifications. Therefore, these entities did not receive a Cancel Notification.
| CFI2 | Facilities who did not receive 48-to 72-hour priority notification | 484 | PG&E does not consider these to be notification failures due to weather factors outside of PG&E’s control. See Table 6A for explanations.
| CFI2 | Facilities who did not receive 1–4-hour imminent notification | 30 | See Table 6C for explanations.
| CFI2 | Facilities who did not receive any notifications before de-energization | 0 | No failures.
| CFI2 | Facilities who were not notified at de-energization initiation | 13 | See Table 6E for explanations.
| CFI2 | Facilities who were not notified immediately before re-energization | 26 | See Table 6F for explanations.
| CFI2 | Facilities who were not notified when re-energization is complete | 3 | See Table 6G for explanations.
| CFI2 | Facilities who did not receive cancellation notification within two hours of the decision to cancel | 2 | See Table 6H for explanations.
| All other affected customers | Customers who did not receive 24–48-hour advance notifications | 544 | Of this total, PG&E considers three to be notification failures and the remaining 541 not to be notification failures. See Table 6B for explanations.
| All other affected customers | Customers who did not receive 1–4-hour imminent notifications | 84 | Of this total, PG&E considers 83 to be notification failures and one not to be notification failures. See Table 6C for explanations.
| All other affected customers | Customers who did not receive any notifications before de-energization | 3 | See Table 6D for explanations.
| All other affected customers | Customers who were not notified at de-energization initiation | 268 | See Table 6E for explanations.
| All other affected customers | Customers who were not notified immediately before re-energization | 667 | See Table 6F for explanations.
| All other affected customers | Customers who were not notified when re-energization is complete | 51 | See Table 6G for explanations.
| All other affected customers | Customers who did not receive cancellation notification within two hours of the decision to cancel | 7 | See Table 6H for explanations.
1 Only includes Tribes, cities, counties, and CCAs.
2 Includes Public Safety Partners who are CFI customers.

## Table 6A
#VALUE!
Table 6A: Explanation of Failures for CFI Who Did Not Receive 48-to 72-Hour Priority Notification
| Total | Explanation
| 484 | These critical facilities did not receive a 48-72 hour (Priority) notification. As the forecast models strengthened and weather materialized faster than anticipated, they entered into scope after this notification window had passed. The total count reflects critical facilities in-scope for their first and/or the second wave of planned de-energization between June 19-20. PG&E does not consider these to be notification failures as the customers were not within scope during the applicable notification timeframe due to weather factors outside of PG&E’s control.

## Table 6B
#VALUE!
Table 6B: Explanation of Failures for All Other Affected Customers Who Did Not Receive 24-to 48-Hour Watch Notification
| Total | Explanation
| 1 | One non-critical customer did not receive any notifications prior to de-energization due to inconsistencies between our scoping processes and grid models. Our scoping process did not account for an abnormal grid condition where this customer’s power was sourced. Therefore, we were not aware that this customer would be impacted by this PSPS until after de-energization.
| 2 | Two non-critical customers marked PG&E’s notifications as spam, therefore they did not receive any notifications. Our notifications vendor honored this setting and did not send notifications to these customers. We have coordinated with our vendor to revise their logic so PSPS notifications are delivered, regardless of customer preferences as these are considered emergency notifications.
| 326 | These non-critical customers did not receive the standard 24–48 hour (Watch) notification prior to de-energization. As the forecast models strengthened and weather materialized faster than anticipated, they entered into scope after this notification window had passed. The total count provided reflects critical facilities that were in scope for either the first and/or second wave of planned de-energization between June 19–20. PG&E does not consider these to be notification failures as the customers were not within scope during the applicable notification timeframe due to weather factors outside of PG&E’s control.
| 215 | These non-critical customers did not receive a Watch notification within the standard 24–48 hour window prior to potential de-energization. However, these customers were sent a Watch notification before the start of the 24-48 hour window. They did not receive a subsequent notification during the 24–48 hour period as they were removed from scope partway through this timeframe. The total count provided reflects critical facilities that were in scope for either the first and/or second wave of the planned de-energization occurring between June 19 – 20. PG&E does not consider these to be notification failures due to weather factors outside of PG&E’s control.

## Table 6C
#VALUE!
Table 6C: Explanation of Failures for CFI and Other Affected Customers Who Did Not Receive 1-4-Hour Imminent Notifications
| Total (CFI) | Total (Customers) | Explanation
| 0 | 1 | Due to a data error, this customer was incorrectly identified as an inactive customer for a portion of the PSPS. PG&E can only notify active customers, therefore this customer did not receive 1-4 hour notifications.
| 0 | 1 | One non-critical customer did not receive any notifications prior to de-energization due to inconsistencies between our scoping processes and grid models. Our scoping process did not account for an abnormal grid condition altering where this customer’s power was sourced. Therefore, we were not aware that this customer would be impacted by this PSPS until after de-energization.
| 10 | 19 | These critical facilities and customers were not included in the proper notification materials created prior to deploying these notifications. Therefore, they did not receive 1-4 hour notifications prior to de-energization due to human error.
| 0 | 1 | This customer was in process of a mobile home park conversion during the PSPS which caused an upstream data change in our system. Therefore, this customer did not receive the 1-4 hour notification prior to de-energization.
| 7 | 59 | These critical facilities and customers received a delayed 1-4 hour notification due to real time weather materializing faster than forecasted, which required de-energization to occur significantly earlier than initially scoped.
| 7 | 59 | Due to the change in de-energization timing, these critical facilities and customers received this notification after their outage began. PG&E considers these to be notification failures despite alignment with the notification windows based on planned de-energization times.
| 1 | 0 | This transmission-level critical facility was not included in the proper notification materials created prior to deploying 1-4 hour notifications, due to human error. Therefore, they received a delayed notification after their planned de-energization time. However, due to de-energization timing delays, this notification was delivered before their actual outage began.
| 10 | 0 | A subset of transmission-level critical facilities received delayed notification due to a human error during the creation and deployment of the notification file. As a result, the notifications were issued 4 hours and 50 minutes after the scheduled de-energization time. Despite the delay, four of these facilities were ultimately not de-energized, as they were successfully mitigated through switching to alternative transmission sources.
| 1 | 0 | This transmission-level critical facility did not receive the 1–4 hour notification before de-energization due to a system error for creating notifications. As a result, our notification materials included a different facility who was notified instead of this facility (false positive). See Section 5.7 for the false positive notification explanation.
| 1 | 0 | This transmission-level critical facility did not receive the 1-4 hour notification prior to de-energization due to a limitation with our scoping models used to identify transmission customers.
| 0 | 2 | Two non-critical customers marked PG&E’s notifications as spam, therefore they did not receive any notifications. Our notifications vendor honored this setting and did not send notifications to these customers. We have coordinated with our vendor to revise their logic so PSPS notifications are delivered regardless of customer preferences as these are considered emergency notifications.
| 0 | 1 | This customer experienced a change in ownership while we were identifying customers to notify 1-4 hours before de-energization. As a result, this customer was temporarily inactive in our system. PG&E does not consider this a notification failure as the customer was inactive during scoping.

## Table 6D
#VALUE!
Table 6D: Explanation of Failures for All Other Affected Customers Who Did Not Receive Any Notifications Before De-Energization
| Total | Explanation
| 1 | One non-critical customer did not receive any notifications prior to de-energization due to inconsistencies between our scoping processes and grid models. Our scoping process did not account for an abnormal grid condition altering where this customer’s power was sourced. Therefore, we were not aware that this customer would be impacted by this PSPS until after de-energization.
| 2 | Two non-critical customers marked PG&E’s notifications as spam, therefore they did not receive any notifications. Our notifications vendor honored this setting and did not send notifications to these customers. We have coordinated with our vendor to revise their logic so PSPS notifications are delivered regardless of customer preferences as these are considered emergency notifications.

## Table 6E
#VALUE!
Table 6E: Explanation of Failures for CFI and All Other Affected Customers Who Did Not Receive Power Off Notification
| Total (CFI) | Total (Customer) | Explanation
| 0 | 1 | Due to a data error, this customer was incorrectly identified as an inactive customer for a portion of the PSPS. PG&E can only notify active customers, therefore this customer did not receive a Power Off Notification.
| 7 | 59 | These critical facilities and customers received a delayed Power Off Notification around four hours after de-energization due to a human error which delayed the system in creating the notifications. As a result, the first batch of notifications could not be launched by our notification vendor. Once alerted, we corrected this error and successfully re-launched the batch.
| 4 | 158 | These critical facilities and customers received a significantly delayed Power Off Notification after their outage had already been restored. The significant length of this delay also resulted in a false positive communication, as explained in Section 5.7. The root cause of these failures have not been identified and are still under investigation. We will report our findings in the 2025 PSPS Post-Season Report.
| 2 | 0 | These critical facilities did not receive any notifications between Power Off and Restoration. They were impacted by a non-PSPS outage prior to the start of their planned PSPS de-energization. Once their PSPS de-energization began, it overlapped with their ongoing non-PSPS outage and they should have been sent PSPS notifications. The root cause of these failures have not been identified and are still under investigation. We will report our findings in the 2025 PSPS Post-Season Report.
| 0 | 43 | These non-critical customers did not receive any notifications between Power Off and Restoration due to incorrect information in our data systems. The system had incorrectly marked these customers as already de-energized for a non-PSPS outage before the PSPS began. As a result, they were not identified as being impacted by this PSPS and therefore not sent any PSPS notifications.
| 0 | 4 | These non-critical customers did not receive Power Off Notifications due to a system error for automated notifications. They received all other required notifications for this PSPS. The root cause of these failures have not been identified and are still under investigation. We will report our findings in the 2025 PSPS Post-Season Report.
| 0 | 1 | These non-critical customers did not receive any notifications between Power Off and Restoration due to incorrect information in our data systems. As a result, the system did not recognize the customer as impacted by PSPS and therefore did not generate the notifications.
| 0 | 2 | Two non-critical customers marked PG&E’s notifications as spam, therefore they did not receive any notifications. Our notifications vendor honored this setting and did not send notifications to these customers. We have coordinated with our vendor to revise their logic so PSPS notifications are delivered regardless of customer preferences as these are considered emergency notifications.

## Table 6F
#VALUE!
Table 6F: Explanation of Failures for CFI and All Other Affected Customers Not Notified Immediately Before Re-energization
| Total (CFI) | Total (Customers) | Explanation
| 0 | 1 | Due to a data error, this customer was incorrectly identified as an inactive customer for a portion of the PSPS. PG&E can only notify active customers, therefore this customer was not notified immediately before re-energization.
| 19 | 377 | These critical facilities and customers were not notified immediately before re-energization due to a system logic error that resulted from the multiple waves of de-energization that occurred during this PSPS. We are continuing to update our processes to prevent this type of issue from occurring in future PSPS events.
| 3 | 8 | These critical facilities and customers were not notified immediately before re-energization as a manual categorization step that triggers this notification was not performed in our data system.
| 2 | 235 | These critical facilities and customers were not notified immediately before re-energization because this notification was delayed until after re-energization. This was due to a manual categorization step that triggers this notification that was performed too late in our data system.
| 2 | 0 | These critical facilities did not receive any notifications between Power Off and Restoration. They were impacted by a non-PSPS outage prior to the start of their planned PSPS de-energization. Once their PSPS de-energization began, it overlapped with their ongoing non-PSPS outage and they should have been sent PSPS notifications. The root cause of these failures have not been identified and are still under investigation. We will report our findings in the 2025 PSPS Post-Season Report.
| 0 | 43 | These non-critical customers missed all notifications from Power Off to Restoration due to incorrect data in our internal outage management platform. The system had incorrectly marked these customers as already de-energized for non-PSPS reasons before the PSPS began. As a result, they were not identified as new PSPS impacts and did not receive appropriate PSPS notifications.
| 0 | 1 | These non-critical customers did not receive any notifications between Power Off and Restoration due to incorrect information in our data systems. As a result, the system did not recognize the customer as impacted by PSPS and therefore did not generate the notifications.
| 0 | 2 | Two non-critical customers marked PG&E’s notifications as spam; therefore, they did not receive any notifications. Our notifications vendor honored this setting and did not send notifications to these customers. We have coordinated with our vendor to revise their logic, so PSPS notifications are delivered, regardless of customer preferences as these are considered emergency notifications.

## Table 6G
#VALUE!
Table 6G: Explanation of Failures for CFI and All Other Affected Customers Who Did Not Receive Restore Notification
| Total (CFI) | Total (Customer) | Explanation
| 0 | 1 | Due to a data error, this customer was incorrectly identified as an inactive customer for a portion of the PSPS. PG&E can only notify active customers. Therefore, this customer did not receive a Restoration Notification.
| 2 | 0 | These critical facilities did not receive any notifications between Power Off and Restoration. They were impacted by a non-PSPS outage prior to the start of their planned PSPS de-energization. Once their PSPS de-energization began, it overlapped with their ongoing non-PSPS outage and they should have been sent PSPS notifications. The root cause of these failures have not been identified and are still under investigation. We will report our findings in the 2025 PSPS Post-Season Report.
| 0 | 43 | These non-critical customers did not receive any notifications between Power Off and Restoration due to incorrect information in our data systems. The system had incorrectly marked these customers as already de-energized for a non-PSPS outage before the PSPS began. As a result, they were not identified as being impacted by this PSPS and therefore not sent any PSPS notifications.
| 0 | 3 | These non-critical customers were not notified when re-energization was complete because their outage was prematurely marked as restored in our data system which triggered automation to launch a Restoration Notification for these customers. As a result, these customers received this notification prior to re-energization.
| 1 | 1 | This critical facility and non-critical customer were not notified when re-energization was complete because their notification files were not launched. The root cause is still under investigation with our notification vendor. We will report our findings in the 2025 PSPS Post-Season Report.
| 0 | 1 | This non-critical customer did not receive any notifications from Power Off to Restoration due to incorrect information in our data system. As a result, the system did not recognize the customer as impacted by PSPS and therefore did not generate the notifications.
| 0 | 2 | Two non-critical customers marked PG&E’s notifications as spam; therefore, they did not receive any notifications. Our notifications vendor honored this setting and did not send notifications to these customers. We have coordinated with our vendor to revise their logic, so PSPS notifications are delivered, regardless of customer preferences as these are considered emergency notifications.

## Table 6H
#VALUE!
Table 6H: Explanation of Failures for CFI and All Other Affected Customers Who Did Not Receive Cancelation Notification
| Total (CFI) | Total (Customer) | Explanation
| 2 | 7 | These four customers and two critical facilities, who are all COLs, were not included in the proper notification materials created prior to deploying the notifications. Therefore, they did not receive Cancelation notifications due to human error.

## Table 7
#VALUE!
Table 7: PSPS Portal Time & Date for Map Sharing
| Date | Time PDF and GIS Maps Shared (PDT)
| 2025-06-18 | 1:15
| 2025-06-18 | 7:32
| 2025-06-18 | 22:25
| 2025-06-19 | 16:26
| 2025-06-19 | 5:21
| 2025-06-20 | 20:45

## Table 8
#VALUE!
Table 8: PSPS Notifications Submitted to Cal OES
| Date | Time PDF and GIS Maps Shared (PDT)
| 2025-06-17 | 18:13
| 2025-06-18 | 6:24
| 2025-06-18 | 7:27
| 2025-06-18 | 15:20
| 2025-06-18 | 21:09
| 2025-06-19 | 5:22
| 2025-06-19 | 8:50
| 2025-06-19 | 10:59
| 2025-06-19 | 15:00
| 2025-06-19 | 16:17
| 2025-06-19 | 18:52
| 2025-06-20 | 7:00
| 2025-06-20 | 7:40
| 2025-06-20 | 10:53
| 2025-06-20 | 14:34
| 2025-06-20 | 16:23
| 2025-06-20 | 23:34
| 2025-06-21 | 6:58
| 2025-06-21 | 14:56
| 2025-06-21 | 19:07
| 2025-06-22 | 6:45
| 2025-06-22 | 10:21
| 2025-06-22 | 14:43

## Table 9
#VALUE!
Table 9: PSPS Notifications Submitted to CPUC
| Date | Time PDF and GIS Maps Shared (PDT)
| 2025-06-17 | 19:13
| 2025-06-18 | 8:24
| 2025-06-19 | 1:40
| 2025-06-19 | 6:53
| 2025-06-20 | 5:48
| 2025-06-20 | 13:16
| 2025-06-20 | 21:26
| 2025-06-21 | 4:56
| 2025-06-21 | 5:02
| 2025-06-21 | 11:11
| 2025-06-21 | 17:46
| 2025-06-22 | 7:40
| 2025-06-22 | 10:21
| 2025-06-22 | 14:58

## Table 10
#VALUE!
Table 10: Generators Available for CFI Customers
| Generator Type | Number of Units | Individual Size (MW) | Run Time (Hrs.)1 | Description
| Diesel Generator | 2 | 0.32 | 37.6 | 13 units on reserve in Sacramento.
| Diesel Generator | 1 | 0.65 | 31 | One unit on reserve in San Leandro.
| Diesel Generator | 7 | 0.1 | 25.3 | Seven units on reserve in Sacramento.
| Diesel Generator | 1 | 0.125 | 25 | One unit on reserve in San Leandro.
| Diesel Generator | 7 | 0.2 | 22.9 | Seven units on reserve in San Leandro.
| Diesel Generator | 3 | 0.275 | 26 | Three units on reserve in Sacramento.
| Diesel Generator | 4 | 0.5 | 24.1 | Four units on reserve in Sacramento.
| Diesel Generator | 2 | 0.57 | 24.1 | Two units on reserve in San Leandro.
| Diesel Generator | 1 | 1 | 35 | One unit on reserve in Sacramento.
| Diesel Generator | 15 | 1.14 | 24 | 15 units on reserve in San Leandro.
| Diesel Generator | 7 | 1.5 | 10 | Seven units on reserve in Benecia.
| Diesel Generator | 18 | 2 | 27.7 | Eight units on reserve in Sacramento. 10 units on reserve in San Leandro.
1 Estimated based on a 75% load. Barring mechanical failure and refueling the temporary generators have the ability to operate continuously throughout a typical PSPS.

## Table 11
#VALUE!
Table 11: CFI Customers that Received Backup Generation
| County | Site Type | Generation Deployed (MW) | Duration of Operation (Hours) | Reason Deployed
| Glenn | Water District | 0.23 | 1900-01-01 02:59 | High risk to environment or public safety.

## Table 12
#VALUE!
Table 12: Number and Nature of Complaints due to the June 19 – 22, 2025 PSPS
| Nature of Complaints | Number of Complaints
| Communications/Notifications Including, but not limited to complaints regarding lack of notice, excessive notices, confusing notice, false alarm notice, problems with getting up-to-date information, inaccurate information provided, not being able to access information in the prevalent languages and/or information accessibility, complaints about website, Public Safety Partner Portal, Representational State Transfer (REST)/Digital Asset Manager (DAM) sites (as applicable). | 74
| PSPS Frequency/Duration Including, but not limited to complaints regarding the frequency and/or duration of PSPS, including delays in restoring power, scope of PSPS and dynamic of weather conditions. | 83
| Safety/Health Concern Including, but not limited to complaints regarding difficulties experienced by AFN/MBL populations, traffic accidents due to non-operating traffic lights, inability to get medical help, well water or access to clean water, inability to keep property cool/warm during outage raising health concern. | 58
| General PSPS Dissatisfaction/Other Including, but not limited to complaints about being without power during PSPS and related hardships such as food loss, income loss, inability to work/attend school, plus any PSPS-related complaints that do not fall into any other category. | 207
| Outreach/Assistance Including, but not limited to complaints regarding CRCs, community crew vehicles, backup power, hotel vouchers, and other assistance provided by utility to mitigate impact of PSPS. | 8

## Table 13
#VALUE!
Table 13: Count and Type of Claim(s) Received
| Description of Claims | Number of Claims
| Business Interruption / Economic Loss | 0
| Food Loss Only | 26
| Property Damage | 2

## Table 14
#VALUE!
Table 14: Lessons Learned from the PSPS
| Issue | Discussion | Resolution
| Customer Notification | While PG&E implemented grounding of a transmission line to mitigate induction risk, there were coordination challenges that resulted in a customer being de-energized earlier than the time previously communicated in a notification. | During the PSPS, the customer was notified prior to shutdown, however prior notifications communicated a different initial outage time. We plan to strengthen our controls related to the timing and execution of lines which require grounding.

## Table 15
#VALUE!
Table 15: Maximum Wind Gusts Recorded Between June 19 – 22, 2025
| County | Maximum Wind Gust (mph) | Station ID | Station Name
| Alameda | 61 | AATC1 | Altamont
| Colusa | 39 | PG697 | Colusa Hills
| Contra Costa | 56 | 234PG | Black Diamond Mines
| Fresno | 39 | PG684 | San Joaquin Ridge
| Glenn | 38 | PG574 | Diamond Ranch Road
| Kern | 42 | PG649 | Beartrap Road
| Kings | 39 | KNLC | Lemoore Naval Air Station
| Merced | 42 | SLRC1 | Los Banos
| Monterey | 50 | PG622 | Old Coast Tower
| San Benito | 42 | PG534 | San Juan Grade
| San Joaquin | 45 | CF138 | I-580 – Hansen Road
| San Luis Obispo | 43 | PG715 | Mt. Lowe
| Santa Barbara | 61 | GVTC1 | Gaviota
| Santa Clara | 37 | PG608 | Mt. Umunhum
| Shasta | 49 | PG299 | Beegum Gorge
| Stanislaus | 33 | 045PG | Mt. Oso
| Sutter | 29 | 553PG | Harter Parkway
| Tehama | 43 | TCKC1 | Thomes Creek
| Trinity | 39 | 437PG | Weaverville

## Appendix A-1.1
#VALUE!
Table A-1.1: Factors Considered in the Decision to Shut Off Power for Each Distribution Circuit De-energized During the June 19 – 22, 2025 PSPS
| Circuit Name | Time | Forecast WS MPH | Forecast Temp 2MF | Forecast Flame Length ft 8hr | Forecast Rate of Spread Chhr 8hr | Forecast RH 2M | Forecast Prob Cat | Forecast DFM 10hr | Forecast DFM 100 hr | Forecast LFM Chamise New | Forecast CFPD | Agency NOAA (Yes/ No) | Agency RFW (Yes/ No) | Observed WS MPH | Observed WG MPH | Observed Temp F | Observed RH % | Observed WS MPH AC | Observed WG MPH AC | Observed Temp F AC | Observed RH% AC | Observed Open PSPS Tags (Yes/ No) | Observed Tx Impacts (Yes/ No) | PSPS Risk vs. Benefit PSPS Potential Risk Consequence | PSPS Risk vs. Benefit PSPS Potential Benefit
| ANTELOPE 1101 | TP15_6/21 | 23 | 89 | 13 | 183.5 | 12.9 | 0.33 | 0.03 | 0.05 | 75 | 1.39 | Yes | Yes | 24 | 30 | 83 | 11 | 21 | 28 | 71 | 19 | No | No | 0.2 | 60.1
| AVENAL 2101 | TP15_6/21 | 22 | 95 | 10.7 | 122 | 9.3 | 0.39 | 0.03 | 0.05 | 70 | 2.32 | Yes | Yes | No* | No* | No* | No* | No* | No* | No* | No* | No | No | 0.2 | 18.1
| BRENTWOOD 2105 | TP01_6/19 | 32 | 101 | 11.3 | 153.4 | 14.1 | 0.32 | 0.04 | 0.06 | 79 | 4.23 | Yes | Yes | 43 | 53 | 84 | 21 | 20 | 30 | 60 | 52 | Yes | No | 1.8 | 609.3
| BUELLTON 1101 | TP14_6/21 | 28 | 79 | 28.5 | 57.3 | 23.1 | 0.35 | 0.06 | 0.09 | 89 | 11.81 | Yes | No | 36 | 54 | 77 | 25 | 32 | 42 | 65 | 44 | Yes | No | 1.2 | 456
| CANTUA 1103 | TP12_6/21 | 21 | 95 | 10.4 | 133.1 | 7 | 0.38 | 0.02 | 0.04 | 67 | 3.08 | Yes | Yes | No* | No* | No* | No* | No* | No* | No* | No* | Yes | No | 0.2 | 18.1
| CARBONA 1101 | TP02_6/19 | 33 | 101 | 15.6 | 263.1 | 7.6 | 0.34 | 0.03 | 0.05 | 74 | 10.18 | Yes | Yes | 49 | 61 | 92 | 5 | 28 | 38 | 62 | 47 | Yes | No | 3 | No1
| CAYETANO 2109 | TP01_6/19 | 28 | 97 | 13.1 | 203.2 | 16.2 | 0.4 | 0.04 | 0.06 | 92 | 3.92 | No | No | 40 | 53 | 77 | 31 | 16 | 23 | 57 | 58 | Yes | No | 2.5 | 1041.2
| CHOLAME 1101 | TP11_6/21 | 26 | 87 | 11 | 143.4 | 15.1 | 0.23 | 0.04 | 0.08 | 76 | 2.1 | Yes | Yes | 26 | 34 | 82 | 14 | 22 | 29 | 72 | 27 | Yes | No | 1 | 912.9
| CLAYTON 2213 | TP03_6/19 | 20 | 95 | 10.2 | 122.7 | 18.2 | 0.43 | 0.04 | 0.07 | 89 | 2.89 | No | No | 43 | 56 | 84 | 7 | 27 | 40 | 58 | 58 | Yes | No | 0.1 | 939
| COALINGA NO 2 1105 | TP12_6/21 | 30 | 94 | 9.7 | 111.1 | 5.9 | 0.36 | 0.03 | 0.05 | 66 | 13.22 | Yes | Yes | 25 | 39 | 78 | 15 | 25 | 38 | 74 | 22 | Yes | No | 0.2 | 116.8
| CORNING 1102 | TP11_6/19 | 23 | 103 | 10.9 | 135.4 | 7.8 | 0.57 | 0.03 | 0.05 | 89 | 4.16 | No | Yes | 21 | 43 | 80 | 20 | 16 | 32 | 62 | 31 | Yes | No | 3.3 | 338.9
| COTTONWOOD 1101 | TP16_6/19 | 21 | 103 | 8.7 | 93.7 | 7.5 | 0.53 | 0.03 | 0.05 | 92 | 5.67 | No | Yes | 18 | 40 | 77 | 22 | 12 | 26 | 59 | 40 | Yes | No | 4.7 | 831.8
| COTTONWOOD 1103 | TP16_6/19 | 19 | 104 | 7.3 | 54.3 | 7.5 | 0.54 | 0.03 | 0.05 | 92 | 4.25 | No | Yes | 21 | 40 | 83 | 22 | 8 | 16 | 65 | 43 | Yes | No | 9.2 | 689.6
| DEVILS DEN 1101 | TP15_6/21 | 25 | 94 | 13.2 | 181.8 | 10.7 | 0.37 | 0.03 | 0.05 | 69 | 2.6 | Yes | Yes | 23 | 36 | 79 | 14 | 11 | 15 | 69 | 22 | No | No | 0.2 | 18.1
| ELK CREEK 1101 | TP12_6/19 | 27 | 103 | 11.3 | 137.9 | 7.4 | 0.57 | 0.03 | 0.05 | 90 | 5.21 | No | Yes | 22 | 38 | 82 | 14 | 16 | 24 | 62 | 29 | Yes | No | 12.4 | 319
| ELK CREEK 1101 | TP02_6/21 | 27 | 97 | 10 | 116.7 | 7.6 | 0.54 | 0.03 | 0.05 | 90 | 6.3 | No | Yes | 22 | 30 | 88 | 16 | 13 | 19 | 77 | 19 | Yes | Yes | 13.9 | 310.9
| FRENCH GULCH 1101 | TP06_6/19 | 22 | 93 | 7.8 | 24.3 | 7.5 | 0.47 | 0.04 | 0.07 | 112 | 5.13 | No | No | 25 | 40 | 89 | 17 | 13 | 22 | 48 | 62 | Yes | No | 4.6 | 84.3
| FRENCH GULCH 1102 | TP06_6/19 | 23 | 95 | 8.5 | 58.3 | 9.3 | 0.47 | 0.03 | 0.06 | 108 | 4.56 | No | No | 27 | 41 | 94 | 11 | 16 | 28 | 57 | 46 | Yes | No | 1.4 | 20
| GIRVAN 1101 | TP06_6/19 | 26 | 103 | 9.1 | 88.3 | 7.1 | 0.49 | 0.03 | 0.05 | 93 | 9.82 | No | No | 27 | 41 | 96 | 9 | 14 | 29 | 59 | 40 | Yes | No | 5.9 | 311.5
| GIRVAN 1102 | TP06_6/19 | 20 | 102 | 7.7 | 57.7 | 7.8 | 0.51 | 0.03 | 0.05 | 102 | 5.85 | No | No | 26 | 43 | 96 | 9 | 13 | 27 | 59 | 40 | Yes | No | 8.4 | 535.2
| GLENN 1101 | TP12_6/19 | 21 | 104 | 11 | 133.3 | 7.6 | 0.54 | 0.03 | 0.05 | 89 | 6.05 | Yes | Yes | 21 | 43 | 81 | 17 | 18 | 25 | 63 | 29 | Yes | No | 0.9 | 196.4
| GLENN 1101 | TP02_6/21 | 21 | 98 | 10.1 | 114.5 | 7.1 | 0.52 | 0.03 | 0.05 | 89 | 5.63 | Yes | Yes | 27 | 34 | 81 | 13 | 7 | 12 | 78 | 19 | Yes | No | 6.7 | 180.4
| GUSTINE 1102 | TP04_6/19 | 32 | 103 | 12.6 | 185.1 | 11.3 | 0.41 | 0.03 | 0.05 | 73 | 11.94 | Yes | Yes | 27 | 42 | 90 | 15 | 18 | 34 | 61 | 42 | Yes | No | 0.3 | 291.2
| HERDLYN 1102 | TP01_6/19 | 38 | 101 | 15.7 | 300.1 | 12.6 | 0.36 | 0.03 | 0.06 | 75 | 7.74 | Yes | Yes | 49 | 61 | 91 | 7 | 28 | 38 | 62 | 48 | No | No | 11 | 710
| HOLLISTER 2102 | TP04_6/19 | 23 | 92 | 10.5 | 140.9 | 14.3 | 0.45 | 0.05 | 0.09 | 90 | 2.86 | Yes | Yes | 27 | 37 | 75 | 29 | 18 | 26 | 55 | 68 | Yes | No | 1.8 | 169.3
| JOLON 1102 | TP10_6/21 | 25 | 86 | 7.7 | 82.8 | 17.2 | 0.33 | 0.03 | 0.06 | 80 | 4.38 | No | No | 21 | 32 | 79 | 11 | 21 | 30 | 72 | 29 | Yes | No | 1.2 | 374.1
| KESWICK 1101 | TP06_6/19 | 25 | 101 | 10.6 | 41.3 | 8.2 | 0.51 | 0.03 | 0.05 | 103 | 12.18 | No | No | 27 | 43 | 94 | 9 | 16 | 28 | 60 | 42 | Yes | No | 7.6 | 311.8
| KING CITY 1102 | TP07_6/19 | 27 | 94 | 12.9 | 200.2 | 12.2 | 0.33 | 0.04 | 0.07 | 78 | 2.77 | Yes | No | 18 | 32 | 75 | 38 | 8 | 15 | 53 | 77 | No | No | 0.7 | 317.3
| KING CITY 1106 | TP07_6/19 | 26 | 100 | 14.4 | 241.8 | 9.1 | 0.42 | 0.03 | 0.06 | 77 | 4.09 | Yes | No | 19 | 32 | 88 | 9 | 8 | 15 | 55 | 61 | Yes | No | 0.9 | 342.6
| KING CITY 1102 | TP09_6/21 | 27 | 88 | 12.8 | 205 | 18.6 | 0.27 | 0.04 | 0.07 | 78 | 2.52 | Yes | No | 16 | 31 | 76 | 26 | 10 | 19 | 66 | 42 | No | No | 0.5 | 311
| KING CITY 1106 | TP09_6/21 | 27 | 88 | 13.1 | 209.3 | 17.3 | 0.34 | 0.03 | 0.06 | 77 | 2.43 | Yes | No | 23 | 33 | 76 | 21 | 14 | 21 | 68 | 36 | Yes | No | 0.7 | 342.6
| LAS POSITAS 2108 | TP02_6/19 | 22 | 92 | 14.8 | 265.6 | 20 | 0.37 | 0.06 | 0.09 | 90 | 2.2 | No | No | 28 | 37 | 81 | 17 | 13 | 17 | 54 | 69 | Yes | No | 1.5 | 1551.9
| LAURELES 1111 | TP15_6/19 | 26 | 92 | 10 | 51.4 | 6.6 | 0.5 | 0.03 | 0.06 | 96 | 8.44 | No | No | 25 | 45 | 81 | 6 | 25 | 45 | 50 | 55 | Yes | No | 2.3 | 68.3
| LOGAN CREEK 2102 | TP12_6/19 | 23 | 105 | 11.5 | 141.4 | 8.4 | 0.43 | 0.03 | 0.05 | 88 | 4.14 | Yes | Yes | 17 | 26 | 81 | 20 | 11 | 17 | 61 | 35 | Yes | No | 1.3 | 156.1
| LOGAN CREEK 2102 | TP02_6/21 | 21 | 98 | 10.5 | 123.9 | 7.2 | 0.41 | 0.03 | 0.05 | 87 | 2.18 | Yes | Yes | 28 | 36 | 88 | 15 | 12 | 16 | 77 | 19 | Yes | No | 1.3 | 124.1
| LOS OSITOS 2101 | TP07_6/19 | 27 | 99 | 12 | 162.4 | 6.9 | 0.47 | 0.03 | 0.05 | 78 | 3.92 | Yes | No | 26 | 36 | 91 | 5 | 8 | 16 | 53 | 41 | Yes | No | 2.4 | 270.5
| LOS OSITOS 2102 | TP09_6/21 | 27 | 87 | 12.5 | 191.4 | 19 | 0.24 | 0.06 | 0.11 | 79 | 2.33 | No | No | 25 | 34 | 76 | 23 | 20 | 26 | 66 | 40 | Yes | No | 1.3 | 500.4
| LOS OSITOS 2103 | TP15_6/19 | 28 | 98 | 9.4 | 83 | 11 | 0.66 | 0.04 | 0.06 | 80 | 12.69 | No | No | 29 | 45 | 91 | 6 | 25 | 45 | 51 | 55 | Yes | No | 4.6 | 314.8
| MAXWELL 1102 | TP03_6/21 | 18 | 98 | 8.8 | 87.8 | 7.8 | 0.36 | 0.03 | 0.05 | 86 | 1.84 | Yes | Yes | 21 | 29 | 79 | 18 | 8 | 11 | 77 | 21 | Yes | No | 1.3 | 86
| MAXWELL 1105 | TP03_6/21 | 18 | 98 | 9.8 | 105.2 | 7.7 | 0.41 | 0.03 | 0.05 | 87 | 2.07 | Yes | Yes | 25 | 35 | 82 | 15 | 12 | 16 | 76 | 21 | Yes | No | 0.9 | 88.2
| MERIDIAN 1102 | TP04_6/21 | 20 | 97 | 9.2 | 97.5 | 8.6 | 0.34 | 0.03 | 0.06 | 86 | 2.4 | Yes | Yes | No* | No* | No* | No* | No* | No* | No* | No* | Yes | No | 0.7 | 0
| OILFIELDS 1102 | TP08_6/19 | 26 | 99 | 12.9 | 185 | 10.8 | 0.34 | 0.05 | 0.08 | 74 | 3.51 | Yes | No | 33 | 46 | 89 | 10 | 14 | 22 | 54 | 59 | No | No | 1 | 621.2
| OILFIELDS 1102 | TP10_6/21 | 27 | 90 | 11.9 | 169.3 | 15.7 | 0.29 | 0.04 | 0.08 | 74 | 3.69 | Yes | No | 26 | 40 | 78 | 24 | 18 | 27 | 69 | 34 | No | No | 0.7 | 568.9
| OILFIELDS 1103 | TP10_6/21 | 31 | 88 | 11.2 | 153.2 | 15 | 0.51 | 0.03 | 0.06 | 75 | 3.35 | Yes | No | 21 | 34 | 85 | 8 | 21 | 30 | 74 | 27 | Yes | No | 15.8 | 425.8
| OREGON TRAIL 1102 | TP06_6/19 | 20 | 102 | 9.7 | 43.3 | 7.1 | 0.47 | 0.03 | 0.05 | 102 | 10.66 | No | No | 27 | 43 | 94 | 11 | 16 | 28 | 60 | 42 | Yes | No | 7.7 | 288.6
| OREGON TRAIL 1103 | TP06_6/19 | 20 | 102 | 9.6 | 29.6 | 7.5 | 0.46 | 0.03 | 0.05 | 102 | 9.07 | No | No | 27 | 43 | 94 | 11 | 16 | 28 | 60 | 42 | Yes | No | 9.1 | 518.5
| PEASE 1103 | TP04_6/21 | 19 | 96 | 9.2 | 103.7 | 9.1 | 0.42 | 0.03 | 0.06 | 89 | 2.71 | Yes | Yes | No* | No* | No* | No* | No* | No* | No* | No* | Yes | No | 0.6 | 0
| RED BLUFF 1103 | TP17_6/19 | 20 | 104 | 8.3 | 81.8 | 9.4 | 0.56 | 0.03 | 0.05 | 92 | 6.89 | No | Yes | 25 | 40 | 81 | 19 | 17 | 27 | 61 | 39 | Yes | No | 2 | 972.7
| SAN ARDO 1101 | TP08_6/19 | 25 | 98 | 12.6 | 170.8 | 13.1 | 0.38 | 0.05 | 0.09 | 74 | 2.38 | Yes | No | 24 | 34 | 82 | 20 | 14 | 25 | 53 | 77 | Yes | No | 1.4 | 305.8
| SAN ARDO 1102 | TP08_6/19 | 29 | 97 | 12.1 | 172 | 8.2 | 0.46 | 0.03 | 0.05 | 77 | 3.56 | Yes | No | 24 | 34 | 88 | 6 | 14 | 25 | 57 | 28 | Yes | No | 5.8 | 478.1
| SAN ARDO 1101 | TP09_6/21 | 26 | 90 | 12.9 | 195 | 15.9 | 0.33 | 0.05 | 0.09 | 74 | 2.36 | No | No | 19 | 31 | 78 | 16 | 11 | 20 | 68 | 33 | Yes | No | 0.9 | 303.4
| SAN ARDO 1102 | TP09_6/21 | 30 | 90 | 13.1 | 197 | 14.1 | 0.38 | 0.03 | 0.05 | 74 | 2.62 | No | No | 26 | 40 | 78 | 22 | 18 | 27 | 69 | 29 | Yes | No | 5.8 | 478.1
| SAN MIGUEL 1106 | TP09_6/19 | 32 | 101 | 12.4 | 170.6 | 8.9 | 0.43 | 0.04 | 0.06 | 72 | 3.03 | Yes | No | 26 | 43 | 90 | 10 | 14 | 23 | 54 | 59 | Yes | No | 4.2 | 700.6
| SAN MIGUEL 1107 | TP09_6/19 | 26 | 101 | 13 | 179 | 8.1 | 0.39 | 0.03 | 0.06 | 75 | 3.56 | Yes | No | 25 | 38 | 93 | 7 | 23 | 26 | 53 | 65 | Yes | No | 5.5 | 321.1
| SAN MIGUEL 1105 | TP11_6/21 | 27 | 89 | 9.4 | 107.3 | 16.1 | 0.28 | 0.04 | 0.08 | 73 | 2.4 | No | No | 23 | 37 | 79 | 19 | 23 | 35 | 70 | 31 | Yes | No | 1.4 | 1040.8
| SAN MIGUEL 1106 | TP11_6/21 | 33 | 89 | 12 | 177.2 | 14.5 | 0.36 | 0.03 | 0.06 | 72 | 2.43 | Yes | No | 23 | 37 | 81 | 14 | 23 | 35 | 70 | 31 | Yes | No | 2.3 | 544.6
| SAN MIGUEL 1107 | TP11_6/21 | 28 | 87 | 12.1 | 172.4 | 13.6 | 0.32 | 0.03 | 0.06 | 74 | 2.67 | Yes | No | 26 | 37 | 82 | 14 | 23 | 35 | 72 | 27 | Yes | No | 2.9 | 311.1
| SANTA NELLA 1103 | TP04_6/19 | 36 | 100 | 13.5 | 204.6 | 12.2 | 0.34 | 0.03 | 0.06 | 77 | 7.16 | Yes | Yes | 27 | 42 | 86 | 18 | 16 | 34 | 60 | 57 | No | No | 1.2 | 0
| SANTA NELLA 1104 | TP04_6/19 | 36 | 97 | 10.4 | 118.5 | 12.6 | 0.27 | 0.04 | 0.07 | 82 | 1.94 | Yes | Yes | 27 | 42 | 86 | 18 | 16 | 34 | 60 | 57 | Yes | No | 0.1 | 410.1
| SANTA YNEZ 1102 | TP14_6/21 | 27 | 81 | 25.3 | 63.4 | 20.5 | 0.48 | 0.05 | 0.07 | 87 | 13.07 | Yes | No | 34 | 50 | 79 | 29 | 16 | 26 | 66 | 41 | Yes | No | 2.1 | 446
| SOLEDAD 2101 | TP07_6/19 | 29 | 92 | 12.4 | 182.8 | 16.5 | 0.4 | 0.04 | 0.07 | 79 | 5.43 | No | No | 34 | 44 | 90 | 6 | 19 | 27 | 59 | 65 | Yes | No | 5 | 431.8
| TEJON 1102 | TP13_6/21 | 32 | 85 | 24.7 | 148.2 | 13.4 | 0.37 | 0.04 | 0.06 | 96 | 8.99 | Yes | Yes | 29 | 50 | 69 | 20 | 25 | 41 | 63 | 25 | Yes | No | 4.9 | 649
| TIDEWATER 2106 | TP03_6/19 | 29 | 96 | 11.6 | 158.1 | 17.4 | 0.38 | 0.04 | 0.06 | 89 | 3.1 | No | No | 43 | 56 | 84 | 17 | 27 | 40 | 58 | 58 | Yes | No | 1.6 | 1321.7
| TYLER 1105 | TP17_6/19 | 24 | 104 | 10.4 | 122.9 | 9.6 | 0.56 | 0.03 | 0.05 | 90 | 7.34 | No | Yes | 27 | 40 | 81 | 19 | 21 | 30 | 61 | 38 | Yes | No | 7.5 | 1135.6
| VASCO 1102 | TP02_6/19 | 30 | 94 | 15.8 | 301.2 | 7.3 | 0.43 | 0.03 | 0.05 | 87 | 2.54 | Yes | Yes | 49 | 61 | 81 | 11 | 28 | 38 | 54 | 66 | Yes | No | 6.6 | 1589.3
| VASCO 1103 | TP02_6/19 | 32 | 94 | 14.6 | 253.2 | 16.5 | 0.24 | 0.05 | 0.08 | 85 | 1.61 | No | No | 49 | 61 | 74 | 29 | 28 | 38 | 54 | 70 | No | No | 0.4 | 1249.2
| WESTLEY 1101 | TP02_6/19 | 24 | 102 | 11.8 | 155.2 | 5.6 | 0.34 | 0.03 | 0.05 | 72 | 3.62 | Yes | Yes | 23 | 26 | 92 | 5 | 16 | 19 | 61 | 47 | No | No | 1.5 | 0
| WESTLEY 1103 | TP02_6/19 | 23 | 101 | 10.9 | 133.4 | 5.8 | 0.45 | 0.03 | 0.04 | 75 | 2.91 | Yes | Yes | 25 | 43 | 98 | 5 | 20 | 24 | 50 | 44 | Yes | No | 1.8 | 332.4
| WILDWOOD 1101 | TP10_6/19 | 23 | 98 | 27.6 | 33.2 | 9.7 | 0.45 | 0.03 | 0.05 | 96 | 4.79 | No | No | 32 | 49 | 89 | 11 | 21 | 35 | 49 | 56 | Yes | No | 1.2 | 334.5
| ZACA 1102 | TP14_6/21 | 26 | 84 | 9 | 94.2 | 12.7 | 0.51 | 0.04 | 0.05 | 87 | 7.11 | Yes | Yes | 28 | 37 | 77 | 17 | 3 | 11 | 58 | 35 | Yes | No | 2.2 | 1286.9
1 PSPS Potential Benefit data is not available for Carbona 1101 and is currently under review. We will provide an update in the 2025 PSPS Post-Season Report.
* Due to no nearby weather stations, subject matter expertise was used by Meteorologist in Charge to detemine when to de-energize Avenal 2101, Cantua 1103, Meridian 1102, and Pease 1103.

## Appendix A-1.2
#VALUE!
Table A-1.2: Description, Units, and Value provided for Factors Considered in the Decision to Shut Off Power for Each Distribution Circuit De-energized During the June 19 – 22, 2025 PSPS
| Forecast / Agency / Observed | Value | Name | Unit | Value Provided | Description
| Forecast | WS MPH | Sustained Wind Speeds | mph | max | Sustained windspeed in miles per hour at 10 meters above ground level.
| Forecast | Temp 2MF | Temperature | degrees F | max | Temperature in Fahrenheit at 2 meters above ground level.
| Forecast | Flame Length ft 8hr | Flame Length | ft | max | Flame length in feet on fire front for first 8 hours of fire spread simulation from Technosylva.
| Forecast | Rate of Spread Chhr 8hr | Rate of Spread | chains/hr | max | Rate of fire spread in chains per hour for first 8 hours of fire spread simulation from Technosylva.
| Forecast | RH 2M | Relative Humidity | % | min | Relative Humidity in percent at 2 meters above ground level.
| Forecast | Prob Cat | Fire Potential Index (FPI) | probability outputs | max | Fire Potential Index (FPI) Model Output - Probability of a catastrophic fire if an ignition were to occur. FPI component of the CFPD model.
| Forecast | DFM 10hr | Dead Fuel Moisture Content 10 hrs | fuel moisture fraction | min | Dead Fuel Moisture in 10-hour fuel moisture class. Can be scaled to percentage by multiplying by 100.
| Forecast | DFM 100hr | Dead Fuel Moisture Content 100 hrs | fuel moisture fraction | min | Dead Fuel Moisture in 100-hour moisture class. Can be scaled to percentage by multiplying by 100.
| Forecast | LMF Chamise New | Live Fuel Moisture Content-shrub | % | min | Live Fuel Moisture Percentage of Chamise (shrub) plant species. (% of species that is comprised of water).
| Forecast | CFPD | Catastrophic Fire Probability (CFPD) | Scaled Probability | max | The product of probability of catastrophic fire (Prob Cat) and IPW - probability of ignition (Prob Ignition). This product is called the (CFPD) Catastrophic Fire Probability distribution. Scaled by 1000 to convert to an integer value.
| Agency | NOAA (Yes/No) | National Oceanic and Atmospheric Administration | N/A | Yes/No During Event | NOAA (SPC) Fire Weather Outlook forecast.
| Agency | RFW (Yes/No) | Red Flag Warning | N/A | Yes/No During Event | Red Flag Warning from the Federal National Weather Service.
| Observed | WS MPH | Observed Sustained Wind Speed During Event | mph | max | The maximum sustained wind speed recorded by weather stations mapped to each circuit from planned de-energization time to anticipated All-Clear time.
| Observed | WG MPH | Observed Peak Wind Gust During Event | mph | max | The maximum wind gust recorded by weather stations mapped to each circuit from planned de-energization time to anticipated All- Clear time.
| Observed | Temp F | Observed Temperature During Event | degrees F | max | The maximum temperature recorded by weather stations mapped to each circuit from planned de-energization time to anticipated All-Clear time.
| Observed | RH_% | Observed Relative Humidity During Event | % | min | Minimum relative humidity recorded by all weather stations mapped to each circuit from planned de-energization time to anticipated All-Clear time.
| Observed | WS MPH AC | Observed Sustained Wind Speed at All-Clear | mph | max | The maximum sustained wind speed recorded by weather stations mapped to each circuit at the All-Clear time.
| Observed | WG MPH AC | Observed Peak Wind Gust at All-Clear | mph | max | The maximum wind gust recorded by weather stations mapped to each circuit at the All-Clear time.
| Observed | Temp F AC | Observed Temperature at All-Clear | degrees F | max | The maximum temperature recorded by weather stations mapped to each circuit at the All-Clear time.
| Observed | RH % AC | Observed Relative Humidity at All-Clear | % | min | Minimum relative humidity recorded by all weather stations mapped to each circuit at the All-Clear time.
| Observed | Open PSPS Tags (Yes/No) | Open PSPS Qualified Tags | N/A | Yes/No During Event | PSPS-Qualified Tags include P1 (tree represents an immediate risk) and P2 (tree is damaged or diseased and could fall into nearby power lines) tree tags and Electric Corrective tags (Priority A - emergency, B - urgent, and E/F - risk-based).
| Observed | Tx Impacts (Yes/No) | Impacted by Transmission | N/A | Yes/No During Event | Distribution lines that would have been de-energized due to de-energization of upstream transmission lines, regardless of whether those distribution lines would have also been de-energized due to direct distribution PSPS.
| Observed | PSPS Potential Risk Consequence | PSPS Potential Risk Consequence | MAVF Score | Yes/No During Event | Measure of the adverse impact to customers due to de-energization.
| Observed | PSPS Potential Benefit | PSPS Potential Benefit | MAVF Score | Yes/No During Event | Measure of the adverse impact to customers due to a catastrophic fire.

## Appendix A-2.1
#VALUE!
Table A-2.1: Factors Considered in the Decision to Shut Off Power for Each Transmission Circuit De-energized During the June 19 – 22, 2025 PSPS
| Circuit Name | Time Place | Forecast WS MPH | Forecast Temp 2MF | Forecast Flame Length ft 8hr | Forecast Rate of Spread Chhr 8hr | Forecast RH 2M | Forecast Prob Cat | Forecast DFM 10hr | Forecast DFM 100hr | Forecast LFM Chamise New | Forecast OA | Forecast CFPT | Agency NOAA (Yes/ No) | Agency RFW (Yes/ No) | Observed WS MPH | Observed WG MPH | Observed Temp F | Observed RH % | Observed WS MPH AC | Observed WG MPH AC | Observed Temp F AC | Observed RH % AC | Observed HFRA (Yes/No) | Observed High Risk Veg Present on Circuit (Yes/No) | PSPS Risk vs. Benefit PSPS Potential Risk Consequence | PSPS Risk vs. Benefit PSPS Potential Benefit
| TESLA-SCHULTE SW STA #1 | TP01_6/19 | 37 | 100 | 15.9 | 303.9 | 12.2 | 0.36 | 0.03 | 0.05 | 77 | 0.006 | 12.55 | No | No | 49 | 61 | 91 | 7 | 37 | 46 | 61 | 50 | No | No | 0.1 | 411.8
| TESLA-SCHULTE SW STA #2 | TP01_6/19 | 37 | 100 | 15.9 | 303.9 | 12.2 | 0.36 | 0.03 | 0.05 | 77 | 0.015 | 12.55 | No | No | 49 | 61 | 91 | 7 | 37 | 46 | 61 | 50 | No | No | 0.1 | 417.8
| AEC SITE #1 TAP | TP01_6/19 | 37 | 96 | 15.8 | 297.8 | 13 | 0.29 | 0.03 | 0.05 | 84 | 0.028 | 6.37 | No | No | 49 | 61 | 87 | 7 | 37 | 46 | 61 | 50 | No | No | 0.1 | 457.8
| AEC SITE #2 TAP | TP01_6/19 | 36 | 95 | 15.8 | 297.8 | 14.5 | 0.27 | 0.04 | 0.06 | 85 | 0.002 | 0.33 | No | No | 49 | 61 | 87 | 7 | 37 | 46 | 61 | 50 | No | No | 0.1 | 589.2
| SAFEWAY TAP | TP01_6/19 | 33 | 99 | 10.9 | 144 | 13 | 0.32 | 0.03 | 0.05 | 80 | 0.0014 | 3.24 | No | No | 40 | 45 | 91 | 7 | 6 | 12 | 61 | 51 | No | No | 0.1 | 306.9
| PITTSBURG-TESLA #2 | TP01_6/19 | 38 | 101 | 14.3 | 257.7 | 14.1 | 0.39 | 0.04 | 0.06 | 82 | 0.004 | 12.62 | No | No | 49 | 61 | 86 | 7 | 37 | 46 | 62 | 40 | Yes | No | 0.1 | 1292.2
| DELTA SWITCHING YARD-TESLA | TP01_6/19 | 38 | 99 | 14.3 | 257.7 | 14.1 | 0.36 | 0.04 | 0.06 | 81 | 0.003 | 12.62 | No | No | 49 | 61 | 86 | 7 | 23 | 27 | 58 | 51 | No | No | 0.1 | 681.3
| ELLIS TAP | TP01_6/19 | 32 | 99 | 7.1 | 54.8 | 14 | 0.35 | 0.04 | 0.06 | 81 | 0.0007 | 0.34 | No | No | 48 | 61 | 86 | 7 | 19 | 26 | 58 | 51 | No | No | 0.1 | 362.6
| KELSO-TESLA | TP01_6/19 | 38 | 99 | 14.3 | 257.7 | 14.1 | 0.36 | 0.04 | 0.06 | 81 | 0.003 | 7.96 | No | No | 49 | 61 | 86 | 7 | 23 | 27 | 58 | 51 | No | No | 0.1 | 731.2
| RALPH TAP | TP01_6/19 | 38 | 97 | 11.9 | 183.7 | 14.7 | 0.25 | 0.05 | 0.08 | 86 | 0.0005 | 0.14 | No | No | 43 | 53 | 79 | 26 | 19 | 24 | 55 | 72 | No | No | 0.1 | 597.6
| TEICHERT TAP | TP01_6/19 | 22 | 101 | 11.1 | 128.5 | 5.9 | 0.32 | 0.03 | 0.05 | 73 | 5e-05 | 0.02 | No | No | 23 | 26 | 92 | 5 | 10 | 12 | 59 | 51 | No | No | 0.1 | 0
| TESLA-LAWRENCE LAB | TP01_6/19 | 37 | 98 | 14.9 | 268.8 | 14.6 | 0.35 | 0.04 | 0.06 | 82 | 0.0123 | 7.96 | No | No | 49 | 61 | 86 | 7 | 23 | 27 | 58 | 51 | No | No | 0.1 | 1287.6
| TESLA-NEWARK #2 | TP01_6/19 | 37 | 98 | 14.9 | 268.8 | 14.6 | 0.35 | 0.04 | 0.06 | 82 | 0.009 | 12.62 | No | No | 49 | 61 | 86 | 7 | 23 | 27 | 58 | 51 | Yes | No | 0.1 | 1464.4
| TESLA-SALADO #1 | TP01_6/19 | 37 | 103 | 15 | 268.4 | 5.6 | 0.38 | 0.03 | 0.05 | 73 | 0.049 | 12.62 | No | No | 49 | 61 | 98 | 4 | 23 | 27 | 64 | 37 | Yes | No | 0.1 | 445.5
| TESLA-SALADO-MANTECA | TP01_6/19 | 37 | 103 | 15 | 268.4 | 5.5 | 0.38 | 0.03 | 0.05 | 73 | 0.049 | 12.62 | No | No | 49 | 61 | 98 | 4 | 23 | 27 | 64 | 37 | Yes | No | 0.1 | 363.2
| TESLA-STOCKTON COGEN JCT | TP01_6/19 | 37 | 100 | 13.8 | 249.2 | 12.2 | 0.36 | 0.03 | 0.05 | 76 | 0.033 | 12.62 | No | No | 49 | 61 | 91 | 7 | 23 | 27 | 60 | 48 | No | No | 0.1 | 433.5
| TESLA-TRACY(115KV) | TP01_6/19 | 37 | 99 | 13.4 | 238.9 | 14 | 0.36 | 0.04 | 0.06 | 81 | 0.004 | 7.96 | No | No | 49 | 61 | 86 | 7 | 23 | 27 | 58 | 51 | No | No | 0.1 | 0
| TESLA-WESTLEY | TP01_6/19 | 37 | 101 | 15 | 268.4 | 5.6 | 0.36 | 0.03 | 0.05 | 73 | 0.001 | 12.62 | No | No | 49 | 61 | 98 | 4 | 23 | 27 | 64 | 37 | No | No | 0.1 | 463.3
| LOS BANOS-MERCY SPRINGS SW STA | TP01_6/19 | 30 | 104 | 14.7 | 219.9 | 7.9 | 0.36 | 0.03 | 0.05 | 70 | 0.01 | 2.67 | No | No | 27 | 42 | 92 | 6 | 14 | 17 | 58 | 50 | No | No | 0.1 | 234.3
| COBURN-OIL FIELDS #2 | TP01_6/19 | 26 | 99 | 11.5 | 156.9 | 11.9 | 0.29 | 0.05 | 0.1 | 74 | 0.003 | 0.92 | No | No | 33 | 46 | 79 | 25 | 11 | 15 | 51 | 83 | No | No | 0.1 | 594.6
| MILLER #1 TAP | TP01_6/19 | 27 | 103 | 13.1 | 190.8 | 5.9 | 0.41 | 0.03 | 0.05 | 74 | No1 | 0.22 | No | No | 20 | 30 | 94 | 4 | 3 | 7 | 63 | 37 | No | No | 0.1 | 186.3
| ELK CREEK TAP | TP02_6/21 | 21 | 98 | 10.3 | 116 | 7.3 | 0.45 | 0.03 | 0.05 | 89 | 0.003 | 0.52 | No | No | 20 | 26 | 67 | 30 | 20 | 25 | 67 | 30 | Yes | No | 0.1 | 1028.7
1 Miller #1 Tap did not meet the required PSPS scoping criteria; therefore, OA is not available.

## Appendix A-2.2
#VALUE!
Table A-2.2: Description, Units, and Value provided for Factors Considered in the Decision to Shut Off Power for Each Transmission Circuit De-energized During the June 19 – 22, 2025 PSPS
| Forecast / Agency / Observed | Value | Name | Unit | Value Provided | Description
| Forecast | WS MPH | Sustained Wind Speed | mph | max | Sustained windspeed in miles per hour at 10 meters above ground level.
| Forecast | Temp 2MF | Temperature | degrees F | max | Temperature in Fahrenheit at 2 meters above ground level.
| Forecast | Flame Length ft 8hr | Flame Length | ft | max | Flame length in feet on fire front for first 8 hours of fire spread simulation from Technoslyva.
| Forecast | Rate of Spread Chhr 8hr | Rate of Spread | chains/hr | max | Rate of fire spread in chains per hour for first 8 hours of fire spread simulation from Technoslyva.
| Forecast | RH 2M | Relative Humidity | % | min | Relative Humidity in percent at 2 meters above ground level.
| Forecast | Prob Cat | Fire Potential Index (FPI) | probability outputs | max | FPI Model Output - Probability of a catastrophic fire if an ignition were to occur. FPI component of the CFPD model.
| Forecast | DFM 10hr | Dead Fuel Moisture Content 10 hrs (%) | fuel moisture fraction | min | Dead Fuel Moisture in 10-hour fuel moisture class. Can be scaled to percentage by multiplying by 100.
| Forecast | DFM 100hr | Dead Fuel Moisture Content 100 hrs (%) | fuel moisture fraction | min | Dead Fuel Moisture in 100-hour moisture class. Can be scaled to percentage by multiplying by 100.
| Forecast | LFM Chamise New | Live Fuel Moisture Content-shrub | % | min | Live Fuel Moisture Percentage of Chamise (shrub) plant species (% of species that are comprised of water).
| Forecast | OA | Transmission Operability Assessment (OA) | Probability | max | IPW Model Output - Probability of Ignition based on the probability of outages by cause. Ignition component of the CFPD model. IPW Model - A model that provides estimates of the probability of an ignition given an outage on an hourly basis.
| Forecast | CPFT | Catastrophic Fire Potential (CFPT) | Scaled Probability | max | The product of probability of catastrophic fire (Prob Cat) and IPW - probability of ignition (Prob Ignition). This product is called the (CFPD) Catastrophic Fire Probability distribution model. Scaled by 1000 to convert to an integer value.
| Agency | NOAA (Yes/No) | National Oceanic and Atmospheric Administration | N/A | Yes/No During Event | NOAA (SPC) Fire Weather Outlook forecast.
| Agency | RFW (Yes/No) | Red Flag Warning | N/A | Yes/No During event | Red Flag Warning from the Federal National Weather Service.
| Observed | WS MPH | Observed Sustained Wind Speed During Event | mph | max | The maximum sustained wind speed recorded by weather stations mapped to each circuit from de-energization time to All-Clear time.
| Observed | WG MPH | Observed Wind Gust During Event | mph | max | The maximum sustained wind gust recorded by weather stations mapped to each circuit from de-energization time to All-Clear time.
| Observed | Temp F | Observed Temperature During Event | degrees F | max | The maximum temperature recorded by weather stations mapped to each circuit from de-energization time to All-Clear time.
| Observed | RH % | Observed Relative Humidity During Event | % | min | Minimum relative humidity recorded by all weather stations mapped to each circuit from de-energization time to All-Clear time.
| Observed | WS MPH AC | Observed Sustained Wind Speed at All-Clear | mph | max | The maximum sustained wind speed recorded by weather stations mapped to each circuit at the All-Clear time.
| Observed | WG MPH AC | Observed Sustained Wind Gust at All-Clear | mph | max | The maximum sustained wind gust recorded by weather stations mapped to each circuit at the All-Clear time.
| Observed | Temp F AC | Observed Temperature at All-Clear | degrees F | max | The maximum temperature recorded by weather stations mapped to each circuit at the All-Clear time.
| Observed | RH % AC | Observed Relative Humidity at All-Clear | % | min | Minimum relative humidity recorded by all weather stations mapped to each circuit at the All-Clear time.
| Observed | HFRA (Yes/No) | High Fire Risk Area | N/A | Yes/No During Event | Labeled ‘Yes’ when Circuit goes through High Fire Risk Area.
| Observed | High Risk Veg Present on Circuit (Yes/No) | High Risk Vegetation Present on Circuit | N/A | Yes/No During Event | High risk vegetation present on the circuit.
| Observed | PSPS Potential Risk Consequence | PSPS Potential Risk Consequence | MAVF Score | Yes/No During Event | Measure of the adverse impact to customers due to de-energization.
| Observed | PSPS Potential Benefit | PSPS Potential Benefit | MAVF Score | Yes/No During Event | Measure of the adverse impact to customers due to a catastrophic fire.

## Appendix B
#VALUE!
Circuits labeled as “non-HFTD” are located outside of the CPUC High Fire-Threat District (HFTD). These circuits or portions of circuits are impacted for one of two reasons: (1) indirect impacts from transmission lines being de-energized or (2) the non-HFTD portion of the circuit are conductive to the HFTD at some point in the path to service. Circuits with an asterisk (*) were sectionalized during the PSPS to further reduce customer impact. The de-energization date and time represents the time the first customer was de-energized on the circuit and the restoration time represents the date and time of the last customer restored on a circuit by circuit.
Table B-1. Circuits De-Energized During the June 19 – 22, 2025 PSPS
| Distribution / Transmission | Circuit Name | De-Energization Date and Time (PDT) | All-Clear Date and Time (PDT) | Restoration Date and Time (PDT) | Key Communities | HFTD Tier(s) | Total Customers | Residential Customers | Commercial / Industrial Customers | MBL Program Customers | AFN other than MBL Program Customers | Other Customers
| Distribution | ANTELOPE 1101* | 2025-06-21 15:16 | 2025-06-22 07:08 | 2025-06-22 11:13 | KERN | Partially Outside HFTD, Tier 2 | 7 | 1 | 6 | 0 | 0 | 0
| Distribution | AVENAL 2101* | 2025-06-21 15:13 | 2025-06-22 07:08 | 2025-06-22 08:27 | KINGS | Outside HFTD | 3 | 0 | 3 | 0 | 0 | 0
| Distribution | BRENTWOOD 2105* | 2025-06-19 09:41 | 2025-06-20 10:18 | 2025-06-20 13:42 | CONTRA COSTA | Partially Outside HFTD, Tier 2 | 83 | 44 | 30 | 4 | 4 | 9
| Distribution | BUELLTON 1101* | 2025-06-21 15:03 | 2025-06-22 07:08 | 2025-06-22 10:42 | SANTA BARBARA | Partially Outside HFTD, Tier 3, Tier 2 | 162 | 80 | 48 | 1 | 8 | 34
| Distribution | CANTUA 1103* | 2025-06-21 13:55 | 2025-06-22 07:08 | 2025-06-22 09:50 | FRESNO | Outside HFTD | 16 | 2 | 6 | 0 | 0 | 8
| Distribution | CARBONA 1101* | 2025-06-19 09:34 | 2025-06-21 04:34 | 2025-06-21 08:52 | ALAMEDA, SAN JOAQUIN | Outside HFTD | 177 | 100 | 42 | 7 | 13 | 35
| Distribution | CAYETANO 2109* | 2025-06-19 09:42 | 2025-06-21 04:34 | 2025-06-21 07:22 | CONTRA COSTA, ALAMEDA | Tier 3 | 59 | 40 | 19 | 6 | 1 | 0
| Distribution | CHOLAME 1101* | 2025-06-21 16:58 | 2025-06-22 07:08 | 2025-06-22 10:18 | SAN LUIS OBISPO | Outside HFTD | 160 | 123 | 7 | 4 | 16 | 30
| Distribution | CLAYTON 2213* | 2025-06-19 10:36 | 2025-06-21 04:34 | 2025-06-21 07:37 | CONTRA COSTA | Tier 2 | 4 | 0 | 4 | 0 | 0 | 0
| Distribution | COALINGA NO 2 1105* | 2025-06-21 14:11 | 2025-06-22 07:08 | 2025-06-22 09:54 | SAN BENITO, MONTEREY, FRESNO | Outside HFTD | 19 | 2 | 14 | 0 | 1 | 3
| Distribution | CORNING 1102* | 2025-06-20 18:16 | 2025-06-21 04:34 | 2025-06-21 11:35 | TEHAMA | Partially Outside HFTD, Tier 2 | 282 | 227 | 46 | 14 | 68 | 9
| Distribution | COTTONWOOD 1101* | 2025-06-20 15:33 | 2025-06-21 04:34 | 2025-06-21 10:47 | SHASTA, TEHAMA | Partially Outside HFTD, Tier 2 | 421 | 385 | 22 | 44 | 111 | 14
| Distribution | COTTONWOOD 1103* | 2025-06-20 15:36 | 2025-06-21 04:34 | 2025-06-21 09:23 | SHASTA, TEHAMA | Partially Outside HFTD, Tier 2 | 894 | 852 | 29 | 73 | 277 | 13
| Distribution | DEVILS DEN 1101* | 2025-06-21 15:09 | 2025-06-22 07:08 | 2025-06-22 10:22 | KINGS | Outside HFTD | 6 | 1 | 5 | 0 | 0 | 0
| Distribution | ELK CREEK 1101 | 2025-06-20 16:18 | 2025-06-22 07:08 | 2025-06-22 12:39 | COLUSA, GLENN | Partially Outside HFTD, Tier 2 | 817 | 678 | 114 | 45 | 173 | 25
| Distribution | FRENCH GULCH 1101 | 2025-06-19 18:42 | 2025-06-21 04:34 | 2025-06-21 13:59 | SHASTA | Partially Outside HFTD, Tier 2 | 234 | 207 | 27 | 25 | 81 | 0
| Distribution | FRENCH GULCH 1102 | 2025-06-19 18:44 | 2025-06-21 04:34 | 2025-06-21 14:23 | SHASTA | Partially Outside HFTD, Tier 2 | 38 | 10 | 27 | 1 | 1 | 1
| Distribution | GIRVAN 1101* | 2025-06-19 18:42 | 2025-06-21 04:34 | 2025-06-21 12:50 | SHASTA | Partially Outside HFTD, Tier 3, Tier 2 | 332 | 288 | 39 | 20 | 52 | 5
| Distribution | GIRVAN 1102* | 2025-06-19 18:43 | 2025-06-20 11:37 | 2025-06-21 12:53 | SHASTA | Partially Outside HFTD, Tier 3 | 590 | 575 | 14 | 47 | 95 | 1
| Distribution | GLENN 1101* | 2025-06-20 16:21 | 2025-06-22 07:08 | 2025-06-22 10:46 | GLENN, TEHAMA | Partially Outside HFTD, Tier 2 | 151 | 84 | 43 | 2 | 16 | 24
| Distribution | GUSTINE 1102* | 2025-06-19 10:11 | 2025-06-21 04:34 | 2025-06-21 09:34 | MERCED | Outside HFTD | 24 | 10 | 11 | 0 | 2 | 3
| Distribution | HERDLYN 1102 | 2025-06-19 09:48 | 2025-06-21 04:34 | 2025-06-21 12:39 | CONTRA COSTA, ALAMEDA, SAN JOAQUIN | Outside HFTD | 802 | 568 | 179 | 43 | 97 | 55
| Distribution | HOLLISTER 2102* | 2025-06-19 10:04 | 2025-06-21 04:34 | 2025-06-21 10:37 | SAN BENITO, SANTA CLARA | Partially Outside HFTD, Tier 2 | 94 | 33 | 49 | 0 | 4 | 12
| Distribution | JOLON 1102* | 2025-06-21 14:07 | 2025-06-22 07:08 | 2025-06-22 08:39 | MONTEREY | Tier 2 | 15 | 2 | 12 | 0 | 0 | 1
| Distribution | KESWICK 1101* | 2025-06-19 18:43 | 2025-06-21 04:34 | 2025-06-21 14:13 | SAN LUIS OBISPO, SHASTA | Partially Outside HFTD, Tier 3, Tier 2 | 524 | 432 | 90 | 27 | 121 | 2
| Distribution | KING CITY 1102* | 2025-06-19 13:01 | 2025-06-22 07:08 | 2025-06-22 12:36 | MONTEREY | Outside HFTD | 60 | 14 | 17 | 0 | 4 | 29
| Distribution | KING CITY 1106* | 2025-06-19 13:13 | 2025-06-22 07:08 | 2025-06-22 11:56 | SAN BENITO, MONTEREY | Outside HFTD | 88 | 42 | 25 | 0 | 5 | 21
| Distribution | LAS POSITAS 2108* | 2025-06-19 09:30 | 2025-06-20 10:18 | 2025-06-20 12:35 | ALAMEDA | Partially Outside HFTD, Tier 2 | 43 | 11 | 30 | 1 | 0 | 2
| Distribution | LAURELES 1111* | 2025-06-20 13:43 | 2025-06-21 04:34 | 2025-06-21 09:18 | MONTEREY | Partially Outside HFTD, Tier 2 | 221 | 174 | 36 | 7 | 20 | 11
| Distribution | LOGAN CREEK 2102* | 2025-06-20 16:23 | 2025-06-22 07:08 | 2025-06-22 13:05 | GLENN | Partially Outside HFTD, Tier 2 | 271 | 106 | 78 | 2 | 17 | 87
| Distribution | LOS OSITOS 2101* | 2025-06-19 12:55 | 2025-06-21 04:34 | 2025-06-21 09:42 | SAN BENITO, MONTEREY, FRESNO | Partially Outside HFTD, Tier 1 | 129 | 76 | 37 | 3 | 9 | 16
| Distribution | LOS OSITOS 2102* | 2025-06-21 16:58 | 2025-06-22 07:08 | 2025-06-22 17:22 | MONTEREY | Outside HFTD | 92 | 26 | 40 | 1 | 6 | 26
| Distribution | LOS OSITOS 2103* | 2025-06-20 13:36 | 2025-06-21 04:34 | 2025-06-21 12:31 | MONTEREY | Partially Outside HFTD, Tier 2 | 382 | 324 | 44 | 10 | 50 | 14
| Distribution | MAXWELL 1102* | 2025-06-21 10:23 | 2025-06-22 07:08 | 2025-06-22 12:05 | COLUSA | Outside HFTD | 145 | 59 | 22 | 5 | 2 | 64
| Distribution | MAXWELL 1105* | 2025-06-21 10:15 | 2025-06-22 07:08 | 2025-06-22 11:37 | COLUSA | Partially Outside HFTD, Tier 2 | 151 | 70 | 38 | 1 | 9 | 43
| Distribution | MERIDIAN 1102* | 2025-06-21 10:58 | 2025-06-22 07:08 | 2025-06-22 09:12 | COLUSA, SUTTER | Outside HFTD | 111 | 40 | 31 | 1 | 2 | 40
| Distribution | OILFIELDS 1102* | 2025-06-19 14:25 | 2025-06-22 07:08 | 2025-06-22 16:31 | MONTEREY | Outside HFTD | 92 | 34 | 29 | 1 | 7 | 29
| Distribution | OILFIELDS 1103* | 2025-06-21 14:08 | 2025-06-22 07:08 | 2025-06-22 16:03 | MONTEREY, SAN LUIS OBISPO | Partially Outside HFTD, Tier 2 | 2446 | 2168 | 231 | 96 | 264 | 47
| Distribution | OREGON TRAIL 1102* | 2025-06-19 18:48 | 2025-06-20 10:18 | 2025-06-20 13:27 | SHASTA | Tier 2 | 497 | 451 | 46 | 54 | 164 | 0
| Distribution | OREGON TRAIL 1103* | 2025-06-19 18:56 | 2025-06-20 10:18 | 2025-06-20 13:19 | SHASTA | Partially Outside HFTD, Tier 3, Tier 2 | 634 | 616 | 18 | 51 | 223 | 0
| Distribution | PEASE 1103* | 2025-06-21 10:52 | 2025-06-22 07:08 | 2025-06-22 08:16 | SUTTER | Outside HFTD | 90 | 53 | 20 | 2 | 1 | 17
| Distribution | RED BLUFF 1103* | 2025-06-20 15:35 | 2025-06-21 04:34 | 2025-06-21 11:40 | TEHAMA | Partially Outside HFTD, Tier 2 | 221 | 209 | 11 | 20 | 41 | 1
| Distribution | SAN ARDO 1101 | 2025-06-19 14:03 | 2025-06-22 07:08 | 2025-06-22 12:29 | MONTEREY | Partially Outside HFTD, Tier 2 | 131 | 43 | 42 | 0 | 6 | 46
| Distribution | SAN ARDO 1102* | 2025-06-19 14:07 | 2025-06-22 07:08 | 2025-06-22 12:48 | MONTEREY, SAN LUIS OBISPO, FRESNO | Partially Outside HFTD, Tier 2 | 439 | 269 | 107 | 3 | 91 | 63
| Distribution | SAN MIGUEL 1105* | 2025-06-21 16:49 | 2025-06-22 07:08 | 2025-06-22 10:57 | SAN LUIS OBISPO | Partially Outside HFTD, Tier 2 | 213 | 185 | 14 | 4 | 52 | 14
| Distribution | SAN MIGUEL 1106 | 2025-06-19 14:01 | 2025-06-22 07:08 | 2025-06-22 10:55 | MONTEREY, SAN LUIS OBISPO | Partially Outside HFTD, Tier 2 | 307 | 174 | 74 | 6 | 22 | 59
| Distribution | SAN MIGUEL 1107* | 2025-06-19 13:58 | 2025-06-22 07:08 | 2025-06-22 10:08 | MONTEREY, SAN LUIS OBISPO, SANTA BARBARA | Partially Outside HFTD, Tier 2 | 501 | 351 | 79 | 21 | 33 | 71
| Distribution | SANTA NELLA 1103* | 2025-06-19 10:15 | 2025-06-21 04:34 | 2025-06-21 08:58 | MERCED | Outside HFTD | 28 | 4 | 19 | 1 | 1 | 5
| Distribution | SANTA NELLA 1104* | 2025-06-19 10:18 | 2025-06-21 04:34 | 2025-06-21 09:02 | MERCED | Outside HFTD | 3 | 0 | 1 | 0 | 0 | 2
| Distribution | SANTA YNEZ 1102* | 2025-06-21 15:04 | 2025-06-22 07:08 | 2025-06-22 10:57 | SANTA BARBARA | Partially Outside HFTD, Tier 3, Tier 2 | 223 | 151 | 59 | 2 | 8 | 13
| Distribution | SOLEDAD 2101* | 2025-06-19 12:56 | 2025-06-21 04:34 | 2025-06-21 11:07 | MONTEREY | Partially Outside HFTD, Tier 2 | 396 | 322 | 39 | 9 | 114 | 35
| Distribution | TEJON 1102* | 2025-06-21 16:46 | 2025-06-22 07:08 | 2025-06-22 10:51 | KERN | Partially Outside HFTD, Tier 2 | 490 | 418 | 66 | 19 | 163 | 6
| Distribution | TIDEWATER 2106* | 2025-06-19 04:47 | 2025-06-21 04:34 | 2025-06-21 08:05 | CONTRA COSTA | Partially Outside HFTD, Tier 2 | 66 | 51 | 14 | 2 | 7 | 1
| Distribution | TYLER 1105* | 2025-06-20 15:30 | 2025-06-21 04:34 | 2025-06-21 10:31 | TEHAMA | Partially Outside HFTD, Tier 2 | 751 | 642 | 63 | 72 | 157 | 46
| Distribution | VASCO 1102* | 2025-06-19 09:34 | 2025-06-21 04:34 | 2025-06-21 12:00 | ALAMEDA | Partially Outside HFTD, Tier 2 | 480 | 344 | 110 | 26 | 31 | 26
| Distribution | VASCO 1103* | 2025-06-19 09:39 | 2025-06-21 04:34 | 2025-06-21 07:50 | ALAMEDA | Outside HFTD | 28 | 15 | 12 | 0 | 1 | 1
| Distribution | WESTLEY 1101* | 2025-06-19 09:44 | 2025-06-21 04:34 | 2025-06-21 09:59 | STANISLAUS, SAN JOAQUIN | Partially Outside HFTD, Tier 2 | 133 | 34 | 49 | 0 | 9 | 50
| Distribution | WESTLEY 1103* | 2025-06-19 09:52 | 2025-06-21 04:34 | 2025-06-21 08:41 | STANISLAUS | Outside HFTD | 26 | 3 | 21 | 0 | 0 | 2
| Distribution | WILDWOOD 1101* | 2025-06-19 17:19 | 2025-06-21 04:34 | 2025-06-21 16:00 | TRINITY, SHASTA, TEHAMA | Tier 2 | 101 | 73 | 25 | 5 | 18 | 3
| Distribution | ZACA 1102* | 2025-06-21 14:59 | 2025-06-22 07:08 | 2025-06-22 10:04 | SANTA BARBARA | Partially Outside HFTD, Tier 3, Tier 2 | 311 | 230 | 55 | 16 | 14 | 26
| Transmission | AEC SITE #1 TAP | 2025-06-19 09:49 | 2025-06-20 07:53 | 2025-06-20 11:13 | ALAMEDA, SAN JOAQUIN | Outside HFTD | 1 | 0 | 0 | 0 | 0 | 0
| Transmission | AEC SITE #2 TAP | 2025-06-19 09:49 | 2025-06-20 07:53 | 2025-06-20 11:13 | SAN JOAQUIN | Outside HFTD | 1 | 0 | 0 | 0 | 0 | 0
| Transmission | COBURN-OIL FIELDS #2 | 2025-06-19 14:36 | 2025-06-21 04:34 | 2025-06-21 14:44 | MONTEREY | Outside HFTD | 0 | 0 | 0 | 0 | 0 | 0
| Transmission | DELTA SWITCHING YARD-TESLA | 2025-06-19 10:23 | 2025-06-21 04:34 | 2025-06-21 12:23 | ALAMEDA | Outside HFTD | 0 | 0 | 0 | 0 | 0 | 0
| Transmission | ELK CREEK TAP | 2025-06-21 10:31 | 2025-06-22 07:08 | 2025-06-22 09:31 | GLENN | Partially Outside HFTD, Tier 2 | 1 | 0 | 0 | 0 | 0 | 0
| Transmission | ELLIS TAP | 2025-06-19 10:34 | 2025-06-21 04:34 | 2025-06-21 15:05 | SAN JOAQUIN | Outside HFTD | 1 | 0 | 0 | 0 | 0 | 0
| Transmission | KELSO-TESLA | 2025-06-19 10:11 | 2025-06-21 04:34 | 2025-06-21 11:14 | ALAMEDA | Outside HFTD | 0 | 0 | 0 | 0 | 0 | 0
| Transmission | LOS BANOS-MERCY SPRINGS SW STA | 2025-06-19 09:30 | 2025-06-21 04:34 | 2025-06-21 11:49 | MERCED | Outside HFTD | 0 | 0 | 0 | 0 | 0 | 0
| Transmission | MILLER #1 TAP | 2025-06-18 19:22 | 2025-06-21 04:34 | 2025-06-21 12:24 | STANISLAUS, MERCED | Outside HFTD | 0 | 0 | 0 | 0 | 0 | 0
| Transmission | PITTSBURG-TESLA #2 | 2025-06-19 09:42 | 2025-06-20 07:53 | 2025-06-21 13:43 | ALAMEDA, CONTRA COSTA | Partially Outside HFTD, Tier 2 | 0 | 0 | 0 | 0 | 0 | 0
| Transmission | RALPH TAP | 2025-06-19 10:11 | 2025-06-21 04:34 | 2025-06-21 11:14 | ALAMEDA | Outside HFTD | 1 | 0 | 0 | 0 | 0 | 0
| Transmission | SAFEWAY TAP | 2025-06-19 10:08 | 2025-06-20 07:53 | 2025-06-20 11:46 | SAN JOAQUIN | Outside HFTD | 1 | 0 | 0 | 0 | 0 | 0
| Transmission | TEICHERT TAP | 2025-06-18 19:22 | 2025-06-21 04:34 | 2025-06-21 12:24 | SAN JOAQUIN | Outside HFTD | 2 | 0 | 0 | 0 | 0 | 0
| Transmission | TESLA-LAWRENCE LAB | 2025-06-18 19:44 | 2025-06-21 04:34 | 2025-06-21 14:31 | ALAMEDA | Outside HFTD | 0 | 0 | 0 | 0 | 0 | 0
| Transmission | TESLA-NEWARK #2 | 2025-06-19 10:17 | 2025-06-21 04:34 | 2025-06-21 10:57 | ALAMEDA | Partially Outside HFTD, Tier 2 | 0 | 0 | 0 | 0 | 0 | 0
| Transmission | TESLA-SALADO #1 | 2025-06-18 19:22 | 2025-06-21 04:34 | 2025-06-21 12:24 | ALAMEDA, STANISLAUS, SAN JOAQUIN | Partially Outside HFTD, Tier 2 | 0 | 0 | 0 | 0 | 0 | 0
| Transmission | TESLA-SALADO-MANTECA | 2025-06-19 09:36 | 2025-06-21 04:34 | 2025-06-21 13:13 | ALAMEDA, STANISLAUS, SAN JOAQUIN | Partially Outside HFTD, Tier 2 | 0 | 0 | 0 | 0 | 0 | 0
| Transmission | TESLA-SCHULTE SW STA #1 | 2025-06-19 09:49 | 2025-06-20 07:53 | 2025-06-20 11:13 | ALAMEDA, SAN JOAQUIN | Outside HFTD | 0 | 0 | 0 | 0 | 0 | 0
| Transmission | TESLA-SCHULTE SW STA #2 | 2025-06-19 10:08 | 2025-06-20 07:53 | 2025-06-20 11:46 | ALAMEDA, SAN JOAQUIN | Outside HFTD | 0 | 0 | 0 | 0 | 0 | 0
| Transmission | TESLA-STOCKTON COGEN JCT (TESLA-VIERRA) | 2025-06-18 19:20 | 2025-06-21 04:34 | 2025-06-21 16:16 | ALAMEDA, SAN JOAQUIN | Outside HFTD | 1 | 0 | 0 | 0 | 0 | 0
| Transmission | TESLA-TRACY(115KV) | 2025-06-19 10:34 | 2025-06-21 04:34 | 2025-06-21 15:05 | ALAMEDA, SAN JOAQUIN | Outside HFTD | 0 | 0 | 0 | 0 | 0 | 0
| Transmission | TESLA-WESTLEY | 2025-06-19 10:13 | 2025-06-21 04:34 | 2025-06-21 14:00 | ALAMEDA, STANISLAUS, SAN JOAQUIN | Outside HFTD | 0 | 0 | 0 | 0 | 0 | 0
| Total | [6 empty] | 16223 | 12526 | 2488 | 804 | 2692 | 1200

## Appendix C
#VALUE!
Table C-1. Damages & Hazards Found Within the De-Energized Areas
| Circuit Name | County | Structure Identifier | Tier 2/3 or Non-HFTD | Damage / Hazard | Type of Damage/Hazard | Description of Damage/Hazard
| King City 1102 | Monterey | 101764470 | Non-HFTD | Damage | Wind Related | Other – broken transformer bushings
| Oilfields 1102 | Monterey | 101764178 | Non-HFTD | Damage | Wind Related | Broken crossarm
| Keswick 1102 | Shasta | 101465959 | Tier 3 | Hazard | Vegetation Contact | Tree leaning into line

## Appendix D
#VALUE!
Table D-1. Public Safety Partners Contacted
| Jurisdiction | Agency/Organization | HFTD or HFRA Tier1 | Date/Time Contacted (PDT)
| Alameda County | Alameda County Fire Department | Tier 2, Tier 3 | 2025-06-17 21:03
| Alameda County | Alameda County Fire Department, OES | Tier 2, Tier 3 | 2025-06-17 21:03
| Alameda County | BART | Tier 2, Tier 3 | 2025-06-17 21:03
| Alameda County | County Administration | Tier 2, Tier 3 | 2025-06-17 21:03
| Alameda County | County Administration, County of Alameda | Tier 2, Tier 3 | 2025-06-17 21:03
| Alameda County | EBMUD | Tier 2, Tier 3 | 2025-06-17 21:03
| Alameda County | EMS | Tier 2, Tier 3 | 2025-06-17 21:03
| Alameda County | Fire Department | Tier 2, Tier 3 | 2025-06-17 21:03
| Alameda County | OES | Tier 2, Tier 3 | 2025-06-17 21:03
| Alameda County | Office of Education | Tier 2, Tier 3 | 2025-06-17 21:03
| Alameda County | Office of Emergency Services | Tier 2, Tier 3 | 2025-06-17 21:03
| Alameda County | Sheriff's Department | Tier 2, Tier 3 | 2025-06-17 21:03
| Alameda County | Sheriff's Office | Tier 2, Tier 3 | 2025-06-17 21:03
| Alameda County CCA | East Bay Community Energy | Tier 2, Tier 3 | 2025-06-17 21:03
| Alameda County Communication Facility | AT&T Mobility LLC | Tier 2 | 2025-06-18 07:27
| Alameda County Communication Facility | AT&T Services Inc. | Tier 2 | 2025-06-18 07:27
| Alameda County Communication Facility | Global Valley Networks | Tier 2 | 2025-06-18 07:27
| Alameda County Communication Facility | GTE Mobile Net of California LP | Tier 2 | 2025-06-18 07:27
| Alameda County Communication Facility | TCI Cablevision | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-18 07:27
| Alameda County Communication Facility | Verizon Wireless | Tier 2 | 2025-06-18 07:27
| Alameda County Healthcare - Hospitals Facility | US Department of Veterans Affairs | Tier 2 | 2025-06-18 07:27
| Alameda County Other Facility | County of Alameda | Tier 2 | 2025-06-18 07:27
| Alameda County Other Facility | T-Mobile USA Inc. | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-18 07:27
| Colusa County | Colusa County Board of Supervisors | HFRA, Tier 2 | 2025-06-18 07:16
| Colusa County | County Administration | HFRA, Tier 2 | 2025-06-18 07:16
| Colusa County | County Public Works | HFRA, Tier 2 | 2025-06-18 07:16
| Colusa County | EMS | HFRA, Tier 2 | 2025-06-18 07:17
| Colusa County | Fire Department | HFRA, Tier 2 | 2025-06-18 07:16
| Colusa County | Fire Department | HFRA, Tier 2 | 2025-06-18 07:17
| Colusa County | OES | HFRA, Tier 2 | 2025-06-18 07:16
| Colusa County | Police Department | HFRA, Tier 2 | 2025-06-18 07:17
| Colusa County | Sheriff's Department | HFRA, Tier 2 | 2025-06-18 07:16
| Colusa County | US Forest Service Fire | HFRA, Tier 2 | 2025-06-18 07:16
| Colusa County Communication Facility | AT&T | Tier 2 | 2025-06-18 07:27
| Colusa County Communication Facility | AT&T Mobility LLC | Tier 2 | 2025-06-18 07:27
| Colusa County Communication Facility | AT&T Services Inc. | Tier 2 | 2025-06-18 07:27
| Colusa County Communication Facility | Citizens Telecommunications of California Inc. | Tier 2 | 2025-06-18 07:27
| Colusa County Communication Facility | Frontier Communications Corporation DIP | Tier 2 | 2025-06-18 07:27
| Colusa County Communication Facility | GTE Mobile Net of California LP | Tier 2 | 2025-06-18 07:27
| Colusa County Communication Facility | Verizon Services Corporation | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-18 07:27
| Colusa County Energy Sector Facility | Western Area Power Administration | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-19 03:01
| Colusa County Emergency Services Facility | California Department of Forestry | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-18 07:27
| Colusa County Emergency Services Facility | County of Colusa | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-18 07:27
| Colusa County Emergency Services Facility | Indian Valley - Bear Valley Fire Protection District | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-18 07:27
| Colusa County Emergency Services Facility | Indian Valley Fire Protection District | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-18 07:28
| Colusa County Energy Sector Facility | City of Santa Clara | HFRA, Tier 2 | 2025-06-18 07:27
| Colusa County Tribal | Cortina Rancheria | Tier 2 | 2025-06-18 07:16
| Colusa County Water and Waste Water Facility | California Department of Forestry | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-18 07:27
| Colusa County Water and Waste Water Facility | County of Colusa | Tier 2 | 2025-06-18 07:27
| Colusa County Williams | Fire Department | HFRA | 2025-06-18 07:16
| Colusa County Williams | Police Department | HFRA | 2025-06-18 07:17
| Contra Costa County | BART | Tier 2, Tier 3 | 2025-06-17 21:03
| Contra Costa County | City Administration | Tier 2, Tier 3 | 2025-06-17 21:03
| Contra Costa County | City Administration | Tier 2, Tier 3 | 2025-06-17 21:03
| Contra Costa County | Contra Costa County Fire Protection District | Tier 2, Tier 3 | 2025-06-17 21:03
| Contra Costa County | Contra Costa County Sheriff Department | Tier 2, Tier 3 | 2025-06-17 21:03
| Contra Costa County | Contra Costa Office of Emergency Services, OES | Tier 2, Tier 3 | 2025-06-17 21:03
| Contra Costa County | County Administration | Tier 2, Tier 3 | 2025-06-17 21:03
| Contra Costa County | County Administrator's Office | Tier 2, Tier 3 | 2025-06-17 21:03
| Contra Costa County | East Bay Regional Parks Fire Department | Tier 2, Tier 3 | 2025-06-17 21:03
| Contra Costa County | EMS | Tier 2, Tier 3 | 2025-06-17 21:03
| Contra Costa County | Fire Department | Tier 2, Tier 3 | 2025-06-17 21:03
| Contra Costa County | OES | Tier 2, Tier 3 | 2025-06-17 21:03
| Contra Costa County | Rodeo Hercules Fire Protection District | Tier 2, Tier 3 | 2025-06-17 21:03
| Contra Costa County | San Ramon Valley Fire Protection District | Tier 2, Tier 3 | 2025-06-17 21:03
| Contra Costa County CCA | MCE Clean Energy | Tier 2, Tier 3 | 2025-06-17 21:03
| Contra Costa County Communication Facility | AT&T Mobility LLC | Tier 2 | 2025-06-18 07:27
| Contra Costa County Communication Facility | AT&T Services Inc. | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-18 07:27
| Contra Costa County Communication Facility | City of Concord | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-18 07:27
| Contra Costa County Communication Facility | Comcast Fresno LLC | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-18 07:27
| Contra Costa County Communication Facility | County of Contra Costa | Tier 3 | 2025-06-18 07:27
| Contra Costa County Communication Facility | GTE Mobile Net of California LP | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-18 07:27
| Contra Costa County Communication Facility | SBA Towers | Tier 2 | 2025-06-18 07:27
| Contra Costa County Communication Facility | Sprint Corporation | Tier 2 | 2025-06-18 07:27
| Contra Costa County Communication Facility | T-Mobile West LLC | Tier 2 | 2025-06-18 07:27
| Contra Costa County Communication Facility | Verizon | Tier 2 | 2025-06-18 07:27
| Contra Costa County Communication Facility | Verizon Wireless | Tier 2 | 2025-06-18 07:27
| Contra Costa County Concord | City Administration | Tier 2 | 2025-06-17 21:03
| Contra Costa County Concord | City Administration | Tier 2 | 2025-06-17 21:03
| Contra Costa County Concord | City Administration | Tier 2 | 2025-06-17 21:03
| Contra Costa County Concord | Contra Costa County Fire Protection District | Tier 2 | 2025-06-17 21:03
| Contra Costa County Concord | Contra Costa Fire Protection District | Tier 2 | 2025-06-17 21:03
| Contra Costa County Concord | Fire Department | Tier 2 | 2025-06-17 21:03
| Contra Costa County Concord | MOTCO Fire Department | Tier 2 | 2025-06-17 21:03
| Contra Costa County Concord | Police Department | Tier 2 | 2025-06-17 21:03
| Contra Costa County Emergency Services Facility | San Ramon Valley Fire District | Tier 3 | 2025-06-18 07:27
| Contra Costa County Other Facility | Contra Costa Water District | Tier 2 | 2025-06-18 07:27
| Contra Costa County Pittsburg | City Administration | Tier 2 | 2025-06-17 21:03
| Contra Costa County Pittsburg | Contra Costa County Fire Protection District | Tier 2 | 2025-06-17 21:03
| Contra Costa County Pittsburg | Contra Costa Fire Protection District | Tier 2 | 2025-06-17 21:03
| Contra Costa County Pittsburg | Police Department | Tier 2 | 2025-06-17 21:03
| Fresno County | City Administration | HFRA, Tier 1 | 2025-06-17 21:03
| Fresno County | County Administration | HFRA, Tier 1 | 2025-06-17 21:03
| Fresno County | County Administration | HFRA, Tier 1 | 2025-06-17 21:03
| Fresno County | County Administration, County of Fresno | HFRA, Tier 1 | 2025-06-17 21:03
| Fresno County | EMS | HFRA, Tier 1 | 2025-06-17 21:03
| Fresno County | Fire Department | HFRA, Tier 1 | 2025-06-17 21:03
| Fresno County | Fresno County OES | HFRA, Tier 1 | 2025-06-17 21:03
| Fresno County | Fresno County Office of Emergency Services | HFRA, Tier 1 | 2025-06-17 21:03
| Fresno County | OES | HFRA, Tier 1 | 2025-06-17 21:03
| Fresno County | Sheriff's Department | HFRA, Tier 1 | 2025-06-17 21:03
| Fresno County Communication Facility | Pinnacle Towers INC | HFRA | 2025-06-20 05:44
| Glenn County | County Administration | HFRA, Tier 2 | 2025-06-18 07:16
| Glenn County | Fire Department | HFRA, Tier 2 | 2025-06-18 07:16
| Glenn County | Glenn County Office of Emergency Services (OES) | HFRA, Tier 2 | 2025-06-18 07:16
| Glenn County | Glenn County Sheriff's Office, Sheriff's Department | HFRA, Tier 2 | 2025-06-18 07:16
| Glenn County | Orland Fire Department | HFRA, Tier 2 | 2025-06-18 07:16
| Glenn County Communication Facility | American Tower Corporation | Tier 2 | 2025-06-18 07:27
| Glenn County Communication Facility | AT&T Services Inc. | HFRA, Tier 2 | 2025-06-18 07:27
| Glenn County Communication Facility | GTE Mobile Net of California LP | HFRA | 2025-06-18 07:27
| Glenn County Communication Facility | Verizon | Tier 2 | 2025-06-18 07:27
| Glenn County Emergency Services Facility | County of Glenn | Tier 2 | 2025-06-18 07:27
| Glenn County Emergency Services Facility | Elk Creek Fire District | Tier 2 | 2025-06-18 07:27
| Glenn County Other Facility | US Army Corps of Engineers | HFRA | 2025-06-18 07:27
| Glenn County Tribal | Grindstone Rancheria | HFRA | 2025-06-18 07:16
| Glenn County Water and Waste Water Facility | Elk Creek Community Service | Tier 2 | 2025-06-18 07:27
| Kern County | County Administration | Tier 2 | 2025-06-20 05:46
| Kern County | EMS | Tier 2 | 2025-06-20 05:46
| Kern County | Fire Department | Tier 2 | 2025-06-20 05:46
| Kern County | OES | Tier 2 | 2025-06-20 05:46
| Kern County | Sheriff's Office | Tier 2 | 2025-06-20 05:46
| Kern County Emergency Services Facility | County of Kern | Tier 2 | 2025-06-20 05:44
| Kern County Water and Waste Water Facility | Lebec Country Water District | Tier 2 | 2025-06-20 05:44
| Merced County | CAL FIRE | HFRA | 2025-06-17 21:03
| Merced County | City Administration | HFRA | 2025-06-17 21:03
| Merced County | County Administration | HFRA | 2025-06-17 21:03
| Merced County | County Administration | HFRA | 2025-06-17 21:03
| Merced County | Fire Department | HFRA | 2025-06-17 21:03
| Merced County | Merced County OES | HFRA | 2025-06-17 21:03
| Merced County | OES | HFRA | 2025-06-17 21:03
| Merced County | Sheriff's Department | HFRA | 2025-06-17 21:03
| Merced County Communication Facility | AT&T Services Inc. | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-18 07:27
| Merced County Communication Facility | T-Mobile West LLC | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-18 07:27
| Merced County Communication Facility | Verizon | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-18 07:27
| Merced County Emergency Services Facility | California Department of Forestry | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-18 07:27
| Merced County Gustine | City Administration | HFRA | 2025-06-17 21:03
| Merced County Gustine | Police Department | HFRA | 2025-06-17 21:03
| Merced County Other Facility | Crown Castle USA Inc. | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-18 07:27
| Monterey County | Big Sur Fire Department | HFRA, Tier 2 | 2025-06-17 21:03
| Monterey County | Board of Supervisors, County Administration | HFRA, Tier 2 | 2025-06-17 21:03
| Monterey County | California Office of Emergency Services | HFRA, Tier 2 | 2025-06-17 21:03
| Monterey County | County Administration | HFRA, Tier 2 | 2025-06-17 21:03
| Monterey County | County of Monterey Department of Emergency Management (DEM) | HFRA, Tier 2 | 2025-06-17 21:03
| Monterey County | County of Monterey Department of Emergency Management, OES | HFRA, Tier 2 | 2025-06-17 21:03
| Monterey County | County of Monterey EMS Agency, EMS | HFRA, Tier 2 | 2025-06-17 21:03
| Monterey County | Department of Emergency Management, OES | HFRA, Tier 2 | 2025-06-17 21:03
| Monterey County | Fire Department | HFRA, Tier 2 | 2025-06-17 21:03
| Monterey County | Hollister Fire Department | HFRA, Tier 2 | 2025-06-17 21:03
| Monterey County | MHOAC | HFRA, Tier 2 | 2025-06-17 21:03
| Monterey County | Monterey Fire (City of Monterey) | HFRA, Tier 2 | 2025-06-17 21:03
| Monterey County | OES | HFRA, Tier 2 | 2025-06-17 21:03
| Monterey County | Sheriff's Department | HFRA, Tier 2 | 2025-06-17 21:03
| Monterey County CCA | King City Community Power | HFRA, Tier 2 | 2025-06-17 21:03
| Monterey County CCA | King City Community Power, Police Department | HFRA, Tier 2 | 2025-06-17 21:03
| Monterey County CCA | Monterey Bay Community Power | HFRA, Tier 2 | 2025-06-17 21:03
| Monterey County Communication Facility | AT&T Mobility LLC | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-18 07:27
| Monterey County Communication Facility | AT&T Services Inc. | HFRA, Tier 2 | 2025-06-18 07:27
| Monterey County Communication Facility | Cingular Wireless Services, Inc. | HFRA | 2025-06-18 07:27
| Monterey County Communication Facility | Crown Castle International | Tier 2 | 2025-06-18 07:27
| Monterey County Communication Facility | Department of the Army | Tier 2 | 2025-06-20 05:44
| Monterey County Communication Facility | Frontier Communications Corporation DIP | HFRA, Tier 2 | 2025-06-18 07:27
| Monterey County Communication Facility | LEVEL 3 COMMUNICATIONS LLC | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-20 05:44
| Monterey County Communication Facility | SBA TOWERS | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-18 07:27
| Monterey County Communication Facility | Sprint Corporation | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-18 07:27
| Monterey County Communication Facility | T-Mobile West A Delaware Corp | HFRA | 2025-06-18 07:27
| Monterey County Communication Facility | T-Mobile West LLC | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-18 07:27
| Monterey County Communication Facility | Verizon | HFRA | 2025-06-18 07:27
| Monterey County Emergency Services Facility | County of Monterey | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-20 05:44
| Monterey County Emergency Services Facility | San Ardo Volunteer Fire Department | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-20 05:45
| Monterey County Emergency Services Facility | South Monterey County FPD | Tier 2 | 2025-06-18 07:27
| Monterey County King City | City Administration | HFRA | 2025-06-17 21:03
| Monterey County King City | Fire Department | HFRA | 2025-06-17 21:03
| Monterey County King City | Police Department | HFRA | 2025-06-17 21:03
| Monterey County Other Facility | Crown Castle USA Inc. | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-18 07:27
| Monterey County Other Facility | San Ardo Water District | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-20 05:44
| Monterey County Other Facility | T-Mobile USA Inc. | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-18 07:27
| Monterey County Other Facility | Western States Teleport | Tier 2 | 2025-06-18 07:27
| Monterey County Salinas | City Administration | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-17 21:03
| Monterey County Salinas | Fire Department | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-17 21:03
| Monterey County Salinas | Police Department | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-17 21:03
| Monterey County Soledad | City Administration | Tier 2 | 2025-06-17 21:03
| Monterey County Soledad | Fire Department | Tier 2 | 2025-06-17 21:03
| Monterey County Soledad | Police Department | Tier 2 | 2025-06-17 21:03
| Monterey County Water and Waste Water Facility | California Department of Forestry | HFRA | 2025-06-18 07:27
| Monterey County Water and Waste Water Facility | City of King City | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-20 05:44
| Monterey County Water and Waste Water Facility | San Ardo Water District | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-20 05:44
| Monterey County Water and Waste Water Facility | San Lucas Wastewater Treatment Facility | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-18 07:27
| San Benito County | County Administration | HFRA, Tier 2 | 2025-06-17 21:03
| San Benito County | EMS | HFRA, Tier 2 | 2025-06-17 21:03
| San Benito County | OES | HFRA, Tier 2 | 2025-06-17 21:03
| San Benito County | OES, Office of Emergency Services | HFRA, Tier 2 | 2025-06-17 21:03
| San Benito County | San Benito County Office of Emergency Services | HFRA, Tier 2 | 2025-06-17 21:03
| San Benito County | Sheriff's Department | HFRA, Tier 2 | 2025-06-17 21:03
| San Benito County | Sheriff's Office | HFRA, Tier 2 | 2025-06-17 21:03
| San Benito County CCA | Monterey Bay Community Power | HFRA, Tier 2 | 2025-06-17 21:03
| San Benito County Communication Facility | AT&T Mobility LLC | Tier 2 | 2025-06-18 07:27
| San Benito County Communication Facility | AT&T Services Inc. | HFRA, Tier 2 | 2025-06-18 07:27
| San Benito County Communication Facility | AT&T Wireless Service LLC | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-18 07:27
| San Benito County Communication Facility | Frontier Communications Corporation DIP | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-18 07:27
| San Benito County Communication Facility | T-Mobile West Corporation | HFRA, Tier 2 | 2025-06-18 07:27
| San Benito County Communication Facility | T-Mobile West LLC | Tier 2 | 2025-06-18 07:27
| San Benito County Communication Facility | Verizon | HFRA, Tier 2 | 2025-06-18 07:27
| San Benito County Hollister | City Administration | HFRA, Tier 2 | 2025-06-17 21:03
| San Benito County Hollister | Fire Department | HFRA, Tier 2 | 2025-06-17 21:03
| San Benito County Hollister | Police Department | HFRA, Tier 2 | 2025-06-17 21:03
| San Joaquin County | Board of Supervisors, County Administration | HFRA | 2025-06-17 21:03
| San Joaquin County | Clements Fire District | HFRA | 2025-06-17 21:03
| San Joaquin County | Collegeville Fire District | HFRA | 2025-06-17 21:03
| San Joaquin County | County Administration | HFRA | 2025-06-17 21:03
| San Joaquin County | EMS | HFRA | 2025-06-17 21:03
| San Joaquin County | Farmington Fire District | HFRA | 2025-06-17 21:03
| San Joaquin County | French Camp McKinley Fire District | HFRA | 2025-06-17 21:03
| San Joaquin County | Liberty Fire District | HFRA | 2025-06-17 21:03
| San Joaquin County | Linden Peters Fire District | HFRA | 2025-06-17 21:03
| San Joaquin County | Mokelumne Fire District | HFRA | 2025-06-17 21:03
| San Joaquin County | Montezuma Fire District | HFRA | 2025-06-17 21:03
| San Joaquin County | OES, Office of Emergency Services | HFRA | 2025-06-17 21:03
| San Joaquin County | Sheriff's Office | HFRA | 2025-06-17 21:03
| San Joaquin County | Thornton Fire District | HFRA | 2025-06-17 21:03
| San Joaquin County | Waterloo-Morada Fire District | HFRA | 2025-06-17 21:03
| San Joaquin County | Woodbridge Fire District | HFRA | 2025-06-17 21:03
| San Joaquin County Communication Facility | AT&T Mobility LLC | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-18 07:27
| San Joaquin County Communication Facility | AT&T Services Inc. | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-18 07:27
| San Joaquin County Communication Facility | AT&T Wireless Service LLC | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-18 07:27
| San Joaquin County Communication Facility | Comcast Cable Communications Management, LLC | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-18 07:27
| San Joaquin County Communication Facility | GTE Mobile Net of California LP | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-18 07:27
| San Joaquin County Communication Facility | Sprint Corporation | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-18 07:27
| San Joaquin County Communication Facility | T-Mobile West LLC | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-18 07:27
| San Joaquin County Communication Facility | TCI Cablevision | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-18 07:27
| San Joaquin County Communication Facility | Verizon | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-18 07:27
| San Joaquin County Energy Sector Facility | Pacific Gas & Electric Company | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-18 07:27
| San Joaquin County Other Facility | Dish Wireless | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-18 07:27
| San Joaquin County Tracy | City Administration | HFRA | 2025-06-17 21:03
| San Joaquin County Tracy | City Administration | HFRA | 2025-06-17 21:03
| San Joaquin County Tracy | Police Department | HFRA | 2025-06-17 21:03
| San Joaquin County Tracy | South San Joaquin County Fire Authority | HFRA | 2025-06-17 21:03
| San Joaquin County Water and Waste Water Facility | County of San Joaquin | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-18 07:27
| San Luis Obispo County | CAL FIRE | HFRA, N/A, Tier 2 | 2025-06-17 21:03
| San Luis Obispo County | CAL FIRE San Luis Obispo County City of Pismo Beach | HFRA, N/A, Tier 2 | 2025-06-17 21:03
| San Luis Obispo County | CAL FIRE / San Luis Obispo County Fire Department | HFRA, N/A, Tier 2 | 2025-06-17 21:03
| San Luis Obispo County | Fire Department | HFRA, N/A, Tier 2 | 2025-06-17 21:03
| San Luis Obispo County | OES | HFRA, N/A, Tier 2 | 2025-06-17 21:03
| San Luis Obispo County | OES, Office of Emergency Services | HFRA, N/A, Tier 2 | 2025-06-17 21:03
| San Luis Obispo County | Sheriff's Department | HFRA, N/A, Tier 2 | 2025-06-17 21:03
| San Luis Obispo County CCA | Monterey Bay Community Power | HFRA, N/A, Tier 2 | 2025-06-17 21:03
| San Luis Obispo County Communication Facility | AT&T Wireless Service LLC | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-18 07:27
| San Luis Obispo County Communication Facility | Frontier Communications Corporation DIP | Tier 2 | 2025-06-18 07:27
| San Luis Obispo County Communication Facility | T-Mobile West LLC | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-18 07:27
| San Luis Obispo County Communication Facility | Verizon | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-18 07:27
| San Luis Obispo County Other Facility | California National Guard | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-18 07:27
| San Luis Obispo County Other Facility | Crown Castle USA Inc. | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-18 07:27
| San Luis Obispo County San Luis Obispo | Fire Department | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-17 21:03
| San Luis Obispo County San Luis Obispo | Police Department | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-17 21:03
| San Luis Obispo County Water and Waste Water Facility | County of San Luis Obispo | Tier 2 | 2025-06-20 05:44
| Santa Barbara County | Fire Department | Tier 2, Tier 3 | 2025-06-20 05:46
| Santa Barbara County | OES | Tier 2, Tier 3 | 2025-06-20 05:46
| Santa Barbara County | Sheriff's Office | Tier 2, Tier 3 | 2025-06-20 05:46
| Santa Barbara County Buellton | Fire Department | Tier 2, Tier 3 | 2025-06-20 05:46
| Santa Barbara County Buellton | Sheriff's Office | Tier 2, Tier 3 | 2025-06-20 05:47
| Santa Barbara County CCA | Monterey Bay Community Power | Tier 2, Tier 3 | 2025-06-20 05:46
| Santa Barbara County Communication Facility | Comcast Cable of Santa Maria | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-20 05:44
| Santa Barbara County Communication Facility | Comcast Cablevision Communications Inc. | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-20 05:44
| Santa Barbara County Solvang | Fire Department | Tier 2, Tier 3 | 2025-06-20 05:47
| Santa Barbara County Solvang | Sheriff's Office | Tier 2, Tier 3 | 2025-06-20 05:47
| Santa Barbara County Water and Waste Water Facility | Central Coast Water Authority | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-20 05:44
| Santa Clara County | BART | Tier 2 | 2025-06-17 21:03
| Santa Clara County | County Administration | Tier 2 | 2025-06-17 21:03
| Santa Clara County | County Communications 9-1-1 Dispatch | Tier 2 | 2025-06-17 21:03
| Santa Clara County | County Emergency Medical System | Tier 2 | 2025-06-17 21:03
| Santa Clara County | County Public Health Department | Tier 2 | 2025-06-17 21:03
| Santa Clara County | EMS | Tier 2 | 2025-06-17 21:03
| Santa Clara County | Fire Department | Tier 2 | 2025-06-17 21:03
| Santa Clara County | Los Altos Office of Emergency Services | Tier 2 | 2025-06-17 21:03
| Santa Clara County | OEM | Tier 2 | 2025-06-17 21:03
| Santa Clara County | OES | Tier 2 | 2025-06-17 21:03
| Santa Clara County | OES | Tier 2 | 2025-06-17 21:03
| Santa Clara County | Office of Supervisor | Tier 2 | 2025-06-17 21:03
| Santa Clara County | Sheriff's Department | Tier 2 | 2025-06-17 21:03
| Santa Clara County | Sheriff's Office | Tier 2 | 2025-06-17 21:03
| Santa Clara County CCA | City Administration | Tier 2 | 2025-06-17 21:03
| Santa Clara County CCA | City Administration | Tier 2 | 2025-06-17 21:03
| Santa Clara County CCA | San Jose Clean Energy | Tier 2 | 2025-06-17 21:03
| Santa Clara County CCA | Santa Clara City Administration | Tier 2 | 2025-06-17 21:03
| Santa Clara County CCA | Silicon Valley Clean Energy | Tier 2 | 2025-06-17 21:03
| Santa Clara County Communication Facility | AT&T Mobility LLC | Tier 2 | 2025-06-18 07:27
| Santa Clara County Communication Facility | Frontier Communications Corporation DIP | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-18 07:27
| Santa Clara County Communication Facility | Sprint Corporation | Tier 2 | 2025-06-18 07:27
| Santa Clara County Communication Facility | T-Mobile West LLC | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-18 07:27
| Santa Clara County Emergency Services Facility | California Department of Forestry | Tier 2 | 2025-06-18 07:27
| Shasta County | Burney Fire District | Tier 2, Tier 3 | 2025-06-17 21:03
| Shasta County | CAL FIRE | Tier 2, Tier 3 | 2025-06-17 21:03
| Shasta County | City of Shasta Lake Station | Tier 2, Tier 3 | 2025-06-17 21:03
| Shasta County | EMS, Sierra-Sacramento Valley EMS Agency | Tier 2, Tier 3 | 2025-06-17 21:03
| Shasta County | Office of Emergency Services | Tier 2, Tier 3 | 2025-06-17 21:03
| Shasta County | Pit River Tribes | Tier 2, Tier 3 | 2025-06-17 21:03
| Shasta County | SHASCOM | Tier 2, Tier 3 | 2025-06-17 21:03
| Shasta County | SHASCOM 9-1-1 | Tier 2, Tier 3 | 2025-06-17 21:03
| Shasta County | Shasta County Sheriff's Office | Tier 2, Tier 3 | 2025-06-17 21:03
| Shasta County | Sheriff's Office | Tier 2, Tier 3 | 2025-06-17 21:03
| Shasta County | Sheriff's Office OES | Tier 2, Tier 3 | 2025-06-17 21:03
| Shasta County Communication Facility | AT&T | Tier 3 | 2025-06-18 07:27
| Shasta County Communication Facility | AT&T Services Inc. | Tier 3, Tier 2 | 2025-06-18 07:27
| Shasta County Communication Facility | Charter Communications Holding Company LLC | Tier 3, Tier 2 | 2025-06-18 07:27
| Shasta County Communication Facility | GTE Mobile Net of California LP | Tier 2 | 2025-06-18 07:27
| Shasta County Communication Facility | Happy Valley Telephone CO | Tier 2 | 2025-06-18 07:27
| Shasta County Communication Facility | Metro PCS Inc. | Tier 2 | 2025-06-18 07:27
| Shasta County Communication Facility | Verizon | Tier 2 | 2025-06-18 07:27
| Shasta County Communication Facility | Verizon Wireless | Tier 3 | 2025-06-18 07:28
| Shasta County Emergency Services Facility | California Department of Forestry | Tier 3, Tier 2 | 2025-06-18 07:27
| Shasta County Emergency Services Facility | County of Shasta | Tier 2 | 2025-06-18 07:27
| Shasta County Emergency Services Facility | French Gulch Volunteer Fire | Tier 2 | 2025-06-18 07:28
| Shasta County Major Transportation Facility | California Highway Patrol | Tier 2 | 2025-06-18 07:27
| Shasta County Water and Waste Water Facility | US Bureau of Reclamation | Tier 3 | 2025-06-18 07:27
| Stanislaus County | County Administration | HFRA, Tier 2 | 2025-06-17 21:03
| Stanislaus County | County Administration | HFRA, Tier 2 | 2025-06-17 21:03
| Stanislaus County | Emergency Management, OES | HFRA, Tier 2 | 2025-06-17 21:03
| Stanislaus County | EMS | HFRA, Tier 2 | 2025-06-17 21:03
| Stanislaus County | Public Health | HFRA, Tier 2 | 2025-06-17 21:03
| Stanislaus County | Sheriff's Department | HFRA, Tier 2 | 2025-06-17 21:03
| Stanislaus County Communication Facility | AT&T Wireless Service LLC | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-18 07:27
| Stanislaus County Communication Facility | Federal Bureau of Investigation | HFRA | 2025-06-18 07:27
| Stanislaus County Communication Facility | Sprint Nextel Corporation | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-18 07:27
| Stanislaus County Communication Facility | Verizon | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 3) | 2025-06-18 07:27
| Sutter County | County Administration | HFRA | 2025-06-19 01:54
| Sutter County | Office of Emergency Management | HFRA | 2025-06-19 01:54
| Sutter County | EMS | HFRA | 2025-06-19 01:54
| Sutter County | OES | HFRA | 2025-06-19 01:54
| Sutter County | Sheriff's Office | HFRA | 2025-06-19 01:54
| Sutter County | Sutter County Fire Department | HFRA | 2025-06-19 01:54
| Tehama County | County Administration | HFRA, Tier 2 | 2025-06-18 07:16
| Tehama County | OES and Sheriff's Office | HFRA, Tier 2 | 2025-06-18 07:16
| Tehama County | Sheriff's Department | HFRA, Tier 2 | 2025-06-18 07:16
| Tehama County | Sheriff's Department, Tehama County Sheriff | HFRA, Tier 2 | 2025-06-18 07:16
| Tehama County | Tehama-Colusa Canal Authority | HFRA, Tier 2 | 2025-06-18 07:17
| Tehama County Communication Facility | AT&T Mobility | Tier 2 | 2025-06-19 00:46
| Tehama County Communication Facility | AT&T Mobility LLC | Tier 2 | 2025-06-19 00:46
| Tehama County Communication Facility | AT&T Services Inc. | Tier 2 | 2025-06-18 07:27
| Tehama County Communication Facility | Ducor Telephone Co. | Tier 2 | 2025-06-19 03:01
| Tehama County Communication Facility | Ducor Telephone Corporation | Tier 2 | 2025-06-19 03:01
| Tehama County Emergency Services Facility | California Department of Forestry | Tier 2 | 2025-06-18 07:27
| Tehama County Emergency Services Facility | County of Tehama | Tier 2 | 2025-06-19 00:46
| Tehama County Government - Jail Facility | California Department of Corrections | Tier 2 | 2025-06-18 07:27
| Tehama County Other Facility | California Department of Forestry | Tier 2 | 2025-06-19 00:46
| Tehama County Other Facility | Tehama County Fire Department | Tier 2 | 2025-06-19 03:01
| Tehama County Red Bluff | City Administration, City of Red Bluff | Tier 2 | 2025-06-18 23:28
| Tehama County Red Bluff | Police Department | Tier 2 | 2025-06-18 23:28
| Trinity County | EMS, Public health | Tier 2 | 2025-06-18 07:16
| Trinity County | HHS | Tier 2 | 2025-06-18 07:16
| Trinity County | OES | Tier 2 | 2025-06-18 07:16
| Trinity County | OES, Office of Emergency Services | Tier 2 | 2025-06-18 07:16
| Trinity County Communication Facility | Frontier Communications Corporation DIP | Tier 2 | 2025-06-18 07:27
| Trinity County Communication Facility | IP Networks Inc. | Tier 2 | 2025-06-18 07:27
1 Catastrophic Fire Behavior runs both in and outside of High Fire Risk Areas (HFRA). The PG&E Meteorology Team evaluates non-HFRA areas for catastrophic wildfire risk in unusual circumstances.

## Appendix E
#VALUE!
Table E-1. Community Resource Centers Provided by PG&E
| # | County | Site Name | Address | Operating Hours (PDT) Day 1 (June 19) | Operating Hours (PDT) Day 2 (June 20) | Operating Hours (PDT) Day 3 (June 21) | Operating Hours (PDT) Day 4 (June 22) | Total Visitors | Indoor / Outdoor | Amenities Provided
| 1 | Alameda | Costco Wholesale Livermore | 2800 Independence Dr | 08:00 - 22:00 | 08:00 - 22:00 | 08:00 - 22:00 | 08:00 - 13:00 | 90 | Outdoor | Wi-Fi, ADA Restroom, Bottled Water, Device Charging,Snacks, Seating
| 2 | Colusa | Stonyford Community Hall | 229 Market St | No | 11:00 - 22:00 | 08:00 - 22:00 | 08:00 - 13:00 | 216 | Indoor | Wi-Fi, ADA Restroom, Bottled Water, Device Charging, Snacks,Cooling/Heating, Seating, Ice
| 3 | Colusa | Williams Community Church | 315 9th Street | No | No | 08:00 - 22:00 | 08:00 - 13:00 | 199 | Outdoor | Wi-Fi, ADA Restroom, Bottled Water, Device Charging, Snacks, Seating
| 4 | Contra Costa | Balfour-Guthrie Park | 1701 Balfour Rd | 08:00 - 22:00 | 08:00 - 22:00 | 08:00 - 12:00 | No | 527 | Outdoor | Wi-Fi, ADA Restroom, Bottled Water, Device Charging, Snacks, Seating
| 5 | Glenn | Elk Creek Junior Senior High School | 3430 Co Rd 309 | No | 11:00 - 22:00 | 08:00 - 22:00 | 08:00 - 13:00 | 86 | Outdoor | Wi-Fi, ADA Restroom, Bottled Water, Device Charging, Snacks, Seating
| 6 | Kern | El Tejon School | 4337 Lebec Rd | No | No | 12:00 - 22:00 | 08:00 - 12:30 | 18 | Indoor | Wi-Fi, ADA Restroom, Bottled Water, Device Charging, Snacks, Cooling/Heating, Seating, Ice
| 7 | Monterey | Carmel Valley Community Park / Carmel Valley Community Youth Center | 25 Ford Rd | 08:00 - 22:00 | 08:00 - 22:00 | 08:00 - 10:00 | No | 56 | Outdoor | Wi-Fi, ADA Restroom, Bottled Water, Device Charging, Snacks, Seating
| 8 | Monterey | Patriot Park Community Center | 1351 Oak Ave | 08:00 - 22:00 | 08:00 - 22:00 | 08:00 - 22:00 | 08;00 - 15:00 | 5409 | Outdoor | Wi-Fi, ADA Restroom, Bottled Water, Device Charging, Snacks, Seating
| 9 | Monterey | Salinas Valley Fairgrounds | 625 Division St. | 08:00 - 22:00 | 08:00 - 22:00 | 08:00 - 22:00 | 08:00 - 15:00 | 2559 | Indoor | Wi-Fi, ADA Restroom, Bottled Water, Device Charging, Snacks, Cooling/Heating, Seating, Ice
| 10 | Monterey | San Antonio Union School | 67550 Lockwood Jolon Road | 08:00 - 22:00 | 08:00 - 22:00 | 08:00 - 22:00 | 08:00 - 15:00 | 219 | Outdoor | Wi-Fi, ADA Restroom, Bottled Water, Device Charging, Snacks, Seating
| 11 | Monterey | Soledad Community Center | 560 Walker Drive | 08:00 - 22:00 | 08:00 - 22:00 | 08:00 - 22:00 | 08:00 - 10:00 | 3238 | Outdoor | Wi-Fi, ADA Restroom, Bottled Water, Device Charging, Snacks, Seating
| 12 | San Joaquin | First Christian Reformed Church | 305 Boesch Dr | No | No | 08:00 - 22:00 | No | 43 | Outdoor | Wi-Fi, ADA Restroom, Bottled Water, Device Charging, Snacks, Seating
| 13 | San Luis Obispo | Cuesta College, North County Campus | 2800 Buena Vista Dr | 08:00 - 22:00 | 08:00 - 22:00 | 08:00 - 22:00 | 08:00 - 16:00 | 93 | Outdoor | Wi-Fi, ADA Restroom, Bottled Water, Device Charging, Snacks, Seating
| 14 | Santa Barbara | Shepherd of The Valley Lutheran Church | 3550 Baseline Ave | No | No | 12:00 - 22:00 | 08:00 - 16:00 | 34 | Outdoor | Wi-Fi, ADA Restroom, Bottled Water, Device Charging, Snacks, Seating
| 15 | Shasta | Dignity Health Mercy Oaks | 100 Mercy Oaks Dr | 12:00 - 22:00 | 08:00 - 22:00 | 08:00 - 22:00 | No | 36 | Indoor | Wi-Fi, ADA Restroom, Bottled Water, Device Charging, Snacks, Cooling/Heating, Seating, Ice
| 16 | Shasta | Happy Valley Community Center | 5400 Happy Valley Rd | No | No | 12:00 - 22:00 | No | 3 | Indoor | Wi-Fi, ADA Restroom, Bottled Water, Device Charging, Snacks, Cooling/Heating, Seating, Ice
| 17 | Stanislaus | Grayson Elementary School | 301 Howard Road | 08:00 - 22:00 | 08:00 - 22:00 | 08:00 - 22:00 | No | 950 | Outdoor | Wi-Fi, ADA Restroom, Bottled Water, Device Charging, Snacks, Seating
| 18 | Tehama | Flournoy Elementary School | 15850 Paskenta Rd | No | 11:00 - 22:00 | 08:00 - 22:00 | No | 87 | Outdoor | Wi-Fi, ADA Restroom, Bottled Water, Device Charging, Snacks, Seating
| 19 | Tehama | Noland Park | 19001 Bowman Rd | No | 11:00 - 22:00 | 08:00 - 22:00 | No | 39 | Outdoor | Wi-Fi, ADA Restroom, Bottled Water, Device Charging, Snacks, Seating
| 20 | Tehama | Rancho Tehama Association | 17605 Park Terrace Road | No | No | 08:00 - 22:00 | No | 158 | Outdoor | Wi-Fi, ADA Restroom, Bottled Water, Device Charging, Snacks, Seating