## Table 1
#VALUE!
Table 1: PSPS Event Summary1
| Total Customers Notified | Total Customers De-energized | Total Customers Canceled | MBL Customers De-energized | Counties De-energized | Tribes De-energized | CFI De-energized | Transmission De-energized | Unique Distribution Circuits in Scope | Distribution Circuits | Damage/ Hazard Count
| 7,790 2 | 5,186 3 | 2618 | 151 | 8 | 0 | 129 | 2 | 24 | 16 | 0 damages 0 hazards
1 The information, times, and figures referenced in this report are based on the best available information available at the time of this report’s submission. The information, times and figures herein are subject to revision based on further analysis and validation.
2 Of the customers who received notifications that their power may be de-energized, two customers stopped service prior to de-energization. See Section 5.7 for more information.
3 Of the customers de-energized, 16 customers did not receive any notifications regarding planned de-energization. See Section 5.5 for more information.

## Table 2
#VALUE!
Table 2: 2026 PG&E’s PSPS Risk-Benefit Consequence Modeling Considerations
| Consequence Type | Wildfire Consequence Considerations | PSPS Consequence Considerations
| Safety | Calculated based on maximum population impacts derived from Technosylva wildfire simulation models and a fatality ratio based on National Fire Protection Association (NFPA) data. | Calculated from an estimate of Equivalent Fatalities (EF) per Million Customer Minutes Interrupted (MMCI). The EF/MMCI ratio is estimated from previous PG&E PSPS outages and other large external outages.1
| Reliability | None. | Calculated directly from the potential number of customers impacted and outage duration based on customer minutes interrupted.
| Financial | Calculated based on maximum building impacts derived from Technosylva wildfire simulation models and a cost per structure burned previously evaluated in 2024 RAMP Report.2 | Calculated based on two financial estimates, 1) distribution of a lump sum cost of execution across all relevant circuits and 2) an estimated proxy cost per customer in scope per PSPS.3
1 Includes 2019-2021 PSPS outages, the 2003 Northeast Blackout in New York City, 2011 Southwest Blackout in San Diego, 2012 Derecho Windstorms, 2012 Superstorm Sandy, 2017 Hurricane Irma and 2021 Blackout event.
2 A.24-05-008.
3 The assumptions used in these calculations, including the proxy cost per customer per PSPS, are subject to be updated and are not intended to prejudge or create precedent with regard to the development of more precise values of resiliency or cost of PSPS metrics being considered in other ongoing proceedings at the CPUC, such as the Risk-Based Decision-Making Rulemaking [R.20.07.013] and the Microgrid and Resiliency Strategies.

## Table 3
#VALUE!
Table 3: Notification Descriptions
| Type of Notification | Recipients | Description
| PRIORITY NOTIFICATION: 48-72 hours in advance of anticipated de-energization | Public Safety Partners and CBOs1 | On July 13, our Meteorology Team noted a potential PSPS and updated the weather forecast on www.pge.com/weather to “elevated” in certain parts of the service area. In the evening of July 13, agency representatives called each County Office of Emergency Services (OES) in PG&E’s electrical service area and select tribes and cities to inform them that PG&E was monitoring an increased potential for a PSPS. As mentioned in Section 1.1, due to the rapidly shifting weather, the initial PSPS scope was established for de-energization after the (48-72hr) Priority Notification window had passed. As a result, Priority Notifications were not sent to Public Safety Partners within 48 – 72 hours prior to anticipated de-energization, in accordance with Phase 1 Guidelines.
| WATCH NOTIFICATION: 24-48 hours in advance of anticipated de-energization | Public Safety Partners, CBOs, and All Customers (including MBL and SIV customers) | Following the EOC activation, we completed the following: • Notified CAISO of the potential PSPS (on July 14 at 06:19 PDT) and shared additional information via email (at 10:14 PDT). • Submitted a PSPS Notification Form to Cal OES and sent an e-mail to the CPUC notifying them that PG&E’s EOC has been activated and that PG&E is monitoring for a potential PSPS. • Agency representatives called potentially impacted County OES and cities to inform them that PG&E is monitoring a potential PSPS. • Sent notifications to other Public Safety Partners,2 via call, text and e-mail, which included: o Estimated window of the de-energization time. o When weather is anticipated to pass. o Estimated Time of Restoration (ETOR). o For Public Safety Partners Only: Links to the PSPS Data Portal where PSPS-specific maps and information are available. o For customers only: Potentially impacted addresses, links to PSPS emergency website with CRC information, and resources for AFN customers, including but not limited to information on the MBL Program, language support, and the Portable Battery Program (PBP). • Sent notifications to MBL customers, including tenants of master metered accounts, and SIV customers. For more information regarding MBL Program notifications, see Section 5.3. • Sent Cancellation Notifications to Public Safety Partners and customers after being removed from scope to inform them that their power would not be shut off. Customer notifications are provided in English, with information on how to receive PSPS information in translated languages. Customers with their language preference selected in their PG&E accounts received in-language (translated) notifications. Public Safety Partner notifications are provided in English.
| WARNING NOTIFICATION: 1-4 hours in advance of anticipated de-energization, if possible | Public Safety Partners, CBOs, and All Customers (including MBL and SIV customers) | During this time, we completed the following: • Submitted a PSPS Notification Form to Cal OES and sent an e-mail to the CPUC notifying them that PG&E has made the decision to de-energize. • Sent notifications to Public Safety Partners and customers which included the same key information and resources as Watch Notifications. • Sent notifications to MBL customers, including tenants of master metered accounts, and SIV customers. For more information regarding MBL Program notifications, see Section 5.3. • Sent Cancellation Notifications to Public Safety Partners and customers after being removed from scope to inform them that their power would not be shut off. Customer notifications are provided in English, with information on how to receive PSPS information in translated languages. Customers with their language preference selected in their PG&E accounts received in-language (translated) notifications. Public Safety Partner notifications are provided in English.
| POWER OFF NOTIFICATION: When de-energization is initiated | Public Safety Partners, CBOs, and All Customers (including MBL and SIV customers) | When de-energization was initiated, we completed the following: • Submitted a PSPS State Notification Form to Cal OES and sent an e-mail to the CPUC to notify them that de-energization has been initiated. • Sent notifications to Public Safety Partners and customers via call, text messages and e-mail, which included: o De-energization time. o When weather is anticipated to pass. o For customers only: Impacted addresses. o For customers only: Links to the PSPS emergency website with CRC information, and resources for AFN customers, including but not limited to information on the MBL Program, Meals on Wheels, language support, and the PBP. • Sent notifications to MBL customers, including tenants of master metered accounts, and SIV customers. For more information regarding MBL Program notifications, see Section 5.3. Customer notifications are provided in English, with information on how to receive PSPS information in translated languages. Customers with their language preference selected in their PG&E accounts received in-language (translated) notifications. Public Safety Partner notifications are provided in English.
| WEATHER “ALL-CLEAR”/ETOR UPDATE NOTIFICATION: Immediately before re-energization begins | Public Safety Partners, CBOs, and All Customers (including MBL and SIV customers) | After weather conditions had passed and areas were deemed safe to begin patrols and restoration, we completed the following: • Submitted a PSPS State Notification Form to Cal OES and sent an e-mail to the CPUC notifying them that PG&E is initiating re-energization patrols. • Sent notifications to other Public Safety Partners and customers, via call, text message and e-mail, which included the ETOR. • Sent “update” notifications to customers if their ETOR changed. Two ways that an ETOR may change include: o New field or meteorology conditions. o Damage found during patrols and repair was needed. Customer notifications are provided in English, with information on how to receive PSPS information in translated languages. Customers with their language preference selected in their PG&E accounts received in-language (translated) notifications. Public Safety Partner notifications are provided in English.
| RESTORATION NOTIFICATION: When re-energization is complete | Public Safety Partners, CBOs, and All Customers (including MBL and SIV customers) | Once all customers were restored, we completed the following: • Sent a notification to Public Safety Partners via call, text and e-mail. • Submitted the final PSPS State Notification Form to Cal OES. • Sent an e-mail to the CPUC confirming restoration of PSPS outages and reclassification of customers if applicable. Once customers, including MBL and SIV customers, were restored, they received automated notifications via call, text, and e-mail. Customer notifications are provided in English, with information on how to receive PSPS information in translated languages. Customers with their language preference selected in their PG&E accounts received in-language (translated) notifications. Public Safety Partner notifications are provided in English.
13 D.21-06-034, Appendix A, page A9, Section G. MBL Program and AFN Communities, No. 4, Each electric investor-owned utility must provide proactive notification and impacted zip code information to paratransit agencies that may serve all the known transit- or paratransit-dependent persons that may need access to a CRC during a PSPS.
14 Other Public Safety Partners refers to first/emergency responders at the local, state, and federal level, water, wastewater, and communication service providers, affected CCAs, publicly owned utilities/electrical cooperatives, the CPUC, the California Governor’s OES and the CAL FIRE.

## Table 4
#VALUE!
Table 4: Notification Timeline Summary
| Jurisdiction or Circuit Type | Jurisdiction or Circuit Name | Notification Requirement | Time of First Notification (PDT) | PG&E Remarks
| County | Alameda | 48-72 Hour Advance Notification (Priority) | Refer to PG&E remark. | As explained in Table 6A: due to rapidly shifting weather, the initial PSPS scope was established after this notification window had passed. Therefore, it was not possible for the agencies in this jurisdiction to receive Priority Notifications.
| County | Alameda | 24-48 Hour Advance Notification (Watch) | 2026-07-14 10:29
| County | Alameda | 1-4 Hour Imminent Notification | 2026-07-15 10:02
| County | Alameda | At De-energization Initiation | 2026-07-15 14:52
| County | Alameda | Immediately Before Re-energization | 2026-07-16 09:05
| County | Alameda | When Re-energization is Complete | 2026-07-16 12:41
| County | Contra Costa | 48-72 Hour Advance Notification (Priority) | Refer to PG&E remark. | As explained in Table 6A: due to rapidly shifting weather, the initial PSPS scope was established after this notification window had passed. Therefore, it was not possible for the agencies in this jurisdiction to receive Priority Notifications.
| County | Contra Costa | 24-48 Hour Advance Notification (Watch) | 2026-07-14 10:29
| County | Contra Costa | 1-4 Hour Imminent Notification | 2026-07-15 10:02
| County | Contra Costa | At De-energization Initiation | 2026-07-15 15:45
| County | Contra Costa | Immediately Before Re-energization | 2026-07-16 08:18
| County | Contra Costa | When Re-energization is Complete | 2026-07-16 11:18
| County | Fresno | 48-72 Hour Advance Notification (Priority) | Refer to PG&E remark. | As explained in Table 6A: due to rapidly shifting weather, the initial PSPS scope was established after this notification window had passed. Therefore, it was not possible for the agencies in this jurisdiction to receive Priority Notifications.
| County | Fresno | 24-48 Hour Advance Notification (Watch) | 2026-07-14 10:29
| County | Fresno | 1-4 Hour Imminent Notification | 2026-07-15 12:02
| County | Fresno | Cancellation Notification | 2026-07-16 07:22
| County | Marin | 48-72 Hour Advance Notification (Priority) | Refer to PG&E remark. | As explained in Table 6A: due to rapidly shifting weather, the initial PSPS scope was established after this notification window had passed. Therefore, it was not possible for the agencies in this jurisdiction to receive Priority Notifications.
| County | Marin | 24-48 Hour Advance Notification (Watch) | 2026-07-14 10:29
| County | Marin | 1-4 Hour Imminent Notification | 2026-07-15 10:23
| County | Marin | At De-energization Initiation | 2026-07-15 18:18
| County | Marin | Immediately Before Re-energization | 2026-07-16 08:18
| County | Marin | When Re-energization is Complete | 2026-07-16 09:51
| County | Merced | 48-72 Hour Advance Notification (Priority) | Refer to PG&E remark. | As explained in Table 6A: due to rapidly shifting weather, the initial PSPS scope was established after this notification window had passed. Therefore, it was not possible for the agencies in this jurisdiction to receive Priority Notifications.
| County | Merced | 24-48 Hour Advance Notification (Watch) | 2026-07-14 10:29
| County | Merced | 1-4 Hour Imminent Notification | 2026-07-15 10:23
| County | Merced | Cancellation Notification | 2026-07-16 07:22
| County | Monterey | 48-72 Hour Advance Notification (Priority) | Refer to PG&E remark. | As explained in Table 6A: due to rapidly shifting weather, the initial PSPS scope was established after this notification window had passed. Therefore, it was not possible for the agencies in this jurisdiction to receive Priority Notifications.
| County | Monterey | 24-48 Hour Advance Notification (Watch) | 2026-07-14 10:29
| County | Monterey | 1-4 Hour Imminent Notification | 2026-07-15 08:43
| County | Monterey | At De-energization Initiation | 2026-07-15 12:52
| County | Monterey | Immediately Before Re-energization | 2026-07-16 08:18
| County | Monterey | When Re-energization is Complete | 2026-07-16 16:27
| County | San Benito | 48-72 Hour Advance Notification (Priority) | Refer to PG&E remark. | As explained in Table 6A: due to rapidly shifting weather, the initial PSPS scope was established after this notification window had passed. Therefore, it was not possible for the agencies in this jurisdiction to receive Priority Notifications.
| County | San Benito | 24-48 Hour Advance Notification (Watch) | 2026-07-14 10:29
| County | San Benito | 1-4 Hour Imminent Notification | 2026-07-15 08:43
| County | San Benito | At De-energization Initiation | 2026-07-15 12:56
| County | San Benito | Immediately Before Re-energization | 2026-07-16 08:18
| County | San Benito | When Re-energization is Complete | 2026-07-16 14:22
| County | San Joaquin | 48-72 Hour Advance Notification (Priority) | Refer to PG&E remark. | As explained in Table 6A: due to rapidly shifting weather, the initial PSPS scope was established after this notification window had passed. Therefore, it was not possible for the agencies in this jurisdiction to receive Priority Notifications.
| County | San Joaquin | 24-48 Hour Advance Notification (Watch) | 2026-07-14 10:29
| County | San Joaquin | 1-4 Hour Imminent Notification | 2026-07-15 10:02
| County | San Joaquin | At De-energization Initiation | 2026-07-15 16:33
| County | San Joaquin | Immediately Before Re-energization | 2026-07-16 09:04
| County | San Joaquin | When Re-energization is Complete | 2026-07-16 13:34
| County | San Luis Obispo | 48-72 Hour Advance Notification (Priority) | Refer to PG&E remark. | As explained in Table 6A: due to rapidly shifting weather, the initial PSPS scope was established after this notification window had passed. Therefore, it was not possible for the agencies in this jurisdiction to receive Priority Notifications.
| County | San Luis Obispo | 24-48 Hour Advance Notification (Watch) | 2026-07-14 10:29
| County | San Luis Obispo | 1-4 Hour Imminent Notification | 2026-07-15 08:43
| County | San Luis Obispo | At De-energization Initiation | 2026-07-15 13:06
| County | San Luis Obispo | Immediately Before Re-energization | 2026-07-16 08:18
| County | San Luis Obispo | When Re-energization is Complete | 2026-07-16 11:59
| County | Santa Barbara | 48-72 Hour Advance Notification (Priority) | Refer to PG&E remark. | As explained in Table 6A: due to rapidly shifting weather, the initial PSPS scope was established after this notification window had passed. Therefore, it was not possible for the agencies in this jurisdiction to receive Priority Notifications.
| County | Santa Barbara | 24-48 Hour Advance Notification (Watch) | 2026-07-14 10:29
| County | Santa Barbara | 1-4 Hour Imminent Notification | 2026-07-15 10:23
| County | Santa Barbara | At De-energization Initiation | 2026-07-15 15:41
| County | Santa Barbara | Immediately Before Re-energization | 2026-07-16 08:20
| County | Santa Barbara | When Re-energization is Complete | 2026-07-16 12:13 | As explained in Table 6G: due to concurrent SCE PSPS outages, agencies in this jurisdiction were only notified after PG&E customers were fully restored from both SCE and PG&E PSPS outages. The delayed notification timestamp is reported here - PG&E does not consider this a notification failure.
| Incorporated City | Concord | 48-72 Hour Advance Notification (Priority) | Refer to PG&E remark. | As explained in Table 6A: due to rapidly shifting weather, the initial PSPS scope was established after this notification window had passed. Therefore, it was not possible for the agencies in this jurisdiction to receive Priority Notifications.
| Incorporated City | Concord | 24-48 Hour Advance Notification (Watch) | 2026-07-14 10:29
| Incorporated City | Concord | 1-4 Hour Imminent Notification | 2026-07-15 12:02
| Incorporated City | Concord | At De-energization Initiation | 2026-07-15 15:46
| Incorporated City | Concord | Immediately Before Re-energization | Refer to PG&E remark. | As explained in Table 6F: due to a delay caused by attempts to fix false positive communications, the agencies in this jurisdiction were not notified immediately before re-energization because the intended notification was not sent until after restoration was complete.
| Incorporated City | Concord | When Re-energization is Complete | 2026-07-16 08:18
| Incorporated City | King City | 48-72 Hour Advance Notification (Priority) | Refer to PG&E remark. | As explained in Table 6A: due to rapidly shifting weather, the initial PSPS scope was established after this notification window had passed. Therefore, it was not possible for the agencies in this jurisdiction to receive Priority Notifications.
| Incorporated City | King City | 24-48 Hour Advance Notification (Watch) | 2026-07-14 10:29
| Incorporated City | King City | 1-4 Hour Imminent Notification | 2026-07-15 08:43
| Incorporated City | King City | At De-energization Initiation | 2026-07-15 12:52
| Incorporated City | King City | Immediately Before Re-energization | 2026-07-16 08:18
| Incorporated City | King City | When Re-energization is Complete | 2026-07-16 16:27
| Incorporated City | Mill Valley | 48-72 Hour Advance Notification (Priority) | Refer to PG&E remark. | As explained in Table 6A: due to rapidly shifting weather, the initial PSPS scope was established after this notification window had passed. Therefore, it was not possible for the agencies in this jurisdiction to receive Priority Notifications.
| Incorporated City | Mill Valley | 24-48 Hour Advance Notification (Watch) | 2026-07-14 10:29
| Incorporated City | Mill Valley | 1-4 Hour Imminent Notification | 2026-07-15 10:23
| Incorporated City | Mill Valley | At De-energization Initiation | 2026-07-15 18:18
| Incorporated City | Mill Valley | Immediately Before Re-energization | 2026-07-16 08:18
| Incorporated City | Mill Valley | When Re-energization is Complete | 2026-07-16 09:51
| Incorporated City | Soledad | 48-72 Hour Advance Notification (Priority) | Refer to PG&E remark. | As explained in Table 6A: due to rapidly shifting weather, the initial PSPS scope was established after this notification window had passed. Therefore, it was not possible for the agencies in this jurisdiction to receive Priority Notifications.
| Incorporated City | Soledad | 24-48 Hour Advance Notification (Watch) | 2026-07-14 10:29
| Incorporated City | Soledad | 1-4 Hour Imminent Notification | 2026-07-15 10:02
| Incorporated City | Soledad | At De-energization Initiation | 2026-07-15 12:58
| Incorporated City | Soledad | Immediately Before Re-energization | 2026-07-16 08:18
| Incorporated City | Soledad | When Re-energization is Complete | 2026-07-16 10:41
| Incorporated City | Solvang | 48-72 Hour Advance Notification (Priority) | Refer to PG&E remark. | As explained in Table 6A: due to rapidly shifting weather, the initial PSPS scope was established after this notification window had passed. Therefore, it was not possible for the agencies in this jurisdiction to receive Priority Notifications.
| Incorporated City | Solvang | 24-48 Hour Advance Notification (Watch) | 2026-07-14 10:30
| Incorporated City | Solvang | Cancellation Notification | 2026-07-14 23:18
| CCA | Alameda County, East Bay Community Energy | 48-72 Hour Advance Notification (Priority) | Refer to PG&E remark. | As explained in Table 6A: due to rapidly shifting weather, the initial PSPS scope was established after this notification window had passed. Therefore, it was not possible for the agencies in this jurisdiction to receive Priority Notifications.
| CCA | Alameda County, East Bay Community Energy | 24-48 Hour Advance Notification (Watch) | 2026-07-14 10:29
| CCA | Alameda County, East Bay Community Energy | 1-4 Hour Imminent Notification | 2026-07-15 10:02
| CCA | Alameda County, East Bay Community Energy | At De-energization Initiation | 2026-07-15 14:52
| CCA | Alameda County, East Bay Community Energy | Immediately Before Re-energization | 2026-07-16 09:05
| CCA | Alameda County, East Bay Community Energy | When Re-energization is Complete | 2026-07-16 12:41
| CCA | Contra Costa County, MCE Clean Energy | 48-72 Hour Advance Notification (Priority) | Refer to PG&E remark. | As explained in Table 6A: due to rapidly shifting weather, the initial PSPS scope was established after this notification window had passed. Therefore, it was not possible for the agencies in this jurisdiction to receive Priority Notifications.
| CCA | Contra Costa County, MCE Clean Energy | 24-48 Hour Advance Notification (Watch) | 2026-07-14 10:29
| CCA | Contra Costa County, MCE Clean Energy | 1-4 Hour Imminent Notification | 2026-07-15 10:02
| CCA | Contra Costa County, MCE Clean Energy | At De-energization Initiation | 2026-07-15 15:45
| CCA | Contra Costa County, MCE Clean Energy | Immediately Before Re-energization | 2026-07-16 08:18
| CCA | Contra Costa County, MCE Clean Energy | When Re-energization is Complete | 2026-07-16 11:18
| CCA | Marin County, MCE Clean Energy | 48-72 Hour Advance Notification (Priority) | Refer to PG&E remark. | As explained in Table 6A: due to rapidly shifting weather, the initial PSPS scope was established after this notification window had passed. Therefore, it was not possible for the agencies in this jurisdiction to receive Priority Notifications.
| CCA | Marin County, MCE Clean Energy | 24-48 Hour Advance Notification (Watch) | 2026-07-14 10:29
| CCA | Marin County, MCE Clean Energy | 1-4 Hour Imminent Notification | 2026-07-15 10:23
| CCA | Marin County, MCE Clean Energy | At De-energization Initiation | 2026-07-15 18:18
| CCA | Marin County, MCE Clean Energy | Immediately Before Re-energization | 2026-07-16 08:18
| CCA | Marin County, MCE Clean Energy | When Re-energization is Complete | 2026-07-16 09:51
| CCA | Monterey County, King City Community Power | 48-72 Hour Advance Notification (Priority) | Refer to PG&E remark. | As explained in Table 6A: due to rapidly shifting weather, the initial PSPS scope was established after this notification window had passed. Therefore, it was not possible for the agencies in this jurisdiction to receive Priority Notifications.
| CCA | Monterey County, King City Community Power | 24-48 Hour Advance Notification (Watch) | 2026-07-14 10:29
| CCA | Monterey County, King City Community Power | 1-4 Hour Imminent Notification | 2026-07-15 08:43
| CCA | Monterey County, King City Community Power | At De-energization Initiation | 2026-07-15 12:52
| CCA | Monterey County, King City Community Power | Immediately Before Re-energization | 2026-07-16 08:18
| CCA | Monterey County, King City Community Power | When Re-energization is Complete | 2026-07-16 16:27
| CCA | Monterey County, Monterey Bay Community Power | 48-72 Hour Advance Notification (Priority) | Refer to PG&E remark. | As explained in Table 6A: due to rapidly shifting weather, the initial PSPS scope was established after this notification window had passed. Therefore, it was not possible for the agencies in this jurisdiction to receive Priority Notifications.
| CCA | Monterey County, Monterey Bay Community Power | 24-48 Hour Advance Notification (Watch) | 2026-07-14 10:29
| CCA | Monterey County, Monterey Bay Community Power | 1-4 Hour Imminent Notification | 2026-07-15 08:43
| CCA | Monterey County, Monterey Bay Community Power | At De-energization Initiation | 2026-07-15 12:52
| CCA | Monterey County, Monterey Bay Community Power | Immediately Before Re-energization | 2026-07-16 08:18
| CCA | Monterey County, Monterey Bay Community Power | When Re-energization is Complete | 2026-07-16 16:27
| CCA | San Benito County, Monterey Bay Community Power | 48-72 Hour Advance Notification (Priority) | Refer to PG&E remark. | As explained in Table 6A: due to rapidly shifting weather, the initial PSPS scope was established after this notification window had passed. Therefore, it was not possible for the agencies in this jurisdiction to receive Priority Notifications.
| CCA | San Benito County, Monterey Bay Community Power | 24-48 Hour Advance Notification (Watch) | 2026-07-14 10:29
| CCA | San Benito County, Monterey Bay Community Power | 1-4 Hour Imminent Notification | 2026-07-15 08:43
| CCA | San Benito County, Monterey Bay Community Power | At De-energization Initiation | 2026-07-15 12:56
| CCA | San Benito County, Monterey Bay Community Power | Immediately Before Re-energization | 2026-07-16 08:18
| CCA | San Benito County, Monterey Bay Community Power | When Re-energization is Complete | 2026-07-16 14:22
| CCA | San Luis Obispo County, Monterey Bay Community Power | 48-72 Hour Advance Notification (Priority) | Refer to PG&E remark. | As explained in Table 6A: due to rapidly shifting weather, the initial PSPS scope was established after this notification window had passed. Therefore, it was not possible for the agencies in this jurisdiction to receive Priority Notifications.
| CCA | San Luis Obispo County, Monterey Bay Community Power | 24-48 Hour Advance Notification (Watch) | 2026-07-14 10:29
| CCA | San Luis Obispo County, Monterey Bay Community Power | 1-4 Hour Imminent Notification | 2026-07-15 08:43
| CCA | San Luis Obispo County, Monterey Bay Community Power | At De-energization Initiation | 2026-07-15 13:06
| CCA | San Luis Obispo County, Monterey Bay Community Power | Immediately Before Re-energization | 2026-07-16 08:18
| CCA | San Luis Obispo County, Monterey Bay Community Power | When Re-energization is Complete | 2026-07-16 11:59
| CCA | Santa Barbara County, Monterey Bay Community Power | 48-72 Hour Advance Notification (Priority) | Refer to PG&E remark. | As explained in Table 6A: due to rapidly shifting weather, the initial PSPS scope was established after this notification window had passed. Therefore, it was not possible for the agencies in this jurisdiction to receive Priority Notifications.
| CCA | Santa Barbara County, Monterey Bay Community Power | 24-48 Hour Advance Notification (Watch) | 2026-07-14 10:29
| CCA | Santa Barbara County, Monterey Bay Community Power | 1-4 Hour Imminent Notification | 2026-07-15 10:23
| CCA | Santa Barbara County, Monterey Bay Community Power | At De-energization Initiation | 2026-07-15 15:41
| CCA | Santa Barbara County, Monterey Bay Community Power | Immediately Before Re-energization | 2026-07-16 08:20
| CCA | Santa Barbara County, Monterey Bay Community Power | When Re-energization is Complete | 2026-07-16 12:13 | As explained in Table 6G: due to concurrent SCE PSPS outages, agencies in this jurisdiction were only notified after PG&E customers were fully restored from both SCE and PG&E PSPS outages. The delayed notification timestamp is reported here - PG&E does not consider this a notification failure.
| Distribution Circuit | ALTO 1124 | 48-72 Hour Advance Notification (Priority) | Refer to PG&E remark. | As explained in Table 6A: due to rapidly shifting weather, the initial PSPS scope was established after this notification window had passed. Therefore, it was not possible for the CFI on this circuit to receive Priority Notifications.
| Distribution Circuit | ALTO 1124 | 24-48 Hour Advance Notification (Watch) | 2026-07-14 10:42
| Distribution Circuit | ALTO 1124 | 1-4 Hour Imminent Notification | 2026-07-15 10:58
| Distribution Circuit | ALTO 1124 | At De-energization Initiation | 2026-07-15 18:25
| Distribution Circuit | ALTO 1124 | Immediately Before Re-energization | 2026-07-16 07:17
| Distribution Circuit | ALTO 1124 | When Re-energization is Complete | 2026-07-16 09:08
| Distribution Circuit | ALTO 1125 | 48-72 Hour Advance Notification (Priority) | Refer to PG&E remark. | As explained in Table 6A: due to rapidly shifting weather, the initial PSPS scope was established after this notification window had passed. Therefore, it was not possible for the CFI on this circuit to receive Priority Notifications.
| Distribution Circuit | ALTO 1125 | 24-48 Hour Advance Notification (Watch) | 2026-07-14 10:42
| Distribution Circuit | ALTO 1125 | 1-4 Hour Imminent Notification | 2026-07-15 10:58
| Distribution Circuit | ALTO 1125 | At De-energization Initiation | 2026-07-15 18:25
| Distribution Circuit | ALTO 1125 | Immediately Before Re-energization | 2026-07-16 07:17
| Distribution Circuit | ALTO 1125 | When Re-energization is Complete | 2026-07-16 09:46
| Distribution Circuit | CABRILLO 1104 | 48-72 Hour Advance Notification (Priority) | Refer to PG&E remark. | As explained in Table 6A: due to rapidly shifting weather, the initial PSPS scope was established after this notification window had passed. Therefore, it was not possible for the CFI on this circuit to receive Priority Notifications.
| Distribution Circuit | CABRILLO 1104 | 24-48 Hour Advance Notification (Watch) | 2026-07-14 10:42
| Distribution Circuit | CABRILLO 1104 | 1-4 Hour Imminent Notification | 2026-07-15 11:05
| Distribution Circuit | CABRILLO 1104 | At De-energization Initiation | 2026-07-15 15:41
| Distribution Circuit | CABRILLO 1104 | Immediately Before Re-energization | 2026-07-16 08:07
| Distribution Circuit | CABRILLO 1104 | When Re-energization is Complete | 2026-07-16 09:32
| Distribution Circuit | CABRILLO 1104 | Cancellation Notification | 2026-07-15 15:40 | As explained in Table 6H: customers on this circuit who were removed from scope received delayed notification of cancellation because they were incorrectly excluded from the original cancellation notification files. The delayed notification timestamp is reported here.
| Distribution Circuit | CARBONA 1101 | 48-72 Hour Advance Notification (Priority) | Refer to PG&E remark. | As explained in Table 6A: due to rapidly shifting weather, the initial PSPS scope was established after this notification window had passed. Therefore, it was not possible for the CFI on this circuit to receive Priority Notifications.
| Distribution Circuit | CARBONA 1101 | 24-48 Hour Advance Notification (Watch) | 2026-07-14 10:42
| Distribution Circuit | CARBONA 1101 | 1-4 Hour Imminent Notification | 2026-07-15 10:22
| Distribution Circuit | CARBONA 1101 | At De-energization Initiation | 2026-07-15 15:35
| Distribution Circuit | CARBONA 1101 | Immediately Before Re-energization | 2026-07-16 09:05
| Distribution Circuit | CARBONA 1101 | When Re-energization is Complete | 2026-07-16 10:47
| Distribution Circuit | GUSTINE 1102 | 48-72 Hour Advance Notification (Priority) | Refer to PG&E remark. | None of the customers in scope or de-energized on this circuit were CFI, so none of them required Priority notifications.
| Distribution Circuit | GUSTINE 1102 | 24-48 Hour Advance Notification (Watch) | 2026-07-14 10:42
| Distribution Circuit | GUSTINE 1102 | 1-4 Hour Imminent Notification | 2026-07-15 10:58
| Distribution Circuit | GUSTINE 1102 | Cancellation Notification | 2026-07-16 07:41
| Distribution Circuit | HAMMONDS 1102 | 48-72 Hour Advance Notification (Priority) | Refer to PG&E remark. | As explained in Table 6A: due to rapidly shifting weather, the initial PSPS scope was established after this notification window had passed. Therefore, it was not possible for the CFI on this circuit to receive Priority Notifications.
| Distribution Circuit | HAMMONDS 1102 | 24-48 Hour Advance Notification (Watch) | 2026-07-14 10:42
| Distribution Circuit | HAMMONDS 1102 | 1-4 Hour Imminent Notification | 2026-07-15 12:22
| Distribution Circuit | HAMMONDS 1102 | Cancellation Notification | 2026-07-16 07:41
| Distribution Circuit | HERDLYN 1102 | 48-72 Hour Advance Notification (Priority) | Refer to PG&E remark. | None of the customers in scope or de-energized on this circuit were CFI, so none of them required Priority notifications.
| Distribution Circuit | HERDLYN 1102 | 24-48 Hour Advance Notification (Watch) | 2026-07-14 10:43
| Distribution Circuit | HERDLYN 1102 | 1-4 Hour Imminent Notification | 2026-07-15 10:26
| Distribution Circuit | HERDLYN 1102 | At De-energization Initiation | 2026-07-15 16:16
| Distribution Circuit | HERDLYN 1102 | Immediately Before Re-energization | 2026-07-16 09:05
| Distribution Circuit | HERDLYN 1102 | When Re-energization is Complete | 2026-07-16 12:06
| Distribution Circuit | KING CITY 1102 | 48-72 Hour Advance Notification (Priority) | Refer to PG&E remark. | As explained in Table 6A: due to rapidly shifting weather, the initial PSPS scope was established after this notification window had passed. Therefore, it was not possible for the CFI on this circuit to receive Priority Notifications.
| Distribution Circuit | KING CITY 1102 | 24-48 Hour Advance Notification (Watch) | 2026-07-14 10:42
| Distribution Circuit | KING CITY 1102 | 1-4 Hour Imminent Notification | 2026-07-15 09:03
| Distribution Circuit | KING CITY 1102 | At De-energization Initiation | 2026-07-15 12:59
| Distribution Circuit | KING CITY 1102 | Immediately Before Re-energization | 2026-07-16 07:34
| Distribution Circuit | KING CITY 1102 | When Re-energization is Complete | 2026-07-16 09:58
| Distribution Circuit | KING CITY 1103 | 48-72 Hour Advance Notification (Priority) | Refer to PG&E remark. | As explained in Table 6A: due to rapidly shifting weather, the initial PSPS scope was established after this notification window had passed. Therefore, it was not possible for the CFI on this circuit to receive Priority Notifications.
| Distribution Circuit | KING CITY 1103 | 24-48 Hour Advance Notification (Watch) | 2026-07-14 10:42
| Distribution Circuit | KING CITY 1103 | 1-4 Hour Imminent Notification | 2026-07-15 10:22
| Distribution Circuit | KING CITY 1103 | Cancellation Notification | 2026-07-16 07:41
| Distribution Circuit | KING CITY 1106 | 48-72 Hour Advance Notification (Priority) | Refer to PG&E remark. | As explained in Table 6A: due to rapidly shifting weather, the initial PSPS scope was established after this notification window had passed. Therefore, it was not possible for the CFI on this circuit to receive Priority Notifications.
| Distribution Circuit | KING CITY 1106 | 24-48 Hour Advance Notification (Watch) | 2026-07-14 10:42
| Distribution Circuit | KING CITY 1106 | 1-4 Hour Imminent Notification | 2026-07-15 09:03
| Distribution Circuit | KING CITY 1106 | At De-energization Initiation | 2026-07-15 13:05
| Distribution Circuit | KING CITY 1106 | Immediately Before Re-energization | 2026-07-16 07:34
| Distribution Circuit | KING CITY 1106 | When Re-energization is Complete | 2026-07-16 10:39
| Distribution Circuit | LAS POSITAS 2110 | 48-72 Hour Advance Notification (Priority) | Refer to PG&E remark. | As explained in Table 6A: due to rapidly shifting weather, the initial PSPS scope was established after this notification window had passed. Therefore, it was not possible for the CFI on this circuit to receive Priority Notifications.
| Distribution Circuit | LAS POSITAS 2110 | 24-48 Hour Advance Notification (Watch) | 2026-07-14 10:42
| Distribution Circuit | LAS POSITAS 2110 | 1-4 Hour Imminent Notification | 2026-07-15 10:22
| Distribution Circuit | LAS POSITAS 2110 | At De-energization Initiation | 2026-07-15 15:45
| Distribution Circuit | LAS POSITAS 2110 | Immediately Before Re-energization | 2026-07-16 09:05
| Distribution Circuit | LAS POSITAS 2110 | When Re-energization is Complete | 2026-07-16 11:18
| Distribution Circuit | LAURELES 1111 | 48-72 Hour Advance Notification (Priority) | Refer to PG&E remark. | As explained in Table 6A: due to rapidly shifting weather, the initial PSPS scope was established after this notification window had passed. Therefore, it was not possible for the CFI on this circuit to receive Priority Notifications.
| Distribution Circuit | LAURELES 1111 | 24-48 Hour Advance Notification (Watch) | 2026-07-14 10:42
| Distribution Circuit | LAURELES 1111 | 1-4 Hour Imminent Notification | 2026-07-15 10:58
| Distribution Circuit | LAURELES 1111 | Cancellation Notification | 2026-07-16 07:41
| Distribution Circuit | LOS OSITOS 2101 | 48-72 Hour Advance Notification (Priority) | Refer to PG&E remark. | As explained in Table 6A: due to rapidly shifting weather, the initial PSPS scope was established after this notification window had passed. Therefore, it was not possible for the CFI on this circuit to receive Priority Notifications.
| Distribution Circuit | LOS OSITOS 2101 | 24-48 Hour Advance Notification (Watch) | 2026-07-14 10:42
| Distribution Circuit | LOS OSITOS 2101 | 1-4 Hour Imminent Notification | 2026-07-15 10:22
| Distribution Circuit | LOS OSITOS 2101 | At De-energization Initiation | 2026-07-15 12:56
| Distribution Circuit | LOS OSITOS 2101 | Immediately Before Re-energization | 2026-07-16 07:34
| Distribution Circuit | LOS OSITOS 2101 | When Re-energization is Complete | 2026-07-16 12:08
| Distribution Circuit | LOS OSITOS 2102 | 48-72 Hour Advance Notification (Priority) | Refer to PG&E remark. | As explained in Table 6A: due to rapidly shifting weather, the initial PSPS scope was established after this notification window had passed. Therefore, it was not possible for the CFI on this circuit to receive Priority Notifications.
| Distribution Circuit | LOS OSITOS 2102 | 24-48 Hour Advance Notification (Watch) | 2026-07-14 10:42
| Distribution Circuit | LOS OSITOS 2102 | 1-4 Hour Imminent Notification | 2026-07-15 10:22
| Distribution Circuit | LOS OSITOS 2102 | At De-energization Initiation | 2026-07-15 12:54
| Distribution Circuit | LOS OSITOS 2102 | Immediately Before Re-energization | 2026-07-16 07:34
| Distribution Circuit | LOS OSITOS 2102 | When Re-energization is Complete | 2026-07-16 16:27
| Distribution Circuit | LOS OSITOS 2103 | 48-72 Hour Advance Notification (Priority) | Refer to PG&E remark. | As explained in Table 6A: due to rapidly shifting weather, the initial PSPS scope was established after this notification window had passed. Therefore, it was not possible for the CFI on this circuit to receive Priority Notifications.
| Distribution Circuit | LOS OSITOS 2103 | 24-48 Hour Advance Notification (Watch) | 2026-07-14 10:42
| Distribution Circuit | LOS OSITOS 2103 | 1-4 Hour Imminent Notification | 2026-07-15 10:58
| Distribution Circuit | LOS OSITOS 2103 | Cancellation Notification | 2026-07-16 07:41
| Distribution Circuit | OILFIELDS 1102 | 48-72 Hour Advance Notification (Priority) | Refer to PG&E remark. | As explained in Table 6A: due to rapidly shifting weather, the initial PSPS scope was established after this notification window had passed. Therefore, it was not possible for the CFI on this circuit to receive Priority Notifications.
| Distribution Circuit | OILFIELDS 1102 | 24-48 Hour Advance Notification (Watch) | 2026-07-14 10:42
| Distribution Circuit | OILFIELDS 1102 | 1-4 Hour Imminent Notification | 2026-07-15 09:03
| Distribution Circuit | OILFIELDS 1102 | At De-energization Initiation | 2026-07-15 13:14
| Distribution Circuit | OILFIELDS 1102 | Immediately Before Re-energization | 2026-07-16 07:34
| Distribution Circuit | OILFIELDS 1102 | When Re-energization is Complete | 2026-07-16 14:01
| Distribution Circuit | OILFIELDS 1103 | 48-72 Hour Advance Notification (Priority) | Refer to PG&E remark. | As explained in Table 6A: due to rapidly shifting weather, the initial PSPS scope was established after this notification window had passed. Therefore, it was not possible for the CFI on this circuit to receive Priority Notifications.
| Distribution Circuit | OILFIELDS 1103 | 24-48 Hour Advance Notification (Watch) | 2026-07-14 10:42
| Distribution Circuit | OILFIELDS 1103 | 1-4 Hour Imminent Notification | 2026-07-15 09:03
| Distribution Circuit | OILFIELDS 1103 | At De-energization Initiation | 2026-07-15 13:06
| Distribution Circuit | OILFIELDS 1103 | Immediately Before Re-energization | 2026-07-16 07:27
| Distribution Circuit | OILFIELDS 1103 | When Re-energization is Complete | 2026-07-16 09:38
| Distribution Circuit | OILFIELDS 1103 | Cancellation Notification | 2026-07-14 23:44
| Distribution Circuit | SAN ARDO 1101 | 48-72 Hour Advance Notification (Priority) | Refer to PG&E remark. | None of the customers in scope or de-energized on this circuit were CFI, so none of them required Priority notifications.
| Distribution Circuit | SAN ARDO 1101 | 24-48 Hour Advance Notification (Watch) | 2026-07-14 10:43
| Distribution Circuit | SAN ARDO 1101 | 1-4 Hour Imminent Notification | 2026-07-15 09:04
| Distribution Circuit | SAN ARDO 1101 | At De-energization Initiation | 2026-07-15 13:32
| Distribution Circuit | SAN ARDO 1101 | Immediately Before Re-energization | 2026-07-16 07:34
| Distribution Circuit | SAN ARDO 1101 | When Re-energization is Complete | 2026-07-16 10:48
| Distribution Circuit | SAN ARDO 1102 | 48-72 Hour Advance Notification (Priority) | Refer to PG&E remark. | As explained in Table 6A: due to rapidly shifting weather, the initial PSPS scope was established after this notification window had passed. Therefore, it was not possible for the CFI on this circuit to receive Priority Notifications.
| Distribution Circuit | SAN ARDO 1102 | 24-48 Hour Advance Notification (Watch) | 2026-07-14 10:42
| Distribution Circuit | SAN ARDO 1102 | 1-4 Hour Imminent Notification | 2026-07-15 09:03
| Distribution Circuit | SAN ARDO 1102 | At De-energization Initiation | 2026-07-15 13:16
| Distribution Circuit | SAN ARDO 1102 | Immediately Before Re-energization | 2026-07-16 07:34
| Distribution Circuit | SAN ARDO 1102 | When Re-energization is Complete | 2026-07-16 11:26
| Distribution Circuit | SANTA NELLA 1103 | 48-72 Hour Advance Notification (Priority) | Refer to PG&E remark. | As explained in Table 6A: due to rapidly shifting weather, the initial PSPS scope was established after this notification window had passed. Therefore, it was not possible for the CFI on this circuit to receive Priority Notifications.
| Distribution Circuit | SANTA NELLA 1103 | 24-48 Hour Advance Notification (Watch) | 2026-07-14 10:42
| Distribution Circuit | SANTA NELLA 1103 | 1-4 Hour Imminent Notification | 2026-07-15 10:58
| Distribution Circuit | SANTA NELLA 1103 | Cancellation Notification | 2026-07-16 07:41
| Distribution Circuit | SANTA NELLA 1104 | 48-72 Hour Advance Notification (Priority) | Refer to PG&E remark. | As explained in Table 6A: due to rapidly shifting weather, the initial PSPS scope was established after this notification window had passed. Therefore, it was not possible for the CFI on this circuit to receive Priority Notifications.
| Distribution Circuit | SANTA NELLA 1104 | 24-48 Hour Advance Notification (Watch) | 2026-07-14 10:42
| Distribution Circuit | SANTA NELLA 1104 | 1-4 Hour Imminent Notification | 2026-07-15 10:58
| Distribution Circuit | SANTA NELLA 1104 | Cancellation Notification | 2026-07-16 07:41
| Distribution Circuit | SANTA YNEZ 1102 | 48-72 Hour Advance Notification (Priority) | Refer to PG&E remark. | As explained in Table 6A: due to rapidly shifting weather, the initial PSPS scope was established after this notification window had passed. Therefore, it was not possible for the CFI on this circuit to receive Priority Notifications.
| Distribution Circuit | SANTA YNEZ 1102 | 24-48 Hour Advance Notification (Watch) | 2026-07-14 10:42
| Distribution Circuit | SANTA YNEZ 1102 | 1-4 Hour Imminent Notification | 2026-07-15 12:22
| Distribution Circuit | SANTA YNEZ 1102 | Cancellation Notification | 2026-07-14 23:44
| Distribution Circuit | SOLEDAD 2101 | 48-72 Hour Advance Notification (Priority) | Refer to PG&E remark. | As explained in Table 6A: due to rapidly shifting weather, the initial PSPS scope was established after this notification window had passed. Therefore, it was not possible for the CFI on this circuit to receive Priority Notifications.
| Distribution Circuit | SOLEDAD 2101 | 24-48 Hour Advance Notification (Watch) | 2026-07-14 10:42
| Distribution Circuit | SOLEDAD 2101 | 1-4 Hour Imminent Notification | 2026-07-15 10:22
| Distribution Circuit | SOLEDAD 2101 | At De-energization Initiation | 2026-07-15 12:58
| Distribution Circuit | SOLEDAD 2101 | Immediately Before Re-energization | 2026-07-16 07:34
| Distribution Circuit | SOLEDAD 2101 | When Re-energization is Complete | 2026-07-16 10:41
| Distribution Circuit | TIDEWATER 2106 | 48-72 Hour Advance Notification (Priority) | Refer to PG&E remark. | As explained in Table 6A: due to rapidly shifting weather, the initial PSPS scope was established after this notification window had passed. Therefore, it was not possible for the CFI on this circuit to receive Priority Notifications.
| Distribution Circuit | TIDEWATER 2106 | 24-48 Hour Advance Notification (Watch) | 2026-07-14 10:42
| Distribution Circuit | TIDEWATER 2106 | 1-4 Hour Imminent Notification | 2026-07-15 12:22
| Distribution Circuit | TIDEWATER 2106 | At De-energization Initiation | 2026-07-15 15:52
| Distribution Circuit | TIDEWATER 2106 | Immediately Before Re-energization | 2026-07-16 07:36
| Distribution Circuit | TIDEWATER 2106 | When Re-energization is Complete | 2026-07-16 07:50
| Transmission Line | COBURN-OIL FIELDS #2 | 48-72 Hour Advance Notification (Priority) | Refer to PG&E remark. | No customers were in scope or de-energized on this Transmission line, so no customer notifications were required.
| Transmission Line | COBURN-OIL FIELDS #2 | 24-48 Hour Advance Notification (Watch) | Refer to PG&E remark. | No customers were in scope or de-energized on this Transmission line, so no customer notifications were required.
| Transmission Line | COBURN-OIL FIELDS #2 | 1-4 Hour Imminent Notification | Refer to PG&E remark. | No customers were in scope or de-energized on this Transmission line, so no customer notifications were required.
| Transmission Line | COBURN-OIL FIELDS #2 | At De-energization Initiation | Refer to PG&E remark. | No customers were in scope or de-energized on this Transmission line, so no customer notifications were required.
| Transmission Line | COBURN-OIL FIELDS #2 | Immediately Before Re-energization | Refer to PG&E remark. | No customers were in scope or de-energized on this Transmission line, so no customer notifications were required.
| Transmission Line | COBURN-OIL FIELDS #2 | When Re-energization is Complete | Refer to PG&E remark. | No customers were in scope or de-energized on this Transmission line, so no customer notifications were required.
| Transmission Line | SAN ARDO TAP | 48-72 Hour Advance Notification (Priority) | Refer to PG&E remark. | No customers were in scope or de-energized on this Transmission line, so no customer notifications were required.
| Transmission Line | SAN ARDO TAP | 24-48 Hour Advance Notification (Watch) | Refer to PG&E remark. | No customers were in scope or de-energized on this Transmission line, so no customer notifications were required.
| Transmission Line | SAN ARDO TAP | 1-4 Hour Imminent Notification | Refer to PG&E remark. | No customers were in scope or de-energized on this Transmission line, so no customer notifications were required.
| Transmission Line | SAN ARDO TAP | At De-energization Initiation | Refer to PG&E remark. | No customers were in scope or de-energized on this Transmission line, so no customer notifications were required.
| Transmission Line | SAN ARDO TAP | Immediately Before Re-energization | Refer to PG&E remark. | No customers were in scope or de-energized on this Transmission line, so no customer notifications were required.
| Transmission Line | SAN ARDO TAP | When Re-energization is Complete | Refer to PG&E remark. | No customers were in scope or de-energized on this Transmission line, so no customer notifications were required.

## Table 5
#VALUE!
Table 5: Positive Notification
| Designation | Total Number of Customers | Number of Notification Attempts Made1 | Timing of Attempts | Who Made the Notification Attempt | Successful Positive Notification
| MBL in scope2 | 288 | 288 | Daily | PG&E | 288
| SIV | 129 | 129 | Daily | PG&E | 129
1 Count of “Notification Attempts Made” includes doorbell rings and Live Agent phone calls.
2 Residential tenants of master-metered customers can also qualify for MBL quantities. The MBL category for the purposes of Table 5 includes MBL customers who are master meter tenants.

## Table 6
#VALUE!
Table 6: Breakdown of Notification Failure
| Notifications Sent to | Notification Failure Description | Number of Entities or Customer Account | Explanation of Failure
| Public Safety Partners Excluding CFI1 | Entities who did not receive 48-to 72-hour priority notification | 89* | See Table 6A for explanation.
|  | Entities who did not receive 24-48 hour advance notification | 4 | See Table 6B for explanations.
|  | Entities who did not receive 1-4-hour imminent notification | 4 | See Table 6C for explanations.
|  | Entities who did not receive any notifications before de-energization | 3 | See Table 6D for explanations.
|  | Entities who were not notified at de-energization initiation | 0 | No failures.
|  | Entities who were not notified immediately before re-energization | 3 | See Table 6F for explanations.
|  | Entities who were not notified when re-energization is complete | 4 | See Table 6G for explanations.
|  | Entities who did not receive cancellation notification within two hours of the decision to cancel | 0 | No failures.
| CFI2 | Facilities who did not receive 48-72-hour priority notification | 180* | See Table 6A for explanations.
|  | Facilities who did not receive 24-48 hour advance notification | 0 | No failures.
|  | Facilities who did not receive 1-4-hour imminent notification | 0 | No failures.
|  | Facilities who did not receive any notifications before de-energization | 0 | No failures.
|  | Facilities who were not notified at de-energization initiation | 0 | No failures.
|  | Facilities who were not notified immediately before re-energization | 0 | No failures.
|  | Facilities who were not notified when re-energization is complete | 0 | No failures.
|  | Facilities who did not receive cancellation notification within two hours of the decision to cancel | 1 | See Table 6H for explanations.
| All other Affected Customers | Customers who did not receive 24-48-hour advance notifications | 31 | See Table 6B for explanations.
|  | Customers who did not receive 1-4-hour imminent notifications | 27 | See Table 6C for explanations.
|  | Customers who did not receive any notifications before de-energization | 16** | See Table 6D for explanations.
|  | Customers who were not notified at de-energization initiation | 17 | See Table 6E for explanations.
|  | Customers who were not notified immediately before re-energization | 18 | See Table 6F for explanations.
|  | Customers who were not notified when re-energization is complete | 18 | See Table 6G for explanations.
|  | Customers who did not receive cancellation notification within two hours of the decision to cancel | 62 | See Table 6H for explanations.
*PG&E does not consider these to be notification failures as we operated within the discretionary parameters prescribed in the CPUC’s PSPS guidelines for utilities. (See D.19-05-042, D.21-06- 034.)
**This category is duplicative with other notification failure categories in this report, meaning all customers reported in this category are already included in the count of notification failures PG&E reported for the more specific notification categories. As a result, the count from this category should not be included in the sum of total notification failures for this PSPS.
1 Only includes cities, counties and CCAs.
2 Includes Public Safety Partners who are CFI customers.

## Table 6A
#VALUE!
Table 6A: Explanation of Failures for Agency Entities and CFI Who Did Not Receive 48-to 72-Hour Priority Notification
| Total (Agency Entities) | Total (CFI) | Explanation
| 89 | 180 | As explained in Section 1.1, due to the rapidly shifting weather, the initial PSPS scope was established for de-energization after the (48 – 72hr) Priority Notification window had passed. As a result, these agency entities and critical facilities were not sent Priority Notifications.*
*PG&E does not consider these to be notification failures as we operated within the discretionary parameters prescribed in the CPUC’s PSPS guidelines for utilities. (See D.19-05-042, D.21-06 034.)

## Table 6B
#VALUE!
Table 6B: Explanation of Failures for Agency Entities and All Other Affected Customers Who Did Not Receive 24-to 48-Hour Watch Notification
| Total (Agency Entities) | Total (Non-CFI Customers) | Explanation
| 4 | 0 | Due to a system logic error in PG&E’s system for pre-outage notifications, these agency entities were incorrectly notified of PSPS impact to areas not in-scope for PSPS. In addition to missing this type of notification, this error also caused false positive communications as discussed in Section 5.7.
| 0 | 31 | These customers did not receive notifications during this PSPS as no valid contact information for the main customer of record was provided to PG&E.*
*PG&E does not consider these to be notification failures as we operated within the discretionary parameters prescribed in the CPUC’s PSPS guidelines for utilities. (See D.19-05-042, D.21-06 034.)

## Table 6C
#VALUE!
Table 6C: Explanation of Failures for Agency Entities and All Other Affected Customers Who Did Not Receive 1-4 Hour Imminent Notifications
| Total (Agency Entities) | Total (Non-CFI Customers) | Explanation
| 4 | 0 | Due to a system logic error in PG&E’s system for pre-outage notifications, these agency entities were incorrectly notified of PSPS impact to areas not in-scope for PSPS. In addition to missing this type of notification, this error also caused false positive communications as discussed in Section 5.7.
| 0 | 1 | This customer was included in PG&E notification files for 1 – 4 Hour Imminent Notifications provided to our notifications vendor. However, this customer was not notified by our notifications vendor. The root cause is still under investigation, and we will report our findings in the 2026 PSPS Post-Season Report.
| 0 | 26 | These customers did not receive notifications during this PSPS as no valid contact information for the main customer of record was provided to PG&E.*
*PG&E does not consider these to be notification failures as we operated within the discretionary parameters prescribed in the CPUC’s PSPS guidelines for utilities. (See D.19-05-042, D.21-06 034.)

## Table 6D
#VALUE!
Table 6D: Explanation of Failures for Agency Entities and All Other Affected Customers Who Did Not Receive Any Notifications Before De-Energization
| Total (Agency Entities) | Total (Non-CFI Customers) | Explanation
| 3 | 0 | Due to a system logic error in PG&E’s system for pre-outage notifications, these agency entities were incorrectly notified of PSPS impact to areas not in-scope for PSPS. In addition to missing this type of notification, this error also caused false positive communications as discussed in Section 5.7.
| 0 | 16 | These customers did not receive notifications during this PSPS as no valid contact information for the main customer of record was provided to PG&E.*
*PG&E does not consider these to be notification failures as we operated within the discretionary parameters prescribed in the CPUC’s PSPS guidelines for utilities. (See D.19-05-042, D.21-06 034.)

## Table 6E
#VALUE!
Table 6E: Explanation of Failures for All Other Affected Customers Who Did Not Receive Power Off Notification
| Total | Explanation
| 17 | These customers did not receive notifications during this PSPS as no valid contact information for the main customer of record was provided to PG&E.*
*PG&E does not consider these to be notification failures as we operated within the discretionary parameters prescribed in the CPUC’s PSPS guidelines for utilities. (See D.19-05-042, D.21-06 034.)

## Table 6F
#VALUE!
Table 6F: Explanation of Failures for Agency Entities and All Other Affected Customers Not Notified Immediately Before Re-energization
| Total (Agency Entities) | Total (Non-CFI Customers) | Explanation
| 3 | 0 | Due to a delay within our in-outage notification systems, caused by attempts to fix false positive communications described in Section 5.7, these agency entities were not notified until after restoration was complete.
| 0 | 17 | These customers did not receive notifications during this PSPS as no valid contact information for the main customer of record was provided to PG&E.*
| 0 | 1 | This non-critical customer was partially mitigated from PSPS de-energization using backup generation provided by PG&E. However, as this customer had already experienced a short outage as part of the PSPS prior to their mitigation, we consider this as an impacted customer with a shortened outage duration. Their PSPS outage was considered to be over when their generator started running. This customer did not receive an automated notification immediately prior to or after the generator started running. However, PG&E does not believe this is a notification failure because the recipient of backup generation was in coordination with PG&E crews who implemented the mitigation.
*PG&E does not consider these to be notification failures as we operated within the discretionary parameters prescribed in the CPUC’s PSPS guidelines for utilities. (See D.19-05-042, D.21-06 034.)

## Table 6G
#VALUE!
Table 6G: Explanation of Failures for Agency Entities and All Other Affected Customers Who Did Not Receive Restore Notification
| Total (Agency Entities) | Total (Non-CFI Customers) | Explanation
| 4 | 0 | PG&E’s automated notification systems will notify agencies of restoration after all impacted customers within their jurisdiction have been restored from PSPS. Concurrent to this PSPS, Southern California Edison (SCE) was also activated for a PSPS which impacted some PG&E customers. Our automated notification systems did not differentiate between PG&E customers impacted by SCE and PG&E’s separate PSPS events. This delayed the Restoration Notifications from being sent until after both SCE and PG&E’s PSPS were fully restored. PG&E does not consider this a notification failure because we notified the county agencies when all PSPS impacts were restored from their county. We are explaining this in the table due to the otherwise perceived delay between when customers were restored from PG&E’s PSPS in this county vs. when the county agencies received this notification.
| 0 | 17 | These customers did not receive notifications during this PSPS as no valid contact information for the main customer of record was provided to PG&E.*
| 0 | 1 | This non-critical customer was partially mitigated from PSPS de-energization using backup generation provided by PG&E. However, as this customer had already experienced a short outage as part of the PSPS prior to their mitigation, we consider this as an impacted customer with a shortened outage duration. Their PSPS outage was considered to be over when their generator started running. This customer did not receive an automated notification immediately prior to or after the generator started running. However, PG&E does not believe this is a notification failure because the recipient of backup generation was in coordination with PG&E crews who implemented the mitigation.
*PG&E does not consider these to be notification failures as we operated within the discretionary parameters prescribed in the CPUC’s PSPS guidelines for utilities. (See D.19-05-042, D.21-06 034.)

## Table 6H
#VALUE!
Table 6H: Explanation of Failures for CFI and All Other Affected Customers Who Did Not Receive Cancelation Notification
| Total (CFI) | Total (Other Customers) | Explanation
| 1 | 62 | Due to process and procedure issues, these customers were incorrectly excluded from the Cancel Notification files. Once we became aware of this issue, we sent these customers a delayed Cancel Notification.

## Table 7
#VALUE!
Table 7: Explanations of False Positive Communications
| Total (Agency Entities) | Total (CFI) | Total (Other Customers) | Explanation
| 11 | 0 | 0 | A data issue caused de-energized transformers to be incorrectly assigned to these agencies’ jurisdictions. As a result, these agencies were incorrectly notified of active PSPS de-energization for their jurisdictions. This issue impacted agencies but did not result in any false communications to customers. Two instances occurred during this PSPS. Once this issue was identified, PG&E began outreach to clarify the situation within one hour in the first instance, and within approximately two hours for the second instance.
| 10 | 0 | 0 | Due to a system logic error in PG&E’s system for pre-outage notifications, these agency entities were incorrectly notified of PSPS impact to areas not de-energized for PSPS. No Cancellation Notifications were sent for these areas because this error was not discovered until after the end of the PSPS. This error also caused notification failures as discussed in Section 5.5.
| 0 | 0 | 2 | These customers stopped their PG&E service after the planned PSPS scope was finalized but before PSPS de-energization occurred. As a result, these customers were correctly notified of PSPS impact while they were still active but are not counted as de-energized customers. Furthermore, they did not require Cancellation Notifications because PG&E did not remove them from scope.*
*PG&E does not consider these to be false communications as we operated within the discretionary parameters prescribed in the CPUC’s PSPS guidelines for utilities. (See D.19-05-042, D.21-06-034.)

## Table 8
#VALUE!
Table 8: Explanations of False Negative Communications
| Total (Agency Entities) | Total (CFI) | Total (Other Customers) | Explanation
| 8 | 0 | 0 | Due to human error, these agency entities received a premature PSPS Restore Notification. Once this issue was identified, PG&E began outreach to clarify the situation within 30 minutes of the false communications.

## Table 9
#VALUE!
Table 9: PSPS Data Portal Map Sharing (Date and Time)
| Date | Time PDF and GIS Maps Shared (PDT)
| 2026-07-14 | 11:15
| 2026-07-14 | 23:00

## Table 10
#VALUE!
Table 10: Notifications Submitted to Cal OES (Date and Time)
| Date | Time Submitted (PDT)
| 2026-07-14 | 7:19
| 2026-07-14 | 14:28
| 2026-07-15 | 6:15
| 2026-07-15 | 13:05
| 2026-07-15 | 14:56
| 2026-07-16 | 6:42
| 2026-07-16 | 8:50
| 2026-07-16 | 14:59
| 2026-07-16 | 16:33

## Table 11
#VALUE!
Table 11: Notifications Submitted to CPUC (Date and Time)
| Date | Time Submitted (PDT)
| 2026-07-14 | 6:38
| 2026-07-14 | 23:12
| 2026-07-15 | 7:55
| 2026-07-15 | 13:00
| 2026-07-15 | 14:55
| 2026-07-15 | 15:53
| 2026-07-15 | 19:17
| 2026-07-16 | 7:35
| 2026-07-16 | 7:48
| 2026-07-16 | 16:23

## Table 12
#VALUE!
Table 12: AFN Customer Programs and Support
| Resource/Program | Resources Provided
| Disability Disaster Access and Resource Program (DDAR) | Partnered with eight local ILCs across 10 counties to provide aid to 113 customers who rely on power for medical or independent living needs, including: • Six batteries • Four batteries previously distributed in impacted counties Although we partner with DDAR to provide hotel accommodations, food vouchers, generator fuel vouchers and accessible transportation, we did not receive any requests for these services during this PSPS.
| PBP | Supported 49 customers in scope by providing batteries through the PBP. Since July 2020, over 28,500 battery units have been delivered through the PBP across our service area.
| Food Bank Partnerships | Partnered with seven local food banks that serve all impacted counties to provide boxes of food for families.
| Meals on Wheels Partnerships | Partnered with Meals on Wheels Organizations in four counties to provide services to customers in scope for the de-energization.
| CA 211 Providers Network | Partnered with eight CA 211 network centers across 10 counties to assist 37 customers with resources. The direct assistance resources provided during this activation included: • 40 food vouchers • Five hotel accommodations • Three water bladders • Three generator fuel vouchers Although we partner with CA 211 to provide accessible transportation, we did not receive any transportation requests for this PSPS.
| Accessible Transportation Partnerships | Partnered with Vivalon and Fresno Economic Opportunities Commission across three counties in preparation for the possibility of any transportation needs.
| Ad-Hoc AFN Backup Generation Solutions | We granted temporary generation exceptions to one AFN customer in need of critical support. This included transportation limitations and medical device requirements that CBO resources were unable to resolve during this PSPS. After exploring all viable options, PG&E delivered backup generation to this individual who relies on power for their health and safety. This specific situation does not meet our typical temporary generation process and procedures standards. However, given the unique circumstances, we went beyond our usual practices to ensure safety for our customers.

## Table 13
#VALUE!
Table 13: Generators Available for CFI Customers
| Number of Units | Individual Size (MW) | Run Time (Hrs.)1 | Description
| 3 | 0.032 | 37.6 | Three units on reserve in Sacramento.
| 1 | 0.036 | 37.6 | One unit on reserve in Sacramento.
| 4 | 0.065 | 31 | Four units on reserve in San Leandro.
| 6 | 0.1 | 25.3 | Six units on reserve in Sacramento.
| 2 | 0.125 | 25 | One unit on reserve in Sacramento and one unit on reserve in San Leandro.
| 2 | 0.15 | 30.3 | Two units on reserve in Sacramento.
| 5 | 0.2 | 22.9 | Five units on reserve in San Leandro.
| 3 | 0.23 | 22.9 | Three units on reserve in San Leandro.
| 3 | 0.275 | 26 | Three units on reserve in Sacramento.
| 3 | 0.5 | 24.1 | Three units on reserve in Sacramento.
| 3 | 0.57 | 24.1 | Three units on reserve in San Leandro.
| 3 | 1 | 35 | Three units on reserve in Sacramento.
| 14 | 1.14 | 24 | 14 units on reserve in San Leandro.
| 7 | 1.5 | 10 | Seven units on reserve in Benecia.
| 17 | 2 | 27.7 | Eight units on reservation in Sacramento and nine units on reserve in San Leandro.
1 Estimated based on a 75% load. Barring mechanical failure and refueling the temporary generators have the ability to operate continuously throughout a typical PSPS.

## Table 14
#VALUE!
Table 14: Number and Nature of Complaints
| Nature of Complaints | Number of Complaints
| Communications/Notifications Including, but not limited to complaints regarding lack of notice, excessive notices, confusing notice, false alarm notice, problems with getting up-to-date information, inaccurate information provided, not being able to access information in the prevalent languages and/or information accessibility, complaints about website, Public Safety Partner Portal, Representational State Transfer (REST)/Digital Asset Manager (DAM) sites (as applicable). | 19
| PSPS Frequency/Duration Including, but not limited to complaints regarding the frequency and/or duration of PSPS, including delays in restoring power, scope of PSPS and dynamic of weather conditions. | 13
| Safety/Health Concern Including, but not limited to complaints regarding difficulties experienced by AFN/MBL populations, traffic accidents due to non-operating traffic lights, inability to get medical help, well water or access to clean water, inability to keep property cool/warm during outage raising health concern. | 14
| General PSPS Dissatisfaction/Other Including, but not limited to complaints about being without power during PSPS and related hardships such as food loss, income loss, inability to work/attend school, plus any PSPS-related complaints that do not fall into any other category. | 43
| Outreach/Assistance Including, but not limited to complaints regarding CRCs, community crew vehicles, backup power, hotel vouchers, and other assistance provided by utility to mitigate impact of PSPS. | 1

## Table 15
#VALUE!
Table 15: Count and Type of Claims Received
| Description of Claims | Number of Claims
| Business Interruption / Economic Loss | 0
| Food Loss Only | 1
| Property Damage | 1

## Table 16
#VALUE!
Table 16: Circuits Requiring More than 24 Hours to Restore
| Circuit Name | Reason the Utility was Unable to Restore the Circuit Within 24 Hours
| None | None

## Table 17
#VALUE!
Table 17: Lessons Learned
| Issue | Discussion | Resolution
| Agency Outreach | Jurisdictions that have not been included in PSPS scope for several years may be relying on outdated messaging templates. An in-scope police department that had not experienced a PSPS in recent years included an incorrect link in one of its advisory messages. | We will work with jurisdictions to ensure they have the latest information to share in their own advisory messages and press releases.
| Technology | During the PSPS, a system issue resulted in 64 customers not receiving cancellation notifications within the required notification window. | The root cause of these notification failures is still under investigation; corrective actions will be identified upon completion of the investigation and reported in the 2026 Post Season Report. All corrective actions will focus on preventing similar communication discrepancies in future PSPS events.

## Table 18
#VALUE!
Table 18: Maximum Wind Gusts Recorded During July 15 – 16, 2026
| County | Maximum Wind Gust (mph) | Station Name
| Alameda | 45 | Altamont RAWS
| Contra Costa | 55 | Black Diamond Mine East
| Marin | 43 | Big Rock
| Monterey | 43 | Las Aquilas
| Santa Barbara | 55 | SCE Coastal View
| San Benito | 28 | San Juan Grade
| San Joaquin | 43 | I-205 MacArthur Drive
| San Luis Obispo | 44 | Davis Peak

## Appendix A-1.1
#VALUE!
Appendix A-1.1 - Factors Considered in the Decision to Shut Off Power for Each Distribution Circuit De-energized During the July 15, 2026 PSPS
| Circuit Name | Time Place | De-energization Date/ Time | Restoration Date/ Time | Threshold | [9 empty] | Forecast | [9 empty] | Observed | [9 empty] | Qualitative Factors
[5 empty] | WS MPH | Flame Length ft 8hr | Rate of Spread Chhr 8hr | RH % | Prob Cat | DFM 10hr | DFM 100 hr | CFPD | NVDI | Benefit to Risk Ratio | WS MPH | Flame Length ft 8hr | Rate of Spread Chhr 8hr | RH % | Prob Cat | DFM 10hr | DFM 100 hr | CFPD | NVDI | Benefit to Risk Ratio | WS MPH | Flame Length ft 8hr | Rate of Spread Chhr 8hr | RH % | Prob Cat | DFM 10hr | DFM 100 hr | CFPD | NVDI | Benefit to Risk Ratio | GACC (Yes/No) | NOAA (Yes/ No) | RFW (Yes/ No) | Open PSPS Tags (Yes/ No) | Tx Impacts (Yes/ No)
| ALTO 1124 | TP01 | 2026-07-15 18:07 | 2026-07-16 09:41 | 19 | 10 | 30 | 30 | 0.2 | 0.09 | 0.12 | 6 | 0.36 | 1 | 37 | 11.1 | 34.7 | 11.4 | 0.329 | 0.032 | 0.062 | 9.7995 | 0.31 | 34.2081 | 26 | No observed values available | No observed values available | 14 | 0.28 | 0.03 | No observed values available | 7.75 | 0.21 | No observed values available | No | No | No | Yes | No
| ALTO 1125 | TP01 | 2026-07-15 18:05 | 2026-07-16 09:36 | 19 | 10 | 30 | 30 | 0.2 | 0.09 | 0.12 | 6 | 0.36 | 1 | 28 | 11.7 | 39.4 | 11.4 | 0.308 | 0.032 | 0.062 | 9.7995 | 0.31 | 98.7587 | 26 | No observed values available | No observed values available | 14 | 0.25 | 0.03 | No observed values available | 3.37 | 0.11 | No observed values available | Yes | No | No | Yes | No
| CABRILLO 1104 | TP11 | 2026-07-15 15:30 | 2026-07-16 09:17 | 19 | 10 | 30 | 30 | 0.2 | 0.09 | 0.12 | 6 | 0.36 | 1 | 33 | 11.6 | 178.2 | 20.6 | 0.229 | 0.043 | 0.088 | 3.4213 | 0.26 | 18565.6189 | 33 | No observed values available | No observed values available | 28 | 0.2 | 0.08 | No observed values available | 2.27 | 0.13 | No observed values available | No | No | Yes | Yes | No
| CARBONA 1101 | TP03 | 2026-07-15 15:25 | 2026-07-16 11:50 | 19 | 10 | 30 | 30 | 0.2 | 0.09 | 0.12 | 6 | 0.36 | 1 | 25 | 11.6 | 157.1 | 9.7 | 0.379 | 0.024 | 0.048 | 3.7192 | 0.231 | 1734.2921 | 35 | No observed values available | No observed values available | 10 | 0.35 | 0.03 | No observed values available | 1.99 | 0.07 | No observed values available | Yes | Yes | No | Yes | No
| HERDLYN 1102 | TP03 | 2026-07-15 15:49 | 2026-07-16 11:24 | 19 | 10 | 30 | 30 | 0.2 | 0.09 | 0.12 | 6 | 0.36 | 1 | 25 | 12.1 | 182.1 | 9.5 | 0.317 | 0.025 | 0.055 | 2.1585 | 0.24 | 2622.479 | 35 | No observed values available | No observed values available | 11 | 0.29 | 0.03 | No observed values available | 1.01 | 0.09 | No observed values available | Yes | Yes | No | No | No
| KING CITY 1102 | TP08 | 2026-07-15 12:49 | 2026-07-16 09:52 | 19 | 10 | 30 | 30 | 0.2 | 0.09 | 0.12 | 6 | 0.36 | 1 | 28 | 13.3 | 168.3 | 10.8 | 0.327 | 0.03 | 0.065 | 2.626 | 0.248 | 868.6639 | 15 | No observed values available | No observed values available | 23 | 0.31 | 0.04 | No observed values available | 1.4 | 0.07 | No observed values available | No | Yes | No | Yes | No
| KING CITY 1106 | TP08 | 2026-07-15 12:53 | 2026-07-16 10:37 | 19 | 10 | 30 | 30 | 0.2 | 0.09 | 0.12 | 6 | 0.36 | 1 | 27 | 14.7 | 211.7 | 9.6 | 0.381 | 0.028 | 0.06 | 3.3586 | 0.249 | 534.5356 | 15 | No observed values available | No observed values available | 17 | 0.38 | 0.04 | No observed values available | 1.46 | 0.07 | No observed values available | No | Yes | No | Yes | No
| LAS POSITAS 2110 | TP03 | 2026-07-15 15:31 | 2026-07-16 11:09 | 19 | 10 | 30 | 30 | 0.2 | 0.09 | 0.12 | 6 | 0.36 | 1 | 24 | 12.2 | 181.1 | 9.6 | 0.28 | 0.03 | 0.069 | 2.2247 | 0.241 | 3107.2083 | 35 | No observed values available | No observed values available | 11 | 0.22 | 0.03 | No observed values available | 1.07 | 0.08 | No observed values available | Yes | Yes | No | Yes | No
| LOS OSITOS 2101 | TP07 | 2026-07-15 12:46 | 2026-07-16 14:12 | 19 | 10 | 30 | 30 | 0.2 | 0.09 | 0.12 | 6 | 0.36 | 1 | 24 | 13.5 | 177 | 10.2 | 0.477 | 0.028 | 0.055 | 5.0696 | 0.247 | 147.8228 | 26 | No observed values available | No observed values available | 16 | 0.46 | 0.05 | No observed values available | 2.77 | 0.11 | No observed values available | No | Yes | No | Yes | No
| LOS OSITOS 2102 | TP07 | 2026-07-15 12:42 | 2026-07-16 16:17 | 19 | 10 | 30 | 30 | 0.2 | 0.09 | 0.12 | 6 | 0.36 | 1 | 29 | 14.2 | 199.8 | 10.9 | 0.235 | 0.039 | 0.09 | 1.8661 | 0.244 | 485.7642 | 26 | No observed values available | No observed values available | 17 | 0.2 | 0.05 | No observed values available | 0.94 | 0.1 | No observed values available | No | Yes | No | No | No
| OILFIELDS 1102 | TP10 | 2026-07-15 13:00 | 2026-07-16 15:43 | 19 | 10 | 30 | 30 | 0.2 | 0.09 | 0.12 | 6 | 0.36 | 1 | 24 | 11.5 | 148.2 | 10.8 | 0.375 | 0.031 | 0.07 | 3.9 | 0.256 | 499.6581 | 26 | No observed values available | No observed values available | 19 | 0.35 | 0.04 | No observed values available | 1.58 | 0.11 | No observed values available | No | Yes | No | Yes | No
| OILFIELDS 1103 | TP10 | 2026-07-15 12:57 | 2026-07-16 11:43 | 19 | 10 | 30 | 30 | 0.2 | 0.09 | 0.12 | 6 | 0.36 | 1 | 27 | 11.5 | 148.2 | 8.9 | 0.632 | 0.027 | 0.059 | 3.1854 | 0.25 | 21.6746 | 26 | No observed values available | No observed values available | 14 | 0.57 | 0.04 | No observed values available | 16.41 | 0.1 | No observed values available | No | Yes | No | Yes | No
| SAN ARDO 1101 | TP10 | 2026-07-15 13:22 | 2026-07-16 10:08 | 19 | 10 | 30 | 30 | 0.2 | 0.09 | 0.12 | 6 | 0.36 | 1 | 27 | 13.5 | 180.1 | 11.3 | 0.372 | 0.034 | 0.076 | 4.1342 | 0.255 | 2615.1975 | 19 | No observed values available | No observed values available | 18 | 0.36 | 0.04 | No observed values available | 1.38 | 0.11 | No observed values available | No | Yes | No | Yes | No
| SAN ARDO 1102 | TP10 | 2026-07-15 13:07 | 2026-07-16 11:33 | 19 | 10 | 30 | 30 | 0.2 | 0.09 | 0.12 | 6 | 0.36 | 1 | 27 | 14.2 | 200.4 | 10.4 | 0.462 | 0.029 | 0.06 | 5.4687 | 0.251 | 41.5236 | 26 | No observed values available | No observed values available | 18 | 0.45 | 0.04 | No observed values available | 1.87 | 0.1 | No observed values available | No | Yes | No | Yes | No
| SOLEDAD 2101 | TP07 | 2026-07-15 12:49 | 2026-07-16 10:29 | 19 | 10 | 30 | 30 | 0.2 | 0.09 | 0.12 | 6 | 0.36 | 1 | 27 | 13.2 | 173.6 | 10.6 | 0.343 | 0.033 | 0.065 | 5.0696 | 0.246 | 291.0215 | 27 | No observed values available | No observed values available | 14 | 0.33 | 0.05 | No observed values available | 2.2 | 0.11 | No observed values available | No | Yes | No | Yes | No
| TIDEWATER 2106 | TP02 | 2026-07-15 15:22 | 2026-07-16 08:43 | 19 | 10 | 30 | 30 | 0.2 | 0.09 | 0.12 | 6 | 0.36 | 1 | 27 | 11.1 | 138 | 9.6 | 0.564 | 0.028 | 0.052 | 2.758 | 0.244 | 1808.9858 | 40 | No observed values available | No observed values available | 13 | 0.5 | 0.03 | No observed values available | 2.05 | 0.1 | No observed values available | Yes | No | No | No | No

## Appendix A-2.1
#VALUE!
Appendix A-2.1 - Factors Considered in the Decision to Shut Off Power for Each Transmission Circuit De-energized During the July 15, 2026 PSPS
| Circuit Name | Time Place | De-energization Date/ Time | Restoration Date/ Time | Threshold | [9 empty] | Forecast | [9 empty] | Observed | [11 empty] | Qualitative Factors
[5 empty] | WS MPH | Flame Length ft 8hr | Rate of Spread Chhr 8hr | RH % | Prob Cat | DFM 10hr | DFM 100 hr | CFPT | NVDI | Benefit to Risk Ratio | WS MPH | Flame Length ft 8hr | Rate of Spread Chhr 8hr | RH % | Prob Cat | DFM 10hr | DFM 100 hr | CFPT | NVDI | Benefit to Risk Ratio | WS MPH | Flame Length ft 8hr | Rate of Spread Chhr 8hr | RH % | Prob Cat | DFM 10hr | DFM 100 hr | CFPT | NVDI | HFRA (Yes/No) | High Risk Veg Present on Circuit (Yes/No) | Benefit to Risk Ratio | GACC (Yes/No) | NOAA (Yes/ No) | RFW (Yes/ No) | Tx Impacts (Yes/ No)
| COBURN-OIL FIELDS #2 | TP10 | 2026-07-15 13:13 | 2026-07-16 09:52 | 19 | 10 | 30 | 30 | 0.2 | 0.09 | 0.12 | 1.5 | 0.36 | 1 | 25 | 13.8 | 196.2 | 10.8 | 0.298 | 0.034 | 0.076 | 0.43 | 0.246 | 53710.1837 | 26 | No observed values available | No observed values available | 18 | 0.28 | 0.04 | No observed values available | No observed values available | 0.12 | Yes | No | No observed values available | No | No | No | No
| SAN ARDO TAP | TP10 | 2026-07-15 13:13 | 2026-07-16 09:52 | 19 | 10 | 30 | 30 | 0.2 | 0.09 | 0.12 | 1.5 | 0.36 | 1 | 24 | 13.5 | 180.1 | 11.7 | 0.189 | 0.036 | 0.08 | No observed values available | 0.255 | 0 | 19 | No observed values available | No observed values available | 20 | 0.17 | 0.04 | No observed values available | No observed values available | 0.09 | No | No | No observed values available | No | No | No | No

## Appendix B
#VALUE!
Appendix B - Circuits De-Energized During the July 15, 2026 PSPS
Circuits labeled as “non-HFTD” are located outside of the CPUC High Fire-Threat District (HFTD). We use a High Fire Risk Area (HFRA) classification which PG&E utilizes in addition to HFTD to determine PSPS scope – these circuits intersected PG&E's HFRA despite not entering HFTD Tier 2 or Tier 3.
| Distribution / Transmission | Circuit Name | De-Energization Date and Time (PDT) | All-Clear Date and Time (PDT) | Restoration Date and Time (PDT) | Key Counties | HFTD Tier(s) | Total Customers | Residential Customers | Commercial / Industrial Customers | MBL Program Customers | AFN other than MBL Program Customers | Other Customers
| Distribution | ALTO 1124 | 2026-07-15 18:07 | 2026-07-16 06:47 | 2026-07-16 09:41 | Marin | Partially Outside HFTD, Tier 3 | 1637 | 1567 | 70 | 47 | 66 | 0
| Distribution | ALTO 1125 | 2026-07-15 18:05 | 2026-07-16 06:47 | 2026-07-16 09:36 | Marin | Tier 3 | 384 | 363 | 21 | 9 | 23 | 0
| Distribution | CABRILLO 1104 | 2026-07-15 15:30 | 2026-07-16 06:47 | 2026-07-16 09:17 | Santa Barbara | Tier 2 | 1 | 0 | 1 | 0 | 0 | 0
| Distribution | CARBONA 1101 | 2026-07-15 15:25 | 2026-07-16 08:38 | 2026-07-16 11:50 | Alameda, San Joaquin | Outside HFTD | 56 | 22 | 14 | 2 | 3 | 20
| Distribution | HERDLYN 1102 | 2026-07-15 15:49 | 2026-07-16 08:38 | 2026-07-16 11:24 | Alameda | Outside HFTD | 4 | 2 | 2 | 0 | 0 | 0
| Distribution | KING CITY 1102 | 2026-07-15 12:49 | 2026-07-16 06:47 | 2026-07-16 09:52 | San Benito, Monterey | Outside HFTD | 58 | 14 | 17 | 0 | 4 | 27
| Distribution | KING CITY 1106 | 2026-07-15 12:53 | 2026-07-16 06:47 | 2026-07-16 10:37 | San Benito, Monterey | Outside HFTD | 88 | 42 | 25 | 0 | 8 | 21
| Distribution | LAS POSITAS 2110 | 2026-07-15 15:31 | 2026-07-16 08:38 | 2026-07-16 11:09 | Contra Costa, Alameda | Outside HFTD | 50 | 22 | 26 | 0 | 0 | 2
| Distribution | LOS OSITOS 2101 | 2026-07-15 12:46 | 2026-07-16 06:47 | 2026-07-16 14:12 | San Benito, Monterey | Outside HFTD | 167 | 92 | 47 | 4 | 10 | 28
| Distribution | LOS OSITOS 2102 | 2026-07-15 12:42 | 2026-07-16 06:47 | 2026-07-16 16:17 | Monterey | Outside HFTD | 89 | 26 | 37 | 1 | 5 | 26
| Distribution | OILFIELDS 1102 | 2026-07-15 13:00 | 2026-07-16 06:47 | 2026-07-16 15:43 | Monterey | Outside HFTD | 100 | 33 | 38 | 1 | 6 | 29
| Distribution | OILFIELDS 1103 | 2026-07-15 12:57 | 2026-07-16 06:47 | 2026-07-16 11:43 | Monterey, San Luis Obispo | Partially Outside HFTD, Tier 2 | 1711 | 1459 | 210 | 70 | 148 | 42
| Distribution | SAN ARDO 1101 | 2026-07-15 13:22 | 2026-07-16 06:47 | 2026-07-16 10:08 | Monterey | Outside HFTD | 14 | 7 | 3 | 0 | 0 | 4
| Distribution | SAN ARDO 1102 | 2026-07-15 13:07 | 2026-07-16 06:47 | 2026-07-16 11:33 | San Benito, Monterey | Partially Outside HFTD, Tier 2 | 598 | 352 | 159 | 12 | 134 | 87
| Distribution | SOLEDAD 2101 | 2026-07-15 12:49 | 2026-07-16 06:47 | 2026-07-16 10:29 | Monterey | Partially Outside HFTD, Tier 2 | 162 | 99 | 32 | 2 | 36 | 31
| Distribution | TIDEWATER 2106 | 2026-07-15 15:22 | 2026-07-16 06:47 | 2026-07-16 08:43 | Contra Costa | Partially Outside HFTD, Tier 2 | 67 | 51 | 15 | 3 | 7 | 1
| Transmission | COBURN-OIL FIELDS #2 | 2026-07-15 13:13 | 2026-07-16 06:47 | 2026-07-16 09:52 | Monterey | Outside HFTD | 0 | 0 | 0 | 0 | 0 | 0
| Transmission | SAN ARDO TAP | 2026-07-15 13:13 | 2026-07-16 06:47 | 2026-07-16 09:52 | Monterey | Outside HFTD | 0 | 0 | 0 | 0 | 0 | 0
| Total | [6 empty] | 5186 | 4151 | 717 | 151 | 450 | 318

## Appendix C
#VALUE!
Appendix C - Public Safety Partners Contacted
| Jurisdiction | Agency/Organization | HFTD or HFRA Tier | Date/Time Contacted (PDT)
| Alameda County | Alameda County Fire Department, Fire Department | HFRA | 7/14/2026 10:30 PDT
| Alameda County | Alameda County Fire Department, OES | HFRA | 7/14/2026 10:29 PDT
| Alameda County | BART | HFRA | 7/14/2026 10:29 PDT
| Alameda County | County Administration | HFRA | 7/14/2026 10:29 PDT
| Alameda County | County Administration | HFRA | 7/14/2026 10:29 PDT
| Alameda County | County Administration | HFRA | 7/14/2026 10:29 PDT
| Alameda County | EBMUD | HFRA | 7/14/2026 10:29 PDT
| Alameda County | EMS | HFRA | 7/14/2026 10:29 PDT
| Alameda County | Fire Department | HFRA | 7/14/2026 10:30 PDT
| Alameda County | OES | HFRA | 7/14/2026 10:29 PDT
| Alameda County | OES, Office of Emergency Services | HFRA | 7/14/2026 10:29 PDT
| Alameda County | Office of Education | HFRA | 7/14/2026 10:29 PDT
| Alameda County | Sheriff's Department | HFRA | 7/14/2026 10:29 PDT
| Alameda County | Sheriff's Office | HFRA | 7/14/2026 10:29 PDT
| Alameda County CCA | East Bay Community Energy | HFRA | 7/14/2026 10:29 PDT
| Alameda County Communication Facility | AT&T Services Inc | HFRA | 7/14/2026 10:42 PDT
| Contra Costa County | BART | Tier 2 | 7/14/2026 10:30 PDT
| Contra Costa County | City of Concord, Concord, California | Tier 2 | 7/14/2026 10:30 PDT
| Contra Costa County | Contra Costa County Fire Protection District, Fire Department | Tier 2 | 7/14/2026 10:29 PDT
| Contra Costa County | Contra Costa County, County Administration | Tier 2 | 7/14/2026 10:29 PDT
| Contra Costa County | Contra Costa Office of Emergency Services | Tier 2 | 7/14/2026 10:29 PDT
| Contra Costa County | County Administration | Tier 2 | 7/14/2026 10:29 PDT
| Contra Costa County | County Administration | Tier 2 | 7/14/2026 10:29 PDT
| Contra Costa County | County Administration, County Administrator's Office | Tier 2 | 7/14/2026 10:29 PDT
| Contra Costa County | EMS | Tier 2 | 7/14/2026 10:29 PDT
| Contra Costa County | East Bay Regional Parks Fire Department | Tier 2 | 7/14/2026 10:29 PDT
| Contra Costa County | OES | Tier 2 | 7/14/2026 10:29 PDT
| Contra Costa County | Rodeo Hercules Fire Protection District | Tier 2 | 7/14/2026 10:29 PDT
| Contra Costa County | San Ramon Valley Fire Protection District | Tier 2 | 7/14/2026 10:29 PDT
| Contra Costa County CCA | MCE Clean Energy | Tier 2 | 7/14/2026 10:29 PDT
| Contra Costa County Communication Facility | AT&T Mobility LLC | Tier 2 | 7/14/2026 10:42 PDT
| Contra Costa County Communication Facility | AT&T Services Inc | HFRA | 7/14/2026 10:42 PDT
| Contra Costa County Communication Facility | City of Concord | Non-HFTD and Non-HFRA; upstream of HFRA but within PSPS scope because downstream of de-energization device. | 7/14/2026 10:42 PDT
| Contra Costa County Communication Facility | Comcast Fresno LLC | Non-HFTD and Non-HFRA; upstream of HFRA but within PSPS scope because downstream of de-energization device. | 7/14/2026 10:42 PDT
| Contra Costa County Communication Facility | SBA Towers | Tier 2 | 7/14/2026 10:42 PDT
| Contra Costa County Communication Facility | T-Mobile West Corporation | HFRA | 7/14/2026 10:42 PDT
| Contra Costa County Communication Facility | T-Mobile West LLC | Tier 2 | 7/14/2026 10:42 PDT
| Contra Costa County Communication Facility | Verizon | HFRA, Tier 2 | 7/14/2026 10:42 PDT
| Contra Costa County Communication Facility | Verizon Wireless | Tier 2 | 7/14/2026 10:42 PDT
| Contra Costa County Concord | City Administration | Tier 2 | 7/14/2026 10:29 PDT
| Contra Costa County Concord | City Clerk Office | Tier 2 | 7/14/2026 10:29 PDT
| Contra Costa County Concord | City of Concord | Tier 2 | 7/14/2026 10:30 PDT
| Contra Costa County Concord | Concord Police Department, Police Department | Tier 2 | 7/14/2026 10:29 PDT
| Contra Costa County Concord | Motco Fire Department | Tier 2 | 7/14/2026 10:29 PDT
| Fresno County | City Administration | HFRA | 7/14/2026 10:29 PDT
| Fresno County | City Administration, City of Kingsburg | HFRA | 7/14/2026 10:30 PDT
| Fresno County | County Administration | HFRA | 7/14/2026 10:29 PDT
| Fresno County | County Administration, County of Fresno | HFRA | 7/14/2026 10:29 PDT
| Fresno County | County Clerk Office | HFRA | 7/14/2026 10:29 PDT
| Fresno County | EMS | HFRA | 7/14/2026 10:29 PDT
| Fresno County | Fire Department | HFRA | 7/14/2026 10:30 PDT
| Fresno County | Fresno County OES | HFRA | 7/14/2026 10:29 PDT
| Fresno County | Fresno County office of Emergency Services | HFRA | 7/14/2026 10:29 PDT
| Fresno County | OES | HFRA | 7/14/2026 10:29 PDT
| Fresno County | Sheriff's Department | HFRA | 7/14/2026 10:29 PDT
| Fresno County Communication Facility | American Tower Corporation | HFRA | 7/14/2026 10:42 PDT
| Fresno County Communication Facility | California Highway Patrol | HFRA | 7/14/2026 10:42 PDT
| Marin County | County Administration | HFRA, Tier 3 | 7/14/2026 10:29 PDT
| Marin County | EMS | HFRA, Tier 3 | 7/14/2026 10:29 PDT
| Marin County | Fire Department | HFRA, Tier 3 | 7/14/2026 10:29 PDT
| Marin County | Fire Department, Southern Marin Fire District | HFRA, Tier 3 | 7/14/2026 10:29 PDT
| Marin County | Fire Protection District | HFRA, Tier 3 | 7/14/2026 10:29 PDT
| Marin County | Health and Human Services, Public Health | HFRA, Tier 3 | 7/14/2026 10:29 PDT
| Marin County | Marin County, Marin County, California | HFRA, Tier 3 | 7/14/2026 10:30 PDT
| Marin County | OES | HFRA, Tier 3 | 7/14/2026 10:29 PDT
| Marin County | Public Health | HFRA, Tier 3 | 7/14/2026 10:29 PDT
| Marin County | Sheriff's Department | HFRA, Tier 3 | 7/14/2026 10:29 PDT
| Marin County | Sheriff's Office | HFRA, Tier 3 | 7/14/2026 10:29 PDT
| Marin County CCA | MCE Clean Energy | HFRA, Tier 3 | 7/14/2026 10:29 PDT
| Marin County Communication Facility | AT&T Services Inc | Tier 3 | 7/14/2026 10:42 PDT
| Marin County Communication Facility | Comcast Cable Communications Management LLC | Tier 3 | 7/14/2026 10:42 PDT
| Marin County Communication Facility | Comcast Fresno LLC | Tier 3 | 7/14/2026 10:42 PDT
| Marin County Communication Facility | EIP Holdings II LLC | Tier 3 | 7/14/2026 10:42 PDT
| Marin County Communication Facility | TCI | Tier 3 | 7/14/2026 10:42 PDT
| Marin County Emergency Services Facility | County of Marin | Tier 3 | 7/14/2026 10:42 PDT
| Marin County Mill Valley | City Administration | HFRA, Tier 3 | 7/14/2026 10:29 PDT
| Marin County Mill Valley | Fire Department | HFRA, Tier 3 | 7/14/2026 10:29 PDT
| Marin County Mill Valley | Mill Valley Police Department | HFRA, Tier 3 | 7/14/2026 10:29 PDT
| Marin County Mill Valley | Public Works | HFRA, Tier 3 | 7/14/2026 10:29 PDT
| Marin County Other Facility | City of Mill Valley | Tier 3 | 7/14/2026 10:42 PDT
| Marin County Other Facility | EIP Holdings II LLC | Tier 3 | 7/14/2026 10:42 PDT
| Merced County | CAL FIRE | HFRA | 7/14/2026 10:29 PDT
| Merced County | County Administration | HFRA | 7/14/2026 10:29 PDT
| Merced County | County Administration | HFRA | 7/14/2026 10:29 PDT
| Merced County | Fire Department | HFRA | 7/14/2026 10:30 PDT
| Merced County | Merced County | HFRA | 7/14/2026 10:29 PDT
| Merced County | Merced County OES | HFRA | 7/14/2026 10:29 PDT
| Merced County | OES | HFRA | 7/14/2026 10:29 PDT
| Merced County | Sheriff's Department | HFRA | 7/14/2026 10:29 PDT
| Merced County Communication Facility | AT&T Services Inc | HFRA, Partially Outside HFRA | 7/14/2026 10:42 PDT
| Merced County Communication Facility | T-Mobile West LLC | HFRA | 7/14/2026 10:42 PDT
| Merced County Communication Facility | Verizon | HFRA | 7/14/2026 10:42 PDT
| Merced County Communication Facility | Verizon Services Corporation | Non-HFTD and Non-HFRA; upstream of HFRA but within PSPS scope because downstream of de-energization device. | 7/14/2026 10:42 PDT
| Merced County Emergency Services Facility | California Department of Forestry | Non-HFTD and Non-HFRA; within PSPS scope because downstream of HFRA | 7/14/2026 10:42 PDT
| Merced County Other Facility | Crown Castle USA Inc | HFRA | 7/14/2026 10:42 PDT
| Monterey County | Big Sur Fire, Fire Department | HFRA, Tier 2 | 7/14/2026 10:29 PDT
| Monterey County | Board of Supervisors, County Administration | HFRA, Tier 2 | 7/14/2026 10:29 PDT
| Monterey County | California Office of Emergency Services | HFRA, Tier 2 | 7/14/2026 10:29 PDT
| Monterey County | California Office of Emergency Services | HFRA, Tier 2 | 7/14/2026 10:29 PDT
| Monterey County | County Administration | HFRA, Tier 2 | 7/14/2026 10:29 PDT
| Monterey County | County of Monterey Department of Emergency Management (DEM) | HFRA, Tier 2 | 7/14/2026 10:29 PDT
| Monterey County | County of Monterey Department of Emergency Management, OES | HFRA, Tier 2 | 7/14/2026 10:30 PDT
| Monterey County | County of Monterey EMS Agency | HFRA, Tier 2 | 7/14/2026 10:29 PDT
| Monterey County | Department of Emergency Management, OES | HFRA, Tier 2 | 7/14/2026 10:29 PDT
| Monterey County | Fire Department | HFRA, Tier 2 | 7/14/2026 10:29 PDT
| Monterey County | Fire Department, Monterey County Regional Fire Protection District | HFRA, Tier 2 | 7/14/2026 10:29 PDT
| Monterey County | Hollister Fire | HFRA, Tier 2 | 7/14/2026 10:29 PDT
| Monterey County | Monterey Fire (City of Monterey) | HFRA, Tier 2 | 7/14/2026 10:29 PDT
| Monterey County | OES | HFRA, Tier 2 | 7/14/2026 10:29 PDT
| Monterey County | Sheriff's Department | HFRA, Tier 2 | 7/14/2026 10:29 PDT
| Monterey County CCA | King City Community Power | HFRA, Tier 2 | 7/14/2026 10:29 PDT
| Monterey County CCA | Monterey Bay Community Power | HFRA, Tier 2 | 7/14/2026 10:29 PDT
| Monterey County Communication Facility | AT&T (New Cingular Wireless) | Tier 2 | 7/14/2026 10:42 PDT
| Monterey County Communication Facility | AT&T Mobility LLC | HFRA, Partially Outside HFTD, Tier 2 | 7/14/2026 10:42 PDT
| Monterey County Communication Facility | AT&T Services Inc | HFRA, Partially Outside HFTD, Tier 2 | 7/14/2026 10:42 PDT
| Monterey County Communication Facility | Charter Communications Holding Company LLC | Non-HFTD and Non-HFRA; within PSPS scope because downstream of HFRA | 7/14/2026 10:42 PDT
| Monterey County Communication Facility | Cingular Wireless Services, INC | HFRA | 7/14/2026 10:42 PDT
| Monterey County Communication Facility | Frontier Communication S Corporation DIP | HFRA | 7/14/2026 10:42 PDT
| Monterey County Communication Facility | Level 3 Communications LLC | Non-HFTD and Non-HFRA; within PSPS scope because downstream of HFRA | 7/14/2026 10:42 PDT
| Monterey County Communication Facility | Sprint Corporation | Non-HFTD and Non-HFRA; upstream of HFRA but within PSPS scope because downstream of de-energization device. | 7/14/2026 10:42 PDT
| Monterey County Communication Facility | T-Mobile West A Delaware Corporation | HFRA | 7/14/2026 10:42 PDT
| Monterey County Communication Facility | T-Mobile West LLC | Non-HFTD and Non-HFRA; within PSPS scope because downstream of HFRA | 7/14/2026 10:42 PDT
| Monterey County Communication Facility | Verizon | HFRA, Partially Outside HFRA | 7/14/2026 10:42 PDT
| Monterey County Communication Facility | West Ern States Teleport | Tier 2 | 7/14/2026 10:42 PDT
| Monterey County Emergency Services Facility | County of Monterey | Non-HFTD and Non-HFRA; within PSPS scope because downstream of HFRA | 7/14/2026 10:42 PDT
| Monterey County Emergency Services Facility | San Ardo Volunteer Fire Department | Non-HFTD and Non-HFRA; within PSPS scope because downstream of HFRA | 7/14/2026 10:42 PDT
| Monterey County Emergency Services Facility | South Monterey County Fire Department | Partially Outside HFTD, Tier 2 | 7/14/2026 10:42 PDT
| Monterey County Other Facility | Crown Castle USA Inc | Non-HFTD and Non-HFRA; within PSPS scope because downstream of HFRA | 7/14/2026 10:42 PDT
| Monterey County Other Facility | San Ardo Water District | Non-HFTD and Non-HFRA; within PSPS scope because downstream of HFRA | 7/14/2026 10:42 PDT
| Monterey County King City | City Administration | HFRA | 7/14/2026 10:29 PDT
| Monterey County King City | Fire Department | HFRA | 7/14/2026 10:29 PDT
| Monterey County King City | Police Department | HFRA | 7/14/2026 10:30 PDT
| Monterey County Soledad | City Administration | Tier 2 | 7/14/2026 10:29 PDT
| Monterey County Soledad | Fire Department | Tier 2 | 7/14/2026 10:30 PDT
| Monterey County Soledad | Police Department | Tier 2 | 7/14/2026 10:29 PDT
| Monterey County Water and Waste Water Facility | City of King City | Non-HFTD and Non-HFRA; upstream of HFRA but within PSPS scope because downstream of de-energization device. | 7/14/2026 10:42 PDT
| Monterey County Water and Waste Water Facility | San Ardo Water District | Non-HFTD and Non-HFRA; within PSPS scope because downstream of HFRA | 7/14/2026 10:42 PDT
| Monterey County Water and Waste Water Facility | San Lucas Wastewater Treatment Facility | Non-HFTD and Non-HFRA; upstream of HFRA but within PSPS scope because downstream of de-energization device. | 7/14/2026 10:42 PDT
| San Benito County | County Administration | HFRA | 7/14/2026 10:29 PDT
| San Benito County | EMS | HFRA | 7/14/2026 10:29 PDT
| San Benito County | OES | HFRA | 7/14/2026 10:29 PDT
| San Benito County | OES, Office of Emergency Services | HFRA | 7/14/2026 10:29 PDT
| San Benito County | San Benito County office of Emergency Services | HFRA | 7/14/2026 10:29 PDT
| San Benito County | Sheriff's Department | HFRA | 7/14/2026 10:29 PDT
| San Benito County | Sheriff's Office | HFRA | 7/14/2026 10:30 PDT
| San Benito County CCA | Monterey Bay Community Power | HFRA | 7/14/2026 10:29 PDT
| San Benito County Communication Facility | AT&T Services Inc | HFRA | 7/14/2026 10:42 PDT
| San Benito County Water and Waste Water Facility | California Department of Forestry | HFRA | 7/14/2026 10:42 PDT
| San Joaquin County | Board of Supervisors, County Administration | HFRA | 7/14/2026 10:29 PDT
| San Joaquin County | Clements Fire District | HFRA | 7/14/2026 10:29 PDT
| San Joaquin County | Collegeville Fire District | HFRA | 7/14/2026 10:29 PDT
| San Joaquin County | County Administration | HFRA | 7/14/2026 10:29 PDT
| San Joaquin County | EMS | HFRA | 7/14/2026 10:29 PDT
| San Joaquin County | Farmington Fire District | HFRA | 7/14/2026 10:29 PDT
| San Joaquin County | French Camp/Mountain House Fire District | HFRA | 7/14/2026 10:29 PDT
| San Joaquin County | Liberty Fire District | HFRA | 7/14/2026 10:29 PDT
| San Joaquin County | Linden Peters Fire District | HFRA | 7/14/2026 10:29 PDT
| San Joaquin County | Mokelumne Fire District | HFRA | 7/14/2026 10:29 PDT
| San Joaquin County | Montezuma Fire District | HFRA | 7/14/2026 10:29 PDT
| San Joaquin County | OES, Office of Emergency Services | HFRA | 7/14/2026 10:29 PDT
| San Joaquin County | Sheriff's Office | HFRA | 7/14/2026 10:29 PDT
| San Joaquin County | Thornton Fire District | HFRA | 7/14/2026 10:29 PDT
| San Joaquin County | Waterloo Morada Rural County Fire Protection District | HFRA | 7/14/2026 10:29 PDT
| San Joaquin County | Woodbridge Fire District | HFRA | 7/14/2026 10:29 PDT
| San Joaquin County Communication Facility | AT&T Services Inc | HFRA | 7/14/2026 10:42 PDT
| San Luis Obispo County | CAL FIRE | Tier 2 | 7/14/2026 10:30 PDT
| San Luis Obispo County | CAL FIRE San Luis Obispo County City of Pismo Beach | Tier 2 | 7/14/2026 10:29 PDT
| San Luis Obispo County | CAL FIRE / San Luis Obispo County Fire Department | Tier 2 | 7/14/2026 10:29 PDT
| San Luis Obispo County | Fire Department | Tier 2 | 7/14/2026 10:30 PDT
| San Luis Obispo County | OES, Office of Emergency Services | Tier 2 | 7/14/2026 10:29 PDT
| San Luis Obispo County | Sheriff's Department | Tier 2 | 7/14/2026 10:30 PDT
| San Luis Obispo County CCA | Monterey Bay Community Power | Tier 2 | 7/14/2026 10:29 PDT
| San Luis Obispo County Communication Facility | AT&T Mobility LLC | Tier 2 | 7/14/2026 10:42 PDT
| San Luis Obispo County Communication Facility | AT&T Services Inc | Tier 2 | 7/14/2026 10:42 PDT
| San Luis Obispo County Communication Facility | Charter Communications Holding Company LLC | Tier 2 | 7/14/2026 10:42 PDT
| San Luis Obispo County Communication Facility | T-Mobile West LLC | Tier 2 | 7/14/2026 10:42 PDT
| San Luis Obispo County Communication Facility | Verizon | Tier 2 | 7/14/2026 10:42 PDT
| San Luis Obispo County Water and Waste Water Facility | County of San Luis Obispo | Tier 2 | 7/14/2026 10:42 PDT
| Santa Barbara County | Fire Department | HFRA, Tier 2, Tier 3 | 7/14/2026 10:29 PDT
| Santa Barbara County | OES | HFRA, Tier 2, Tier 3 | 7/14/2026 10:29 PDT
| Santa Barbara County | Sheriff's Office | HFRA, Tier 2, Tier 3 | 7/14/2026 10:29 PDT
| Santa Barbara County CCA | Monterey Bay Community Power | HFRA, Tier 2, Tier 3 | 7/14/2026 10:29 PDT
| Santa Barbara County Communication Facility | Comcast Cable of Santa Maria | Non-HFTD and Non-HFRA; upstream of HFRA but within PSPS scope because downstream of de-energization device. | 7/14/2026 10:42 PDT
| Santa Barbara County Communication Facility | Comcast Cablevision Communications Inc | Non-HFTD and Non-HFRA; upstream of HFRA but within PSPS scope because downstream of de-energization device. | 7/14/2026 10:42 PDT
| Santa Barbara County Communication Facility | Frontier Communication | Tier 2 | 7/14/2026 10:42 PDT
| Santa Barbara County Communication Facility | Frontier Communication S Corporation DIP | Tier 3 | 7/14/2026 10:42 PDT
| Santa Barbara County Solvang | Fire Department | HFRA, Tier 2, Tier 3 | 7/14/2026 10:30 PDT
| Santa Barbara County Solvang | Sheriff's Office | HFRA, Tier 2, Tier 3 | 7/14/2026 10:30 PDT
| Santa Barbara County Water and Waste Water Facility | Central Coast Water Authority | Non-HFTD and Non-HFRA; upstream of HFRA but within PSPS scope because downstream of de-energization device. | 7/14/2026 10:42 PDT

## Appendix D
#VALUE!
Appendix D - Community Resource Centers Provided by PG&E
| # | County | Site Name | Address | Operating Hours (PDT) |  | Total Visitors | Indoor / Outdoor | Amenities Provided | Communities, Time Places, or Potential Circuits Supported
[5 empty] | Day 1 (July 15) | Day 2 (July 16)
| 1 | Marin | Mill Valley Community Center | 180 Camino Alto, Mill Valley CA 94941 | 12:00 - 22:00 | 08:00 - 11:00 | 17 | Outdoor* | WiFi, ADA Restroom, Bottled Water, Device Charging, Snacks, Seating | Time Place 1
| 2 | Monterey | Salinas Valley Fairgrounds | 625 Division Street, King City, CA 93930 | 11:30 - 22:00 | 08:00 - 16:30 | 2299 | Indoor | WiFi, ADA Restroom, Bottled Water, Device Charging, Snacks, Seating, Cooling/Heating, Ice | Time Places 6, 7, 8, 9, 10
| 3 | Monterey | Carmel Valley Community Park / Carmel Valley Community Youth Center | 25 Ford Road, Carmel Valley, CA 93924 | 11:30 - 22:00 | 08:00 - 16:30 | 85 | Outdoor* | WiFi, ADA Restroom, Bottled Water, Device Charging, Snacks, Seating | Time Places 6, 7, 8, 9, 10
| 4 | Monterey | San Antonio Union School | 67550 Lockwood Jolon Road, Lockwood, CA 93932 | 11:30 - 22:00 | 08:00 - 16:30 | 90 | Outdoor* | WiFi, ADA Restroom, Bottled Water, Device Charging, Snacks, Seating | Time Places 6, 7, 8, 9, 10
| 5 | San Luis Obispo | Cuesta College, North County Campus | 2800 Buena Vista Drive, Paso Robles, CA 93446 | 11:30 - 22:00 | 08:00 - 12:00 | 3 | Outdoor* | WiFi, ADA Restroom, Bottled Water, Device Charging, Snacks, Seating | Time Place 10
*Covered tents with air conditioning were provided at all outdoor sites during this PSPS due to high forecasted temperatures throughout the territory.

## Appendix E
#VALUE!
Appendix E - DEFINITIONS
| Term | Unit/Value | Definition
| Access and Functional Needs (AFN) Populations | None | Includes individuals who have developmental or intellectual disabilities, physical disabilities, chronic conditions, injuries, limited English proficiency or who are non-English speaking, older adults, children, people living in institutionalized settings, or those who are low income, homeless, or transportation disadvantaged, including, but not limited to, those who are dependent on public transit or those who are pregnant.
| AFN Characteristics | None | Includes blind/low vision, deaf/hard of hearing, senior, non-English speaking, durable medical equipment, assistive technology, low income, or life support. In accordance with D.21-06-034, PG&E includes customers who have voluntarily indicated they are “dependent on electricity for durable medical equipment or assistive technology” in an effort to identify customers “above and beyond those in the medical baseline population” or self-identified vulnerable population to include persons reliant on electricity to maintain necessary life functions including for durable medical equipment and assistive technology. This includes Assistive Technology, Blind, Disabled, Durable Medical Equipment, Hearing Disability–Deaf or Hard of Hearing, Senior or Vision Disability-Low Vision.
| Benefit to Risk Ratio | Fraction – Max (Threshold, Forecast Factor) | Adverse impact to customers due to a catastrophic fire prevented by PSPS de-energization divided by adverse impact to customers due to PSPS de-energization. No observed value is available for this factor.
| California Alternate Rates for Energy (CARE) | None | A state mandated program. As determined by PU Code Section 739.1(a), annual household must be no greater than 200% of the federal poverty guideline levels.
| Catastrophic Fire Probability Distribution (CFPD) | Scaled Probability – Max (Threshold, Forecast, Observed Factor) | The probability of fire ignitions due to weather impacting the Distribution electric system combined with the probability that a fire will be catastrophic if it starts. In Appendix A-1.1, this is the product of catastrophic fire (Prob Cat) and Ignition Probability Weather (IPW) minus probability of ignition (Prob Ignition). Scaled by 1000 to convert to an integer value.
| Catastrophic Fire Probability Transmission (CFPT) | Scaled Probability – Max (Threshold, Forecast and Observed Factor) | In Appendix A-2.1, this is the product of probability of catastrophic fire (Prob Cat) and Operability Assessment Probability of Failure. This product is called the (CFPT) Catastrophic Fire Probability Transmission model. Scaled by 1000 to convert to an integer value.
| Critical Facilities and Infrastructure (CFI) | None | “Critical Facilities” and “Critical Infrastructure” refer to facilities and infrastructure that are essential to public safety and require additional assistance and advance planning to ensure resiliency during de-energization. The CPUC adopted the following interim list of CFI, as aligned with Department of Homeland Security’s Critical Infrastructure Sectors: • Emergency Services Sector: Police Stations, Fire Stations, Emergency Operations Centers • Government Facilities Sector: Schools, Jails and Prisons • Healthcare and Public Health Sector: Public Health Departments, Medical facilities, including hospitals, skilled nursing facilities, nursing homes, blood banks, health care facilities, dialysis centers and hospice facilities • Energy Sector: Public and private utility facilities vital to maintaining or restoring normal service, including, but not limited to, interconnected publicly owned utilities and electric cooperatives • Water and Wastewater Systems Sector: Facilities associated with the provision of drinking water or processing of wastewater including facilities used to pump, divert, transport, store, treat and deliver water or wastewater • Communications Sector: Communication carrier infrastructure including selective routers, central offices, head ends, cellular switches, remote terminals and cellular sites • Chemical Sector: Facilities associated with the provision of manufacturing, maintaining, or distributing hazardous materials and chemicals • Note: Some customers meet the criteria of being both a Public Safety Partner & Critical Facility, which include Emergency services sector, water and wastewater providers, communication service providers and emergency hospitals.
| Customer or Customer Accounts | None | Active service points or meter.
| Dead Fuel Moisture Content (DFM) 10hr | Fuel Moisture Fraction – Min (Threshold, Forecast, Observed Factor) | The amount of moisture in dead vegetation (i.e. fallen leaves, tree branches, and logs). In Appendix A-1.1, “DFM 10hr” is Dead Fuel Moisture provided in 10-hour fuel moisture class. Can be scaled to percentage by multiplying by 100.
| Dead Fuel Moisture Content (DFM) 100hr | Fuel Moisture Fraction – Min (Threshold, Forecast Factor) | The amount of moisture in dead vegetation (i.e. fallen leaves, tree branches, and logs). In Appendix A-1.1, “DFM 100hr” is Dead Fuel Moisture provided in 100-hour moisture class. Can be scaled to percentage by multiplying by 100. No observed value is available for this factor.
| Emergency Operations Center (EOC) | None | A central command and control facility responsible for carrying out the principles of emergency preparedness and emergency management, or disaster management functions at a strategic level during an emergency and ensuring the continuity of operation of a company.
| EV charging station levels | None | • Level 1 Charging: 120-Volt; Connectors Used: J1772, NACS/J3400; Charging Speed: 3 to 5 Miles Per Hour • Level 2 Charging: 208-Volt to 240-Volt; Connectors Used: J1772, NACS/J3400; Charging Speed: 12 to 80 Miles Per Hour • Level 3 Charging: 400-Volt to 900-Volt (DC Fast Charge & Supercharging); Connectors Used: Combined Charging System (Combo), CHAdeMO & NACS/J3400; Charging Speed: 3 to 20 Miles Per Minute
| Family Electric Rate Assistance Program (FERA) | None | CPUC established program for households of any size with incomes between 200% and 250% of federal poverty guidelines. (PU Code Section 739.12)
| Fire Index Area (FIA) | None | Boundaries originally designated by the California Department of Forestry and Fire Protection and United States Forest Service for the purpose of establishing a fire-danger rating for that area based on local conditions. There are 109 rating areas in PG&E’s service area.
| Fire Index Rating | None | A rating used by fire agencies to determine the risk of fire and its likely behavior. Its calculation considers fuel moisture, humidity, wind speed, air temperature, and historical fire occurrence. These ratings are as follows: • R1: Very little or no fire danger • R2: Moderate fire danger • R3: When fire danger is so high that care must be taken using fire-starting equipment. Local conditions may limit the use of machinery and equipment to certain hours of the day • R4: Fire danger is critical. The use of equipment and open flames are limited to specific areas and times • R5: Fire danger is so critical that the use of equipment and open flames are not allowed at any time • R5-Plus: Fire danger is at R5 "plus" high risk weather trigger of strong wind
| First/Emergency Responders | None | Individuals who, in the early stages of an incident, are responsible for the protection and preservation of life, property, evidence, and the environment, including emergency response providers. The term “emergency response providers” includes federal, state, and local governmental and nongovernmental public safety, fire, law enforcement, emergency response, emergency medical services providers (including hospital emergency facilities), and related personnel, agencies and authorities.
| Flame Length ft 8hr | Feet – Max (Threshold, Forecast Factor) | Flame length in feet on fire front for first eight hours of fire spread simulation from Technosylva. No observed value is available for this factor.
| Full-Scale Exercise (FSE) | None | A complex, resource-intensive operations-based exercise often involving multiple agencies, jurisdictions/organizations, and real-time movement of resources.
| Functional Exercise (FE) | None | An operations-based exercise designed to test and evaluate capabilities and functions in a realistic, real-time environment. Movement of resources is usually simulated.
| Geographic Area Coordination Center (GACC) | Yes/No During PSPS (Qualitative Factor) | High fire risk issued by the Federal North or South Operations Predictive Services.
| Hazard Awareness and Center (HAWC) | None | The operations center that monitors for wildfires. HAWC leadership communicates and informs other PG&E Business Units and Executive Leadership about threats from wildfires in the service area.
| High Fire Risk Area (HFRA) | None | Area where risk factors for the potential of catastrophic fire from utility infrastructure ignition during offshore wind events is higher than others. HFRA boundaries were developed based on the CPUC’s HFTD boundaries.
| High Fire Threat Districts (HFTDs) | None | Per D.17-01-009, areas of the State designated by the CPUC and California Department of Forestry & Fire Protection (CAL FIRE) to have elevated wildfire risk, indicating where utilities must take additional action (per GO 95, GO 165, and GO 166) to mitigate wildfire risk. The districts have three levels: • Zone 1: High Hazard Zones on the U.S. Forest Service-California Department of Forestry and CAL FIRE joint map of Tree Mortality High Hazard Zones • Tier 2: Elevated risk for utility-associated wildfires • Tier 3: Extreme risk for utility-associated wildfires
| High Impact Critical Customers | None | Non-residential customers that may present a significant community impact in the event they experience a sustained outage but do not meet the CPUC criteria for a Critical Facility Customer.
| High Priority Vegetation Tag | None | “Priority 1” and “Priority 2” vegetation tags are created when trained vegetation inspectors identify trees or limbs that currently present elevated risk and must be worked on an expedited basis. Inspectors use Priority 1 tags for vegetation (i) in contact or showing signs of previous contact with a primary conductor; (ii) actively failing or at immediate risk of failing and which could strike PG&E’s facilities; or (iii) presenting an immediate risk to PG&E’s facilities. Inspectors use Priority 2 tags for vegetation that does not rise to the level of Priority 1 but has encroached within the PG&E minimum clearance requirements or has an identifiable potential safety issue requiring expedited work.
| High Wind Advisory | Yes/No During PSPS (Qualitative Factor) | Advisory of high winds issued by the Federal National Weather Service.
| High Wind Warning (HWW) | Yes/No During PSPS (Qualitative Factor) | Warning of high winds issued by the Federal National Weather Service.
| Life Support | None | Customers that require critical life support equipment in their home.
| Medical Baseline (MBL) Program | None | This program assists residential customers who rely on power for certain medical needs, as certified by a licensed medical practitioner. Eligible customers receive an extra monthly allotment of energy or discount, depending on their current rate plan. The program also includes additional notifications in advance of a PSPS.
| Monitoring Stage | None | The seven days ahead of a weather event when weather patterns are being monitored. Utility provides seven-day proactive de-energization potential rolling forecast or implements an escalating notification system similar to the National Weather Service’s “weather watch” and “weather warning” system on its public website.
| National Oceanic and Atmospheric Administration (NOAA) | Yes/No During PSPS (Qualitative Factor) | Fire weather forecast issued by NOAA (SPC).
| Officer-in-Charge (OIC) | None | A position specific to PSPS to engage higher-level management accountability in the decision to de-energize and restore power while also enabling rapid decision-making during real-time. The OIC approves all PSPS Decision Records and associated documentation following a PSPS.
| Open PSPS Tags | Yes/No During PSPS (Qualitative Factor) | PSPS-Qualified Tags include P1 (tree represents an immediate risk) and P2 (tree is damaged or diseased and could fall into nearby power lines) tree tags and Electric Corrective tags (Priority A - emergency, B - urgent, and E/F - risk-based).
| Page View | None | The number of times a web page was viewed by individual users.
| Patrol Inspection | None | In accordance with GO 165, a visual inspection of applicable utility equipment and structures that is designed to identify obvious structural problems and hazards. Patrol inspections may be carried out during other company business.
| Prob Cat | Probability Outputs – Max (Threshold, Forecast, Observed Factor) | Fire Potential Index (FPI) Model Output minus Probability of a catastrophic fire if an ignition were to occur. FPI component of the CFPD model.
| PSPS Mitigation | None | The efforts taken to avoid de-energization including backup generation, backup storage, distribution microgrid, islanding, patrols, sectionalization, switching, temporary substation microgrid, Transmission switching and vegetation management (expedite priority trees that prevent circuit from being removed from scope).
| Public Safety Partner | None | First/emergency response providers at the federal, state and local levels including, water, wastewater and communication service providers, affected community choice aggregators, publicly owned utilities/electrical cooperatives, the CPUC, the California Governor’s Office of Emergency Services (OES) and the California Department of Forestry and Fire Protection. The term “emergency response providers” includes federal, state, and local governmental and nongovernmental public safety, fire, law enforcement, emergency response, emergency medical services providers (including hospital emergency facilities), and related personnel, agencies and authorities.
| Rate of Spread Chhr 8hr | Chains/Hour – Max (Threshold, Forecast Factor) | Rate of fire spread in chains per hour for first eight hours of fire spread simulation from Technosylva. No observed value is available for this factor.
| Red Flag Warning (RFW) | Yes/No During PSPS (Qualitative Factor) | Red Flag Warning from the Federal National Weather Service.
| Relative Humidity (RH) | Percentage – Min (Threshold, Forecast, Observed Factor) | Relative Humidity in percent at two meters above ground level. For observed values, this is the minimum relative humidity recorded by all weather stations mapped to each circuit from planned de-energization time to anticipated All-Clear time.
| Self-Identified Vulnerable (SIV) | None | Customers who have indicated they are “dependent on electricity for durable medical equipment or assistive technology” as well as customers that are not enrolled or qualify for the MBL Program and “certify that they have a serious illness or condition that could become life threatening if service is disconnected.” In accordance with D.21-06-034, PG&E includes customers who have indicated they are “dependent on electricity for durable medical equipment or assistive technology” in an effort to identify customers “above and beyond those in the medical baseline population” to include persons reliant on electricity to maintain necessary life functions including for durable medical equipment and assistive technology. This designation remains on their account for one year, at which a customer can recertify their SIV Status.
| Site Visit | None | A continuous session that begins when a user arrives on a site and ends after either 30 minutes of inactivity or 12 hours of continuous activity.
| SIV Program | None | A PG&E program inclusive of customers who have indicated they are “dependent on electricity for durable medical equipment or assistive technology” as well as customers that are not enrolled or qualify for the MBL Program and “certify that they have a serious illness or condition that could become life threatening if service is disconnected.” In accordance with D.21-06-034, PG&E includes customers who have indicated they are “dependent on electricity for durable medical equipment or assistive technology” in an effort to identify customers “above and beyond those in the medical baseline population” to include persons reliant on electricity to maintain necessary life functions including for durable medical equipment and assistive technology. This designation remains on their account for one year, at which a customer can recertify their SIV Status.
| Sustained Wind | None | The average observed wind speed value over a two-minute period.
| Tabletop Exercise (TTX) | None | A discussion-based exercise in response to a scenario, intended to generate a dialogue of various issues to facilitate a conceptual understanding, identify strengths and areas for improvement, and/or achieve changes in perceptions about plans, policies, or procedures.
| Time Place (TP) | None | A portion of the PG&E grid that is electrically and geographically coherent and is forecast to experience consistent timing for severe fire weather. TPs are identified for each PSPS and receive consistent treatment for notifications and de-energization. Once actual weather conditions occur, Weather “All-Clear” and service restoration times may vary due to actual weather conditions across various TPs as well as within a TP.
| Transmission (Tx) Impacts | Yes/No During PSPS (Qualitative Factor) | Distribution lines that would have been de-energized due to de-energization of upstream Transmission lines, regardless of whether those Distribution lines would have also been de-energized due to direct Distribution PSPS.
| Vulnerable Populations | None | Individuals who have physical, developmental, intellectual disabilities; chronic conditions or injuries, are limited English proficient or non-English speaking; older adults, children, people living in institutionalized settings, low-income, homeless and/or transportation-disadvantaged (i.e., dependent on public transit) and pregnant women. This term is also used interchangeable with AFN.
| Weather “All-Clear” | None | When severe weather has passed, the OIC gives approval to start patrols and restoration for all impacted areas at once or for specific areas.
| Wind Gust | None | A rapid fluctuation of wind speed with variations of ten knots or more between peaks and lulls, typically, determined by averaging observed values over a three-second period.
| WS MPH | MPH – Max (Threshold, Forecast, Observed Factor) | Sustained windspeed in miles per hour at 10 meters above ground level. The observed values show the maximum sustained wind speed recorded by weather stations mapped to each circuit from planned de-energization time to anticipated All-Clear time.