## Table 1
Table 1: Customers Notified and De-energized
Total Customers |  |  | Medical Baseline (MBL) Customers | Number of Counties | Number of Tribes | Number of Circuits |  |  | Damage / Hazard Count | Critical Facilities and Infrastructure De-energized
Notified | De-energized | Cancelled | De-energized | De-energized | De-energized | Transmission De-energized | Unique Distribution Circuits in Any Version of Scope | Distribution Circuits De-energized
8444 1 | 3928 2 | 4527 | 324 | 7 | 2 | 3 3 | 31 | 18 | 1 damage 0 Hazards | 135
1 Of the 8,444 customers notified in scope, 6 customers were notified but were not de-energized. See Table 9 for details.
2 Of the 3,928 customers de-energized, 16 did not receive notifications as their contact information was not available. Further explanation is provided in Table 9.
3 Of the 3 transmission lines de-energized, 1 circuit is considered a foreign line and was de-energized by the customer.

## Table 2
Table 2: 2022 PSPS Risk-Benefit Consequence Modeling Considerations
Consequence Type | Wildfire Consequence Considerations | PSPS Consequence Considerations
Safety | Calculated based on maximum population impacts derived from Technosylva wildfire simulation models and a fatality ratio based on National Fire Protection Association (NFPA) data. | Calculated from an estimate of Equivalent Fatalities (EF) per Million Customer Minutes Interrupted (MMCI). The EF/MMCI ratio is estimated from previous PG&E PSPS events and other large external outage events.1
Reliability | N/A | Calculated directly from the potential number of customers impacted and outage duration based on customer minutes interrupted.
Financial | Calculated based on maximum building impacts derived from Technosylva wildfire simulation models and a cost per structure burned previously evaluated in 2020 RAMP Report.2 | Calculated based on two financial estimates 1) distribution of a lump sum cost of execution across all relevant circuits and 2) an estimated proxy cost per customer in scope per PSPS event.3
1 Previous PG&E PSPS events include 2019-2021 events, and other large external outage events include the 2003 Northeast Blackout in New York City, 2011 Southwest Blackout in San Diego, 2012 Derecho Windstorms, 2012 Superstorm Sandy, 2017 Hurricane Irma, 2021 Blackout event.
2 See A.20-06-012.
3 The assumptions used in these calculations, including the proxy cost per customer per PSPS event, are subject to be updated and are not intended to prejudge or create precedent with regard to the development of more precise values of resiliency or cost of PSPS metrics being considered in other ongoing proceedings at the California Public Utilities Commission, such as the Risk-Based Decision-Making Rulemaking [R.20.07.013] and the Microgrid and Resiliency Strategies.

## Table 3
Table 3: Impact Analysis during August 30-31, 2023 PSPS Event
Impact Analysis
Size (ac) | 4696.23
Initial Attack Assessment | 3-High
No. of Buildings | 86
Total Population | 65
No. Places | 4

## Table 4
Table 4: Notification Descriptions
Type of Notification | Recipients | Description
PRIORITY NOTIFICATION: 48-72 hours in advance of anticipated de-energization | Public Safety Partners1, Community Based Organizations2, transmission level customers | On August 27, 2023, PG&E’s Meteorology Team noted a potential PSPS and updated the weather forecast on pge.com/weather to “elevated” in certain parts of the service area. At this time, local PG&E representatives called each County OES in PG&E’s electrical service area and select Tribes and cities to inform them that PG&E is monitoring an increased potential of PSPS outages. Following PG&E’s activation of its EOC, the following was completed: •PG&E submitted a PSPS State Notification Form to Cal OES and sent an e-mail to the CPUC notifying them that PG&E’s EOC has been activated and that PG&E is monitoring for potential PSPS outages. •PG&E sent notifications to other Public Safety Partners3 via call, text and e-mail; these notifications included the following information: o Estimated window of the de-energization time. o When weather is anticipated to pass. o Estimated Time of Restoration (ETOR). o For Public Safety Partners only: Links to the PSPS Portal where event-specific maps and information are available.
WATCH NOTIFICATION: 24-48 hours in advance of anticipated de-energization | Public Safety Partners, Community Based Organizations, All Customers (including MBL program customers and SIV customers), and transmission level customers | During this time, the following was completed: • PG&E submitted a PSPS State Notification Form to Cal OES and sent an e-mail to the CPUC notifying them of a scope change. • PG&E sent notifications to other Public Safety Partners, transmission level customers, and all customers via call, text message and e-mail; these notifications included the following information: o Estimated window of the de-energization time. o When the adverse weather is anticipated to pass. o Estimated Time of Restoration (ETOR). o For Public Safety Partners only: Links to the PSPS Portal where event-specific maps and information are available. o For Customers only: Potentially impacted addresses, links to PSPS Updates webpage with Community Resource Center information, and resources for customers with access and functional needs, including but not limited to information on the MBL program, Meals on Wheels, language support, and the Portable Battery Program. o For transmission-level customers only: Transmission Substation Name and Line name serving substation. • PG&E sent notifications via call, text and e-mail to MBL program customers, including tenants of master metered accounts, and SIV customers every hour until the customer confirmed receipt of the notification. • PG&E also attempted to send Cancellation Notifications to Public Safety Partners and customers within two hours of being removed from scope; this was to inform them that power would not be shut off. Customer notifications were provided in English, with information on how to receive event information in 15 non-English languages, referred to herein as “translated languages”4. Customers with their language preference selected in their PG&E accounts received in-language (translated) notifications. Public Safety Partner notifications were provided in English.
WARNING NOTIFICATION: 1-4 hours in advance of anticipated de-energization, if possible | Public Safety Partners, Community Based Organizations All Customers (including MBL program customers, SIV customers), and transmission level customers | When forecasted weather conditions showed that a safety shutoff was approved to move forward, and power would be de-energized in approximately 1-4 hours, the following was completed: • PG&E submitted a PSPS State Notification Form to Cal OES and sent an e-mail to the CPUC notifying them that PG&E has made the decision to de-energize. • PG&E sent notifications via call, text and e-mail to other Public Safety Partners, transmission level customers, and customers; these notifications included the same the following information: o Estimated window of the de-energization time. o When the adverse weather is anticipated to pass. o Estimated Time of Restoration (ETOR). o For Public Safety Partners only: Links to the PSPS Portal where event-specific maps and information are available. o For Customers only: Potentially impacted addresses, links to PSPS Updates webpage with Community Resource Center information, and resources for customers with access and functional needs, including but not limited to information on the MBL program, Meals on Wheels, language support, and the Portable Battery Program. o For transmission-level customers only: Transmission Substation Name and Line name serving substation. • PG&E sent notifications via call, text and e-mail to MBL program customers, including tenants of master metered accounts, and SIV customers every hour until the customer confirmed receipt of the notification. • PG&E also attempted to send Cancellation Notifications to Public Safety Partners and customers within two hours of being removed from scope; this was to inform them that power would not be shut off. Customer notifications were provided in English, with information on how to get event information in translated languages. Customers with their language preference selected in their PG&E accounts received in-language (translated) notifications. Public Safety Partner notifications were provided in English.
POWER OFF NOTIFICATION: When de-energization is initiated | Public Safety Partners, All Customers (including MBL program customers and SIV customers) and transmission level customers | When shut off was initiated, the following was completed: • PG&E submitted a PSPS State Notification Form to Cal OES and sent an e-mail to the CPUC to notify them that de-energization has been initiated. • Agency Representatives of PG&E conducted a live call and/or sent an e-mail, as appropriate, to County OES that were within the potential PSPS scope area and select Tribes and cities to inform them that customers within their jurisdiction were beginning to be de-energized. • PG&E Grid Control Center (GCC) conducted live agent calls to impacted transmission level customers. • PG&E sent notification to other Public Safety Partners, transmission level customers, and customers via call, text messages, and e-mail, which included: o Impacted addresses (for customers only). o De-energization time. o When the adverse weather is anticipated to pass. o For Customers Only: Links to the PSPS Updates webpage with Community Resource Center information, and resources for customers with access and functional needs, including but not limited to information on the MBL program, Meals on Wheels, language support, and the Portable Battery Program. Customer notifications were provided in English, with information on how to receive event information in translated languages. Customers with their language preference selected in their PG&E accounts received in-language (translated) notifications. Public Safety Partner notifications were provided in English.
WEATHER “ALL-CLEAR”/ETOR UPDATE NOTIFICATION: Immediately before re-energization begins | Public Safety Partners, All Customers (including MBL program customers and SIV customers) and transmission level customers | After the weather passed and the area is deemed safe to begin patrols and restoration, PG&E completed the following: • Submitted a PSPS State Notification Form to Cal OES and sent an e-mail to the CPUC notifying them that PG&E is initiating re-energization patrols. • Sent notifications to other Public Safety Partners, transmission level customers5 and customers via call, text message and e-mail; these notifications included the ETOR. • Sent “event update” notifications via call, text and e-mail to customers if their ETOR changed; two ways that an ETOR may change include: o New field or meteorology conditions. o Damage was found during patrols and repair is needed. Customer notifications were provided in English, with information on how to receive event information in translated languages. Customers with their language preference selected in their PG&E accounts received in-language (translated) notifications. Public Safety Partner notifications were provided in English.
RESTORATION NOTIFICATION: When re-energization is complete | Public Safety Partners, Community Based Organizations, All Customers (including MBL program customers and SIV customers), and transmission level customers | PG&E Grid Control Center (GCC) conducted live agent calls to notify impacted transmission level customers of restoration. Once customers, including MBL program customers and SIV customers, were restored, they received notifications via call, text and e-mail. This was done using an automated process that issued customer notifications every 15 minutes upon restoration of service. Customer notifications were provided in English, with information on how to receive event information in translated languages. Customers with their language preference selected in their PG&E accounts received in-language (translated) notifications. Once all customers were restored, PG&E submitted the final PSPS State Notification Form to Cal OES, sent an e-mail to the CPUC confirming restoration of PSPS outages and reclassification of customers if applicable, and sent a notification to Public Safety Partners via call, text and e-mail. Public Safety Partner notifications were provided in English.
1 Transmission level customers were not notified during the 48-72 hour notification timeframe as they were not in scope. PG&E executed Priority Notifications for transmission level customers as soon as they were brought into scope.
2 Phase 3 D.21-06-034, Appendix A, page A9, Section G. Medical Baseline and Access and Functional Needs (AFN) Communities, No. 4, Each electric investor-owned utility must provide proactive notification and impacted zip code information to paratransit agencies that may serve all the known transit- or paratransit-dependent persons that may need access to a community resource center during a proactive de-energization event.
3 Other Public Safety Partners refers to first/emergency responders at the local, state, and federal level, water, wastewater, and communication service providers, affected community choice aggregators, publicly-owned utilities/electrical cooperatives, the CPUC, the California Governor’s Office of Emergency Services, and the California Department of Forestry and Fire Protection.
4 Translated languages refers to Spanish, Chinese (Mandarin and Cantonese), Vietnamese, Tagalog, Korean, Russian, Arabic, Punjabi, Farsi, Japanese, Khmer, Hmong, Thai, Hindi, and Portuguese. A language is prevalent if it is spoken by 1,000 or more persons in the utility’s territory or if it’s spoken by 5 percent or more of the population within a “public safety answering point” in the utility territory (D.20-03-004). Details on the community outreach efforts for PSPS and wildfire-related outreach including efforts to reach all languages prevalent in PG&E’s service area can be found in PG&E’s Notification Plan, include in our 2023 PSPS Pre-Season Report.
5 Transmission lines serving impacted Transmission-level Customers and Municipal Utilities may cut across multiple Fire Index Areas (FIAs) and will only be notified when all those FIAs that the line cuts across have been given the All-Clear.

## Table 5
Table 5: Customer Notification Timeline Summary Prior to De-energization for October 22-24, 2022 Weather Event
Event Order | Minimum Timeline1 | Notification Sent to: | Approximate Time Sent (PDT) | Message | Notes | Who made the Notification
Prior to De-energization | 72-48 hours | Tribal/Local Governments and CCAs* | 8/27/2023 9:33:00 PM | Priority |  | PG&E
|  | Public Safety Partners** | 8/27/2023 8:34:00 PM | Priority |  | PG&E
| 48-24 hours | Tribal/Local Governments and CCAs* | 8/28/2023 3:16:00 PM | Watch |  | PG&E
|  | Public Safety Partners** | 8/28/2023 3:22:00 PM | Watch |  | PG&E
|  | All Customers*** | 8/28/2023 3:20:00 PM | Watch |  | PG&E
| 24-12 hours2 | Tribal/Local Governments and CCAs* | 8/29/2023 11:32:00 AM | Watch |  | PG&E
|  | Public Safety Partners** | 8/29/2023 11:35:00 AM | Watch |  | PG&E
|  | All Customers*** | 8/29/2023 11:31:00 AM | Watch |  | PG&E
| 4-1 hours | Tribal/Local Governments and CCAs* | 8/29/2023 11:15:00 PM | Warning |  | PG&E
|  | Tribal/Local Governments and CCAs* | 8/29/2023 10:30:00 PM | Warning |  | PG&E
|  | Tribal/Local Governments and CCAs* | 8/30/2023 12:11:00 AM | Warning |  | PG&E
|  | Tribal/Local Governments and CCAs* | 8/30/2023 1:40:00 AM | Warning |  | PG&E
|  | Public Safety Partners** | 8/29/2023 10:53:00 PM | Warning |  | PG&E
|  | Public Safety Partners** | 8/29/2023 11:34:00 PM | Warning |  | PG&E
|  | Public Safety Partners** | 8/30/2023 12:24:00 AM | Warning |  | PG&E
|  | Public Safety Partners** | 8/30/2023 1:52:00 AM | Warning |  | PG&E
|  | All Customers*** | 8/29/2023 10:48:00 PM | Warning |  | PG&E
|  | All Customers*** | 8/29/2023 11:40:00 PM | Warning |  | PG&E
|  | All Customers*** | 8/30/2023 12:20:00 AM | Warning |  | PG&E
|  | All Customers*** | 8/30/2023 1:51:00 AM | Warning |  | PG&E
Initiation (During) | When de-energization is initiated (Powe off) | Public Safety Partners** | 8/30/2023 6:45:00 AM | Power Off |  | PG&E
|  | Public Safety Partners** | 8/30/2023 8:32:00 AM | Power Off |  | PG&E
|  | Public Safety Partners** | 8/30/2023 8:37:00 AM | Power Off |  | PG&E
|  | Public Safety Partners** | 8/30/2023 8:38:00 AM | Power Off |  | PG&E
|  | Public Safety Partners** | 8/30/2023 8:40:00 AM | Power Off |  | PG&E
|  | Public Safety Partners** | 8/30/2023 8:41:00 AM | Power Off |  | PG&E
|  | Public Safety Partners** | 8/30/2023 9:23:00 AM | Power Off |  | PG&E
|  | All Customers*** | 8/30/2023 6:45:00 AM | Power Off |  | PG&E
|  | All Customers*** | 8/30/2023 8:32:00 AM | Power Off |  | PG&E
|  | All Customers*** | 8/30/2023 8:37:00 AM | Power Off |  | PG&E
|  | All Customers*** | 8/30/2023 8:38:00 AM | Power Off |  | PG&E
|  | All Customers*** | 8/30/2023 8:40:00 AM | Power Off |  | PG&E
|  | All Customers*** | 8/30/2023 8:41:00 AM | Power Off |  | PG&E
|  | All Customers*** | 8/30/2023 9:23:00 AM | Power Off |  | PG&E
| Immediately before re-energization (All-Clear/ETOR) | Tribal/Local Governments and CCAs* | 8/30/2023 8:01:00 PM | Inspecting/Weather All-Clear |  | PG&E
|  | Public Safety Partners** | 8/30/2023 4:19:00 PM | Inspecting/Weather All-Clear |  | PG&E
|  | Public Safety Partners** | 8/30/2023 4:33:00 PM | Inspecting/Weather All-Clear |  | PG&E
|  | Public Safety Partners** | 8/30/2023 4:48:00 PM | Inspecting/Weather All-Clear |  | PG&E
|  | All Customers*** | 8/30/2023 4:19:00 PM | Inspecting/Weather All-Clear |  | PG&E
|  | All Customers*** | 8/30/2023 4:33:00 PM | Inspecting/Weather All-Clear |  | PG&E
|  | All Customers*** | 8/30/2023 4:48:00 PM | Inspecting/Weather All-Clear |  | PG&E
|  | Public Safety Partners** | 8/30/2023 10:45:00 AM | ETOR Update |  | PG&E
|  | Public Safety Partners** | 8/30/2023 11:45:00 AM | ETOR Update |  | PG&E
|  | Public Safety Partners** | 8/30/2023 5:14:00 PM | ETOR Update |  | PG&E
|  | Public Safety Partners** | 8/30/2023 5:30:00 PM | ETOR Update |  | PG&E
|  | Public Safety Partners** | 8/30/2023 5:44:00 PM | ETOR Update |  | PG&E
|  | Public Safety Partners** | 8/30/2023 6:00:00 PM | ETOR Update |  | PG&E
|  | Public Safety Partners** | 8/30/2023 6:15:00 PM | ETOR Update |  | PG&E
|  | Public Safety Partners** | 8/30/2023 6:29:00 PM | ETOR Update |  | PG&E
|  | Public Safety Partners** | 8/30/2023 6:51:00 PM | ETOR Update |  | PG&E
|  | Public Safety Partners** | 8/30/2023 7:03:00 PM | ETOR Update |  | PG&E
|  | Public Safety Partners** | 8/30/2023 7:17:00 PM | ETOR Update |  | PG&E
|  | Public Safety Partners** | 8/30/2023 7:31:00 PM | ETOR Update |  | PG&E
|  | Public Safety Partners** | 8/30/2023 7:44:00 PM | ETOR Update |  | PG&E
|  | Public Safety Partners** | 8/31/2023 8:01:00 AM | ETOR Update |  | PG&E
|  | Public Safety Partners** | 8/31/2023 9:00:00 AM | ETOR Update |  | PG&E
|  | Public Safety Partners** | 8/31/2023 9:59:00 AM | ETOR Update |  | PG&E
|  | All Customers*** | 8/30/2023 10:45:00 AM | ETOR Update |  | PG&E
|  | All Customers*** | 8/30/2023 11:45:00 AM | ETOR Update |  | PG&E
|  | All Customers*** | 8/30/2023 5:14:00 PM | ETOR Update |  | PG&E
|  | All Customers*** | 8/30/2023 5:30:00 PM | ETOR Update |  | PG&E
|  | All Customers*** | 8/30/2023 5:44:00 PM | ETOR Update |  | PG&E
|  | All Customers*** | 8/30/2023 6:00:00 PM | ETOR Update |  | PG&E
|  | All Customers*** | 8/30/2023 6:15:00 PM | ETOR Update |  | PG&E
|  | All Customers*** | 8/30/2023 6:29:00 PM | ETOR Update |  | PG&E
|  | All Customers*** | 8/30/2023 6:51:00 PM | ETOR Update |  | PG&E
|  | All Customers*** | 8/30/2023 7:03:00 PM | ETOR Update |  | PG&E
|  | All Customers*** | 8/30/2023 7:17:00 PM | ETOR Update |  | PG&E
|  | All Customers*** | 8/30/2023 7:31:00 PM | ETOR Update |  | PG&E
|  | All Customers*** | 8/30/2023 7:44:00 PM | ETOR Update |  | PG&E
|  | All Customers*** | 8/31/2023 8:01:00 AM | ETOR Update |  | PG&E
|  | All Customers*** | 8/31/2023 9:00:00 AM | ETOR Update |  | PG&E
|  | All Customers*** | 8/31/2023 9:59:00 AM | ETOR Update |  | PG&E
Restoration (After) | After re-energization was completed (Restoration) | Tribal/Local Governments and CCAs* | 8/30/2023 9:35:00 PM | Restore |  | PG&E
|  | Tribal/Local Governments and CCAs* | 8/30/2023 9:42:00 PM | Restore |  | PG&E
|  | Tribal/Local Governments and CCAs* | 8/30/2023 9:47:00 PM | Restore |  | PG&E
|  | Tribal/Local Governments and CCAs* | 8/30/2023 9:50:00 PM | Restore |  | PG&E
|  | Tribal/Local Governments and CCAs* | 8/30/2023 9:51:00 PM | Restore |  | PG&E
|  | Tribal/Local Governments and CCAs* | 8/31/2023 11:50:00 AM | Restore |  | PG&E
|  | Tribal/Local Governments and CCAs* | 8/31/2023 12:45:00 PM | Restore |  | PG&E
|  | Public Safety Partners** | 8/30/2023 5:17:00 PM | Restore | First initial Restoration Notification sent. | PG&E
|  | Public Safety Partners** | 8/31/2023 12:02:00 PM | Restore | Last Restoration Notification sent. | PG&E
|  | All Customers*** | 8/30/2023 5:17:00 PM | Restore | First initial Restoration Notification sent. | PG&E
|  | All Customers*** | 8/31/2023 12:02:00 PM | Restore | Last Restoration Notification sent. | PG&E
Cancellation | Cancellation within 2-hours of decision to cancel**** | Public Safety Partners* | 8/30/2023 1:45:00 PM | Cancel | Completed via PSS Agency Representative 50 or less customer impact live call | PG&E
|  | Public Safety Partners** | 8/29/2023 8:30:00 PM | Cancel | Only Public Safety Partners removed from scope received the cancel notification. The Decision to descope these customers was 08/29/2023 19:44 | PG&E
|  | Public Safety Partners** | 8/30/2023 1:35:00 PM | Cancel | Only Public Safety Partners removed from scope received the cancel notification. The Decision to descope these customers was 08/30/2023 13:10 | PG&E
|  | All Customers*** | 8/29/2023 8:30:00 PM | Cancel | Only Customers removed from scope received the cancel notification. The Decision to descope these customers was 08/29/2023 19:44 | PG&E
|  | All Customers*** | 8/30/2023 1:35:00 PM | Cancel | Only Customers removed from scope received the cancel notification. The Decision to descope these customers was 08/30/2023 13:10 | PG&E
1 D.19-05-042, Appendix A, Timing of Notification.
2 While not a CPUC requirement, PG&E provides an additional 24-12 hour notification to Tribal/Local Governments, Public Safety Partners and Customers.
*A subset of Public Safety Partners, including Tribes, cities, counties, and community choice aggregators
**A subset of Public Safety Partners, including water, wastewater, and communication service providers
***All Customers, including MBL program customers and SIV customers
**** For Cancellation sent 2 hours after the decision to cancel, see Table 9

## Table 6
Table 6: Notifications to Customers where Positive or Affirmative Notification was Attempted1
Designation | Total Number of customers2 | Notification Attempts Made | Timing of Attempts3 | Who made the Notification Attempt | Successful Positive Notification4
MBL5 | 803 | 803 Watch Notifications | 8/28/2023 3:20 PM PDT | PG&E | 775 Watch Notifications
|  | 794 Warning Notifications6 | 8/29/2023 7:47 AM PDT |  | 533 Warning Notifications
|  | 1,597 Overall Notifications | 8/28/2023 3:20 PM PDT |  | 1,308 Overall Notifications
MBL behind a master meter7 | 1 | 1 Watch Notifications | 8/28/2023 3:21 PM PDT | PG&E | 1 Watch Notifications
|  | 1 Warning Notifications | 8/30/2023 12:22 AM PDT |  | 0 Warning Notifications
|  | 2 Overall Notifications | 8/28/2023 3:21 PM PDT |  | 1 Overall Notifications
SIV | 205 | 204 Watch Notifications | 8/28/2023 03:20 PM PDT | PG&E | 188 Watch Notifications
|  | 205 Warning Notifications | 8/29/2023 07:57 AM PDT |  | 127 Warning Notifications
|  | 409 Overall Notifications | 8/28/2023 03:20 PM PDT |  | 315 Overall Notifications
1 Counts of “Notification Attempts Made” will not reflect the actual total of customers notified as both MBL and SIV customers can appear in both subset groups.
2 Total number of customers notified where notification was attempted. Count includes customers that may have been removed from scope or received Cancellation Notifications prior to de-energization, but still received Watch and/or Warning notifications.
3 Initial start time notification was sent.
4 PG&E considers successful positive notifications as those in which the notification was successfully delivered to the customer (i.e., no bounce back) and the customer acknowledges receipt of the notification.
5 Residential tenants of master-metered customers can also qualify for Medical Baseline quantities. The Medical Baseline category for the purposes of Table 6 does not include MBL program customers who are master meter tenants. The Medical Baseline category for the purposes of Table 6 does not include MBL program customers who are master meter tenants.
6 Count of Warning Notifications includes doorbell rings and Live Agent phone calls.
7 PG&E has additional processes in place to ensure MBL customers are notified. Master meter tenants are contacted directly to be considered a positive notification. Contacting the property or building manager does not count as a positive notification.

## Table 7
Table 7: Outcomes of Notifications to De-energized Medical Baseline Program Customers
Count | Type of Notifications to De-energized MBL Customers (based on Service Point ID [SPID]) | Description
324 | Total De-energized MBL Program Customers | The number of customers de-energized who participate in PG&E’s MBL Program
324 | Total Notifications Attempted / Sent | The total sum of automated notifications attempted via call, text, and e-mail, in-person doorbell ring visit attempts and/or Live Agent phone calls.
0 | Total Notifications Not Attempted / Sent | Total MBL program customers de-energized that PG&E did not attempt to notify.
324 | Total Notifications Delivered | The total sum of automated notifications sent via call, text, and e-mail, in-person doorbell ring visit attempts and/or Live Agent phone calls that were executed (i.e., active phone number, deliverable e-mail address, and/or accessible to deliver in-person doorbell ring).
0 | Total Notifications Not Delivered | Total MBL program customers de-energized whose notification was not delivered.
319 | Total Notifications Received | Customers who acknowledged their notification by taking one of the following actions: answered an automated or Live Agent phone call, responded to a text message, opened an e-mail, or greeted an in-person doorbell ring (excludes voicemails left, text message delivered only and not confirmed, door hanger left).
5 | Total Notifications Not Received | Total MBL program customers de-energized who did not confirm receipt / acknowledge their automated notifications, Live Agent phone calls or in-person doorbell ring. Customers who did not answer a doorbell ring were left a door hanger.

## Table 8
Table 8: Count and Type of Additional Notifications
Count | Type of Additional Notifications to Impacted Medical Baseline Customers (based on SPID) | Description
103 | Total In-Person Visits / Doorbell Rings | Doorbell ring attempts to impacted MBL program customers where PG&E made contact with the customer (either in person or via phone call in advance of visit) or left a door hanger.1
87 | Live Agent Phone Calls | Call attempts made by Live Agent representatives to MBL program customers that had not yet confirmed receipt of their automated notification or answered the door during PG&E’s in-person visit.
1 Customers may have confirmed receipt of their notifications in multiple channels (e.g., automated notification and/or doorbell ring); therefore, the counts of total attempted and successful notifications are not mutually exclusive.

## Table 9
Table 9: Notification Failure Causes
Notifications Sent to: | Notification Type | Notification Delays | Timing of Notifications | Explanation of Delay | Notification Failures | Explanation of Failure
Public Safety Partners excluding Critical Facilities and Infrastructure1 | Entities who did not receive 48-to 72-hour priority notification | 0 | No notification delays | No notification delays | 0 | No notification failures
| Entities who did not receive 24-48-hour notification | 0 | No notification delays | No notification delays | 0 | No notification failures
| Entities who did not receive 1–4-hour imminent notification | 0 | No notification delays | No notification delays | 0 | No notification failures
| Entities who did not receive notifications at de-energization initiation | 0 | No notification delays | No notification delays | 0 | No notification failures
| Entities who were not notified immediately before re-energization | 0 | No notification delays | No notification delays | 0 | No notification failures
| Entities who did not receive notification when re-energization was complete | 0 | No notification delays | No notification delays | 0 | No notification failures
| Entities who did not receive cancellation notification within two hours of the decision to cancel | 0 | All entities received 2-hour cancellation notifications | All entities received 2-hour cancellation notifications | 0 | All entities received 2-hour cancellation notifications
Critical Facilities and Infrastructure2 | Facilities who did not receive 48-to 72-hour priority notification | 17 | See Table 9A for timing | See Table 9A for explanation | 0 | No notification failures
| Facilities who did not receive 24-48-hour notification | 9 | See Table 9B for timing | See Table 9B for explanation | 0 | No notification failures
| Facilities who did not receive 1–4-hour imminent notification | 0 | All Facilities received 1-4 hour imminent notifications | All Facilities received 1-4 hour imminent notifications | 0 | All Facilities received 1-4 hour imminent notifications
| Facilities who were not notified at de-energization initiation | 133 | See Table 9C for timing | See Table 9C for explanation | 1 | See Table 9D for explanation
| Facilities who were not notified immediately before re-energization | 0 | No notification delays | No notification delays | 1 | See Table 9E for explanation
| Facilities who were not notified when re-energization was complete | 0 | No notification delays | No notification delays | 1 | See Table 9F for explanation
| Facilities who did not receive cancellation notification within two hours of the decision to cancel | 0 | No notification delays | No notification delays | 0 | No notification failures
All other affected customers | Customers who did not receive 24–48-hour watch notifications | 339 | See Table 9G for timing | See Table 9G for explanation | 0 | No notification failures
| Customers who did not receive 1–4-hour imminent notifications43 | 0 | No notification delays | No notification delays | 0 | No notification failures
| Customers who were not notified at de-energization initiation | 3768 | See Table 9H for timing | See Table 9H for explanation | 8 | See Table 9I for explanation
| Customers who were not notified immediately before re-energization | 0 | No notification delays | No notification delays | 8 | See Table 9J for explanation
| Customers who were not notified when re-energization was complete | 0 | No notification delays | No notification delays | 9 | See Table 9K for explanation
| Customers who did not receive cancellation notification within two hours of the decision to cancel | 0 | No notification delays | No notification delays | 5 | See Table 9L for explanation
1 Only includes Tribes, cities, counties, CBOs and Community Choice Aggregators.
2 Includes Public Safety Partners who are critical facilities and infrastructure customers

## Table 9A-9L
Table 9A: Explanation of Delayed Priority Notifications (48-72 Hour) to Critical Facilities and Infrastructure
Facility Count | Time Notifications Sent | Explanation for Delay
1 | 42 hours ahead of planned outage start time | In this PSPS event, transmission impacts were not in scope 72-48 hours before de-energization was anticipated. This transmission customer was notified once they were added to scope.
7 | 38 hours ahead of planned outage start time | Due to changing weather conditions, these facilities were not in scope 72–48-hours before de-energization was anticipated. These facilities were notified once they were added to scope.
9 | 15 hours ahead of planned outage start time | Due to changing weather conditions, these facilities were not in scope 72–48-hours before de-energization was anticipated. These facilities were notified once they were added to scope.
Table 9B: Explanation of Delayed Watch Notifications (24-48 Hour) to Critical Facilities and Infrastructure
Facility Count | Time Notifications Sent | Explanation for Delay
9 | 15 hours ahead of planned outage start time | Due to changing weather conditions, these facilities were not in scope 48–24 hours before de-energization was anticipated. These facilities were notified once they were added to scope.
Table 9C: Explanation of Delayed Power-Off Notifications to Critical Facilities and Infrastructure
Facility Count | Time Notifications Sent | Explanation for Delay
7 | 2-3 hours after actual outage start time | We experienced a delay to the initial “Power Off” notifications for customers stemming from an internal process error. While our internal outage platform automation was turned on, automating the generation of notification files, we identified a gap that the vendor was not notified of the automation being turned on. This resulted in the vendor not immediately processing the notification files despite PG&E providing the files in a timely manner. During a staffing shift change this error was discovered and immediate requests were made to the vendor to process and launch all de-energization customer notifications that were delayed. All customers received the “Power Off” notifications prior to the “All Clear” notifications being launched. The timing variances magnitude of these delays were dependent on each facilities’ outage start time. The closer the facility’s outage start time was to the time the issue was resolved, the shorter the delay.
74 | 4-5 hours after actual outage start time
8 | 5-6 hours after actual outage start time
41 | 6-7 hours after actual outage start time
3 | 7-8 hours after actual outage start time
Table 9D: Explanation of Failed Power-Off Notifications to Critical Facilities and Infrastructure
Facility Count | Explanation for Failure
1 | Our internal outage platform did not capture the de-energization of one facility (Communications). As automated notifications rely on this platform’s data, notifications sent after de-energization, including a “Power Off” notification, were not sent. Once the error was detected, impacted customer and critical facility counts were corrected. The root cause of this issue is under evaluation.
Table 9E: Explanation of Failed All-Clear Notifications to Critical Facilities and Infrastructure
Facility Count | Explanation for Failure
1 | Our internal outage platform did not capture the de-energization of one facility (Communications). As automated notifications rely on this platform’s data, notifications sent after de-energization, including an “All Clear” and “ETOR” notifications, were not sent. Once the error was detected, impacted customer and critical facility counts were corrected. The root cause of this issue is under evaluation.
Table 9F: Explanation of Failed Restoration Notifications to Critical Facilities and Infrastructure
Facility Count | Explanation of Failure
1 | Our internal outage platform did not capture the de-energization of one facility (Communications). As automated notifications rely on this platform’s data, notifications sent after de-energization, including a “Restoration” notification, were not sent. Once the error was detected, impacted customer and critical facility counts were corrected. The root cause of this issue is under evaluation.
Table 9G: Explanation of Delayed Watch Notifications (24-48 Hour) to All Other Affected Customers
Customer Count | Time Notifications Sent | Explanation for Delay
339 | 15 hours ahead of planned outage start time | Due to changing weather conditions, these customers were not in scope during the 48–24-hour window in advance of anticipated de-energization. These customers were notified once they were added to scope. This count includes 23 MBL customers.
Table 9H: Explanation of Delayed Power-Off Notifications to All Other Affected Customers
Customer Count | Time Notifications Sent | Explanation for Delay
43 | 2-3 hours after actual outage start time | We experienced a delay to the initial “Power Off” notifications for customers stemming from an internal process error. While our internal outage platform automation was turned on, automating the generation of notification files, we identified a gap that the vendor was not notified of the automation being turned on. This resulted in the vendor not immediately processing the notification files despite PG&E providing the files in a timely manner. During a staffing shift change this error was discovered and immediate requests were made to the vendor to process and launch all de-energization customer notifications that were delayed. Thes customers received the “Power Off” notifications prior to the “All Clear” notifications being launched. Of all the customer power off notifications, 323 were MBL customers.
0 | 3-4 hours after actual outage start time
2012 | 4-5 hours after actual outage start time
122 | 5-6 hours after actual outage start time
1457 | 6-7 hours after actual outage start time
133 | 7-8 hours after actual outage start time
1 | 8-9 hours after actual outage start time
Table 8I: Explanation of Failed Power-Off Notifications to All Other Affected Customers
Customer Count | Explanation of Failure
2 | These customers were on a Remote Grid and experienced an outage on the secondary, with no corresponding primary outage. As a result, this outage was not included in our internal outage platform that tracks primary outages. As a result, these customers did not receive automated notifications sent through that system. No MBL customers were affected by this notification failure.
3 | Our internal outage platform did not capture the de-energization of these three customers. As automated notifications rely on this platform’s data, notifications sent after de-energization, including a “Power Off” notification, were not sent. Once the error was detected, impacted customer and critical facility counts were corrected. The root cause of this issue is under evaluation. No MBL customers were affected by this notification failure.
2 | These customers did not receive any automated notifications triggered through PG&E’s internal outage platform as they are not listed as active customers used for tracking outages. These service points were planned for de-energization and counted as de-energized customers for this report but were not counted as impacted customers in our internal outage platform. As a result, they did not receive the automated notifications triggered by platform. Customer count includes one MBL customers. The root cause of this issue is still being investigated.
1 | This customer was not included in the table of customer contact information used to launch automated notifications through our internal outage platform. As a result, they could not be notified. The root cause of this customer’s exclusion from this table is under evaluation. No MBL customers were affected by this notification failure.
Table 9J: Explanation of Failed All Clear Notifications to All Other Affected Customers
Customer Count | Explanation for Failure
2 | These customers were on a Remote Grid and experienced an outage on the secondary, with no corresponding primary outage. As a result, this outage was not included in our internal outage platform that tracks primary outages, and thus these customers did not receive automated notifications sent through that system. No MBL customers were affected by this notification failure.
3 | Our internal outage platform did not capture the de-energization of these customers. As automated notifications rely on this platform’s data, notifications sent after de-energization, including a “Power Off” notification, were not sent. Once the error was detected, impacted customer and critical facility counts were corrected. The root cause of this issue is under investigation. No MBL customers were affected by this notification failure.
2 | These customers did not receive any automated notifications triggered through PG&E’s internal outage platform as they are not listed as active customers used for tracking outages. These service points were planned for de-energization and counted as de-energized customers for this report but were not counted as impacted customers in our internal outage platform. As a result, they did not receive the automated notifications triggered by platform. Customer count includes one MBL customers. The root cause of this issue is still being investigated.
1 | This customer was not included in the table of customer contact information used to launch automated notifications through our internal outage platform. As a result, they could not be notified. The root cause of this customer’s exclusion from this table is under investigation. No MBL customers were affected by this notification failure.
Table 9K: Explanation of Failed Restoration Notifications to All Other Affected Customers
Customer Count | Explanation of Failure
2 | These customers were on a Remote Grid and experienced an outage on the secondary, with no corresponding primary outage. As a result, this outage was not included in our internal outage platform that tracks primary outages, and thus these customers did not receive automated notifications sent through that system. No MBL customers were affected by this notification failure.
3 | Our internal outage platform did not capture the de-energization of these customers. As automated notifications rely on this platform’s data, notifications sent after de-energization, including a “Restoration” notification, were not sent. Once the error was detected, impacted customer and critical facility counts were corrected. The root cause of this issue is under investigation. No MBL customers were affected by this notification failure.
2 | These customers did not receive any automated notifications triggered through PG&E’s internal outage platform as they are not listed as active customers used for tracking outages. These service points were planned for de-energization and counted as de-energized customers for this report but were not counted as impacted customers in our internal outage platform. As a result, they did not receive the automated notifications triggered by platform. Customer count includes one MBL customers. The root cause of this issue is still being investigated.
1 | This customer was not included in the table of customer contact information used to launch automated notifications through our internal outage platform. As a result, they could not be notified. The root cause of this customer’s exclusion from this table is under investigation. No MBL customers were affected by this notification failure.
1 | This customer was not included in the table of customer contact information used to launch automated notifications through our internal outage platform at the time of restoration. This customer discontinued service with PG&E during the PSPS Event. The table was updated to reflect this change and the customer received all previous automated notifications. No MBL customers were affected by this notification failure.
Table 9L: Explanation of Failed Cancellation Notifications to All Other Affected Customers
Customer Count | Explanation of Failure
5 | These customers had valid contact information during earlier phases of the PSPS event, so they were notified that they were in PSPS scope. At the time, these customers were descoped later in the PSPS event, they no longer had valid contact information, which meant they could not be notified of cancellation. Of these customers, two had service agreements that ended partway through the PSPS event. One of these customers is included in our de-energized customer count because their service point was de-energized in the PSPS event even though the customer is no longer active. This customer is not counted as a false positive as they were de-energized. Customer counts include one MBL customer.

## Table 10
Table 10: PSPS Portal Time & Date for Map Sharing
Date | Time PDF Maps Shared | Time GIS Layers Shared
2023-08-27 | 8:09 PM PDT | 8:09 PM PDT
2023-08-28 | 2:02 PM PDT | 2:02 PM PDT
2023-08-29 | 10:28 AM PDT | 10:28 AM PDT
2023-08-29 | 8:13 PM PDT | 8:13 PM PDT
2023-08-30 | 1:38 PM PDT | 1:38 PM PDT

## Table 11
Table 11: Customer Notifications Based on Language Preference
Language | Total Notifications1 | Percent
English | 602753 | 99.16%
Spanish | 4297 | 0.707%
Chinese – Cantonese | 263 | 0.043%
Chinese – Mandarin | 359 | 0.059%
Hmong | 100 | 0.016%
Vietnamese | 93 | 0.015%
Total | 607865 | 100%
1 Total notifications do not include doorbell rings and Live Agent phone calls.

## Table 12
Table 12: Call Center Support Services1
Total Calls Handled | PSPS Calls Handled | Average Response Time for PSPS-related Calls (Seconds) | Number of calls handled by Call Center Translation Services | Number of languages Supported by Call Center Translation Services
79873 | 783 | 19 | 4841 | 290+
1 Metrics are provided from August 28 - 31, 2023.

## Table 13
Table 13: PG&E Website Traffic for October 22-24 Weather Event1
Web Page | Unique Visitors | Visits | Page Views
PG&E’s Website (pge.com) | 750031 | 938703 | 1492821
PG&E’s Emergency Website (pgealerts.alerts.pge.com) 2, 3 | 106065 | 158553 | 320155
1 Website traffic from August 27-31, 2023
2 The PSPS Event Updates page is at the following pgealerts.alerts.pge.com/updates. PG&E also uses the following shortened URL for the same site: www.pge.com/pspsupdates.
3 The emergency website metrics are a subset of the pge.com/ website traffic reported.

## Table 14
Table 14: Unique Visitors to the Translated Versions of PG&E’s Website for the October 22-24 Weather Event 1, 2
Language | Unique Visitors | Percent
English | 478639 | 99.99%
Spanish | 54 | 0.01%
Chinese | 6 | 0%
Hindi | 2 | 0%
Farsi | 2 | 0%
Thai | 1 | 0%
Japanese | 1 | 0%
Portuguese | 0 | 0%
Russian | 0 | 0%
Vietnamese | 0 | 0%
Korean | 0 | 0%
Panjabi | 0 | 0%
Arabic | 0 | 0%
Tagalog | 0 | 0%
Hmong | 0 | 0%
Khmer | 0 | 0%
Grand Total3 | 750031 | 100%
1 Not all webpages within PG&E’s Website are offered in the translated languages listed. If the language is not included in the selector on the webpage, the visitor can call 1-833-208-4167 for assistance in 250+ other languages.
2 Unique visitors from August 27-31, 2023.
3 There is some overlap in unique visitors by language because some visitors viewed webpages in different languages.

## Table 15
Table 15: Unique Visitors to the Translated Versions of PG&E’s Emergency Website for the October 22-24 Weather Event 1
Language | Unique Visitors | Percent
English | 105209 | 99.2%
Spanish | 571 | 0.5%
Chinese | 29 | 0%
Portuguese | 3 | 0%
Panjabi | 3 | 0%
Hindi | 2 | 0%
Farsi | 2 | 0%
Thai | 1 | 0%
Vietnamese | 1 | 0%
Russian | 1 | 0%
Arabic | 0 | 0%
Tagalog | 0 | 0%
Korean | 0 | 0%
Japanese | 0 | 0%
Hmong | 0 | 0%
Khmer | 0 | 0%
Grand Total2 | 106065 | 100%
1 Unique visitors from August 27-31, 2023.
2 There is some overlap in unique visitors by language because some visitors viewed webpages in different languages.

## Table 16
Table 16: Generators Available for Critical Facilities and Infrastructure Customers
Generator Type | Number of Units | Individual Size (MW) | Run Time (Hrs.)1 | Description
Diesel Generator | 2 | 0.032 | 3 | 2 units on reserve in Sacramento.
Diesel Generator | 3 | 0.065 | 28.5 | 3 units on reserve in San Leandro.
Diesel Generator | 9 | 0.1 | 31.9 | 1 unit pre-staged at ICU Hospital; 8 units on reserve in Sacramento
Diesel Generator | 1 | 0.125 | 36 | 1 unit on reserve in San Leandro.
Diesel Generator | 6 | 0.15 | 30 | 1 unit on reserve in Sacramento; 5 units on reserve in San Leandro.
Diesel Generator | 3 | 0.2 | 29 | 3 units on reserve in San Leandro.
Diesel Generator | 4 | 1 | 21 | 3 units pre-staged at ICU Hospital; 1 unit on reserve in Sacramento.
Diesel Generator | 7 | 150 | 14 | 7 units on reserve in Benecia.
1 Estimated based on a 75% load. Barring mechanical failure and refueling the temporary generators have the ability to operate continuously throughout a typical PSPS event.

## Table 17
Table 17: Critical Facility and Infrastructure Customers Energized with Backup Generation
County | Site Type | Generation Deployed | Duration of Operation | Reason Deployed
Tehama | Radio Repeater | 0.200 MW | 46 hours | Public safety
Glenn | Community Service Water | 0.300 MW | 47 hours | High risk to environment

## Table 18
Table 18: Number and Nature of Complaints due to the October 22-24 Weather Event
Nature of Complaints | Number of Complaints
Communications/Notifications Including, but not limited to complaints regarding lack of notice, excessive notices, confusing notice, false alarm notice, problems with getting up-to-date information, inaccurate information provided, not being able to get information in the prevalent languages and/or information accessibility, complaints about website, Public Safety Partner Portal, Representational State Transfer (REST)/Digital Asset Manager (DAM) sites (as applicable). | 19
PSPS Frequency/Duration Including, but not limited to complaints regarding the frequency and/or duration of PSPS events, including delays in restoring power, scope of PSPS and dynamic of weather conditions. | 19
Safety/Health Concern Including, but not limited to complaints regarding difficulties experienced by AFN/MBL populations, traffic accidents due to non-operating traffic lights, inability to get medical help, well water or access to clean water, inability to keep property cool/warm during outage raising health concern. | 3
General PSPS Dissatisfaction/Other Including, but not limited to complaints about being without power during PSPS event and related hardships such as food loss, income loss, inability to work/attend school, plus any PSPS-related complaints that do not fall into any other category. | 7
Outreach/Assistance Including, but not limited to complaints regarding Community Resource Centers, community crew vehicles, backup power, hotel vouchers, other assistance provided by utility to mitigate impact of PSPS. | 6

## Table 19
Table 19: Weather All-Clear Times
All-Clear Zones | Weather All-Clear Date and Time
245C, 241A | 08/30/2023 13:45 PDT
248A, 280H, 280G, 280C, 246C, 246F, 244A, 244B, 247A, 247B, 175F, 177B, 170B, 177A, 246A, 245A | 08/30/2023 14:51 PDT
170A, 245B, 246B | 08/30/2023 15:20 PDT

## Table 20
Table 20: Lessons Learned from the PSPS Event
Issue | Discussion | Resolution
Data Sharing and Reporting | An update of PG&E’s 7-day forecast update was out of sync with internal processes resulting in Counties included before approved scope. | Continue further synchronization of updates with trainings and job aids.
Data Sharing and Reporting | While statuses were being updated on PG&E’s website, Cities and Counties observed information that had not yet been updated but were in the process of being updated. | To address this timing issue, we are updating the website language to provide clarification and redirect customers to the Address Look Up tool to view real-time status during PSPS.
Customer Notification | Power Off notifications were delayed due to coordination issues with vendor. See Table 9C and 9H for more information. | Updated internal guidance and training materials to ensure the customer notification lead notifies the vendor when our internal outage platform automation is turned on and updated.

## Table 21
Table 21: Maximum Wind Gusts Recorded 8/30/23 in Impacted Counties
County | Maximum Wind Gust (mph) | Station ID | Station Name
Butte | 49 | JBGC1 | Jarbo Gap
Colusa | 28 | PG280 | Huffmaster Road
Glenn | 39 | PG845 | Road 65
Lake | 39 | PG126 | Mt St Helena East
Shasta | 41 | PG070 | Round Mountain
Tehama | 40 | PG599 | Tuscan Buttes
Yolo | 44 | PG490 | Bald Mountain Tower

## Table A-1.1
Table A-1.1: Factors Considered in the Decision to Shut Off Power for Each Distribution Circuit De-energized During the August 30 – 31, 2023 PSPS Event
Circuit Name | Time Place | Forecast | [18 empty] | Agency Observed |  |  |  | Observed
|  | WS_mph | ws_ mph_ 50m | wg_ ec_ mph | temp _ 2m_ f | flame_ length_ ft_ 2hr | rate_ of_ spread _chhr _2hr | area_ acres_ 8hr | rh_ 2m | vpd2m _mb | prob _cat | dfm_ 10hr | dfm_ 100 hr | dfm_ 1000 hr | lfm_ herb | lfm_ woody | lfm_ chamise _new | sum_ tree ovr | prob_ ignition | cfpd | HWW | HWA | RFW | GACC_High Risk | Observed ws_ mph | Observed wg_ mph | Observed temp_ | Observed RH_ | Observed ws_ mph_ AC | Observed wg_ mph_ AC | Observed temp_ | Observed RH_ | open | Tx impacts | PSPS Potential Risk Consequence | PSPS Potential Benefit
[27 empty] | f | % |  |  | f_ AC | %_ AC | _ psps_ tags | _yes
_no
BIG BEND 1101 | TP 12 | 19 | 31 | 43 | 94 | 9.6 | 45.5 | 3210.1 | 9.6 | 48.7 | 0.894 | 0.035 | 0.061 | 0.084 | 36 | 72 | 67 | 54176.2 | 0.002021 | 14.7 | No | No | No | Yes | 30 | 49 | 97 | 13 | 11 | 17 | 97 | 13 | Yes | No | 0.6003 | 26.8
CEDAR CREEK 1101 | TP 1 | 28 | 38 | 58 | 95 | 30.8 | 40.2 | 2239.3 | 7.3 | 51.2 | 0.82 | 0.032 | 0.066 | 0.083 | 40 | 79 | 71 | 87136.2 | 0.004618 | 20.9 | No | No | No | No | 22 | 41 | 97 | 12 | 11 | 20 | 97 | 12 | Yes | Yes | 1.7098 | 43.8
CLARK ROAD 1102 | TP 12 | 27 | 34 | 43 | 96 | 12.4 | 45.5 | 2686.8 | 9.3 | 52.1 | 0.906 | 0.033 | 0.059 | 0.083 | 36 | 79 | 70 | 21285.1 | 0.002021 | 14.7 | No | No | No | Yes | 30 | 49 | 97 | 13 | 10 | 17 | 98 | 13 | Yes | No | 0.3779 | 78.9
CORNING 1101 | TP 4 | 23 | 29 | 44 | 99 | 8.8 | 85.9 | 18716 | 9 | 57.9 | 0.842 | 0.035 | 0.064 | 0.08 | 33 | 72 | 67 | 6259.9 | 0.001451 | 10 | No | No | Yes | Yes | 24 | 34 | 98 | 10 | 17 | 24 | 99 | 10 | Yes | No | 2.1801 | 325.7
CORNING 1102 | TP 4 | 23 | 29 | 44 | 99 | 10.5 | 124.8 | 26658 | 9 | 56.5 | 0.919 | 0.033 | 0.06 | 0.073 | 34 | 63 | 66 | 1979 | 0.000993 | 7.8 | No | No | Yes | Yes | 24 | 36 | 98 | 7 | 14 | 24 | 99 | 9 | Yes | No | 0.76211 | 121.5
CORNING REMOTE 0001 | TP 4 | 20 | 28 | 43 | 98 | 8.1 | 75.5 | 10414 | 9.7 | 54.5 | 0.77 | 0.035 | 0.063 | 0.078 | 37 | 70 | 67 | 14.3 | 0.001149 | 8.8 | No | No | Yes | Yes | 21 | 34 | 98 | 10 | 14 | 21 | 99 | 11 | Yes | No | N/A1 | N/A1
CORNING REMOTE 0002 | TP 4 | 20 | 28 | 42 | 98 | 6.9 | 41.2 | 5422.1 | 9.5 | 55.2 | 0.634 | 0.035 | 0.063 | 0.079 | 40 | 71 | 67 | 408.6 | 0.000923 | 5.8 | No | No | Yes | Yes | 21 | 34 | 98 | 10 | 14 | 21 | 99 | 11 | Yes | No | N/A1 | N/A1
COTTONWOOD 1102 | TP 2 | 15 | 21 | 34 | 99 | 10.5 | 47.9 | 7563.8 | 8.7 | 58.7 | 0.809 | 0.036 | 0.068 | 0.078 | 34 | 61 | 65 | 5633.5 | 0.00064 | 3.1 | No | No | Yes | Yes | 19 | 29 | 98 | 11 | 11 | 22 | 98 | 12 | Yes | No | 0.42172 | 319.3
ELK CREEK 1101 | TP 4 | 23 | 29 | 45 | 98 | 14.8 | 77.7 | 11496 | 9.1 | 55.5 | 0.928 | 0.033 | 0.059 | 0.072 | 34 | 62 | 64 | 1421.4 | 0.001142 | 9.4 | No | No | Yes | Yes | 25 | 38 | 109 | 6 | 13 | 20 | 109 | 8 | Yes | Yes | 2.285 | 136.1
GIRVAN 1101 | TP 2 | 20 | 28 | 43 | 99 | 10.6 | 79 | 13187 | 8.8 | 57.3 | 0.913 | 0.035 | 0.066 | 0.076 | 30 | 70 | 65 | 23867.7 | 0.001269 | 9.4 | No | No | Yes | Yes | 19 | 36 | 100 | 12 | 10 | 17 | 100 | 13 | Yes | No | 0.84772 | 209.1
GLENN 1101 | TP 4 | 23 | 29 | 39 | 98 | 8.5 | 83.7 | 14059 | 9.6 | 54.8 | 0.708 | 0.034 | 0.06 | 0.075 | 36 | 70 | 66 | -99 | 0.000621 | 4.2 | No | No | Yes | Yes | 23 | 36 | 98 | 7 | 12 | 19 | 98 | 10 | Yes | No | 0.09211 | 32.2
HIGHLANDS 1103 | TP 8 | 19 | 30 | 46 | 94 | 11.6 | 50.5 | 5337.3 | 9.4 | 47.1 | 0.9 | 0.04 | 0.068 | 0.077 | 38 | 61 | 72 | 1149.6 | 0.001142 | 8.5 | No | No | Yes | No | 22 | 37 | 98 | 9 | 9 | 16 | 98 | 9 | Yes | No | 0.13552 | 131.4
JESSUP 1101 | TP 2 | 16 | 22 | 36 | 99 | 8.4 | 36.8 | 3107.6 | 8.8 | 57.3 | 0.882 | 0.035 | 0.068 | 0.078 | 35 | 74 | 65 | 7072.7 | 0.000843 | 6.3 | No | No | Yes | Yes | 19 | 29 | 96 | 12 | 10 | 20 | 97 | 14 | Yes | No | 0.39706 | 262.4
LOGAN CREEK 2102 | TP 5 | 19 | 26 | 39 | 99 | 9.5 | 106.6 | 29275 | 8.7 | 56.8 | 0.844 | 0.034 | 0.062 | 0.075 | 34 | 66 | 65 | 547 | 0.00086 | 6.2 | No | No | Yes | Yes | 20 | 33 | 109 | 10 | 11 | 18 | 109 | 10 | Yes | No | 0.09723 | 23.3
MADISON 2101 | TP 6 | 20 | 26 | 35 | 99 | 6.5 | 34.3 | 3165.3 | 7.7 | 57.2 | 0.728 | 0.033 | 0.061 | 0.072 | 35 | 64 | 67 | 108.2 | 0.000545 | 3.9 | No | No | Yes | Yes | 25 | 44 | 101 | 11 | 10 | 17 | 101 | 11 | Yes | No | 0.10691 | 132.1
MAXWELL 1105 | TP 5 | 21 | 27 | 39 | 100 | 8.7 | 83 | 14387 | 8 | 58.5 | 0.865 | 0.032 | 0.059 | 0.071 | 31 | 64 | 64 | 261 | 0.000585 | 4.9 | No | No | Yes | Yes | 19 | 28 | 97 | 11 | 7 | 13 | 97 | 15 | Yes | No | 0.10691 | 132.1
ROUND MOUNTAIN 1101 | TP 1 | 22 | 28 | 36 | 90 | 29.2 | 30.3 | 1512.6 | 8.1 | 44.6 | 0.365 | 0.034 | 0.072 | 0.094 | 47 | 85 | 72 | 9575.7 | 0.0008 | 2.3 | No | No | No | No | 22 | 41 | 90 | 13 | 11 | 20 | 90 | 13 | Yes | No | 0.15221 | 14.3
WHITMORE 1101 | TP 1 | 21 | 32 | 48 | 92 | 13.6 | 30.7 | 1530 | 7.8 | 47.5 | 0.727 | 0.032 | 0.065 | 0.081 | 43 | 84 | 76 | 58930.2 | 0.003268 | 15.2 | No | No | No | No | 21 | 41 | 95 | 10 | 10 | 20 | 94 | 13 | Yes | No | 0.9208 | 9.4
1 Due to no customer impact, PSPS Potential Risk Consequence and Potential Benefit was not calculated for CORNING REMOTE 001 and CORNING REMOTE 002 circuits.

## Table A-1.2
Table A-1.2: Description, Units, and Value provided for Factors Considered in the Decision to Shut Off Power for Each Distribution Circuit De-energized During the October 22-24 Weather Event
Value | Unit | Value provided | Description
Forecast | ws_mph | Sustained wind speeds | mph
Forecast | ws_mph_50m | Sustained wind speeds at 50 m | mph
Forecast | wg_ec_mph | Forecasted Peak Wind Gust | mph
Forecast | temp_2m_f | Temperature | degrees F
Forecast | flame_length_ft_2hr | Flame length | ft
Forecast | rate_of_spread_chhr_2hr | Rate of spread | chains/hr
Forecast | area_acres_8hr | Acres burned | acres
Forecast | rh_2m | Relative Humidity | %
Forecast | vpd2m_mb | Vapor Pressure Deficit | mb
Agency | HWW | High Wind Warning | N/A
Agency | HWA | High Wind Advisory | N/A
Agency | RFW | Red Flag Warning | N/A
Agency | GACC_HighRisk | GACC High Risk | N/A
Forecast | prob_cat | Fire Potential Index (FPI) | probability outputs
Forecast | dfm_10hr | Dead Fuel Moisture Content 10 hrs | fuel moisture fraction
Forecast | dfm_100hr | Dead Fuel Moisture Content 100 hrs | fuel moisture fraction
Forecast | dfm_1000hr | Dead Fuel Moisture Content 1000 hrs | fuel moisture fraction
Forecast | lfm_herb | Live Fuel Moisture Content-herbacous | %
Forecast | lfm_woody | Live Fuel Moisture Content-woody | %
Forecast | lfm_chamise_new | Live Fuel Moisture Content-shrub | %
Forecast | sum_tree_ovr | Tree Overstike | ft
Forecast | prob_ignition | Ignition Probability Weather (IPW) Model Output | Probability
Forecast | cfpd | Catastrophic Fire Probability (CFPD) | Scaled Probability
Observed | Observed ws_mph | Observed Sustained Wind Speed during Event | mph
Observed | Observed wg_mph | Observed Peak Wind Gust during Event | mph
Observed | Observed temp_f | Observed Temperature during Event | degrees F
Observed | Observed RH_% | Observed Relative Humidity During Event | %
Observed | Observed ws_mph_AC | Observed Sustained Wind Speed at All Clear | mph
Observed | Observed wg_mph_AC | Observed Peak Wind Gust at All Clear | mph
Observed | Observed temp_f_AC | Observed Temperature at All Clear | degrees F
Observed | Observed RH_%_AC | Observed Relative Humidity at All Clear | %
Observed | open_psps_tags | Open PSPS Qualified Tags | N/A
Observed | Tx_impacts_yes_no | Impacted by Transmission | N/A

## Table A-2.1
Table A-2.1: Factors Considered in the Decision to Shut Off Power for Each Transmission Circuit De-energized During the August 30 – 31, 2023 PSPS Event
Circuit Name | Time Place | cfpd | flame_length_ft_2hr | rate_of_spread_chhr_2hr | area_acres_8hr | ws_mph | wg_ec_mph | ws_mph_50m | temp_2m_f | rh_2m | vpd2m_mb | dfm_10hr | dfm_100hr | dfm_1000hr | lfm_herb | lfm_chamise_new | lfm_woody | prob_cat | prob_ignition | OA | cdft | sum_tree_ovr | HWW | HWA | RFW | GACC_HighRisk | Observed ws_mph | Observed wg_mph | Observed temp_f | Observed RH_% | Observed ws_mph_AC | Observed wg_mph_AC | Observed temp_f_AC | Observed RH_%_AC | High Fire Risk Area (Y/N) | High Risk Vegetation Present on Circuit (Y/N) | open_psps_tags | transmission_impacts_yes_no
ELK CREEK TAP | TP 5 | 14.7 | 7 | 46 | 8129 | 20 | 36 | N/A | 95 | 9 | 51 | 0.04 | 0.064 | 0.076 | 34 | 66 | N/A | 0.791 | 0.002021 | 3.08e-07 | 0.000229 | N/A | No | No | Yes | Yes | 23 | 35 | 105 | 8 | 13 | 22 | 105 | 8 | Y | N | Yes | No
ELK CREEK TAP (CITY OF SANTA CLARA) | TP 5 | 20.9 | 7 | 46 | 8129 | 20 | 36 | N/A | 95 | 9 | 51 | 0.04 | 0.064 | 0.076 | 34 | 66 | N/A | 0.791 | 0.004618 | 3.08e-07 | 0.000229 | N/A | No | No | Yes | Yes | 13 | 24 | 98 | 8 | 10 | 18 | 99 | 8 | Y | N | Yes | Yes
KILARC-CEDAR CREEK | TP 1 | 14.7 | 10 | 26 | 1135 | 23 | 49 | N/A | 79 | 21 | 27 | 0.05 | 0.07 | 0.08 | 45 | 73 | N/A | 0.625 | 0.002021 | 0.00031 | 0.17 | N/A | No | No | No | No | 22 | 41 | 92 | 8 | 14 | 26 | 93 | 14 | Y | N | Yes | No

## Table A-2.2
Table A-2.2: Description, Units, and Value provided for Factors Considered in the Decision to Shut Off Power for Each Transmission Circuit De-energized During the August 30 – 31, 2023 PSPS Event
Forecast / Agency / Observed | Value | Name | Unit | Value provided | Description
Forecast | ws_mph | Sustained wind speeds | mph | max | Sustained windspeed in miles per hour at 10 meters above ground level.
Forecast | ws_mph_50m | Sustained wind speeds at 50 m | mph | max | Sustained windspeed in miles per hour at 50 meters above ground level.
Forecast | wg_ec_mph | Forecasted Peak Wind Gust | mph | max | Wind gust in miles per hour at 10 meters above ground level.
Forecast | temp_2m_f | Temperature | degrees F | max | Temperature in Fahrenheit at 2 meters above ground level.
Forecast | flame_length_ft_2hr | Flame length | ft | max | Flame length in feet on fire front for first 2 hours of fire spread simulation from Technoslyva.
Forecast | rate_of_spread_chhr_2hr | Rate of spread | chains/hr | max | Rate of fire spread in chains per hour for first 2 hours of fire spread simulation from Technoslyva.
Forecast | area_acres_8hr | Acres burned | acres | max | Acres burned in the 8-hour fire spread simulation from Technosylva.
Forecast | rh_2m | Relative Humidity | % | min | Relative Humidity in percent at 2 meters above ground level.
Forecast | vpd2m_mb | Vapor Pressure Deficit | mb | max | Vapor Pressure Deficit in millibar at 2m above surface
Agency | HWW | High Wind Warning | N/A | Yes/No during event | High Wind Warning from the Federal National Weather Service.
Agency | HWA | High Wind Advisory | N/A | Yes/No during event | High Wind Advisory from the Federal National Weather Service.
Agency | RFW | Red Flag Warning | N/A | Yes/No during event | Red Flag Warning from the Federal National Weather Service.
Agency | GACC_HighRisk | GACC High Risk | N/A | Yes/No during event | High Risk issued by the Federal North or South Operations Predictive Services.
Forecast | prob_cat | Fire Potential Index (FPI) | probability outputs | max | Fire Potential Index (FPI) Model Output - Probability of a catastrophic fire if an ignition were to occur. FPI component of the CFPD model.
Forecast | dfm_10hr | Dead Fuel Moisture Content 10 hrs | fuel moisture fraction | min | Dead Fuel Moisture in 10-hour fuel moisture class. Can be scaled to percentage by multiplying by 100.
Forecast | dfm_100hr | Dead Fuel Moisture Content 100 hrs | fuel moisture fraction | min | Dead Fuel Moisture in 100-hour moisture class. Can be scaled to percentage by multiplying by 100.
Forecast | dfm_1000hr | Dead Fuel Moisture Content 1000 hrs | fuel moisture fraction | min | Dead Fuel Moisture in 1000-hour moisture class. Can be scaled to percentage by multiplying by 100.
Forecast | lfm_herb | Live Fuel Moisture Content-herbacous | % | min | Live Fuel Moisture Percentage of herbaceous plant species. (% of species that is comprised of water)
Forecast | lfm_woody | Live Fuel Moisture Content-woody | % | min | Live Fuel Moisture Percentage of woody plant species. (% of species that is comprised of water)
Forecast | lfm_chamise_new | Live Fuel Moisture Content-shrub | % | min | Live Fuel Moisture Percentage of Chamise (shrub) plant species. (% of species that is comprised of water)
Forecast | sum_tree_ovr | Tree Overstike | ft | max | Sum of tree overstrike in a 2 x 2 km grid cell area in ft.
Forecast | OA | Transmission Operability Assessment (OA) | Probability | max | Ignition Probability Weather (IPW) Model Output - Probability of Ignition based on the probability of outages by cause. Ignition component of the CFPD model. Ignition Probability Weather Model - A model that provides estimates of the probability of an ignition given an outage on an hourly basis
Forecast | cfpt | Catastrophic Fire Potential (CFPT) | Scaled Probability | max | The product of probability of catastrophic fire (Prob_Cat) and IPW - probability of ignition (prob_ignition). This product is called the (CFPD) Catastrophic Fire Probability distribution model. Scaled by 1000 to covert to an integer value.
Observed | Observed ws_mph | Observed Sustained Wind Speed during Event | mph | max | The maximum sustained wind speed recorded by weather stations mapped to each circuit from de-energization time to all-clear time.
Observed | Observed wg_mph | Observed Peak Wind Gust during Event | mph | max | The maximum sustained wind gust recorded by weather stations mapped to each circuit from de-energization time to all-clear time.
Observed | Observed temp_f | Observed Temperature during Event | degrees F | max | The maximum temperature recorded by weather stations mapped to each circuit from de-energization time to all-clear time.
Observed | Observed RH_% | Observed Relative Humidity During Event | % | min | Minimum relative humidity recorded by all weather stations mapped to each circuit from de-energization time to all-clear time.
Observed | Observed ws_mph_AC | Observed Sustained Wind Speed at All Clear | mph | max | The maximum sustained wind speed recorded by weather stations mapped to each circuit at the all-clear time.
Observed | Observed wg_mph_AC | Observed Peak Wind Gust at All Clear | mph | max | The maximum sustained wind gust recorded by weather stations mapped to each circuit at the all-clear time.
Observed | Observed temp_f_AC | Observed Temperature at All Clear | degrees F | max | The maximum temperature recorded by weather stations mapped to each circuit at the all-clear time.
Observed | Observed RH_%_AC | Observed Relative Humidity at All Clear | % | min | Minimum relative humidity recorded by all weather stations mapped to each circuit at the all-clear time.
Observed | High Fire Risk Area | High Fire Risk Area | N/A | Yes/No During Event | Labeled ‘Yes’ when Circuit goes through High Fire Risk Area.
Observed | High Risk Vegetation Present on Circuit | High Risk Vegetation Present on Circuit | N/A | Yes/No During Event | High risk vegetation present on the circuit
Observed | Transmission_impacts_yes_no | Impacted by Transmission | N/A | Yes/No During Event | Distribution lines that would have been de-energized due to de-energization of upstream transmission lines, regardless of whether those distribution lines would have also been de-energized due to direct distribution PSPS.
Observed | PSPS Potential Risk Consequence | PSPS Potential Risk Consequence | MAVF Score | Yes | Measure of the adverse impact to customers due to de-energization.
Observed | PSPS Potential Benefit | PSPS Potential Benefit | MAVF Score | Yes | Measure of the adverse impact to customers due to a catastrophic fire.

## Table B-1
Table B-1: Circuits De-Energized During the August 30-31, 2023 PSPS Event
Distribution / Transmission | Circuit Name | De-Energization Date and Time | All-Clear Date and Time | Restoration Date and Time | County | HFTD Tier(s) | Total Customers | Residential Customers | Commercial / Industrial Customers | Medical Baseline Customers | AFN other than MBL Customers | Other Customers
Distribution | BIG BEND 1101* | 2023-08-30 01:42 | 2023-08-30 14:51 | 2023-08-30 18:34 | BUTTE | Tier 3, Tier 2 | 198 | 176 | 20 | 12 | 53 | 2
Distribution | CEDAR CREEK 1101* | 2023-08-30 02:00 | 2023-08-30 14:51 | 2023-08-31 11:21 | SHASTA | Partially Outside HFTD, Tier 3, Tier 2 | 697 | 624 | 68 | 59 | 181 | 5
Distribution | CLARK ROAD 1102* | 2023-08-30 01:40 | 2023-08-30 14:51 | 2023-08-30 17:41 | BUTTE | Partially Outside HFTD, Tier 3 | 151 | 136 | 12 | 11 | 38 | 3
Distribution | CORNING 1101* | 2023-08-30 04:06 | 2023-08-30 15:20 | 2023-08-30 19:15 | TEHAMA | Partially Outside HFTD, Tier 2 | 827 | 754 | 70 | 101 | 362 | 3
Distribution | CORNING 1102* | 2023-08-30 04:05 | 2023-08-30 15:20 | 2023-08-30 20:10 | TEHAMA | Partially Outside HFTD, Tier 2 | 287 | 228 | 51 | 19 | 69 | 8
Distribution | CORNING REMOTE 0001 | 2023-08-30 05:05 | 2023-08-30 15:20 | 2023-08-30 17:50 | TEHAMA | Tier 2 | 1 | 1 | 0 | 0 | 0 | 0
Distribution | CORNING REMOTE 0002 | 2023-08-30 05:17 | 2023-08-30 15:20 | 2023-08-30 17:33 | TEHAMA | Tier 2 | 1 | 1 | 0 | 0 | 0 | 0
Distribution | COTTONWOOD 1102* | 2023-08-30 02:29 | 2023-08-30 14:51 | 2023-08-30 18:39 | SHASTA | Partially Outside HFTD, Tier 2 | 65 | 57 | 5 | 7 | 15 | 3
Distribution | ELK CREEK 1101* | 2023-08-30 04:09 | 2023-08-30 15:20 | 2023-08-31 10:31 | COLUSA, GLENN | Partially Outside HFTD, Tier 2 | 839 | 683 | 128 | 56 | 181 | 28
Distribution | GIRVAN 1101* | 2023-08-30 02:00 | 2023-08-30 14:51 | 2023-08-30 18:48 | SHASTA | Partially Outside HFTD, Tier 3, Tier 2 | 332 | 287 | 40 | 19 | 58 | 5
Distribution | GLENN 1101* | 2023-08-30 04:10 | 2023-08-30 15:20 | 2023-08-30 18:14 | GLENN | Partially Outside HFTD, Tier 2 | 5 | 3 | 1 | 0 | 0 | 1
Distribution | HIGHLANDS 1103* | 2023-08-30 05:54 | 2023-08-30 14:51 | 2023-08-30 17:19 | LAKE | Partially Outside HFTD, Tier 2 | 50 | 35 | 11 | 3 | 10 | 4
Distribution | JESSUP 1101* | 2023-08-30 02:03 | 2023-08-30 14:51 | 2023-08-30 19:11 | SHASTA | Tier 2 | 137 | 133 | 3 | 13 | 40 | 1
Distribution | LOGAN CREEK 2102* | 2023-08-30 04:04 | 2023-08-30 14:51 | 2023-08-30 17:08 | GLENN | Partially Outside HFTD, Tier 2 | 9 | 3 | 4 | 0 | 1 | 2
Distribution | MADISON 2101* | 2023-08-30 04:16 | 2023-08-30 14:51 | 2023-08-30 17:31 | YOLO | Partially Outside HFTD, Tier 2 | 20 | 9 | 11 | 1 | 3 | 0
Distribution | MAXWELL 1105* | 2023-08-30 04:06 | 2023-08-30 14:51 | 2023-08-30 17:53 | COLUSA | Partially Outside HFTD, Tier 2 | 44 | 29 | 9 | 1 | 2 | 6
Distribution | ROUND MOUNTAIN 1101 | 2023-08-29 14:05 | 2023-08-30 14:51 | 2023-08-30 19:23 | SHASTA | Outside HFTD | 0 | 0 | 0 | 0 | 0 | 0
Distribution | WHITMORE 1101* | 2023-08-30 02:01 | 2023-08-30 14:51 | 2023-08-31 11:39 | SHASTA | Partially Outside HFTD, Tier 3, Tier 2 | 264 | 236 | 24 | 22 | 64 | 4
Transmission | KILARC-CEDAR CREEK | 2023-08-30 03:34 | 2023-08-30 14:51 | 2023-08-30 17:46 | Transmission Line | Partially Outside HFTD, Tier 2 | 0 | 0 | 0 | 0 | 0 | 0
Transmission | ELK CREEK TAP | 2023-08-30 04:36 | 2023-08-30 14:51 | 2023-08-30 17:58 | Transmission Line | Partially Outside HFTD, Tier 2 | 0 | 0 | 0 | 0 | 0 | 0
Transmission | ELK CREEK TAP (CITY OF SANTA CLARA) | 2023-08-30 04:36 | 2023-08-30 14:51 | 2023-08-30 17:58 | Transmission Line | Tier 3 | 1 1 | 0 | 0 | 0 | 0 | 0
Total | [6 empty] | 3928 | 3395 | 457 | 324 | 1077 | 75
1 Customer Line de-energized with Elk Creek Tap per TOTL WC #T23-014873.

## Table C-1
Table C-1: Damages and Hazards Found Within the De-erngized Areas
Circuit Name | County | Structure Identifier | Tier 2/3 or Non-HFTD | Damage / Hazard | Type of Damage/Hazard | Description of Damage
Cedar Creek 1101 | Shasta | 104054736 | Tier 2 | Damage | Wind related | Broken tie wire

## Table E-1
Table E-1. Public Safety Partners Contacted
Organization/Jurisdiction | Title | HFTD Tier | Date/Time Contacted
Butte County Communication Facility | AT&T MOBILITY | Tier 3 | 08/29/2023 11:32 PDT
Butte County Communication Facility | AT&T SERVICES INC | Tier 3 | 08/29/2023 11:32 PDT
Butte County Emergency Services Facility | COUNTY OF BUTTE | Tier 3 | 08/29/2023 11:32 PDT
Butte County Other Facility | CALIFORNIA DEPARTMENT OF FORESTRY | Tier 3 | 08/29/2023 11:32 PDT
Butte County | Assistant OES Director | Tier 2, Tier 3, Zone 1, HFRA | 08/29/2023 11:26 PDT
Butte County | Board Chair | Tier 2, Tier 3, Zone 1, HFRA | 08/29/2023 11:26 PDT
Butte County | Chief | Tier 2, Tier 3, Zone 1, HFRA | 08/29/2023 11:26 PDT
Butte County | Chief Administrative Officer | Tier 2, Tier 3, Zone 1, HFRA | 08/29/2023 11:26 PDT
Butte County | County Administrative Officer | Tier 2, Tier 3, Zone 1, HFRA | 08/29/2023 11:26 PDT
Butte County | County Clerk-Recorder | Tier 2, Tier 3, Zone 1, HFRA | 08/29/2023 11:26 PDT
Butte County | Director | Tier 2, Tier 3, Zone 1, HFRA | 08/29/2023 11:26 PDT
Butte County | Division Chief | Tier 2, Tier 3, Zone 1, HFRA | 08/29/2023 11:27 PDT
Butte County | General | Tier 2, Tier 3, Zone 1, HFRA | 08/29/2023 11:26 PDT
Butte County | General CAL FIRE | Tier 2, Tier 3, Zone 1, HFRA | 08/29/2023 11:26 PDT
Butte County | General Services Director | Tier 2, Tier 3, Zone 1, HFRA | 08/29/2023 11:26 PDT
Butte County | Lieutenant | Tier 2, Tier 3, Zone 1, HFRA | 08/29/2023 11:26 PDT
Butte County | OES Director | Tier 2, Tier 3, Zone 1, HFRA | 08/29/2023 11:26 PDT
Butte County | Probation Officer | Tier 2, Tier 3, Zone 1, HFRA | 08/29/2023 11:26 PDT
Butte County | Public Health Director | Tier 2, Tier 3, Zone 1, HFRA | 08/29/2023 11:26 PDT
Butte County | Senior Contracts/Procurement Agent and EOC Logistics Chief | Tier 2, Tier 3, Zone 1, HFRA | 08/29/2023 11:26 PDT
Butte County | Sergeant | Tier 2, Tier 3, Zone 1, HFRA | 08/29/2023 11:26 PDT
Butte County | Supervisor | Tier 2, Tier 3, Zone 1, HFRA | 08/29/2023 11:26 PDT
Butte County Tribal | Casino Director of Security | Tier 2, Tier 3, HFRA * | 08/29/2023 11:26 PDT
Butte County Tribal | Chairman | Tier 2, Tier 3, HFRA * | 08/29/2023 11:26 PDT
Butte County Tribal | Chairwoman | Tier 2, Tier 3, HFRA * | 08/29/2023 11:26 PDT
Butte County Tribal | Land Manager | Tier 2, Tier 3, HFRA * | 08/29/2023 11:26 PDT
Butte County Tribal | Tribal Administration | Tier 2, Tier 3, HFRA * | 08/29/2023 11:26 PDT
Butte County Tribal | Tribal Administrator | Tier 2, Tier 3, HFRA * | 08/29/2023 11:26 PDT
Butte County Tribal | Tribal Chairman | Tier 2, Tier 3, HFRA * | 08/29/2023 11:26 PDT
Butte County Tribal | Vice Chairwoman | Tier 2, Tier 3, HFRA * | 08/29/2023 11:26 PDT
Colusa County Communication Facility | AT&T | Tier 2 | 08/27/2023 20:34 PDT
Colusa County Communication Facility | AT&T MOBILITY LLC | Tier 2 | 08/27/2023 20:34 PDT
Colusa County Communication Facility | AT&T SERVICES INC | Tier 2 | 08/27/2023 20:34 PDT
Colusa County Communication Facility | FRONTIER COMMUNICATIONS CORPORATION DIP | Tier 2 | 08/27/2023 20:34 PDT
Colusa County Communication Facility | GTE MOBILNET OF CALIFORNIA LP | Tier 2 | 08/27/2023 20:34 PDT
Colusa County Emergency Services Facility | CALIFORNIA DEPARTMENT OF FORESTRY | N/A ** | 08/27/2023 20:34 PDT
Colusa County Emergency Services Facility | COUNTY OF COLUSA | N/A ** | 08/27/2023 20:34 PDT
Colusa County Energy Sector Facility | CITY OF SANTA CLARA | N/A ** | 08/27/2023 20:34 PDT
Colusa County Water and Waste Water Facility | CALIFORNIA DEPARTMENT OF FORESTRY | N/A ** | 08/27/2023 20:34 PDT
Colusa County Water and Waste Water Facility | COUNTY OF COLUSA | Tier 2 | 08/27/2023 20:34 PDT
Colusa County | Board Chair | Tier 2, Tier 3, HFRA | 08/27/2023 21:29 PDT
Colusa County | County Clerk/Recorder | Tier 2, Tier 3, HFRA | 08/27/2023 21:29 PDT
Colusa County | County Supervisor | Tier 2, Tier 3, HFRA | 08/27/2023 21:29 PDT
Colusa County | Deputy Chief | Tier 2, Tier 3, HFRA | 08/27/2023 21:29 PDT
Colusa County | Director | Tier 2, Tier 3, HFRA | 08/27/2023 21:29 PDT
Colusa County | Division Chief | Tier 2, Tier 3, HFRA | 08/27/2023 21:29 PDT
Colusa County | Emergency Service Technician | Tier 2, Tier 3, HFRA | 08/27/2023 21:29 PDT
Colusa County | MHOAC | Tier 2, Tier 3, HFRA | 08/27/2023 21:29 PDT
Colusa County | OES Coordinator/Sergeant | Tier 2, Tier 3, HFRA | 08/28/2023 09:00 PDT
Colusa County | OES Director | Tier 2, Tier 3, HFRA | 08/28/2023 09:00 PDT
Colusa County | Sheriff | Tier 2, Tier 3, HFRA | 08/27/2023 21:29 PDT
Colusa County | Supervisor | Tier 2, Tier 3, HFRA | 08/27/2023 21:29 PDT
Colusa County | Vice Chair | Tier 2, Tier 3, HFRA | 08/27/2023 21:29 PDT
Glenn County Communication Facility | AMERICAN TOWER CORPORATION | Tier 2 | 08/27/2023 20:34 PDT
Glenn County Communication Facility | AT&T SERVICES INC | Tier 2 | 08/27/2023 20:34 PDT
Glenn County Communication Facility | VERIZON | Tier 2 | 08/27/2023 20:34 PDT
Glenn County Emergency Services Facility | COUNTY OF GLENN | Tier 2 | 08/27/2023 20:34 PDT
Glenn County Emergency Services Facility | ELK CREEK FIRE DISTRICT | Tier 2 | 08/27/2023 20:35 PDT
Glenn County Water and Waste Water Facility | ELK CREEK COMMUNITY SERVICE | Tier 2 | 08/27/2023 20:34 PDT
Glenn County | CAO | Tier 2, HFRA | 08/27/2023 21:29 PDT
Glenn County | County Administrative Officer | Tier 2, HFRA | 08/27/2023 21:29 PDT
Glenn County | Deputy Director OES | Tier 2, HFRA | 08/27/2023 21:29 PDT
Glenn County | Director of Public Works Agency | Tier 2, HFRA | 08/27/2023 21:29 PDT
Glenn County | Fire Chief | Tier 2, HFRA | 08/27/2023 21:29 PDT
Glenn County | General | Tier 2, HFRA | 08/27/2023 21:29 PDT
Glenn County | Sheriff | Tier 2, HFRA | 08/27/2023 21:29 PDT
Glenn County Tribal | Chairman | Tier 2, HFRA * | 08/27/2023 21:29 PDT
Glenn County Tribal | Interim Tribal Secretary | Tier 2, HFRA * | 08/27/2023 21:29 PDT
Glenn County Tribal | Tribal Administrator | Tier 2, HFRA * | 08/27/2023 21:29 PDT
Lake County | OES Manager | Tier 2 | 08/28/2023 08:55 PDT
Lake County Communication Facility | AT&T SERVICES INC | Tier 2 | 08/28/2023 15:20 PDT
Lake County Tribal | Chairman | Tier 2, Tier 3, HFRA * | 08/28/2023 15:08 PDT
Lake County Tribal | Cultural Resources | Tier 2, Tier 3, HFRA * | 08/28/2023 15:08 PDT
Lake County Tribal | Environmental Director | Tier 2, Tier 3, HFRA * | 08/28/2023 15:08 PDT
Lake County Tribal | Tribal Administrator | Tier 2, Tier 3, HFRA * | 08/28/2023 15:08 PDT
Lake County Tribal | Vice Chairperson | Tier 2, Tier 3, HFRA * | 08/28/2023 15:08 PDT
Napa County | OES Officer | Tier 2 | 08/28/2023 11:29 PDT
Napa County Communication Facility | AT&T MOBILITY LLC | Tier 2 | 08/27/2023 20:34 PDT
Napa County Communication Facility | CALIFORNIA HIGHWAY PATROL | Tier 2 | 08/27/2023 20:34 PDT
Napa County CCA | General | N/A ** | 08/27/2023 21:29 PDT
Shasta County Communication Facility | AT&T MOBILITY LLC | Tier 2 | 08/27/2023 20:34 PDT
Shasta County Communication Facility | AT&T SERVICES INC | Tier 3 | 08/27/2023 20:34 PDT
Shasta County Communication Facility | CHARTER COMMUNICATIONS HOLDING COMPANY LLC | Tier 2 | 08/28/2023 15:20 PDT
Shasta County Communication Facility | FRONTIER COMMUNICATIONS CORPORATION DIP | Tier 3 | 08/27/2023 20:34 PDT
Shasta County Communication Facility | GTE MOBILNET OF CALIFORNIA LP | Tier 2 | 08/27/2023 20:34 PDT
Shasta County Communication Facility | HAPPY VALLEY TELEPHONE CO | Tier 2 | 08/27/2023 20:34 PDT
Shasta County Communication Facility | METRO PCS INC | N/A ** | 08/28/2023 15:20 PDT
Shasta County Communication Facility | SPRINT CORPORATION | Tier 2 | 08/27/2023 20:34 PDT
Shasta County Communication Facility | T-MOBILE WEST LLC | Tier 2 | 08/28/2023 15:20 PDT
Shasta County Communication Facility | TDS TELECOM | Tier 2 | 08/28/2023 15:20 PDT
Shasta County Emergency Services Facility | CALIFORNIA DEPARTMENT OF FORESTRY | Tier 2 | 08/27/2023 20:34 PDT
Shasta County Emergency Services Facility | COUNTY OF SHASTA | Tier 2 | 08/27/2023 20:34 PDT
Shasta County Other Facility | CALIFORNIA DEPARTMENT OF FORESTRY | Tier 3 | 08/27/2023 20:34 PDT
Shasta County Other Facility | HAPPY VALLEY TELEPHONE CO | N/A ** | 08/28/2023 15:20 PDT
Shasta County | Chief | Tier 2, Tier 3, Zone 1, HFRA | 08/27/2023 21:29 PDT
Shasta County | Emergency Command Center | Tier 2, Tier 3, Zone 1, HFRA | 08/27/2023 21:29 PDT
Shasta County | Fire Chief | Tier 2, Tier 3, Zone 1, HFRA | 08/27/2023 21:29 PDT
Shasta County | General | Tier 2, Tier 3, Zone 1, HFRA | 08/27/2023 21:29 PDT
Shasta County | Lieutenant | Tier 2, Tier 3, Zone 1, HFRA | 08/27/2023 21:29 PDT
Shasta County | RDMHS | Tier 2, Tier 3, Zone 1, HFRA | 08/27/2023 21:29 PDT
Shasta County | Sergeant | Tier 2, Tier 3, Zone 1, HFRA | 08/27/2023 21:29 PDT
Shasta County | Sheriff-Coroner | Tier 2, Tier 3, Zone 1, HFRA | 08/27/2023 21:29 PDT
Shasta County | Supervisor | Tier 2, Tier 3, Zone 1, HFRA | 08/27/2023 21:29 PDT
Shasta County Anderson | Chief Treatment Plant Operator | Tier 2, HFRA | 08/28/2023 15:08 PDT
Shasta County Anderson | City Manager | Tier 2, HFRA | 08/28/2023 15:08 PDT
Shasta County Anderson | Deputy Public Works Director | Tier 2, HFRA | 08/28/2023 15:08 PDT
Shasta County Anderson | Fire Chief | Tier 2, HFRA | 08/28/2023 15:08 PDT
Shasta County Anderson | Police Chief | Tier 2, HFRA | 08/28/2023 15:08 PDT
Shasta County Anderson | Public Works Superintendent | Tier 2, HFRA | 08/28/2023 15:08 PDT
Shasta County Tribal | Administrative Assistant | Tier 2, HFRA * | 08/27/2023 21:29 PDT
Shasta County Tribal | Chairman | Tier 2, HFRA * | 08/27/2023 21:29 PDT
Shasta County Tribal | Interim Tribal Administrator | Tier 2, HFRA * | 08/27/2023 21:29 PDT
Shasta County Tribal | Maintenance Supervisor | Tier 2, HFRA * | 08/27/2023 21:29 PDT
Shasta County Tribal | OES Director | Tier 2, HFRA * | 08/27/2023 21:29 PDT
Shasta County Tribal | Tribal Chairwoman | Tier 2, HFRA * | 08/27/2023 21:29 PDT
Shasta County Tribal | Senior Director | Tier 2, HFRA * | 08/27/2023 21:29 PDT
Shasta County Tribal | Tribal Leader | Tier 2, HFRA * | 08/27/2023 21:29 PDT
Tehama County Communication Facility | AT&T MOBILITY | Tier 2 | 08/27/2023 20:34 PDT
Tehama County Communication Facility | AT&T MOBILITY LLC | Tier 2 | 08/27/2023 20:34 PDT
Tehama County Communication Facility | AT&T SERVICES INC | Tier 2 | 08/27/2023 20:34 PDT
Tehama County Communication Facility | DUCOR TELEPHONE CO | Tier 2 | 08/27/2023 20:34 PDT
Tehama County Communication Facility | DUCOR TELEPHONE CORP | Tier 2 | 08/27/2023 20:34 PDT
Tehama County Communication Facility | GTE MOBILNET OF CALIFORNIA LP | Tier 2 | 08/28/2023 15:20 PDT
Tehama County Communication Facility | T MOBILE WEST A DELAWARE CORP | Tier 2 | 08/28/2023 15:20 PDT
Tehama County Communication Facility | T-MOBILE WEST LLC | Tier 2 | 08/28/2023 15:20 PDT
Tehama County Communication Facility | VERIZON | Tier 2 | 08/28/2023 15:20 PDT
Tehama County Emergency Services Facility | CALIFORNIA DEPARTMENT OF FORESTRY | Tier 2 | 08/27/2023 20:34 PDT
Tehama County Emergency Services Facility | COUNTY OF TEHAMA | N/A ** | 08/28/2023 15:20 PDT
Tehama County Government - Jail Facility | CALIFORNIA DEPARTMENT OF CORRECTIONS | Tier 2 | 08/27/2023 20:34 PDT
Tehama County Other Facility | BURNS,SHERRI | Tier 2 | 08/27/2023 20:34 PDT
Tehama County Other Facility | CALIFORNIA DEPARTMENT OF FORESTRY | Tier 2 | 08/27/2023 20:34 PDT
Tehama County Other Facility | DUCOR TELEPHONE CO | Tier 2 | 08/27/2023 20:34 PDT
Tehama County | Chief Administrator | Tier 2, HFRA | 08/27/2023 21:29 PDT
Tehama County | Communications Supervisor | Tier 2, HFRA | 08/27/2023 21:29 PDT
Tehama County | County Clerk / Recorder | Tier 2, HFRA | 08/27/2023 21:29 PDT
Tehama County | OES Deputy Director | Tier 2, HFRA | 08/27/2023 21:29 PDT
Tehama County | Sheriff | Tier 2, HFRA | 08/27/2023 21:29 PDT
Tehama County Corning | City Clerk | N/A ** | 08/27/2023 21:29 PDT
Tehama County Corning | City Manager | N/A ** | 08/27/2023 21:29 PDT
Tehama County Corning | Police Chief | N/A ** | 08/27/2023 21:29 PDT
Tehama County Red Bluff | Chief of Police | Tier 2, HFRA | 08/27/2023 21:29 PDT
Tehama County Red Bluff | City Manager | Tier 2, HFRA | 08/27/2023 21:29 PDT
Yolo County | OES | Tier 2 | 08/27/2023 1900 PDT
Yolo County Communication Facility | AT&T MOBILITY LLC | Tier 2 | 08/27/2023 20:34 PDT
Yolo County Communication Facility | GTE MOBILNET OF CALIFORNIA LP | Tier 2 | 08/27/2023 20:34 PDT
Yolo County Communication Facility | SPRINT CORPORATION | Tier 2 | 08/27/2023 20:34 PDT
Yolo County CCA | General | N/A ** | 08/27/2023 21:29 PDT
* Impacted federally and non-federally recognized tribes' HFRA/HFTD classifications reflect county designations.
** Some Public Safety Partners are outside of HFTD/HFRA boundaries but were also de-energized for safety. We mark these as N/A in Appendix E as they do not have classifications assigned.

## Table G-1
Table G-1. Community Resource Centers Provided by PG&E
# | County | Site Name | Address | Operating Hours (PDT) |  | Total Visitors | Indoor / Outdoor | Amenities Provided
|  |  |  | Day 1 | Day 2
|  |  |  | Mon-DD | Mon-DD
1 | Butte | Concow Elementary School | 11679 Nelson Bar Rd | 0800-2200 | N/A | 24 | Outdoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging
2 | Colusa | Stonyford Community Hall | 229 Market St | 0800-2200 | 0800-1130 | 86 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging, Cooling & Heating, Ice
3 | Glenn | Elk Creek Junior Senior High School | 3430 Co Rd 309 | 0800-2200 | N/A | 73 | Outdoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging
4 | Shasta | Happy Valley Community Center | 5400 Happy Valley Rd | 0800-2200 | N/A | 36 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging, Cooling & Heating, Ice
5 | Shasta | Hill Country Health and Wellness Center | 29632 CA-299 | 0800-2200 | N/A | 187 | Outdoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging
6 | Tehama | Rancho Tehama Association | 17605 Park Terrace Rd | 0800-2200 | N/A | 337 | Outdoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging
7 | Tehama | Noland Park | 19001 Bowman Rd | 0800-1400 | N/A | 2 | Outdoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging
8 | Tehama | Flournoy Elementary School | 15850 Paskenta Rd | 0800-2200 | N/A | 63 | Outdoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging