## WMP2022_Cal Advocates_004-Q09
(A) | (B) | (C) | (D) | (E) | (F) | (G) | (H) | (H)
ETL No | Transmission Line Name | Wildfire Risk Score (Line Average) | Project Start (Kickoff Date) | Forecasted In-Service Date | Covered Conductor Miles | Underground Miles | Conductor Replacement Miles | Conductor Removal Miles | Total Miles | 2022 Notes
ETL.1420, ETL.1430 | DRUM-RIO OSO #1 & #2 | 2.28, 4.76 | 2017-12-29 | 2022-03-24 | NA for transmission | NA | 4.2 | 0 | 4.2
ETL.4040 | TRINITY-COTTONWOOD (phase 3) | 19.42 | 2021-09-01 | 2022-08-20 | NA for transmission | NA | 6 | 0 | 6
ETL.4100 | VACA-VACAVILLE-JAMESON-NORTH TOWER | 0.08 | 2021-03-01 | 2022-05-16 | NA for transmission | NA | 0.38 | 0 | 0.38
ETL.3190 | CARIBOU-PALERMO | 147.34 | 2020-07-27 | 2022-12-31 | NA for transmission | NA | 0 | 22 | 22 | De-construction in 2022.
ETL.4040 | TRINITY-COTTONWOOD (phase 4) | 19.42 | 2020-09-01 | 2022-12-23 | NA for transmission | NA | 18.51 |  | 18.51 | Risks include delay in land rights acquisition, force majeure events
ETL.1350 | CRAGVIEW-CASCADE (phase 1) | 18.11 | 2021-04-06 | 2023-11-30 | NA for transmission | NA | 8.6 |  | 8.6 | To complete engineering in 2022.
ETL.1231, ETL.2395 | GRIZZLY TAP | 39.76, 4.69 | 2021-09-13 | 2022-12-14 | NA for transmission | NA | 4 |  | 4 | At risk due to customer rebuild project
ETL.6880 | FULTON-CALISTOGA | 8.45 | 2021-01-27 | 2024-12-30 | NA for transmission | NA | 24.7 |  | 24.7 | To complete Detailed Scoping activities (Clearance start window in 2023)
ETL.1350 | CRAGVIEW-CASCADE (phase 1/2) | 18.11 | 2020-06-24 | 2023-01-05 | NA for transmission | NA | 13 |  | 13 | Project risks include supply chain issues and increased durations to acquire environmental permits
ETL.6490 | COLGATE-GRASS VALLEY | 34.6554 | 2022-03-29 | 01/14/2027 | NA for transmission | NA | TBD |  | TBD | To complete Detailed Scoping activities.
ETL.1470 | EAGLE ROCK-CORTINA | 23.2181 | 2022-01-11 | 03/20/2024 | NA for transmission | NA | TBD |  | TBD | To complete Detailed Scoping activities.
ETL.7290 | KILARC-CEDAR CREEK | 26.7985 | 2022-06-10 | 06/20/2025 | NA for transmission | NA | TBD |  | TBD | To complete Detailed Scoping activities in Q1 2023.
ETL.6440 | COLEMAN-RED BLUFF | 14.5005 | 2022-10-26 | 02/01/2027 | NA for transmission | NA | TBD |  | TBD | To complete Detailed Scoping activities.
ETL.8180 | TULUCAY-NAPA #1 | 62.7821 | 2021-01-27 | 2024-06-26 | NA for transmission | NA | TBD |  | TBD | To complete Detailed Scoping activities in 2022.
ETL.6520 | COLGATE-SMARTVILLE #2 | 19.3622 | 2021-03-01 | 2025-03-03 | NA for transmission | NA | TBD |  | TBD | To complete Detailed Scoping activities in 2022.
ETL.3500 | SALT SPRINGS-TIGER CREEK | 4.5777 | 2016-11-01 | 2023-11-07 | NA for transmission | NA | TBD |  | TBD | Clearance window in 2023.
ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | 0.071845 | 2022-08-11 | 2027-08-06 | NA for transmission | NA | TBD |  | TBD | To complete Detailed Scoping activities in 2023.
ETL.6330 | CENTERVILLE-TABLE MTN-OROVILLE | 6.9588 | 2020-12-17 | 2025-07-24 | NA for transmission | NA | TBD |  | TBD | To complete Detailed Scoping activities in 2022.
ETL.7490 | MAPLE CREEK-HOOPA | 14.0702 | 2020-12-15 | 2026-10-08 | NA for transmission | NA | TBD |  | TBD | To complete Detailed Scoping activities in 2022.
ETL.1420, ETL.1430 | DRUM-RIO OSO #1 & #2 | 2.28, 4.76 | 2021-04-30 | 2026-09-29 | NA for transmission | NA | TBD |  | TBD | To complete Detailed Scoping activities in 2022.
ETL.8350 | WEST POINT-VALLEY SPRINGS | 0.72108 | 2018-03-20 | 2024-05-14 | NA for transmission | NA | TBD |  | TBD | To complete Detailed Scoping activities in 2022.
ETL.7990 | SMARTVILLE-NICOLAUS #1 | 0.31449 | 2020-12-10 | 2025-06-03 | NA for transmission | NA | TBD |  | TBD | To complete Detailed Scoping activities in 2022.
ETL.6810 | ESSEX JCT-ORICK | N/A | 2016-05-25 | 2026-04-09 | NA for transmission | NA | TBD |  | TBD | To complete Detailed Scoping activities in 2023.
ETL.8060 | SPAULDING-SUMMIT | 15.8637 | 2021-06-09 | 2027-03-17 | NA for transmission | NA | TBD |  | TBD | To complete Detailed Scoping activities in 2023.
ETL.7560 | WEIMAR #1 | 131.4302 | 2020-08-18 | 2025-07-01 | NA for transmission | NA | TBD |  | TBD | To complete Detailed Scoping activities in 2022.
ETL.2540 | METCALF-GREEN VALLEY | 39.1639 | 2018-08-21 | 04/27/2026 | NA for transmission | NA | TBD |  | TBD | Clearance window in 2025.
ETL.7590 | MONTA VISTA-BURNS | 50.2285 | 2018-04-10 | 2027-02-04 | NA for transmission | NA | TBD |  | TBD | To complete Detailed Scoping activities in 2022.
ETL.7590 | MONTA VISTA-BURNS | 50.2285 | 2018-04-10 | 2026-06-19 | NA for transmission | NA | TBD |  | TBD | To complete Detailed Scoping activities in 2022.
ETL.8400 | DEL MONTE-FORT ORD #1 | 1.7087e-08 | 2018-06-29 | 2023-10-30 | NA for transmission | NA | TBD |  | TBD | To complete Detailed Scoping activities in 2022.
ETL.7000 | HAMILTON BRANCH-CHESTER | 3.8844 | 2018-06-19 | 2024-09-18 | NA for transmission | NA | TBD |  | TBD | Land and permit to be completed in 2022; clearance window 2024.
ETL.1420 | DRUM-RIO OSO #2 | 2.2818 | 2016-02-01 | 2024-02-01 | NA for transmission | NA | TBD |  | TBD | IFC and clearance window in 2022
ETL.7590 | MONTA VISTA-BURNS | 50.2285 | 2018-04-10 | 2025-07-04 | NA for transmission | NA | TBD |  | TBD | To complete Detailed Scoping activities in 2022.
ETL.3960 | TEMBLOR-SAN LUIS OBISPO | 0.0032768 | 2016-01-18 | 11/14/2023 | NA for transmission | NA | TBD |  | TBD | Engineering and IFC to be completed in 2022; clearance window in 2023.
ETL.3180 | OLEUM-NORTH TOWER-CHRISTIE | 0.0031422 | 2019-06-12 | 2025-05-09 | NA for transmission | NA | TBD |  | TBD | Clearance window in 2024
ETL.3160 | OLEUM-G #2 | 0.0035443 | 2018-10-16 | 01/16/2026 | NA for transmission | NA | TBD |  | TBD | To complete Detailed Scoping activities in 2022.
ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 | 0.071845 | 2019-11-12 | 2025-11-17 | NA for transmission | NA | TBD |  | TBD | To complete Detailed Scoping activities in 2022.
ETL.2720, ETL.2730, ETL.2740, ETL. 2750 | MORAGA-OAKLAND X 1, 2, 3 & 4 | 0.002, 0.002, 0.010, 0.098 | 2014 | 2029 | NA for transmission | NA | TBD |  | TBD | Engineering and permitting activities in 2022.
ETL.7150, ETL.1850, ETL.1860 | IGNACIO-ALTO, IGNACIO-SAN RAFAEL #1, IGNACIO-LAS GALLINAS | 0.217, 0.269, 0.002 | 2022 | 2027 | NA for transmission | NA | TBD |  | TBD | Kickoff and scoping activities in 2022.

## background data(1) (hidden)
Remove? | Investment Code | Investment Name | Parent Investment/ Tdot | MWC | MAT | Program | Asset Strategy Engineer | Description | Loading Order | CPUC Fire Threat Zone/Rating | Circuit ID | Functional Location | Station/Line/Circuit | Kick-Off | 2022 Notes | Construction Start | Forecasted In-Service Date | 2022 Investment Plan 2022 Forecast | 2022 Investment Plan 2023 Forecast | 2022 Investment Plan 2024 Forecast | 2022 Investment Plan 2025 Forecast | 2022 Investment Plan 2026 Forecast
| 5790356 | Colgate-Grass Valley 60kV Structure Repl | T.0005865 / T.0005865 | 93 | 93P | Transmission Lines |  | The Colgate-Grass Valley 60 kV Line is located in Nevada County. The Colgate-Grass Valley 60 kV Line is approximately 13.2 miles long and is supported by 326 structures, of which, 287 are in Tier 2 and Tier 3 high fire threat districts (HFTDs). The project will increase system performance and reduce fire ignition risk in Nevada County by performing the following work: • Replace 139 wood poles on the Colgate-Grass Valley 60 kV Line2 • Replace insulators on 8 structures not identified for repalcement • Replace Colgate-Grass Valley 60 kV Line Switch No. 47 • Review Colgate-Grass Valley 60 kV Line Switch No. 75 • Review Structure Nos. 000/003, A003/091, 010/232 and 012/303 for age and condition • Review all conductor for age and condition to determine if replacement is required • Identify any distribution underbuild and coordinate with distribution planning • Vegetation Management to provide 80-foot clearance when implementing structure replacement or line reconductoring • Include all open maintenance tags within the project scope where applicable | 1. Work that Prevents Fire Ignition | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | ETL.6490 | ETL.6490 | COLGATE-GRASS VALLEY | 2022-03-29 | To complete Detailed Scoping activities. | 12/18/2026 | 01/14/2027 | 1 | 761 | 887 | 554 | 864
| 5789154 | Cascade-Cottonwood 115kV Repl Struc | T.0005682 / T.0005682 | 93 | 93P | Transmission Lines |  | The project will increase system performance and reduce fire ignition risk in Shasta County by performing the following work: • Replace approximately 19.5 miles of conductor on the Cascade – Cottonwood 115 kV Line with 715 all aluminum conductor (AAC); • Upgrade substation terminal equipment to match new conductor rating, if needed; • Replace all wood poles with new Light Duty Steel (LDS) Poles; • Perform field analysis on existing steel structures to verify if replacements are needed; • Replace existing switch no. 149 with SCADA-operable switch; and • Vegetation Management to provide 100-foot clearance when implementing structure replacement or line reconductoring • Include all open maintenance tags within the project scope where applicable. | 2. Overhead with Strong Safety Link | Tier 2 - Elevated, Tier 1 | ETL.1240 | ETL.1240 | CASCADE-COTTONWOOD | 2024-06-14 | Future Work | 02/09/2029 | 03/08/2029 | 3 | 3 | 314 | 958 | 845
| 5789712 | Eagle Rock-Cortina Struc Repl & Reinsul | T.0005743 / T.0005743 | 93 | 93P | Transmission Lines |  | The Eagle Rock-Cortina 115 kV line is approximately 43.4 miles long with 322 structures that is located in the Northern region. Two hundred Ninety-Two (292) of these structures are in high fire tier districts (HFTD’s). In order to increase system performance and reduce fire ignition risk, asset components on the line are being performed with the following scope of work: • Replacement of 112 wood pole with steel structures; • Replacement of aging insulators on 119 structures; • Replacement of aging switch on structure 000/001; • Vegetation Management to provide 100-foot clearance when implementing structure replacement or line reconductoring • Include all open maintenance tags within the project scope where applicable | 2. Overhead with Strong Safety Link | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | ETL.1470 | ETL.1470 | EAGLE ROCK-CORTINA | 2022-01-11 | To complete Detailed Scoping activities. | 11/22/2023 | 03/20/2024 | 3 | 824 | 1143 | 840 | 1218
Yes - no reconductoring | 5785458 | ValleySprings-Martell No.2 60k Update | T.0003024 / T.0003024 | 60 | 60X | Capacity |  | Phase 1 of this project will replace 6 manually operated switches with SCADA-operable switches on the Valley Springs-Martell No. 1, Valley Springs – Clay, and the Pardee No. 2 Tap 60kV lines. The associated wood poles will be replaced with 4 Tubular Steel Poles (TSP) and 2 Engineered Direct Embedded Poles (EDEP) as required. This project will improve customer electric service reliability by reducing outage durations and allowing greater operational flexibility. Phase 2 of this project will replace 4 manually operated switches with SCADA-operable switches on the Clay - Martell 60kV line. The associated wood poles will be replaced with 3 Fiberglass Poles and one Engineered Direct Embedded Poles (EDEP) as required. The manual switches will be replaced with either Cleveland/Price or SEECO switches. The project is being constructed in 2 phases due to testing required for the new fiberglass pole design. | 5. Compliance / Commitments with Strong Safety Link | Tier 2 - Elevated, Tier 1 | ETL.8264 | ETL.8264 | VALLEY SPRINGS-CLAY |  |  |  |  | 7 |  | 475 | 1027 | 32
Maybe - already counted? Says phase 3 though | 5790354 | Cragview-Cascade 115kV Ph. 3 | T.0005874 / T.0005874 | 93 | 93N | NERC Compliance |  | The project scope of work includes identifying the scope associated with the below discrepancies and infractions: - T-line to Ground Discrepancies – GO 95 – 6 Discrepancies - Wire to Wire Infractions – PGE Standard and GO 95 – 46 Discrepancies | 5. Compliance / Commitments with Strong Safety Link | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | ETL.1350 | ETL.1350 | CRAG VIEW-CASCADE | 2023-01-05 | Was not included in 2022 count due to significant project risks, including supply chain issues and increased durations to acquire environmental permits) | 08/15/2022 | 12/06/2022 | 10
| 5772894 | Kilarc-Cedar Creek 60 kV Reliability | T.0002386 / T.0002386 | 94 | 94L | Reliability |  | This project proposes to Evaluate the line and complete targeted reliability improvements as recommended on the Kilarc – Cedar Creek 60kV Line. | 1. Work that Prevents Fire Ignition | Tier 3 - Extreme | ETL.7290 | ETL.7290 | KILARC-CEDAR CREEK | 2022-06-10 | To complete Detailed Scoping activities in Q1 2023. | 11/14/2024 | 06/20/2025 | 52 | 486 | 3493 | 4399
| 5791526 | Ph 3-Maple Ck- Willow Ck REL | T.0000609 / T.0000609 | 94 | 94L | Reliability |  | Objective Statement: Increase reliability along the Maple Creek-Hoopa 60kV line by rebuilding a 20-mile section with new transmission poles and other reliability work. | 1. Work that Prevents Fire Ignition | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | ETL.7490 | ETL.7490 | MAPLE CREEK-HOOPA | 2015-04-06 |  | 08/05/2022 | 11/29/2022 | 65.1188 | 12406.4078
Yes - already counted | 5747900 | Drum-Rio Oso 115 kV Re-Build (Phase 1) | T.0000036 / T.0000036 | 94 | 94L | Reliability |  | The project proposes to abandon and rebuild the first 11 miles of the 45-mile long Drum-Rio Oso #1 and #2 circuits. Specifically, 241 lattice steel structures and conductors in the current 11 mile tower line (dual tower configuration) will be replaced with a double-circuit 115kV tower line (single tower configuration) using fire resistant, self-weathering steel poles and components, conductors in the centerline of the existing ROW.The project will also widen the existing ROW, where required, as the current ROW is only 70 feet wide. By replacing the existing dual tower configuration with a single, double-circuit tower line and siting them in the existing ROW centerline, the project will eliminate the need for a more rigorous permitting process, avoid costlier ROW land acquisition costs, and provide the new tower line greater clearance distances from the edges of the ROW. | 1. Work that Prevents Fire Ignition | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | ETL.1420 | ETL.1420 | DRUM-RIO OSO #1 |  |  | 11/01/2021 | 03/07/2022 | 74.3314
| 5790859 | Coleman Jct -Vina -Gerber 60 kV Str | T.0005935 / T.0005935 | 93 | 93P | Transmission Lines |  | The Coleman Junction -Vina - Gerber 60 kV Line section is part of the Coleman - Red Bluff 60 kV Line located in Tehama County. The Coleman - Red Bluff 60 kV Line is approximately 48.1 miles long and is supported by 834 structures; 312 of these structures are in High Fire Threat Districts (HFTDs). There is an ongoing project to replace structures and conductor on the Coleman - Red Bluff 60 kV Line, between Coleman Power House and Red Bluff Substation. This new project will complete work on the remaining portions of the line between Coleman Junction, Vina and Gerber substations. | 1. Work that Prevents Fire Ignition | Tier 2 - Elevated, Tier 1 | ETL.6440 | ETL.6440 | COLEMAN-RED BLUFF |  |  | 07/17/2025 | 02/01/2027 | 247 | 753 | 1074 | 19460 | 19280
| 5792143 | Caribou-Palermo 10391: Remove Structures | T.0006251 / T.0006251 | 93 | 93J | Transmission Lines |  | This project proposes to remove the abandoned structures of the de-energized Caribou-Palermo 115 kV Line. | 1. Work that Prevents Fire Ignition | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | ETL.3190 | ETL.3190 | CARIBOU-PALERMO |  |  | 02/23/2023 | 09/20/2024 | 311 | 7
| 5789523 | MORAGA-OAKLAND X 115KV 1&2: RECONDUCTOR | T.0000349 / T.0000349 | 60 | 60X | Capacity |  | MORAGA-OAKLAND X 115KV 1&2: RECONDUCTOR | 5. Compliance / Commitments with Strong Safety Link | Tier 3 - Extreme | ETL.2740 | ETL.2720 | MORAGA-OAKLAND #3 |  |  |  |  | 400 | 5250 | 10180 | 24567 | 39000
| 5789524 | MORAGA-OAKLAND X 115KV 3&4: RECONDUCTOR | T.0000349 / T.0000349 | 60 | 60X | Capacity |  | MORAGA-OAKLAND X 115KV 3&4: RECONDUCTOR | 5. Compliance / Commitments with Strong Safety Link | Tier 3 - Extreme | ETL.2740 | ETL.2740 | MORAGA-OAKLAND #3 |  |  |  |  | 400 | 2100 | 5400 | 20950 | 39500
| 5747771 | IGNACIO AREA UPDGRADE PROJECT | T.0004526 / T.0004526 | 93 | 93P | Capacity |  | Ignacio Area Reinforcement Project | [9 empty] | 500 | 2000 | 8000 | 13000 | 15000
| 5791021 | Tulucay-Napa #1-Repl Steel Poles | T.0005976 / T.0005976 | 93 | 93P | Transmission Lines |  | The project will increase system performance and reduce fire ignition risk in Napa County by performing the following work: • Replace 4 steel structures on the Tulucay-Napa #1 60 kV Line; • Replace 8 steel structures on the Cordelia #2 Tap 60 kV; • Replace 126 existing wood poles with steel structures on the Tulucay-Napa #1 60 kV Line; • Replace 19 existing wood poles with steel structures on the Cordelia #1 Tap 60 kV; • Replace 77 existing wood poles with steel structures on the Cordelia #2 Tap 60 kV; • Replace 2.33 miles of conductor from pole no. T001/006 to 006/107 on the Cordelia #1 Tap 60 kV; • Replace existing ceramic insulators on 26 structures with modern equivalent insulators; • Replace 5 existing switches with Supervisory Control and Data Acquisition (SCADA)-operable switches; • Vegetation Management to provide 80-foot clearance when implementing structure replacement or line reconductoring; and • Include all open maintenance tags within the project scope where applicable. | 1. Work that Prevents Fire Ignition | Tier 2 - Elevated, Tier 1 | ETL.8180 | ETL.8180 | TULUCAY-NAPA #1 |  |  | 10/06/2023 | 07/11/2024 | 536 | 6953 | 15682 | 113
| 5790663 | Colgate-Smartville #2 Reinf Sw Repl | T.0005916 / T.0005916 | 93 | 93P | Transmission Lines |  | The Colgate-Smartville #2 60 kV Reinforcement Project is located in Yuba and Nevada Counties. The Colgate-Smartville #2 60 kV line is 11.13 miles long and is supported by 155 structures. The line is a single circuit that is supported on single wood poles. All the structures are in Tier 2 high fire tier districts (HFTDs). The assessment by Transmission Line Asset Strategy (TLAS) included the two 60 kV taps connected to the Colgate-Smartville #2 60 kV line. They are the Narrows #2 Tap at structure 010/127 and the Smartville Tap at structure 000/001. The project will increase system performance and reduce fire ignition risk in Yuba and Nevada Counties by performing the following work: ● Replace 98 non-steel structures on Colgate-Smartville #2 60 kV line that includes reviewing 11.13 miles of conductor and increase inspection because of aging asset. ● Replace 68 insulators on the Colgate-Smartville #2 line ● Replace 2 non-steel structures on Smartville Tap ● Replace 47 non-steel structures for Narrows #2 Tap ● Replace one (1) steel structure for Narrows #2 Tap ● Replace one (1) switch with SCADA on Colgate-Smartville #2 line; SW#29 ● Replace two (2) switches with SCADA on Smartville Tap; SW#97 & SW#99 ● Replace two (2) switches with SCADA on Narrows #2 Tap; SW#47 & SW#59 | 1. Work that Prevents Fire Ignition | Tier 2 - Elevated | ETL.6520 | ETL.6520 | COLGATE-SMARTVILLE #2 |  |  | 05/28/2025 | 06/24/2025 | 548 | 299 | 4315 | 292
Yes - just the land rights portion of scope? | 5539023 | MORAGA-OAKLAND X 115KV 1-4: LAND RIGHTS | T.0000349 / T.0000349 | 60 | 60X | Capacity |  | MORAGA-OAKLAND X 115KV 1-4: LAND RIGHTS | 5. Compliance / Commitments with Strong Safety Link | Tier 3 - Extreme | ETL.2740 | ETL.2720 | MORAGA-OAKLAND #3 |  |  |  |  | 690 | 2200 | 3200 | 1120
| 5760915 | SALT SPRINGS-TIGER CREEK NERC PROJECT | T.0000076 / T.0000076 | 93 | 93N | NERC Compliance |  | The project scope includes replacing towers with TSP H-Frame structures and replacing conductor at several sections along the circuit to mitigate NERC discrepancies and replace sections of conductor with unknown properties on the Salt Springs-Tiger Creek 115kV circuit. | 5. Compliance / Commitments with Strong Safety Link | Tier 3 - Extreme, Tier 2 - Elevated | ETL.3500 | ETL.3500 | SALT SPRINGS-TIGER CREEK |  |  | 04/14/2023 | 11/07/2023 | 719 | 3470.734 | 21135.2016
| 5783641 | Stan-Melones Tap Lines: Repl CU cond | T.0004515 / T.0004515 | 93 | 93C | Transmission Lines |  | This project proposes to reconductor 13.52 miles of 2/0 7-strand Copper (CU) conductor on the Stanislaus-Melones Sw Sta-Manteca No. 1 and Stanislaus-Melones Sw Sta-Riverbank Jct Sw Sta 115 kV lines with 715 All Aluminum Conductor (AAC). The total project cost is estimated at $16.00 million[1] based on preliminary cost estimates (AACE Class 5)[2]. Completion of this project is needed to replace obsolete and failing conductor and to mitigate safety and reliability risks. | 2. Overhead with Strong Safety Link | Tier 2 - Elevated, Tier 1 | ETL.3830 | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 |  |  | 01/04/2027 | 04/30/2027 | 960.3304 | 1334 | 1644 | 17182 | 101
| 5790821 | Centerville-Table Mtn-Oroville-SCADA Sw | T.0005931 / T.0005931 | 93 | 93P | Transmission Lines |  | The Centerville – Table Mountain – Oroville 60 kV Line is located in Butte County. The Centerville – Table Mountain – Oroville 60 kV Line is approximately 25.6 miles long and is supported by 481 structures. The Centerville – Table Mountain – Oroville 60 kV Line is configured as a single conductor line and is supported by 481 structures, of which 169 structures are in high fire threat districts (HFTDs). The project will increase system performance and reduce fire ignition risk in Butte County by performing the following work: • Replace 122 existing structures with Light Duty Steel (LDS) Poles on the Centerville – Table Mountain – Oroville 60 kV Line; • Perform field analysis on the entire 25.6 mile long Centerville – Table Mountain – Oroville 60 kV Line to verify if conductor replacement is needed; • Replace Switch Nos. 27 and 67 with a Supervisory Control and Data Acquisition (SCADA)-operable switch on the Centerville – Table Mountain – Oroville 60 kV Line; • Replace existing ceramic insulators on 96 structures with modern equivalent insulators on the Centerville – Table Mountain – Oroville 60 kV Line; • Vegetation Management to provide 80-foot clearance when implementing structure replacement or line reconductoring; and • Include all open maintenance tags within the project scope where applicable. | 2. Overhead with Strong Safety Link | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | ETL.6330 | ETL.6330 | CENTERVILLE-TABLE MTN-OROVILLE |  |  | 01/19/2027 | 02/15/2027 | 1018 | 937 | 1092 | 3521 | 1713
| 5790604 | Willow Creek-Hoopa 60 kV Str Project | T.0005899 / T.0005899 | 93 | 93P | Transmission Lines |  | The Willow Creek – Hoopa 60 kV Line section, located in the Humboldt County, is part of the Maple Creek – Hoopa 60 kV radial Line. The line section is roughly 9 miles long and is supported by roughly 127 structures. 96 of these structures are located in high fire threat districts (HFTDs). There is an existing project inflight to replace structures, conductor and associated equipment on the line section between Maple Creek and Willow Creek substations. This project will replace structures, conductor and associated equipment between the Willow Creek and Hoopa substations. The project will increase system performance and reduce fire ignition risk in Humboldt County by performing the following work: • Replace 127 structures on the Willow Creek - Hoopa 60 kV Line2 section • Reconductor roughly 9 miles of conductor on the Willow Creek - Hoopa 60 kV Line section • Review 1 switch on the Willow Creek - Hoopa 60 kV Line section for possible upgrade to SCADA-operable switch • Review 14 structures on the Willow Creek - Hoopa 60 kV Line section for age information • Identify any distribution under-build and coordinate with distribution planning • Vegetation Management to provide 80-foot clearance when implementing structure replacement or line reconductoring. | 1. Work that Prevents Fire Ignition | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | ETL.7490 | ETL.7490 | MAPLE CREEK-HOOPA |  |  | 07/14/2026 | 08/10/2026 | 1044 | 3526 | 1937 | 143
| 5791639 | Drum-Rio Oso 115kV Line Reinforcement | T.0006067 / T.0006067 | 93 | 93P | Transmission Lines |  | The project will increase system performance and reduce fire ignition risk in Nevada and Placer Counties by performing the following work: • Replace approximately 34.0 miles of conductor on the Drum – Rio Oso #1 and #2 115 kV Lines from structure no. 011/111 to Rio Oso Substation with 477 aluminum conductor steel supported (ACSS); • Upgrade substation terminal equipment to match new conductor rating, if needed; • Replace existing 408 structures with self-weathering tubular steel poles (TSPs) on the Drum – Rio Oso #1 and #2 115 kV Line; • Replace existing 40 structures with self-weathering steel poles on the Brunswick #1 and #2 Tap 115 kV; • Replace existing 4 structures with self-weathering steel poles on the Dutch Flat #2 Tap 115 kV; • Replace existing ceramic insulators on all structures with modern equivalent insulators on the Drum – Rio Oso #1 and #2 115 kV Lines, Brunswick #1 and #2 Tap 115 kV and Dutch Flat #2 Tap 115 kV; • Conduct field verification on the Dutch Flat #2 Tap 115 kV to determine if conductor replacement is needed; • Vegetation Management to provide 100-foot clearance when implementing structure replacement or line reconductoring | 1. Work that Prevents Fire Ignition | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | ETL.1420 | ETL.1420 | Drum-Rio Oso |  |  | 09/02/2026 | 09/29/2026 | 1056 | 795 | 1120 | 3678 | 10000
| 5767631 | (CONT.EST) ELECTRA-VLY SPNGS REL./RECOND | T.0003726 / T.0003726 | 94 | 94L | Reliability |  | This project proposes to reconductor the West Point-Valley Springs 60kV Line between Electra Substation and Valley Springs Substation to provide additional system capability to the area that serves electric customers in Calaveras County. The project scope of work includes the following: • Replace 181 wood poles with Light Duty Steel Poles (LDSP) and composite poles • Reconductor 10.9 miles line section with 715 All Aluminum Conductor (AAC) • Raise existing Tower 7/58 by 10 feet on the Tiger Creek-Valley Springs/Electra-Bellota 230kV • Install one SCADA Line Switch | 1. Work that Prevents Fire Ignition | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | ETL.8350 | ETL.8350 | WEST POINT-VALLEY SPRINGS |  |  | 04/04/2025 | 05/08/2025 | 1108 | 2213 | 1119
| 5778137 | Smartville - Nicolas #1 Conductor Repl | T.0003636 / T.0003636 | 93 | 93C | Transmission Lines |  | Restore Wheatland from the Smartville-Nicolaus #2 60kV line (Close Wheatland SW 65, Open SW 45) OR consider restoring from the Smartville source after isolating trouble, if between Wheatland and East Nicolaus | 1. Work that Prevents Fire Ignition | Tier 2 - Elevated, Tier 1 | ETL.7990 | ETL.7990 | SMARTVILLE-NICOLAUS #1 |  |  | 12/20/2028 | 04/10/2029 | 1132 | 988 | 3403 | 6653 | 4627
Yes - already counted | 5790867 | Fulton-Calistoga 60 kV Line - Conductor | T.0005946 / T.0005946 | 93 | 93P | Transmission Lines |  | An emergency project was recently completed that replaced all of the structures, conductors and associated hardware on the 16.6-mile section of the line from Fulton to St. Helena Junction. This new project will further increase system performance and reduce fire ignition risk in Sonoma and Napa Counties by reconductoring the Fulton-Calistoga 60 kV line from St. Helena Junction up to Middletown Substation and from St. Helena Junction down to Dunbar Substation. | 1. Work that Prevents Fire Ignition | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | ETL.6880 | ETL.6880 | FULTON-CALISTOGA |  |  | 03/01/2022 | 01/31/2023 | 1133 | 1929 | 12437 | 17586 | 19526
| 5767554 | (CONT. EST) ESSEX JCT ORICK RELIABILITY | T.0000451 / T.0000451 | 94 | 94L | Reliability |  | The purpose of this project is to determine the scope of improving reliability on the Essex Junction-Orick 60kV. Essex Junction-Orick 60kV was placed on the list of worst performing circuits. This line is approximately 30 miles long and has a total of 371 structures. This project proposes to do any of the following items that are deemed appropriate by a thorough patrol and inspection: tree trimming, replace insulators, replace bond connectors with AMPACT connectors, bridge all distribution cross arms, reframe structures, secure or replace static ground wires, remove links to shorten jumpers and increase clearance, repair/replace structures, replace quadrant clams, replace vibration dampers, and adjust or replace switches. | 1. Work that Prevents Fire Ignition | Zone 1, Tier 1 | ETL.6810 | ETL.6810 | ESSEX JCT-ORICK |  |  | 03/18/2024 | 09/03/2024 | 1179.8397 | 452.2388 | 10575
Yes - bucket | 5510404 | GO95 Steel N - Low Cond Proj |  | 93 | 93T | Maintenance |  | Bucket placeholder for GO95 compliance on conductors | 5. Compliance / Commitments with Strong Safety Link | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | [7 empty] | 1239.6928 | 1239.6928 | 1240 | 1239.6928 | 1239.6928
| 5790359 | Spaulding-Summit 60 kV | T.0005849 / T.0005849 | 93 | 93P | Transmission Lines |  | The Spaulding – Summit 60 kV Line is located in Placer and Nevada counties. The Line is 19.65 miles long and is supported by 594 non-steel structures and 31 steel structures, a total of 626 structures. 460 of these structures are located in high fire threat districts (HFTD). The project will increase system performance and reduce fire ignition risk in Placer and Nevada counties by performing the following work: • Replace 574 Structures on the Spaulding - Summit 60 kV Line2 • Review 7.86 miles of AAC, ACSR and CU conductor on the Spaulding - Summit 60 kV Line, due to age, to determine if replacement is required • Replace 0.97 miles of ACSR conductor on the Spaulding - Summit 60 kV Line, due to high probability of failure • Replace 0.37 miles of ACSR conductor on the Tap Line between 005/205 and CISCO Grove, due to high probability of failure • Replace 8 switches with SCADA-operable switches on the Spaulding - Summit 60 kV Line • Replace 1 switch with SCADA-operable switch on the CISCO Grove Tap 60 kV Line • Identify any distribution under-build and coordinate with distribution planning • Vegetation Management to provide 80-foot clearance when implementing structure replacement or line reconductoring. | 1. Work that Prevents Fire Ignition | Zone 1, Tier 2 - Elevated, Tier 1 | ETL.8060 | ETL.8060 | SPAULDING-SUMMIT |  |  | 06/26/2025 | 03/23/2026 | 1247 | 661 | 967 | 3274 | 853
| 5789865 | Weimar#1 Conductor Repl Project | T.0005798 / T.0005798 | 93 | 93P | Transmission Lines |  | The Weimar No. 1 60 kV Line is located in Plaecr County. The line is approximately 13.8 miles long and is supported by 210 structures, of which, 208 are in Tier 2 and Tier 3 high fire tier districts (HFTD’s). The project will increase system performance and reduce fire ignition risk in Placer County by performing the following work: • Reconductor the approximately 9 miles of the Weimar No. 1 60 kV Line • Replace at least 157 structures (152 wood & 5 steel poles) 2 • Inspect 4 structures and replace if necessary (000/001, 000/011, 009/143, 009/144) • Replace all insulators on at least 42 pole structures, if all not replaced due to reconductoring • Replace KPF Switch No. 15 on Pole No. 009/143 • Assess remainder of line to ensure safety and compliance • Identify any distribution underbuild and coordinate with distribution planning • Vegetation Management to provide 80-foot clearance when implementing structure replacement or line reconductoring. • Include all open maintenance tags within the project scope where applicable | 1. Work that Prevents Fire Ignition | Tier 3 - Extreme, Tier 2 - Elevated | ETL.7560 | ETL.7560 | WEIMAR #1 |  |  | 05/10/2024 | 12/30/2024 | 1499 | 3197 | 1617 | 85
| 5794382 | MORAGA-CLAREMONT # 1 Line 115 kV | T.0006882 / T.0006882 | 93 | 93P | Transmission Lines |  | MORAGA-CLAREMONT # 1 Line 115 kV | 1. Work that Prevents Fire Ignition | Tier 3 - Extreme | ETL.2700 | ETL.2700 | MORAGA-CLAREMONT |  |  |  |  | 1500 | 1500 | 5000 | 5000 | 5000
| 5794383 | MORAGA-CLAREMONT # 2 Line 115 kV | T.0006882 / T.0006882 | 93 | 93P | Transmission Lines |  | MORAGA-CLAREMONT # 2 Line 115 kV | 1. Work that Prevents Fire Ignition | Tier 3 - Extreme | ETL.2700 | ETL.2700 | MORAGA-CLAREMONT |  |  |  |  | 1500 | 1500 | 5000 | 5000 | 5000
| Tx006487 | Newark-Lawrence Lab - HFTD |  | 93 | 93J | Transmission Lines |  | Newark-Lawrence Lab - HFTD | 1. Work that Prevents Fire Ignition | Tier 2 - Elevated | ETL.3060 | ETL.3060 | NEWARK-LAWRENCE LAB |  |  |  |  | 1500
| 5778199 | STANISLAUS-MELONES ST STA-MANTECA RPL P1 | T.0003638 / T.0003638 | 93 | 93C | Transmission Lines |  | This project proposes to reconductor 13 miles of 2/0 solid CU with the appropriate rated conductor and replace the wood poles with steel as appropriate. The total project cost is estimated at between $15M to $20M based on preliminary cost estimates and benchmark costs for similar work (AACE Class 5). This project has an estimated In Service Date of December, 2021. This project will replace an obsolete conductor that isn’t currently used within PG&E. It will improve circuit resilience, increase operational flexability and refresh asset life to about 90 years. | 1. Work that Prevents Fire Ignition | Tier 2 - Elevated, Tier 1 | ETL.3820 | ETL.3820 | STANISLAUS-MANTECA #2 |  |  | 04/07/2027 | 08/03/2027 | 1536.6613 | 1510.0468 | 11309.4476 | 25895.7809 | 7756.5164
| 5531782 | METCALF-GREEN VLY 115kV: ACQUIRE EASE | T.0004271 / T.0004271 | 60 | 60X | Capacity |  | Improve electric transmission system reliability and operational flexibility in both the Morgan Hill – Gilroy and Santa Cruz – Watsonville areas by upgrading existing transmission facilities. To mitigate these system problems and resolve the customer outage issues and reduce the reliance on local gas-fired generation in the Morgan Hill – Gilroy area, this project will: • Reconductor a portion of the Metcalf – Green Valley 115 kV Line and re-terminate it into the 115 kV bus at Morgan Hill Substation, creating the Morgan Hill-Green Valley 115 kV Line. • Convert the Morgan Hill 115 kV bus to a breaker-and-a-half (BAAH) configuration to improve reliability and operational flexibility. | 8. Compliance/Commitments (But Low Safety Risk) | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | ETL.2540 | ETL.2540 | METCALF-GREEN VALLEY |  |  | 02/14/2025 | 04/27/2026 | 1850
| Tx006588 | Fulton-Ignacio-Lakeville - HFTD |  | 93 | 93J | Transmission Lines |  | Fulton-Ignacio-Lakeville - HFTD | 1. Work that Prevents Fire Ignition | Tier 3 - Extreme | ETL.2823 | ETL.2823 | FULTON-LAKEVILLE-IGNACIO |  |  |  |  | 3000 | 1200
| 5767513 | Monta Vista-Big Basin Sw 19 to Big Basin | T.0000262 / T.0000262 | 94 | 94L | Reliability |  | Address 15 miles of aging infrastructure on the Monta Vista – Burns 60 kV Line located in Tier 2 and 3 fire risk zones in Santa Clara and Santa Cruz Counties between Monta Vista and Big Basin Substations. The work includes the installation, replacement and reframing of poles, vibration dampers and insulators. The project will also address any line maintenance tags that are to be completed at that time, as well as completing the right-of-way (ROW) expansion tree trimming project for the line. During this timeframe the project scope was reduced to the 15-mile section from Monta Vista to Big Basin in order to better address risk mitigation and gain execution efficiencies. | 1. Work that Prevents Fire Ignition | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | ETL.7590 | ETL.7590 | MONTA VISTA-BURNS |  |  | 10/22/2025 | 12/07/2026 | 3501.3533 | 1779 | 9377 | 53
| 5767514 | Monta Vista-Big Basin M.V. Sub to Sw 67 | T.0000262 / T.0000262 | 94 | 94L | Reliability |  | Address 15 miles of aging infrastructure on the Monta Vista – Burns 60 kV Line located in Tier 2 and 3 fire risk zones in Santa Clara and Santa Cruz Counties between Monta Vista and Big Basin Substations. The work includes the installation, replacement and reframing of poles, vibration dampers and insulators. The project will also address any line maintenance tags that are to be completed at that time, as well as completing the right-of-way (ROW) expansion tree trimming project for the line. During this timeframe the project scope was reduced to the 15-mile section from Monta Vista to Big Basin in order to better address risk mitigation and gain execution efficiencies. | 1. Work that Prevents Fire Ignition | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | ETL.7590 | ETL.7590 | MONTA VISTA-BURNS |  |  | 09/24/2025 | 04/21/2026 | 3538 | 10523 | 244
| 5781040 | DEL MONTE - FORT ORD#1 | T.0004114 / T.0004114 | 93 | 93T | Transmission Lines |  | The project will rebuild the 4.2- and 4.1-mile sections of the lines with 397.5 kcmil all-aluminum conductor (AAC) mounted on new LSP’s. Completion of the project will ensure reliable service to the existing 14,200 and future customers served from Fort Ord Substation. The expected in-service date is May 2020. The total project cost for the project is estimated at roughly $8.00M based on preliminary cost estimates (AACE Class 5). | 1. Work that Prevents Fire Ignition | Tier 2 - Elevated, Tier 1 | ETL.8400 | ETL.8400 | DEL MONTE-FORT ORD #1 |  |  | 05/26/2023 | 08/29/2023 | 3597
| 5778198 | Hamilton Branch Chester Conductor Repl | T.0003637 / T.0003637 | 93 | 93C | Transmission Lines |  | Reconductor 4.5 miles of #2 ACSR, 2.2 miles of 2/0 CU, and 1.4 miles of 4/0 ACSR. This conductor fails on average every two years and the local maintenance group has requested that it be reconductored due to the large amount of automatic splices that need to be jumpered out and replaced. These splices were installed during storms in years past by local distribution crews. Automatic splices are not allowed on transmission per our current standards. Due to its close proximity to Lake Almanor, it passes through a fairly high populated resort area along with dense forest. | 1. Work that Prevents Fire Ignition | Tier 2 - Elevated, Tier 1 | ETL.7000 | ETL.7000 | HAMILTON BRANCH-CHESTER |  |  | 04/06/2023 | 01/03/2024 | 5340.199 | 21187.737
| 5788868 | Drum-Rio Oso 115 kV Re-Build (Phase 3) | T.0000036 / T.0000036 | 94 | 94L | Reliability |  | The project proposes to abandon and rebuild the first 11 miles of the 45-mile long Drum-Rio Oso #1 and #2 circuits. Specifically, 241 lattice steel structures and conductors in the current 11 mile tower line (dual tower configuration) will be replaced with a double-circuit 115kV tower line (single tower configuration) using fire resistant, self-weathering steel poles and components, conductors in the centerline of the existing ROW.The project will also widen the existing ROW, where required, as the current ROW is only 70 feet wide. By replacing the existing dual tower configuration with a single, double-circuit tower line and siting them in the existing ROW centerline, the project will eliminate the need for a more rigorous permitting process, avoid costlier ROW land acquisition costs, and provide the new tower line greater clearance distances from the edges of the ROW. | 1. Work that Prevents Fire Ignition | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | ETL.1420 | ETL.1420 | DRUM-RIO OSO #2 |  |  | 09/25/2023 | 02/08/2024 | 5881.1229 | 10984.1526 | 329.5518
| 5767318 | Monta Vista-Big Basin Sw 67 to Sw 19 | T.0000262 / T.0000262 | 94 | 94L | Reliability |  | Address 15 miles of aging infrastructure on the Monta Vista – Burns 60 kV Line located in Tier 2 and 3 fire risk zones in Santa Clara and Santa Cruz Counties between Monta Vista and Big Basin Substations. The work includes the installation, replacement and reframing of poles, vibration dampers and insulators. The project will also address any line maintenance tags that are to be completed at that time, as well as completing the right-of-way (ROW) expansion tree trimming project for the line. During this timeframe the project scope was reduced to the 15-mile section from Monta Vista to Big Basin in order to better address risk mitigation and gain execution efficiencies. | 1. Work that Prevents Fire Ignition | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | ETL.7590 | ETL.7590 | MONTA VISTA-BURNS |  |  | 01/03/2024 | 04/09/2025 | 8535.8576 | 5420
| 5750606 | Temblor-San Luis Obispo 115kV NERC Prj | T.0000423 / T.0000423 | 93 | 93N | NERC Compliance |  | Replace single conductor on 38 miles, retension 8 spans, raise 8 towers via top cage extensions, install 3 interset Tubular Steel Poles, convert 6 suspension towers to dead-ends, replace 2 switches, and modify 64 tower foundations on the Temblor-San Luis Obispo 115kV line to comply with CPUC General Order 95 (GO-95) requirements. | 5. Compliance / Commitments with Strong Safety Link | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | ETL.3960 | ETL.3960 | TEMBLOR-SAN LUIS OBISPO |  |  | 05/10/2023 | 11/14/2023 | 10000 | 16000 | 200
| 5782298 | Martinez Junction to Oleum Substation | T.0004296 / T.0004296 | 93 | 93C | Transmission Lines |  | This project proposes to reconductor three miles of 3/0 and 250 CU from Oleum PP to tower 3/21 at Junction, and reconductor another 1.8 miles of 250 Cu conductor from the junction south to tower 9/53 with a conductor capacity at least 508 Amps summer emergency in order to mitigate the overload for only a few years until the North Tower 115kV loop project will be in service. On July 24, 2016, one end of the copper conductor at Oleum – North Tower – Christie 115 kV Line was found downed on Highway 4. The downed conductor caused a power outage to approximately 25,199 PG&E customers. A fire had ensued due to this event and burned approximately 51 acres of grassland and cattle fence posts. | 1. Work that Prevents Fire Ignition | Tier 2 - Elevated, Tier 1 | ETL.3180 | ETL.3180 | OLEUM-NORTH TOWER-CHRISTIE |  |  | 01/03/2023 | 02/29/2024 | 10144 | 3430
| 5784525 | Drum-Rio Oso 115 kV Re-Build (Phase 2) | T.0000036 / T.0000036 | 94 | 94L | Reliability |  | The project proposes to abandon and rebuild the first 11 miles of the 45-mile long Drum-Rio Oso #1 and #2 circuits. Specifically, 241 lattice steel structures and conductors in the current 11 mile tower line (dual tower configuration) will be replaced with a double-circuit 115kV tower line (single tower configuration) using fire resistant, self-weathering steel poles and components, conductors in the centerline of the existing ROW.The project will also widen the existing ROW, where required, as the current ROW is only 70 feet wide. By replacing the existing dual tower configuration with a single, double-circuit tower line and siting them in the existing ROW centerline, the project will eliminate the need for a more rigorous permitting process, avoid costlier ROW land acquisition costs, and provide the new tower line greater clearance distances from the edges of the ROW. | 1. Work that Prevents Fire Ignition | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | ETL.1430 | ETL.1430 | DRUM-RIO OSO #2 |  |  | 10/03/2022 | 03/07/2023 | 11199.3947 | 49.7498
Yes - already counted | 5792158 | Trinity-Cottonwood 115kV Ph. 4 | T.0000120 / T.0000120 | 93 | 93N | NERC Compliance |  | The project will address the GO-95 clearance issues associated with the Trinity-Cottonwood 115kV line by completing 130 structure replacements and modifications, 21 spans of reconductoring, and 56 discrepancies. Key drivers of the changes in scope and costs are the emergency work resulting from the Carr Fire that reduced the number of structure replacements and modifications, spans of reconductoring, NERC discrepancies on this project, and the resulting re-estimation of the job cost. | 5. Compliance / Commitments with Strong Safety Link | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | ETL.4040 | ETL.4040 | TRINITY-COTTONWOOD |  |  | 07/01/2022 | 11/15/2022 | 11674.336
| 5778135 | OLEUM - G #2 CONDUCTOR REPL (7/50-11/72) | T.0003634 / T.0003634 | 93 | 93C | Transmission Lines |  | Reconductor 9.7 miles of 366 ACSR and 1.3 miles of 250 CU of Oleum-G #1 & #2 115 kV lines. This conductor failed while raising towers for a NERC related project. Subsequent testing performed by PG&E’s ATS department determined that the conductor has deteriorated to the end of the asset life. | 1. Work that Prevents Fire Ignition | Tier 3 - Extreme, Tier 2 - Elevated, Tier 1 | ETL.3160 | ETL.3160 | OLEUM-G #2 |  |  | 05/29/2024 | 01/16/2026 | 11709 | 10986 | 5761 | 35
Yes - bucket | Ex110932 | Conductor replacements |  | 93 | 93C | Transmission Lines |  |  | 1. Work that Prevents Fire Ignition | [8 empty] | 12000
| 5782307 | STANISLAUS-MELONES-MANTECA 115 KV RPL P2 | T.0004301 / T.0004301 | 93 | 93C | Transmission Lines |  | This project proposes to reconductor 99.2 miles of 2/0 7-strand Hemp Core Copper (CU) conductor on the Stanislaus-Melones Sw Sta-Manteca No. 1, Stanislaus-Manteca No. 2, and Stanislaus-Melones Sw Sta-Riverbank Jct Sw Sta 115 kV lines with 715 All Aluminum Conductor (AAC). The total project cost is estimated at between $115 million - $230 million[1] based on preliminary cost estimates (AACE Class 5)[2]. Completion of this project is needed to replace obsolete and failing conductor and to mitigate safety and reliability risks. | 1. Work that Prevents Fire Ignition | Tier 2 - Elevated, Tier 1 | ETL.3830 | ETL.3830 | STANISLAUS-MELONES SW STA-MANTECA #1 |  |  | 06/03/2025 | 11/17/2025 | 21710.1427 | 34177.8719 | 19499.9607 | 3888.4938
Yes - bucket | Ex110975 | (Placeholder - Incremental NERC) |  | 93 | 93N | NERC Compliance |  | Gate funding placeholder | 5. Compliance / Commitments with Strong Safety Link | [8 empty] | 110000