## Distribution
Sap Equipment ID | Circuit Name | Division (Region) | Inspection Review Date | Monitor Review Date | QC Review Date | Inspection Form Prompt | Inspection Form Response | Monitor Team Comments | Agree/Disagree W/FM | QC Spec Disagree Finding | Reference | Comments | QC Actions | Tag update/Creation needed? | Did Insp create/update tag | Compliance Supervisor Referal | Email Notifcation sent?
9.10 REPORT
102010238 | SANTA ROSA LL34 POLES | Sonoma(N) | 2021-06-22 | 2021-08-24 | 2021-12-06 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101981214 | SANTA ROSA LL34 POLES | Sonoma(N) | 2021-06-23 | 2021-08-24 | 2021-12-06 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102010225 | SANTA ROSA LL34 POLES | Sonoma(N) | 2021-06-23 | 2021-08-24 | 2021-12-06 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102010239 | SANTA ROSA LL34 POLES | Sonoma(N) | 2021-06-23 | 2021-08-24 | 2021-12-06 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101981190 | SANTA ROSA LL34 POLES | Sonoma(N) | 2021-06-24 | 2021-08-24 | 2021-12-06 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103957477 | SILVERADO MAP KK42 POLES | North Bay(C) | 2021-06-24 | 2021-08-26 | 2021-12-06 | Other Required Data: 3 or more splices present in one phase of the span | [Answer left blank] | There are 2 phases on the pole. There are 4 splices on the span south of the pole, with 3 splices on the west phase and 1 splice on the east phase. Span does not cross over a major roadway. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103973982 | SILVERADO MAP KK42 POLES | North Bay(C) | 2021-06-24 | 2021-08-26 | 2021-12-06 | Other Required Data: 3 or more splices present in one phase of the span | [Answer left blank] | There are 2 phases on the pole. There are 4 splices on the span north of the pole, with 3 splices on the west phase and 1 splice on the east phase. Span does not cross over a major roadway. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102289595 | SILVERADO MAP KK42 POLES | North Bay(C) | 2021-06-25 | 2021-08-26 | 2021-12-06 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102289628 | SILVERADO MAP KK42 POLES | North Bay(C) | 2021-06-25 | 2021-08-26 | 2021-12-06 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
104012104 | COAST M1322 POLES | Central Coast(S) | 2021-07-01 | 2021-08-17 | 2021-12-06 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101682103 | COAST O1304 POLES | Central Coast(S) | 2021-07-08 | 2021-08-17 | 2021-12-06 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101803094 | COAST K1122 POLES | Central Coast(S) | 2021-07-10 | 2021-08-18 | 2021-12-06 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | High voltage sign is missing. | Disagree | Condition is not compelling | 1. High Voltage Sign Not Installed as Required - TD-2305M-JA02, Rev. 8 - Pg. 61 | The one high sign on the back of the pole satisfies the standard found in OH: Marking, Rev. #18: 11/01/18 022168 Page 3 of 35. Marking, Numbering, and Identification of Line Structures 3. Routine Inspection A. The requirement in 1, “Poles That Support Line Conductors,” must be satisfied with the following exceptions: 1. Sign the Pole: It is acceptable to have only one sign, or stacked pairs of signs, below the lowest line conductor energized above 750 V, except as noted in 4 “Special Locations.” B. The requirements in 2, Poles That Do Not Support Line Conductors,” must be satisfied with the following exceptions: 1. Risers: It is acceptable to have only one sign, or stacked pairs of signs, below risers energized above 750 V. 4. Special Locations: If the pole is signed, high-voltage signs are required on both sides of the pole in the following locations:  Near water areas suitable for sailboats.  Near established boat ramps and associated rigging areas.  Adjacent to swimming pools.  In agricultural areas with movable irrigation piping.  Locations, where in the judgement of the employee, high-voltage signs should be visible from all sides of the poles. | N\A | N\A | N\A | N\A | N\A
100278603 | PENINSULA D0710 POLES | Peninsula(C) | 2021-07-12 | 2021-08-19 | 2021-12-07 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101803085 | COAST K1122 POLES | Central Coast(S) | 2021-07-12 | 2021-08-18 | 2021-12-07 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100475149 | DIABLO D0822 POLES | Diablo(C) | 2021-07-17 | 2021-08-17 | 2021-12-07 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100475056 | DIABLO D0822 POLES | Diablo(C) | 2021-07-19 | 2021-08-17 | 2021-12-07 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100475063 | DIABLO D0822 POLES | Diablo(C) | 2021-07-19 | 2021-08-17 | 2021-12-07 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101679380 | COAST M1321 POLES | Central Coast(S) | 2021-07-19 | 2021-08-17 | 2021-12-07 | Other Required Data: 3 or more splices present in one phase of the span | [Answer left blank] | There are 2 phases on this pole. On the span north of the pole, there are 4 splices on the west phase. Span does not cross over a major roadway. | Agree | N/A | N¦A | Agree there are splices, can't review original inspection record, link is not available in attainment report. | N\A | N\A | N\A | N\A | N\A
101668606 | COAST L1217 POLES | Central Coast(S) | 2021-07-22 | 2021-08-25 | 2021-12-15 | Other Required Data: 3 or more splices present in one phase of the span | [Answer left blank] | There are 2 phases on the pole. There are 12 splices on the span southeast of the pole, with 5 splices on the northeast phase and 7 splices on the southwest phase. Span does not cross over a major roadway. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101800381 | COAST L1217 POLES | Central Coast(S) | 2021-07-22 | 2021-08-25 | 2021-12-15 | Other Required Data: 3 or more splices present in one phase of the span | [Answer left blank] | There are 2 phases on the pole. There are 7 splices on the span southeast of the pole, with 4 splices on the northeast phase and 3 splices on the southwest phase. Span does not cross over a major roadway. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103973756 | COAST L1217 POLES | Central Coast(S) | 2021-07-22 | 2021-08-25 | 2021-12-15 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103973756 | COAST L1217 POLES | Central Coast(S) | 2021-07-22 | 2021-08-25 | 2021-12-15 | Other Required Data: 3 or more splices present in one phase of the span | [Answer left blank] | There are 2 phases on this pole. There are 5 splices on the span southwest of the pole, with 3 splices on the southeast phase and 2 splices on the northwest phase. There are 4 splices on the span northwest of the pole, with 1 splice on the southwest phase and 3 splices on the northeast phase. The monitor team also notes this observation in connection with an adjacent asset(Equipment No. 101668679) Neither span crosses over a major roadway. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102289397 | SILVERADO MAP KK40 POLES | North Bay(C) | 2021-06-05 | 2021-08-25 | 2021-01-21 | Common Equipment/Other Equipment: Does this structure have equipment? | No | There is equipment (non-exempt universal fuses) present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102289397 | SILVERADO MAP KK40 POLES | North Bay(C) | 2021-06-05 | 2021-08-25 | 2021-01-21 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Structure with non-exempt universal fuses has dried ground vegetation within 10' of its base. | Agree | N/A | N¦A |  | Create "Other tag" | Yes | No | Yes | No
102289391 | SILVERADO MAP KK40 POLES | North Bay(C) | 2021-06-07 | 2021-08-25 | 2021-01-21 | Hardware and Framing: Animal mitigation broken, damaged, or missing (if required) | [Answer left blank] | Animal mitigation appears to be loose. | Agree | N/A | N¦A | 121486440 | Update a EC | Yes | No | Yes | No
102289391 | SILVERADO MAP KK40 POLES | North Bay(C) | 2021-06-07 | 2021-08-25 | 2021-01-21 | Other Required Data: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102289274 | SILVERADO MAP KK40 POLES | North Bay(C) | 2021-06-08 | 2021-08-25 | 2021-01-21 | Common Equipment/Other Equipment: Does this structure have equipment? | Yes | The structure does not have equipment. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102289274 | SILVERADO MAP KK40 POLES | North Bay(C) | 2021-06-08 | 2021-08-25 | 2021-01-21 | Hardware and Framing: Select if there are risks, hazards or other maintenance conditions not previously captured in the checklist for Hardware Framing at this location | [Answer left blank] | The center phase insulator bracket appears to be loose, and the pole top to which it is connected appears to be cracked/damaged. | Agree | N/A | N¦A | 121496396 | Update a EC | Yes | No | Yes | No
103916428 | SILVERADO MAP KK40 POLES | North Bay(C) | 2021-06-09 | 2021-08-25 | 2021-01-21 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | Pole number is visible. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102289240 | SILVERADO MAP KK40 POLES | North Bay(C) | 2021-06-10 | 2021-08-25 | 2021-01-21 | Hardware and Framing: Tap clamps installed incorrectly | [Answer left blank] | Tap clamps are not installed on tap guards. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
102289245 | SILVERADO MAP KK40 POLES | North Bay(C) | 2021-06-10 | 2021-08-25 | 2021-01-21 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks along the length of the pole including near where the hardware is attached. | Agree | N/A | N¦A | Condition is already attached to an EC Notification (116755194). Inspector did complete FSR to update Notification but did not indicate condition in Structure section of Inspection Record. | N\A | N\A | N\A | N\A | N\A
102289245 | SILVERADO MAP KK40 POLES | North Bay(C) | 2021-06-10 | 2021-08-25 | 2021-01-21 | Hardware and Framing: Molding missing, broken, damaged, or loose | [Answer left blank] | The molding is damaged and appears to have been burnt. | Agree | N/A | N¦A | Condition is already attached to an EC Notification (116755194). Inspector did complete FSR to update Notification but did not indicate condition in Hardware & Framing section of Inspection Record. | N\A | N\A | N\A | N\A | N\A
102289245 | SILVERADO MAP KK40 POLES | North Bay(C) | 2021-06-10 | 2021-08-25 | 2021-01-21 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | The high voltage sign is partially missing. | Disagree | Condition is not compelling | 1. High Voltage Sign Not Installed as Required - TD-2305M-JA02, Rev. 8 - Pg. 61 | The one high sign on the back of the pole satisfies the standard found in OH: Marking, Rev. #18: 11/01/18 022168 Page 3 of 35. Marking, Numbering, and Identification of Line Structures 3. Routine Inspection A. The requirement in 1, “Poles That Support Line Conductors,” must be satisfied with the following exceptions: 1. Sign the Pole: It is acceptable to have only one sign, or stacked pairs of signs, below the lowest line conductor energized above 750 V, except as noted in 4 “Special Locations.” B. The requirements in 2, Poles That Do Not Support Line Conductors,” must be satisfied with the following exceptions: 1. Risers: It is acceptable to have only one sign, or stacked pairs of signs, below risers energized above 750 V. 4. Special Locations: If the pole is signed, high-voltage signs are required on both sides of the pole in the following locations:  Near water areas suitable for sailboats.  Near established boat ramps and associated rigging areas.  Adjacent to swimming pools.  In agricultural areas with movable irrigation piping.  Locations, where in the judgement of the employee, high-voltage signs should be visible from all sides of the poles. | N\A | N\A | N\A | N\A | N\A
102289735 | SILVERADO MAP LL43 POLES | North Bay(C) | 2021-06-11 | 2021-08-26 | 2021-01-21 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | Pole number is visible. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102289735 | SILVERADO MAP LL43 POLES | North Bay(C) | 2021-06-11 | 2021-08-26 | 2021-01-21 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102289740 | SILVERADO MAP LL43 POLES | North Bay(C) | 2021-06-11 | 2021-08-26 | 2021-01-21 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | Pole number is visible. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102289752 | SILVERADO MAP LL43 POLES | North Bay(C) | 2021-06-11 | 2021-08-26 | 2021-01-21 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | Pole number is visible. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102289757 | SILVERADO MAP LL43 POLES | North Bay(C) | 2021-06-11 | 2021-08-26 | 2021-01-21 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | Pole number is visible. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102289758 | SILVERADO MAP LL43 POLES | North Bay(C) | 2021-06-11 | 2021-08-26 | 2021-01-21 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | Pole number is visible. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102289758 | SILVERADO MAP LL43 POLES | North Bay(C) | 2021-06-11 | 2021-08-26 | 2021-01-21 | Other Required Data: 3 or more splices present in one phase of the span | Energized Phases: 3, Splice Count: (3, 3, 3) for a total of 9 Splices. Span crosses over major roadway: No | The pole has 3 phases. There are 10 splices on the span northwest of the pole, with 3 splices on the southwest phase, 4 splices on the center phase, and 3 splices on the northeast phase. Span does not cross over a major roadway. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102289760 | SILVERADO MAP LL43 POLES | North Bay(C) | 2021-06-11 | 2021-08-26 | 2021-01-24 | Other Required Data: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103119545 | SILVERADO MAP KK40 POLES | North Bay(C) | 2021-06-11 | 2021-08-25 | 2021-01-24 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | Pole number is visible. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103916671 | SILVERADO MAP KK40 POLES | North Bay(C) | 2021-06-11 | 2021-08-25 | 2021-01-24 | PromptPG&E Inspection Form ResponseMonitor Team CommentsNon-Time-Dependent Issues: Guy marker missing, damaged, or broken | [Answer left blank] | The guy marker is no longer attached to the guy. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
103916671 | SILVERADO MAP KK40 POLES | North Bay(C) | 2021-06-11 | 2021-08-25 | 2021-01-24 | Common Equipment/Other Equipment: Does this structure have equipment? | [Answer left blank] | There is equipment (in-line fuses) present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103916777 | SILVERADO MAP KK40 POLES | North Bay(C) | 2021-06-11 | 2021-08-25 | 2021-01-24 | Anchor and Guys: Does or should this location have a Guy? | No | The pole has a guy. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102289864 | SILVERADO MAP LL43 POLES | North Bay(C) | 2021-06-12 | 2021-08-26 | 2021-01-24 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | Pole number is visible. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102289872 | SILVERADO MAP LL43 POLES | North Bay(C) | 2021-06-12 | 2021-08-26 | 2021-01-24 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | Pole number is visible. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102289876 | SILVERADO MAP LL43 POLES | North Bay(C) | 2021-06-12 | 2021-08-26 | 2021-01-24 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | Pole number is visible. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102289876 | SILVERADO MAP LL43 POLES | North Bay(C) | 2021-06-12 | 2021-08-26 | 2021-01-24 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102289881 | SILVERADO MAP LL43 POLES | North Bay(C) | 2021-06-12 | 2021-08-26 | 2021-01-24 | Vegetation: Tree causing strain or abrasion to secondary or service (only 1 service) | [Answer left blank] | Tree limb appears to be causing strain to service conductor. | Agree | N/A | N¦A | 121531408 | Update a EC | Yes | No | Yes | No
102289881 | SILVERADO MAP LL43 POLES | North Bay(C) | 2021-06-12 | 2021-08-26 | 2021-01-24 | Other Required Data: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102289881 | SILVERADO MAP LL43 POLES | North Bay(C) | 2021-06-12 | 2021-08-26 | 2021-01-24 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | Pole number is visible. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102289881 | SILVERADO MAP LL43 POLES | North Bay(C) | 2021-06-12 | 2021-08-26 | 2021-01-24 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102289890 | SILVERADO MAP LL43 POLES | North Bay(C) | 2021-06-12 | 2021-08-26 | 2021-01-24 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | Pole number is visible. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102289890 | SILVERADO MAP LL43 POLES | North Bay(C) | 2021-06-12 | 2021-08-26 | 2021-01-24 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103829332 | SILVERADO MAP LL43 POLES | North Bay(C) | 2021-06-12 | 2021-08-26 | 2021-01-24 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | Pole number is visible. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102289367 | NAPA MAP KK4018 POLES | North Bay(C) | 2021-06-14 | 2021-08-25 | 2021-01-24 | Conductor: Conductor has splices tied in proximity to insulator preventing free movement of splice with conductor | [Answer left blank] | Splices appear to be tied within 2' of insulators. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101981233 | SANTA ROSA LL34 POLES | Sonoma(N) | 2021-06-22 | 2021-08-24 | 2021-01-24 | Hardware and Framing: Animal mitigation broken, damaged, or missing (if required) | [Answer left blank] | Animal mitigation is loose. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101981233 | SANTA ROSA LL34 POLES | Sonoma(N) | 2021-06-22 | 2021-08-24 | 2021-01-24 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102010220 | SANTA ROSA LL34 POLES | Sonoma(N) | 2021-06-22 | 2021-08-24 | 2021-01-24 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks throughout the pole including near where hardware is attached. | Agree | N/A | N¦A | 111635053 | Update a EC | Yes | No | Yes | No
102010220 | SANTA ROSA LL34 POLES | Sonoma(N) | 2021-06-22 | 2021-08-24 | 2021-01-24 | Common Equipment/Other Equipment: Transformer flashed or corroded, e.g. integrity of the metal is breached – holes in metal, cover not securable, metal is damaged, separation, layering, bulging or bubbling | [Answer left blank] | The transformer appears to be corroded. | Agree | N/A | N¦A | 111635053 | Update a EC | Yes | No | Yes | No
102010220 | SANTA ROSA LL34 POLES | Sonoma(N) | 2021-06-22 | 2021-08-24 | 2021-01-24 | Common Equipment/Other Equipment: IFD (aka "Turkey Popper") has activated on the transformer (orange band is visible) | [Answer left blank] | Transformer IFD has activated. | Agree | N/A | N¦A | 111635053 | Update a EC | Yes | No | Yes | No
102010220 | SANTA ROSA LL34 POLES | Sonoma(N) | 2021-06-22 | 2021-08-24 | 2021-01-24 | Anchor and Guys: Necessary guys missing or loose | [Answer left blank] | Two communications guys are loose. | Agree | N/A | N¦A |  | Create "Other tag" | Yes | No | Yes | No
102010220 | SANTA ROSA LL34 POLES | Sonoma(N) | 2021-06-22 | 2021-08-24 | 2021-01-24 | Anchor and Guys: Guy wire broken, damaged, clearance issues, corroded, covered by vegetation, overgrown, strain or abrasion | [Answer left blank] | A tree appears to be causing strain on one of the communications guys. | Agree | N/A | N¦A |  | Create "Other tag" | Yes | No | Yes | No
102010220 | SANTA ROSA LL34 POLES | Sonoma(N) | 2021-06-22 | 2021-08-24 | 2021-01-24 | Hardware and Framing: Tap clamps installed incorrectly | [Answer left blank] | Tap clamps are not installed on tap guards. | Agree | N/A | N¦A | 111635053 | Update a EC | Yes | No | Yes | No
102010220 | SANTA ROSA LL34 POLES | Sonoma(N) | 2021-06-22 | 2021-08-24 | 2021-01-24 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | Open wire secondary is present at this location. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101981194 | SANTA ROSA LL34 POLES | Sonoma(N) | 2021-06-23 | 2021-08-24 | 2021-01-24 | Non-Time-Dependent Issues: Visibility strips missing, broken, mismatched, or no longer reflective | [Answer left blank] | One of the visibility strips is missing. | Agree | N/A | N¦A | 119170990 | Update a EC | Yes | No | Yes | No
101981234 | SANTA ROSA LL34 POLES | Sonoma(N) | 2021-06-23 | 2021-08-24 | 2021-01-24 | Hardware and Framing: Secondary connectors (mini wedge and Insulink) installed on primary conductor | [Answer left blank] | Insulink connectors are installed on primary jumpers. | Agree | N/A | N¦A | Condition is already attached to an EC Notification (117023802). Inspector did complete FSR to update Notification but did not indicate condition in Hardware & Framing section of Inspection Record. | N\A | N\A | N\A | N\A | N\A
102010469 | SANTA ROSA LL34 POLES | Sonoma(N) | 2021-06-23 | 2021-08-24 | 2021-01-24 | Vegetation: Tree causing strain or abrasion to secondary or service (only 1 service) | [Answer left blank] | Vegetation appears to be causing strain to the service conductor. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
103600818 | SANTA ROSA LL34 POLES | Sonoma(N) | 2021-06-23 | 2021-08-24 | 2021-01-24 | Non-Time-Dependent Issues: Visibility strips missing, broken, mismatched, or no longer reflective | [Answer left blank] | Visibility strips are partially detached. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101981187 | SANTA ROSA LL34 POLES | Sonoma(N) | 2021-06-24 | 2021-08-24 | 2021-01-24 | Non-Time-Dependent Issues: Pole steps are less than 8' 6" above the ground or any other accessible surface | [Answer left blank] | Pole step is at 7' 10" (94"). | Agree | N/A | N¦A | 119126863 | Update a EC | Yes | No | Yes | No
101981187 | SANTA ROSA LL34 POLES | Sonoma(N) | 2021-06-24 | 2021-08-24 | 2021-01-24 | Other Required Data: Tree anchor installed in tree by design | [Answer left blank] | There appears to be a tree anchor installed in tree by design. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101981226 | SANTA ROSA LL34 POLES | Sonoma(N) | 2021-06-24 | 2021-08-24 | 2021-01-24 | Anchor and Guys: Guy wire broken, damaged, clearance issues, corroded, covered by vegetation, overgrown, strain or abrasion | [Answer left blank] | Vegetation appears to be in contact with guy wire above the guy insulator. | Agree | N/A | N¦A | Condition is already attached to an EC Notification (117025790). Inspector did complete FSR to update Notification but did not indicate condition in Anchor & Guy section of Inspection Record. | N\A | N\A | N\A | N\A | N\A
101995551 | SANTA ROSA LL34 POLES | Sonoma(N) | 2021-06-24 | 2021-08-24 | 2021-01-24 | Structure: Pole leaning or out of plumb by more than 10% of its height above the ground | [Answer left blank] | Insulink connectors are installed on primary jumpers. | Agree | N/A | N¦A | Condition is already attached to an EC Notification (117017097). Inspector did complete FSR to update Notification but did not indicate condition in Hardware & Framing section of Inspection Record. | N\A | N\A | N\A | N\A | N\A
101995551 | SANTA ROSA LL34 POLES | Sonoma(N) | 2021-06-24 | 2021-08-24 | 2021-01-24 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102289681 | SILVERADO MAP KK42 POLES | North Bay(C) | 2021-06-24 | 2021-08-26 | 2021-01-24 | Conductor: Primary or secondary conductor has diminished clearance mid span or uneven conductor sag | [Answer left blank] | The primary conductor running north across the field appears to have uneven sag. | Agree | N/A | N¦A | 121605506 | Update a EC | Yes | No | Yes | No
102289681 | SILVERADO MAP KK42 POLES | North Bay(C) | 2021-06-24 | 2021-08-26 | 2021-01-24 | Anchor and Guys: Guy wire broken, damaged, clearance issues, corroded, covered by vegetation, overgrown, strain or abrasion | [Answer left blank] | Vegetation appears to be in contact with the guy wire above the guy insulator. | Agree | N/A | N¦A | 121605506 | Update a EC | Yes | No | Yes | No
102289681 | SILVERADO MAP KK42 POLES | North Bay(C) | 2021-06-24 | 2021-08-26 | 2021-01-24 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | Pole number is visible. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102290228 | SILVERADO MAP KK42 POLES | North Bay(C) | 2021-06-24 | 2021-08-26 | 2021-01-24 | Common Equipment/Other Equipment: Transformer shows signs of leaking, seeping, or weeping oil | [Answer left blank] | Transformer appears to show signs of seeping oil, as oil stains are present. | Agree | N/A | N¦A | 121591830 | Update a EC | Yes | No | Yes | No
102289606 | SILVERADO MAP KK42 POLES | North Bay(C) | 2021-06-25 | 2021-08-26 | 2021-01-24 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | Pole number is visible. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102289606 | SILVERADO MAP KK42 POLES | North Bay(C) | 2021-06-25 | 2021-08-26 | 2021-01-24 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102289676 | SILVERADO MAP KK42 POLES | North Bay(C) | 2021-06-25 | 2021-08-26 | 2021-01-24 | Hardware and Framing: Crossarm integrity compromised by any of the following; damaged, broken, burnt, decayed, rotten, loose, missing hardware or showing severe signs of bent bolts or brackets, damaged bracing, gun shots, insect damage or woodpecker damage, splitting, or fails to meet clearance requirements | [Answer left blank] | There appears to be uneven tension on the insulators, causing the crossarm to twist and bow. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
102289921 | SILVERADO MAP KK42 POLES | North Bay(C) | 2021-06-25 | 2021-08-26 | 2021-01-24 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | Pole number is visible. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102289934 | SILVERADO MAP KK42 POLES | North Bay(C) | 2021-06-25 | 2021-08-26 | 2021-01-24 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | Pole number is visible. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
104015288 | SILVERADO MAP KK42 POLES | North Bay(C) | 2021-06-25 | 2021-08-26 | 2021-01-24 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | Pole number is visible. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100566280 | SAN JOSE F2022 POLES | San Jose(S) | 2021-07-01 | 2021-08-19 | 2021-01-24 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks and signs of decay throughout the pole, including at the top near where hardware is attached. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100566280 | SAN JOSE F2022 POLES | San Jose(S) | 2021-07-01 | 2021-08-19 | 2021-01-24 | Anchor and Guys: Guy wire broken, damaged, clearance issues, corroded, covered by vegetation, overgrown, strain or abrasion | [Answer left blank] | Vegetation is in contact with down guy above the guy insulator. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100566280 | SAN JOSE F2022 POLES | San Jose(S) | 2021-07-01 | 2021-08-19 | 2021-01-24 | Hardware and Framing: Crossarm integrity compromised by any of the following; damaged, broken, burnt, decayed, rotten, loose, missing hardware or showing severe signs of bent bolts or brackets, damaged bracing, gun shots, insect damage or woodpecker damage, splitting, or fails to meet clearance requirements | [Answer left blank] | The crossarm appears to be splitting, and the hardware appears to be loose. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100566282 | SAN JOSE F2022 POLES | San Jose(S) | 2021-07-01 | 2021-08-19 | 2021-01-25 | Conductor: Conductor has splices tied in proximity to insulator preventing free movement of splice with conductor | [Answer left blank] | A splice appears to be tied within 2' of an insulator. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100566282 | SAN JOSE F2022 POLES | San Jose(S) | 2021-07-01 | 2021-08-19 | 2021-01-25 | Hardware and Framing: Crossarm integrity compromised by any of the following; damaged, broken, burnt, decayed, rotten, loose, missing hardware or showing severe signs of bent bolts or brackets, damaged bracing, gun shots, insect damage or woodpecker damage, splitting, or fails to meet clearance requirements | [Answer left blank] | The top crossarm appears to be cracked/decayed on the west (roadside) phase. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100566282 | SAN JOSE F2022 POLES | San Jose(S) | 2021-07-01 | 2021-08-19 | 2021-01-25 | Hardware and Framing: Molding missing, broken, damaged, or loose | [Answer left blank] | Molding is broken approximately 12' above ground level. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100566282 | SAN JOSE F2022 POLES | San Jose(S) | 2021-07-01 | 2021-08-19 | 2021-01-25 | Hardware and Framing: Grounds exposed, broken, damaged, disconnected, unsecured, or missing (if required) | [Answer left blank] | Molding is broken approximately 12' above ground level, exposing approximately 6" of ground wire. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100566282 | SAN JOSE F2022 POLES | San Jose(S) | 2021-07-01 | 2021-08-19 | 2021-01-25 | Non-Time-Dependent Issues: Pole steps are less than 8' 6" above the ground or any other accessible surface | [Answer left blank] | Pole step is at 7' 6" (90"). | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100566283 | SAN JOSE F2022 POLES | San Jose(S) | 2021-07-01 | 2021-08-19 | 2021-01-25 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks in the top third of the pole, including near where the hardware is attached. | Disagree | N/A | N¦A | Pole appears to have normal cracks and splits due to weather and ageing of pole. | N\A | N\A | N\A | N\A | N\A
100566284 | SAN JOSE F2022 POLES | San Jose(S) | 2021-07-01 | 2021-08-19 | 2021-01-25 | Hardware and Framing: Molding missing, broken, damaged, or loose | [Answer left blank] | Molding is broken (i) approximately 8' from the ground, exposing approximately 2" of ground wire; and (ii) at the communications level, exposing approximately 8" of ground wire. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100566284 | SAN JOSE F2022 POLES | San Jose(S) | 2021-07-01 | 2021-08-19 | 2021-01-25 | Hardware and Framing: Grounds exposed, broken, damaged, disconnected, unsecured, or missing (if required) | [Answer left blank] | Molding is broken (i) approximately 8' from the ground, exposing approximately 2" of ground wire; and (ii) at the communications level, exposing approximately 8" of ground wire. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100566285 | SAN JOSE F2022 POLES | San Jose(S) | 2021-07-01 | 2021-08-19 | 2021-01-25 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks in the pole near where hardware is attached. The pole also is damaged at its base. | Disagree | N/A | N¦A | Pole appears to have normal cracks and splits due to weather and ageing of pole. | N\A | N\A | N\A | N\A | N\A
100566285 | SAN JOSE F2022 POLES | San Jose(S) | 2021-07-01 | 2021-08-19 | 2021-01-25 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | High voltage sign is missing from one side of the pole. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100566285 | SAN JOSE F2022 POLES | San Jose(S) | 2021-07-01 | 2021-08-19 | 2021-01-25 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100566286 | SAN JOSE F2022 POLES | San Jose(S) | 2021-07-01 | 2021-08-19 | 2021-01-25 | Anchor and Guys: Anchor rod broken, damaged, corroded, covered by vegetation/overgrown, soil-eroded, graded, or buried | [Answer left blank] | The anchor rod is buried. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100566288 | SAN JOSE F2022 POLES | San Jose(S) | 2021-07-01 | 2021-08-19 | 2021-01-25 | Hardware and Framing: Molding missing, broken, damaged, or loose | [Answer left blank] | Molding is broken at 7' 11" above ground level, exposing 2" of ground wire. There is also exposed ground wire at the communications level. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | Yes
100566288 | SAN JOSE F2022 POLES | San Jose(S) | 2021-07-01 | 2021-08-19 | 2021-01-25 | Hardware and Framing: Grounds exposed, broken, damaged, disconnected, unsecured, or missing (if required) | [Answer left blank] | Molding is broken at 7' 11" above ground level, exposing 2" of ground wire. There is also exposed ground wire at the communications level. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100566288 | SAN JOSE F2022 POLES | San Jose(S) | 2021-07-01 | 2021-08-19 | 2021-01-25 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100566290 | SAN JOSE F2022 POLES | San Jose(S) | 2021-07-01 | 2021-08-19 | 2021-01-25 | Conductor: Does this structure have PG&E owned conductor? | Yes | There is no conductor present on this structure. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100566291 | SAN JOSE F2022 POLES | San Jose(S) | 2021-07-01 | 2021-08-19 | 2021-01-25 | Conductor: Conductor has splices tied in proximity to insulator preventing free movement of splice with conductor | [Answer left blank] | A splice appears to be tied within 2' of an insulator. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100566291 | SAN JOSE F2022 POLES | San Jose(S) | 2021-07-01 | 2021-08-19 | 2021-01-25 | Anchor and Guys: Guy wire broken, damaged, clearance issues, corroded, covered by vegetation, overgrown, strain or abrasion | [Answer left blank] | Vegetation appears to be causing strain on the down guy. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100566291 | SAN JOSE F2022 POLES | San Jose(S) | 2021-07-01 | 2021-08-19 | 2021-01-25 | Anchor and Guys: Anchor rod broken, damaged, corroded, covered by vegetation/overgrown, soil-eroded, graded, or buried | [Answer left blank] | The anchor rod is buried. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100566291 | SAN JOSE F2022 POLES | San Jose(S) | 2021-07-01 | 2021-08-19 | 2021-01-25 | Hardware and Framing: Animal mitigation broken, damaged, or missing (if required) | [Answer left blank] | Animal mitigation is loose on one of the transformer bushings. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100566291 | SAN JOSE F2022 POLES | San Jose(S) | 2021-07-01 | 2021-08-19 | 2021-01-25 | Non-Time-Dependent Issues: Pole steps are less than 8' 6" above the ground or any other accessible surface | [Answer left blank] | Pole step is at 7' 2" (86"). | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100566298 | SAN JOSE F2022 POLES | San Jose(S) | 2021-07-01 | 2021-08-19 | 2021-01-25 | Conductor: Conductor has splices tied in proximity to insulator preventing free movement of splice with conductor | [Answer left blank] | Splices appear to be tied within 2' of insulators. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100566298 | SAN JOSE F2022 POLES | San Jose(S) | 2021-07-01 | 2021-08-19 | 2021-01-25 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Structure with non-exempt universal fuses has dried vegetation within 10' of its base. | Agree | N/A | N¦A |  | Create "Other tag" | Yes | No | Yes | No
100566298 | SAN JOSE F2022 POLES | San Jose(S) | 2021-07-01 | 2021-08-19 | 2021-01-25 | Non-Time-Dependent Issues: Pole steps are less than 8' 6" above the ground or any other accessible surface | [Answer left blank] | Pole step is at 7' 7" (91"). | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100566298 | SAN JOSE F2022 POLES | San Jose(S) | 2021-07-01 | 2021-08-19 | 2021-01-25 | Other Required Data: Is there non-exempt equipment at the inspection location (Universal or Open Link Fuse) | [Answer left blank] | Non-exempt universal fuses are present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100566307 | SAN JOSE F2022 POLES | San Jose(S) | 2021-07-01 | 2021-08-19 | 2021-01-25 | Conductor: Conductor has splices tied in proximity to insulator preventing free movement of splice with conductor | [Answer left blank] | A splice appears to be tied within 2' of an insulator. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100566307 | SAN JOSE F2022 POLES | San Jose(S) | 2021-07-01 | 2021-08-19 | 2021-01-25 | Anchor and Guys: Guy wire broken, damaged, clearance issues, corroded, covered by vegetation, overgrown, strain or abrasion | [Answer left blank] | There appears to be vegetation in contact with guy above the guy insulator. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100566307 | SAN JOSE F2022 POLES | San Jose(S) | 2021-07-01 | 2021-08-19 | 2021-01-25 | Other Required Data: Support structure or stub present. | [Answer left blank] | Pole has existing pole-top extension. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100566309 | SAN JOSE F2022 POLES | San Jose(S) | 2021-07-01 | 2021-08-19 | 2021-01-26 | Common Equipment/Other Equipment: Does this structure have equipment? | No | There is equipment (universal fuses and solid blade disconnects) present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100566309 | SAN JOSE F2022 POLES | San Jose(S) | 2021-07-01 | 2021-08-19 | 2021-01-26 | Anchor and Guys: Necessary guys missing or loose | [Answer left blank] | Down guy and overhead guy are loose. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100566309 | SAN JOSE F2022 POLES | San Jose(S) | 2021-07-01 | 2021-08-19 | 2021-01-26 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Structure with non-exempt universal fuses and solid blade disconnects has dried ground vegetation within 10' of its base. | Agree | N/A | N¦A |  | Create "Other tag" | Yes | No | Yes | No
100566309 | SAN JOSE F2022 POLES | San Jose(S) | 2021-07-01 | 2021-08-19 | 2021-01-26 | Other Required Data: Is there non-exempt equipment at the inspection location (Universal or Open Link Fuse) | No | Non-exempt universal fuses are present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100566309 | SAN JOSE F2022 POLES | San Jose(S) | 2021-07-01 | 2021-08-19 | 2021-01-26 | Other Required Data: Is there non-exempt equipment at the inspection location (Solid Blade or In-line disconnect) | [Answer left blank] | Non-exempt solid blade disconnects are present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101803211 | COAST M1322 POLES | Central Coast(S) | 2021-07-01 | 2021-08-17 | 2021-01-26 | Non-Time-Dependent Issues: Pole steps are less than 8' 6" above the ground or any other accessible surface | [Answer left blank] | Pole step is at 8' 5" (101"). | Agree | N/A | N¦A | 116709831 | Update a EC | Yes | No | Yes | No
101803211 | COAST M1322 POLES | Central Coast(S) | 2021-07-01 | 2021-08-17 | 2021-01-26 | Other Required Data: Tree anchor installed in tree by design | Yes | There is no tree anchor present. There is a tree connect running a secondary conductor next to a garage. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101803211 | COAST M1322 POLES | Central Coast(S) | 2021-07-01 | 2021-08-17 | 2021-01-26 | Other Required Data: 3 or more splices present in one phase of the span | [Answer left blank] | There are 2 phases on this pole. On the span south of the pole, there are 3 splices on the west phase. Span does not cross over a major roadway. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101684499 | COAST O1501 POLES | Central Coast(S) | 2021-07-02 | 2021-08-24 | 2021-01-26 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Structure with a non-exempt universal fuse has dried ground vegetation within 10' of its base. | Agree | N/A | N¦A |  | Create "Other tag" | Yes | No | Yes | No
101684499 | COAST O1501 POLES | Central Coast(S) | 2021-07-02 | 2021-08-24 | 2021-01-26 | Vegetation: Support Structure with non-exempt equipment, has dried vegetation (dead branches) above 8' to top of conductors, within 10' radius of Support Structure | [Answer left blank] | Structure with a non-exempt universal fuse has dried vegetation within a 10' radius of the structure, near its midsection. | Disagree | N/A | ELEC-1000 Training | Attached photos by Federal Monitor show tree limbs appearing to be green and healthy above 8' from the ground level. REF 2021 California Power Line Fire Prevention Field Guide pg. 37 | N\A | N\A | N\A | N\A | N\A
101684499 | COAST O1501 POLES | Central Coast(S) | 2021-07-02 | 2021-08-24 | 2021-01-26 | Other Required Data: Is there non-exempt equipment at the inspection location (Universal or Open Link Fuse) | [Answer left blank] | Non-exempt universal fuse is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101684499 | COAST O1501 POLES | Central Coast(S) | 2021-07-02 | 2021-08-24 | 2021-01-26 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101684504 | COAST O1501 POLES | Central Coast(S) | 2021-07-02 | 2021-08-24 | 2021-01-26 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks in the pole near where hardware is attached. | Agree | N/A | N¦A | 119236090 | Update a EC | Yes | No | Yes | No
101684504 | COAST O1501 POLES | Central Coast(S) | 2021-07-02 | 2021-08-24 | 2021-01-26 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | Open wire secondary is present at this location. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101798469 | COAST O1501 POLES | Central Coast(S) | 2021-07-02 | 2021-08-24 | 2021-01-26 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | Open wire secondary is present at this location. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101668583 | COAST L1212 POLES | Central Coast(S) | 2021-07-03 | 2021-08-25 | 2021-01-26 | Vegetation: Tree causing strain or abrasion to secondary or service (2 or more services) | [Answer left blank] | Vegetation appears to be causing strain on a service conductor north of the pole. | Agree | N/A | N¦A | 121661716 | Update a EC | Yes | No | Yes | No
101668583 | COAST L1212 POLES | Central Coast(S) | 2021-07-03 | 2021-08-25 | 2021-01-26 | Other Required Data: Tree anchor installed in tree by design | [Answer left blank] | There appears to be a tree anchor installed in tree by design. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101668584 | COAST L1212 POLES | Central Coast(S) | 2021-07-03 | 2021-08-25 | 2021-01-26 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101668584 | COAST L1212 POLES | Central Coast(S) | 2021-07-03 | 2021-08-25 | 2021-01-26 | Other Required Data: Tree anchor installed in tree by design | [Answer left blank] | There appears to be a tree anchor installed in tree by design. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101668584 | COAST L1212 POLES | Central Coast(S) | 2021-07-03 | 2021-08-25 | 2021-01-26 | Other Required Data: 3 or more splices present in one phase of the span | [Answer left blank] | There are 2 phases on this pole. There are 11 splices on the span south of the pole, with 4 splices on the west phase and 7 splices on the east phase. Span does not cross over a major roadway.The Monitor team also notes this observation in connection with an adjacent asset (Equipment No. 103416832) | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101668604 | COAST L1212 POLES | Central Coast(S) | 2021-07-03 | 2021-08-25 | 2021-01-26 | Common Equipment/Other Equipment: Transformer shows signs of leaking, seeping, or weeping oil | [Answer left blank] | Transformer appears to show signs of seeping oil, as oil stains are present. | Agree | N/A | N¦A | 116793140 | Update a EC | Yes | No | Yes | No
101668604 | COAST L1212 POLES | Central Coast(S) | 2021-07-03 | 2021-08-25 | 2021-01-26 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101684505 | COAST O1501 POLES | Central Coast(S) | 2021-07-03 | 2021-08-24 | 2021-01-26 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | Open wire secondary is present at this location. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101684506 | COAST O1501 POLES | Central Coast(S) | 2021-07-03 | 2021-08-24 | 2021-01-26 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks in the pole near where the hardware is attached and there is a woodpecker hole that appears to be larger than 4". | Agree | N/A | N¦A | 119301187 | Update a EC | Yes | No | Yes | No
101684506 | COAST O1501 POLES | Central Coast(S) | 2021-07-03 | 2021-08-24 | 2021-01-26 | Common Equipment/Other Equipment: Obvious paralleled transformer condition at this location | [Answer left blank] | There appears to be a paralleled transformer condition, with a paralleled transformer two spans north of the structure. | Agree | N/A | N¦A | 119301187 | Update a EC | Yes | No | Yes | No
101684506 | COAST O1501 POLES | Central Coast(S) | 2021-07-03 | 2021-08-24 | 2021-01-26 | Vegetation: Tree causing strain or abrasion to secondary or service (2 or more services) | [Answer left blank] | Vegetation appears to be causing strain on the secondary conductor. | Agree | N/A | N¦A |  | Create "Other tag" | Yes | No | Yes | No
101684506 | COAST O1501 POLES | Central Coast(S) | 2021-07-03 | 2021-08-24 | 2021-01-26 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | Open wire secondary is present at this location. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101684517 | COAST O1501 POLES | Central Coast(S) | 2021-07-03 | 2021-08-24 | 2021-01-26 | Anchor and Guys: Does or should this location have a Guy? | No | A span guy is present at this location. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101684517 | COAST O1501 POLES | Central Coast(S) | 2021-07-03 | 2021-08-24 | 2021-01-26 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | Open wire secondary is present at this location. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101798464 | COAST O1501 POLES | Central Coast(S) | 2021-07-03 | 2021-08-24 | 2021-01-26 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | Open wire secondary is present at this location. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101798464 | COAST O1501 POLES | Central Coast(S) | 2021-07-03 | 2021-08-24 | 2021-01-26 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | Pole number is visible. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103416832 | COAST L1212 POLES | Central Coast(S) | 2021-07-03 | 2021-08-25 | 2021-01-26 | Conductor: Conductor has splices tied in proximity to insulator preventing free movement of splice with conductor | [Answer left blank] | A splice appears to be tied within 2' of an insulator. | Agree | N/A | N¦A | 122377746 | Update a EC | Yes | No | Yes | No
103416832 | COAST L1212 POLES | Central Coast(S) | 2021-07-03 | 2021-08-25 | 2021-01-26 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103416832 | COAST L1212 POLES | Central Coast(S) | 2021-07-03 | 2021-08-25 | 2021-01-26 | Other Required Data: Tree anchor installed in tree by design | [Answer left blank] | There appears to be a tree anchor installed in tree by design. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103416832 | COAST L1212 POLES | Central Coast(S) | 2021-07-03 | 2021-08-25 | 2021-01-26 | Other Required Data: 3 or more splices present in one phase of the span | [Answer left blank] | There are 2 phases on this pole. There are 11 splices on the span north of the pole, with 4 splices on the west phase and 7 splices on the east phase. Span does not cross over a major roadway.The Monitor team also notes this observation in connection with an adjacent asset (Equipment No. 101668584). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101684510 | COAST O1501 POLES | Central Coast(S) | 2021-07-05 | 2021-08-24 | 2021-01-26 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks throughout the pole including near where the hardware is attached. | Agree | N/A | N¦A | 119290274 | Update a EC | Yes | No | Yes | No
101684510 | COAST O1501 POLES | Central Coast(S) | 2021-07-05 | 2021-08-24 | 2021-01-26 | Common Equipment/Other Equipment: Obvious paralleled transformer condition at this location | [Answer left blank] | There appears to be a paralleled transformer condition, with a paralleled transformer two spans southeast of the structure. | Agree | N/A | N¦A | Condition is already attached to an EC Notification (119290274). Inspector did complete FSR to update Notification but did not indicate condition in Equipment section of Inspection Record. | Update a EC | Yes | No | Yes | No
101684510 | COAST O1501 POLES | Central Coast(S) | 2021-07-05 | 2021-08-24 | 2021-01-26 | Hardware and Framing: Crossarm integrity compromised by any of the following; damaged, broken, burnt, decayed, rotten, loose, missing hardware or showing severe signs of bent bolts or brackets, damaged bracing, gun shots, insect damage or woodpecker damage, splitting, or fails to meet clearance requirements | [Answer left blank] | There is cracking in the primary crossarm near where the hardware is attached. | Agree | N/A | N¦A | 119290274 | Update a EC | Yes | No | Yes | No
101684510 | COAST O1501 POLES | Central Coast(S) | 2021-07-05 | 2021-08-24 | 2021-01-26 | Hardware and Framing: Molding missing, broken, damaged, or loose | [Answer left blank] | There is a half-inch break in the molding at 7'4" above the ground. There is also a gap of approximately 4" at the communications level. | Agree | N/A | N¦A | 119290274 | Update a EC | Yes | No | Yes | Yes
101684510 | COAST O1501 POLES | Central Coast(S) | 2021-07-05 | 2021-08-24 | 2021-01-26 | Hardware and Framing: Grounds exposed, broken, damaged, disconnected, unsecured, or missing (if required) | [Answer left blank] | There is a half-inch section of exposed ground wire 7'4" above the ground. There is also approximately 4" of exposed ground wire at the communications level. | Agree | N/A | N¦A | 119290274 | Update a EC | Yes | No | Yes | Yes
101684510 | COAST O1501 POLES | Central Coast(S) | 2021-07-05 | 2021-08-24 | 2021-01-26 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101684510 | COAST O1501 POLES | Central Coast(S) | 2021-07-05 | 2021-08-24 | 2021-01-26 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | Open wire secondary is present at this location. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101684513 | COAST O1501 POLES | Central Coast(S) | 2021-07-05 | 2021-08-24 | 2021-01-26 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | Open wire secondary is present at this location. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101684519 | COAST O1501 POLES | Central Coast(S) | 2021-07-05 | 2021-08-24 | 2021-01-26 | Conductor: Primary, secondary, and/or service conductors broken, damaged, burnt, corroded, loose, frayed or bird caging | [Answer left blank] | The primary conductor southwest of the pole is bird caging near midspan. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101684519 | COAST O1501 POLES | Central Coast(S) | 2021-07-05 | 2021-08-24 | 2021-01-26 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | Pole number is visible. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101684519 | COAST O1501 POLES | Central Coast(S) | 2021-07-05 | 2021-08-24 | 2021-01-26 | Other Required Data: 3 or more splices present in one phase of the span | [Answer left blank] | There are 2 phases on the pole. There are 6 splices on the span east of the pole, with 3 splices on the north phase and 3 splices on the south phase. There are 7 splices on the span southwest of the pole, with 4 splices on the southeast (top) phase and 3 splices on the northwest (bottom) phase. Neither span crosses over a major roadway. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101684532 | COAST O1501 POLES | Central Coast(S) | 2021-07-05 | 2021-08-24 | 2021-01-26 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101684532 | COAST O1501 POLES | Central Coast(S) | 2021-07-05 | 2021-08-24 | 2021-01-26 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | Open wire secondary (to street light) is present at this location. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101684533 | COAST O1501 POLES | Central Coast(S) | 2021-07-05 | 2021-08-24 | 2021-01-26 | Common Equipment/Other Equipment: Obvious paralleled transformer condition at this location | [Answer left blank] | There appears to be a paralleled transformer condition. | Agree | N/A | N¦A | Condition is already attached to an EC Notification (119303549). Inspector did complete FSR to update Notification but did not indicate condition in Equipment section of Inspection Record. | Update a EC | Yes | No | Yes | No
101684533 | COAST O1501 POLES | Central Coast(S) | 2021-07-05 | 2021-08-24 | 2021-01-26 | Anchor and Guys: Does or should this location have a Guy? | [Answer left blank] | There is a span guy supporting the adjacent asset. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101684533 | COAST O1501 POLES | Central Coast(S) | 2021-07-05 | 2021-08-24 | 2021-01-26 | Hardware and Framing: Molding missing, broken, damaged, or loose | [Answer left blank] | There is a small crack in the molding approximately 15" above the ground. | Agree | N/A | N¦A | 119303549 | Update a EC | Yes | No | Yes | No
101684533 | COAST O1501 POLES | Central Coast(S) | 2021-07-05 | 2021-08-24 | 2021-01-26 | Hardware and Framing: Grounds exposed, broken, damaged, disconnected, unsecured, or missing (if required) | [Answer left blank] | There is a small portion of exposed ground wire approximately 15" above the ground. | Agree | N/A | N¦A | 119303549 | Update a EC | Yes | No | Yes | No
101684533 | COAST O1501 POLES | Central Coast(S) | 2021-07-05 | 2021-08-24 | 2021-01-26 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101684533 | COAST O1501 POLES | Central Coast(S) | 2021-07-05 | 2021-08-24 | 2021-01-26 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | Open wire secondary is present at this location. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101797908 | COAST O1501 POLES | Central Coast(S) | 2021-07-05 | 2021-08-24 | 2021-01-27 | Anchor and Guys: Guy wire broken, damaged, clearance issues, corroded, covered by vegetation, overgrown, strain or abrasion | [Answer left blank] | Vegetation appears to be in contact with the guy wire above the guy insulator. | Agree | N/A | N¦A | Condition is already attached to an EC Notification (117180145). Inspector did complete FSR to update Notification but did not indicate condition in Anchor & Guy section of Inspection Record. | N\A | N\A | N\A | N\A | N\A
101797908 | COAST O1501 POLES | Central Coast(S) | 2021-07-05 | 2021-08-24 | 2021-01-27 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | Open wire secondary is present at this location. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101797910 | COAST O1501 POLES | Central Coast(S) | 2021-07-05 | 2021-08-24 | 2021-01-27 | Anchor and Guys: Does or should this location have a Guy? | No | A span guy is present at this location. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101797910 | COAST O1501 POLES | Central Coast(S) | 2021-07-05 | 2021-08-24 | 2021-01-27 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101797910 | COAST O1501 POLES | Central Coast(S) | 2021-07-05 | 2021-08-24 | 2021-01-27 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | Open wire secondary is present at this location. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101798465 | COAST O1501 POLES | Central Coast(S) | 2021-07-05 | 2021-08-24 | 2021-01-27 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks in the pole near where the hardware is attached. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101798465 | COAST O1501 POLES | Central Coast(S) | 2021-07-05 | 2021-08-24 | 2021-01-27 | Hardware and Framing: Crossarm integrity compromised by any of the following; damaged, broken, burnt, decayed, rotten, loose, missing hardware or showing severe signs of bent bolts or brackets, damaged bracing, gun shots, insect damage or woodpecker damage, splitting, or fails to meet clearance requirements | [Answer left blank] | The lower primary crossarm appears to be loose. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101798465 | COAST O1501 POLES | Central Coast(S) | 2021-07-05 | 2021-08-24 | 2021-01-27 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101798465 | COAST O1501 POLES | Central Coast(S) | 2021-07-05 | 2021-08-24 | 2021-01-27 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | Open wire secondary is present at this location. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101806429 | COAST O1501 POLES | Central Coast(S) | 2021-07-05 | 2021-08-24 | 2021-01-27 | Common Equipment/Other Equipment: Obvious paralleled transformer condition at this location | [Answer left blank] | There appears to be a paralleled transformer condition, with a paralleled transformer two spans west of the structure. | Agree | N/A | N¦A | Condition is already attached to an EC Notification (119290739). Inspector did complete FSR to update Notification but did not indicate condition in Equipment section of Inspection Record. | N\A | N\A | N\A | N\A | N\A
101806429 | COAST O1501 POLES | Central Coast(S) | 2021-07-05 | 2021-08-24 | 2021-01-27 | Hardware and Framing: Molding missing, broken, damaged, or loose | [Answer left blank] | Molding is loose from 8' 2" to approximately 10' above the ground. | Agree | N/A | N¦A | 119290739 | Update a EC | Yes | No | Yes | No
101806429 | COAST O1501 POLES | Central Coast(S) | 2021-07-05 | 2021-08-24 | 2021-01-27 | Hardware and Framing: Grounds exposed, broken, damaged, disconnected, unsecured, or missing (if required) | [Answer left blank] | Ground wire is exposed from 8' 2" to approximately 10' above the ground. | Agree | N/A | N¦A | 119290739 | Update a EC | Yes | No | Yes | No
101806429 | COAST O1501 POLES | Central Coast(S) | 2021-07-05 | 2021-08-24 | 2021-01-27 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | Open wire secondary is present at this location. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100489129 | DIABLO E0802 POLES | Diablo(C) | 2021-07-07 | 2021-08-18 | 2021-01-27 | Conductor: Conductor has splices tied in proximity to insulator preventing free movement of splice with conductor | [Answer left blank] | A splice appears to be tied within 2' of an insulator. | Disagree | Condition is not compelling | ELEC-1000 Training | Splice is within 2' of dead end shoe therefore does not need room to allow free monement of splice with conductor. | N\A | N\A | N\A | N\A | N\A
101668916 | COAST L1317 POLES | Central Coast(S) | 2021-07-07 | 2021-08-18 | 2021-01-27 | Conductor: Conductor has splices tied in proximity to insulator preventing free movement of splice with conductor | [Answer left blank] | A splice appears to be tied within 2' of an insulator. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101668916 | COAST L1317 POLES | Central Coast(S) | 2021-07-07 | 2021-08-18 | 2021-01-27 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | Open wire secondary is present at this location. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101668916 | COAST L1317 POLES | Central Coast(S) | 2021-07-07 | 2021-08-18 | 2021-01-27 | Other Required Data: 3 or more splices present in one phase of the span | [Answer left blank] | There are 3 phases on this pole. On the span north of the pole, there is a total of 8 splices, with 4 splices on the west phase, 2 splices on the center phase, and 2 splices on the east phase. Span does not cross over a major roadway. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101801480 | COAST L1317 POLES | Central Coast(S) | 2021-07-07 | 2021-08-18 | 2021-01-27 | Conductor: Conductor has splices tied in proximity to insulator preventing free movement of splice with conductor | [Answer left blank] | Splices appear to be tied within 2' of insulators. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101801480 | COAST L1317 POLES | Central Coast(S) | 2021-07-07 | 2021-08-18 | 2021-01-27 | Conductor: Open wire secondary conductor with rack construction has missing spreader brackets for spans> 135' | [Answer left blank] | An open wire secondary conductor span with rack construction appears to be over 135', without spreader brackets. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101801480 | COAST L1317 POLES | Central Coast(S) | 2021-07-07 | 2021-08-18 | 2021-01-27 | Common Equipment/Other Equipment: Does this structure have equipment? | No | There is equipment (non- exempt universal fuses and transformer) present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101801480 | COAST L1317 POLES | Central Coast(S) | 2021-07-07 | 2021-08-18 | 2021-01-27 | Hardware and Framing: Molding missing, broken, damaged, or loose. | [Answer left blank] | Molding is broken. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101801480 | COAST L1317 POLES | Central Coast(S) | 2021-07-07 | 2021-08-18 | 2021-01-27 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Structure with non-exempt universal fuses and a non- exempt split bolt connector has dried ground vegetation within 10' of its base. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101801480 | COAST L1317 POLES | Central Coast(S) | 2021-07-07 | 2021-08-18 | 2021-01-27 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | Open wire secondary is present at this location. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101801480 | COAST L1317 POLES | Central Coast(S) | 2021-07-07 | 2021-08-18 | 2021-01-27 | Other Required Data: Is there non-exempt equipment at the inspection location (Universal or Open Link Fuse) | [Answer left blank] | Non-exempt universal fuses are present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101801480 | COAST L1317 POLES | Central Coast(S) | 2021-07-07 | 2021-08-18 | 2021-01-27 | Other Required Data: Is there non-exempt equipment at the inspection location (Hot tap clamp or Split Bolt connector) | [Answer left blank] | A non-exempt split bolt connector is present. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101801480 | COAST L1317 POLES | Central Coast(S) | 2021-07-07 | 2021-08-18 | 2021-01-27 | Other Required Data: 3 or more splices present in one phase of the span | [Answer left blank] | There are 3 phases on the pole. There are 11 splices on the span west of the pole, with 3 splices on the south phase, 5 splices on the center phase, and 3 splices on the north phase. There are 7 splices on the span north of the pole, with 3 splices on the west phase and 4 splices on the center phase. Neither span crosses over a major roadway. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101799579 | COAST O1304 POLES | Central Coast(S) | 2021-07-08 | 2021-08-17 | 2021-01-27 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Structure with non-exempt universal fuse has dried vegetation within 10' of its base. | Agree | N/A | N¦A |  | Create "Other tag" | Yes | No | Yes | No
101799579 | COAST O1304 POLES | Central Coast(S) | 2021-07-08 | 2021-08-17 | 2021-01-27 | Vegetation: Support Structure with non-exempt equipment, has dried vegetation (dead branches) above 8' to top of conductors, within 10' radius of Support Structure | [Answer left blank] | Structure with non-exempt universal fuse has dried vegetation within 10' of its mid-section. | Agree | N/A | N¦A |  | Create "Other tag" | Yes | No | Yes | No
101799579 | COAST O1304 POLES | Central Coast(S) | 2021-07-08 | 2021-08-17 | 2021-01-27 | Other Required Data: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101799579 | COAST O1304 POLES | Central Coast(S) | 2021-07-08 | 2021-08-17 | 2021-01-27 | Other Required Data: Is there non-exempt equipment at the inspection location (Universal or Open Link Fuse) | [Answer left blank] | Non-exempt universal fuse is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101799579 | COAST O1304 POLES | Central Coast(S) | 2021-07-08 | 2021-08-17 | 2021-01-27 | Other Required Data: 3 or more splices present in one phase of the span | [Answer left blank] | There are 3 phases on the pole. There are 20 splices on the span north of the pole, with 7 splices on the west phase, 10 splices on the center phase, and 3 splices on the east phase. Span does not cross over a major roadway. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101801507 | COAST L1317 POLES | Central Coast(S) | 2021-07-08 | 2021-08-18 | 2021-01-27 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | Open wire secondary is present at this location. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100299523 | PENINSULA D0806 POLES | Peninsula(C) | 2021-07-10 | 2021-08-19 | 2021-01-27 | Common Equipment/Other Equipment: Transformer shows signs of leaking, seeping, or weeping oil | [Answer left blank] | Transformer shows signs of seeping oil, as oil stains are present. | Agree | N/A | N¦A | 116871871 | Update a EC | Yes | No | Yes | No
100299523 | PENINSULA D0806 POLES | Peninsula(C) | 2021-07-10 | 2021-08-19 | 2021-01-27 | Anchor and Guys: Does or should this location have a Guy? | No | There are two span guys, one on each side of the pole. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100299523 | PENINSULA D0806 POLES | Peninsula(C) | 2021-07-10 | 2021-08-19 | 2021-01-27 | Vegetation: Tree causing strain or abrasion to secondary or service (only 1 service) | [Answer left blank] | A tree appears to be causing strain to the service conductor. | Agree | N/A | N¦A |  | Create "Other tag" | Yes | No | Yes | No
100299527 | PENINSULA D0806 POLES | Peninsula(C) | 2021-07-10 | 2021-08-19 | 2021-01-27 | Structure: Pole leaning or out of plumb by more than 10% of its height above the ground | [Answer left blank] | The pole appears to be leaning by more than 10% of its height above ground. | Agree | N/A | N¦A | Condition is already attached to an EC Notification (116872361). Inspector did complete FSR to update Notification but did not indicate condition in Structure section of Inspection Record. | N\A | N\A | N\A | N\A | N\A
100299527 | PENINSULA D0806 POLES | Peninsula(C) | 2021-07-10 | 2021-08-19 | 2021-01-27 | Hardware and Framing: Tap clamps installed incorrectly | [Answer left blank] | Tap clamps are not installed on tap guards. | Agree | N/A | N¦A | Condition is already attached to an EC Notification (116872361). Inspector did complete FSR to update Notification but did not indicate condition in Hardware & Framing section of Inspection Record. | Update a EC | Yes | No | Yes | No
100299527 | PENINSULA D0806 POLES | Peninsula(C) | 2021-07-10 | 2021-08-19 | 2021-01-27 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Structure with non-exempt open link fuses appears to have dried ground vegetation within 10' of its base. | Agree | N/A | N¦A |  | Update a EC | Yes | No | Yes | No
100299527 | PENINSULA D0806 POLES | Peninsula(C) | 2021-07-10 | 2021-08-19 | 2021-01-27 | Vegetation: Support Structure with non-exempt equipment, has dried vegetation (dead branches) above 8' to top of conductors, within 10' radius of Support Structure | [Answer left blank] | Structure with non-exempt open link fuses appears to have dried vegetation within 10' of its midsection. | Agree | N/A | N¦A | 117543438 | Update a EC | Yes | No | Yes | No
100299527 | PENINSULA D0806 POLES | Peninsula(C) | 2021-07-10 | 2021-08-19 | 2021-01-27 | Other Required Data: Is there non-exempt equipment at the inspection location (Universal or Open Link Fuse) | [Answer left blank] | Non-exempt open link fuses are present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100299528 | PENINSULA D0806 POLES | Peninsula(C) | 2021-07-10 | 2021-08-19 | 2021-01-27 | Vegetation: Structure is overgrown with vegetation | [Answer left blank] | Midsection of pole is overgrown with vegetation, preventing full inspection. | Agree | N/A | N¦A |  | Create "Other tag" | Yes | No | Yes | No
100299528 | PENINSULA D0806 POLES | Peninsula(C) | 2021-07-10 | 2021-08-19 | 2021-01-27 | Vegetation: Support Structure with non-exempt equipment, has dried vegetation from ground to 8' above ground, within 10' radius of Support Structure base | [Answer left blank] | Structure with non-exempt universal fuses has dried vegetation within 10' of its base. | Agree | N/A | N¦A |  | Create "Other tag" | Yes | No | Yes | No
100299528 | PENINSULA D0806 POLES | Peninsula(C) | 2021-07-10 | 2021-08-19 | 2021-01-27 | Non-Time-Dependent Issues: Pole steps are less than 8' 6" above the ground or any other accessible surface | [Answer left blank] | Pole step is at 8' 2" (98"). | Agree | N/A | N¦A | 116872513 | Update a EC | Yes | No | Yes | No
100299528 | PENINSULA D0806 POLES | Peninsula(C) | 2021-07-10 | 2021-08-19 | 2021-01-27 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | Open wire secondary is present at this location. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100299528 | PENINSULA D0806 POLES | Peninsula(C) | 2021-07-10 | 2021-08-19 | 2021-01-27 | Other Required Data: Is there non-exempt equipment at the inspection location (Universal or Open Link Fuse) | [Answer left blank] | Non-exempt universal fuses are present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100299529 | PENINSULA D0806 POLES | Peninsula(C) | 2021-07-10 | 2021-08-19 | 2021-01-27 | Anchor and Guys: Necessary guys missing or loose | [Answer left blank] | Guy is loose. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100299529 | PENINSULA D0806 POLES | Peninsula(C) | 2021-07-10 | 2021-08-19 | 2021-01-27 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | Open wire secondary is present at this location. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100299534 | PENINSULA D0806 POLES | Peninsula(C) | 2021-07-10 | 2021-08-19 | 2021-01-28 | Conductor: Does this structure have PG&E owned conductor? | Yes | There is no conductor present on this structure. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100311992 | PENINSULA D0806 POLES | Peninsula(C) | 2021-07-10 | 2021-08-19 | 2021-01-28 | Conductor: Conductor has splices tied in proximity to insulator preventing free movement of splice with conductor | [Answer left blank] | A splice appears to be tied within 2' of an insulator. | Agree | N/A | N¦A | 121707454 | Update a EC | Yes | No | Yes | No
100311992 | PENINSULA D0806 POLES | Peninsula(C) | 2021-07-10 | 2021-08-19 | 2021-01-28 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | Open wire secondary is present at this location. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100311992 | PENINSULA D0806 POLES | Peninsula(C) | 2021-07-10 | 2021-08-19 | 2021-01-28 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101673005 | COAST K1122 POLES | Central Coast(S) | 2021-07-10 | 2021-08-18 | 2021-01-28 | Conductor: Conductor has splices tied in proximity to insulator preventing free movement of splice with conductor | [Answer left blank] | A splice appears to be tied within 2' of an insulator. | Disagree | Condition is not compelling | ELEC-1000 Training | Splice is within 2' of dead end shoe therefore does not need room to allow free monement of splice with conductor. | N\A | N\A | N\A | N\A | N\A
101673005 | COAST K1122 POLES | Central Coast(S) | 2021-07-10 | 2021-08-18 | 2021-01-28 | Non-Time-Dependent Issues: Pole steps are less than 8' 6" above the ground or any other accessible surface | [Answer left blank] | Pole step is at 8' 0" (96"). | Agree | N/A | N¦A | 121707161 | Update a EC | Yes | No | Yes | No
101673005 | COAST K1122 POLES | Central Coast(S) | 2021-07-10 | 2021-08-18 | 2021-01-28 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101673010 | COAST K1122 POLES | Central Coast(S) | 2021-07-10 | 2021-08-18 | 2021-01-28 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | The top of the pole has cracks near where the hardware is attached. | Agree | N/A | N¦A | 119621725 | Update a EC | Yes | No | Yes | No
101673010 | COAST K1122 POLES | Central Coast(S) | 2021-07-10 | 2021-08-18 | 2021-01-28 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101678297 | COAST N1320 POLES | Central Coast(S) | 2021-07-10 | 2021-08-17 | 2021-01-28 | Common Equipment/Other Equipment: Does this structure have equipment? | Yes | There is no equipment present on this structure. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101803099 | COAST K1122 POLES | Central Coast(S) | 2021-07-10 | 2021-08-18 | 2021-01-28 | Hardware and Framing: Molding missing, broken, damaged, or loose | [Answer left blank] | Molding is broken approximately 15" above the ground. | Agree | N/A | N¦A |  | Update a EC | Yes | No | Yes | Yes
101803099 | COAST K1122 POLES | Central Coast(S) | 2021-07-10 | 2021-08-18 | 2021-01-28 | Hardware and Framing: Grounds exposed, broken, damaged, disconnected, unsecured, or missing (if required) | [Answer left blank] | Ground wire is exposed approximately 15" above the ground. | Agree | N/A | N¦A |  | Update a EC | Yes | No | Yes | Yes
101803099 | COAST K1122 POLES | Central Coast(S) | 2021-07-10 | 2021-08-18 | 2021-01-28 | Other Required Data: 3 or more splices present in one phase of the span | [Answer left blank] | There are 3 phases on the pole. On the span south of the pole, there are 9 splices, with 1 splice on the east phase, 5 splices on the center phase, and 3 splices on the west phase. Span does not cross over a major roadway. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101803106 | COAST K1122 POLES | Central Coast(S) | 2021-07-10 | 2021-08-18 | 2021-01-28 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Structure with non-exempt universal fuses has dried vegetation within 10' of its base. | Agree | N/A | N¦A |  | Create "Other tag" | Yes | No | Yes | No
101804083 | COAST L1317 POLES | Central Coast(S) | 2021-07-10 | 2021-08-18 | 2021-01-28 | Other Required Data: Tree anchor installed in tree by design | [Answer left blank] | There appears to be a tree anchor installed in tree by design. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101804083 | COAST L1317 POLES | Central Coast(S) | 2021-07-10 | 2021-08-18 | 2021-01-28 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | Open wire secondary is present at this location. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100526380 | DE ANZA I1423 POLES | De Anza(S) | 2021-07-11 | 2021-08-26 | 2021-01-28 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Structure with non-exempt universal fuses has dried ground vegetation within a 10' radius of its base. | Agree | N/A | N¦A |  | Create "Other tag" | Yes | No | Yes | No
100526380 | DE ANZA I1423 POLES | De Anza(S) | 2021-07-11 | 2021-08-26 | 2021-01-28 | Non-Time-Dependent Issues: Visibility strips missing, broken, mismatched, or no longer reflective | [Answer left blank] | Visibility strips are missing. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100557089 | DE ANZA I1423 POLES | De Anza(S) | 2021-07-11 | 2021-08-26 | 2021-01-28 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | The pole appears to have cracks at the top near where hardware is attached. | Agree | N/A | N¦A | 121710185 | Update a EC | Yes | No | Yes | No
100557089 | DE ANZA I1423 POLES | De Anza(S) | 2021-07-11 | 2021-08-26 | 2021-01-28 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Structure with non-exempt fuses has dried ground vegetation within a 10' radius of its base. | Agree | N/A | N¦A |  | Create "Other tag" | Yes | No | Yes | No
100557094 | DE ANZA I1423 POLES | De Anza(S) | 2021-07-11 | 2021-08-26 | 2021-01-28 | Anchor and Guys: Guy wire broken, damaged, clearance issues, corroded, covered by vegetation, overgrown, strain or abrasion | [Answer left blank] | Vegetation appears to be in contact with guy wire above the guy insulator. | Agree | N/A | N¦A | 117163256 | Update a EC | Yes | No | Yes | No
100557094 | DE ANZA I1423 POLES | De Anza(S) | 2021-07-11 | 2021-08-26 | 2021-01-28 | Vegetation: Support Structure with non-exempt equipment, has dried vegetation from ground to 8' above ground, within 10' radius of Support Structure base | [Answer left blank] | Structure with non-exempt open link fuses has dried vegetation from the ground to 8' above the ground, within a 10' radius of the structure. | Agree | N/A | N¦A |  | Create "Other tag" | Yes | No | Yes | No
101676902 | COAST N1521 POLES | Central Coast(S) | 2021-07-11 | 2021-08-24 | 2021-01-28 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks and a hole in the top section of the pole near where the hardware is attached. | Agree | N/A | N¦A | 119477966 | Update a EC | Yes | No | Yes | No
101676902 | COAST N1521 POLES | Central Coast(S) | 2021-07-11 | 2021-08-24 | 2021-01-28 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | Open wire secondary is present at this location. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101803104 | COAST K1122 POLES | Central Coast(S) | 2021-07-11 | 2021-08-18 | 2021-01-28 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks and a hole in the top section of the pole near where the hardware is attached. | Agree | N/A | N¦A | 119621343 | Update a EC | Yes | No | Yes | No
100278597 | PENINSULA D0710 POLES | Peninsula(C) | 2021-07-12 | 2021-08-19 | 2021-01-28 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Structure with non-exempt open link fuses has dried vegetation within 10' of its base. | Agree | N/A | N¦A |  | Create "Other tag" | Yes | No | Yes | No
100278597 | PENINSULA D0710 POLES | Peninsula(C) | 2021-07-12 | 2021-08-19 | 2021-01-28 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | Open wire secondary is present at this location. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100278597 | PENINSULA D0710 POLES | Peninsula(C) | 2021-07-12 | 2021-08-19 | 2021-01-28 | Other Required Data: Is there non-exempt equipment at the inspection location (Universal or Open Link Fuse) | [Answer left blank] | Non-exempt open link fuses are present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100278597 | PENINSULA D0710 POLES | Peninsula(C) | 2021-07-12 | 2021-08-19 | 2021-01-28 | Other Required Data: 3 or more splices present in one phase of the span | [Answer left blank] | There are 3 phases on the pole. On the span east of the pole, there is a total of 7 splices, with 4 splices on the north phase, 1 splice on the center phase, and 2 splices on the south phase. Span does not cross over a major roadway. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100278601 | PENINSULA D0710 POLES | Peninsula(C) | 2021-07-12 | 2021-08-19 | 2021-01-28 | Hardware and Framing: Molding missing, broken, damaged, or loose | [Answer left blank] | Molding is broken at approximately 8' 4". | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100278601 | PENINSULA D0710 POLES | Peninsula(C) | 2021-07-12 | 2021-08-19 | 2021-01-28 | Hardware and Framing: Grounds exposed, broken, damaged, disconnected, unsecured, or missing (if required) | [Answer left blank] | Ground wire is exposed at approximately 8' 4". | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100278601 | PENINSULA D0710 POLES | Peninsula(C) | 2021-07-12 | 2021-08-19 | 2021-01-28 | Non-Time-Dependent Issues: Pole steps are less than 8' 6" above the ground or any other accessible surface | [Answer left blank] | Pole step is at 8' 1" (97"). | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100278601 | PENINSULA D0710 POLES | Peninsula(C) | 2021-07-12 | 2021-08-19 | 2021-01-28 | Other Required Data: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100278993 | PENINSULA D0710 POLES | Peninsula(C) | 2021-07-12 | 2021-08-19 | 2021-01-28 | Vegetation: Support Structure with non-exempt equipment, has dried vegetation from ground to 8' above ground within 10' radius of Support Structure base. | [Answer left blank] | Structure with non-exempt universal fuses has dried ground vegetation from ground to 8' above ground within 10' of its base. | Agree | N/A | N¦A |  | Create "Other tag" | Yes | No | Yes | No
100278993 | PENINSULA D0710 POLES | Peninsula(C) | 2021-07-12 | 2021-08-19 | 2021-01-28 | Other Required Data: 3 or more splices present in one phase of the span | [Answer left blank] | There are 2 phases on the asset. There are 5 splices on the span north of the pole, with 3 splices on the west phase and 2 splices on the east phase. Span does not cross over a major roadway. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100296300 | PENINSULA D0811 POLES | Peninsula(C) | 2021-07-12 | 2021-08-18 | 2021-01-28 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | Open wire secondary is present at this location. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100296300 | PENINSULA D0811 POLES | Peninsula(C) | 2021-07-12 | 2021-08-18 | 2021-01-28 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100296303 | PENINSULA D0811 POLES | Peninsula(C) | 2021-07-12 | 2021-08-18 | 2021-01-28 | Anchor and Guys: Does or should this location have a Guy? | Yes | The structure has a span guy. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100296303 | PENINSULA D0811 POLES | Peninsula(C) | 2021-07-12 | 2021-08-18 | 2021-01-28 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | Open wire secondary is present at this location. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100296307 | PENINSULA D0811 POLES | Peninsula(C) | 2021-07-12 | 2021-08-18 | 2021-01-28 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Structure with non-exempt open universal fuses and split bolt connectors has dried ground vegetation within 10' of its base. | Agree | N/A | N¦A |  | Create "Other tag" | Yes | No | Yes | No
100296307 | PENINSULA D0811 POLES | Peninsula(C) | 2021-07-12 | 2021-08-18 | 2021-01-28 | Non-Time-Dependent Issues: Pole steps are less than 8' 6" above the ground or any other accessible surface | [Answer left blank] | Pole step is at 8' 0" (96 inches). | Agree | N/A | N¦A | 121713486 | Update a EC | Yes | No | Yes | No
100296307 | PENINSULA D0811 POLES | Peninsula(C) | 2021-07-12 | 2021-08-18 | 2021-01-28 | Other Required Data: Is there non-exemptequipment at the inspection location (Universal or Open Link Fuse) | [Answer left blank] | Non-exempt enclosed cutouts with universal fuses are present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100296307 | PENINSULA D0811 POLES | Peninsula(C) | 2021-07-12 | 2021-08-18 | 2021-01-28 | Other Required Data: Is there non-exempt equipment at the inspection location (Hot tap clamp or Split Bolt connector) | [Answer left blank] | Non-exempt split bolt connectors are present. | Agree | N/A | N¦A | Condition is already attached to an EC Notification (121713486). | N\A | N\A | N\A | N\A | N\A
100317713 | PENINSULA D0710 POLES | Peninsula(C) | 2021-07-12 | 2021-08-19 | 2021-01-28 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Structure with non-exempt universal fuses has dried vegetation within 10' of its base. | Agree | N/A | N¦A |  | Create "Other tag" | Yes | No | Yes | No
100317713 | PENINSULA D0710 POLES | Peninsula(C) | 2021-07-12 | 2021-08-19 | 2021-01-28 | Other Required Data: Is there non-exempt equipment at the inspection location (Universal or Open Link Fuse) | [Answer left blank] | Non-exempt universal fuses are present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100317713 | PENINSULA D0710 POLES | Peninsula(C) | 2021-07-12 | 2021-08-19 | 2021-01-28 | Other Required Data: 3 or more splices present in one phase of the span | [Answer left blank] | There are 3 phases on the pole. On the span west of the pole, there is a total of 7 splices: 3 splices on the south phase, 1 splice on the center phase, and 3 splices on the north phase. Span does not cross over a major roadway. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100525556 | DE ANZA I1423 POLES | De Anza(S) | 2021-07-12 | 2021-08-26 | 2021-01-31 | Conductor: Conductor has splices tied in proximity to insulator preventing free movement of splice with conductor | [Answer left blank] | A splice appears to be tied within 2' of an insulator. | Agree | N/A | N¦A |  | Update a EC | Yes | No | Yes | No
100525556 | DE ANZA I1423 POLES | De Anza(S) | 2021-07-12 | 2021-08-26 | 2021-01-31 | Other Required Data: Is there non-exempt equipment at the inspection location (Hot tap clamp or Split Bolt connector) | [Answer left blank] | Non-exempt split bolt connectors are present. | Agree | N/A | N¦A | Condition is already attached to an EC Notification (121715989). | N\A | N\A | N\A | N\A | N\A
101673068 | COAST K1122 POLES | Central Coast(S) | 2021-07-12 | 2021-08-18 | 2021-01-31 | Common Equipment/Other Equipment: IFD (aka "Turkey Popper") has activated on the transformer (orange band is visible) | [Answer left blank] | Transformer IFD appears to have activated. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
103828034 | COAST K1122 POLES | Central Coast(S) | 2021-07-12 | 2021-08-18 | 2021-01-31 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | The pole number is visible. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103828035 | COAST K1122 POLES | Central Coast(S) | 2021-07-12 | 2021-08-18 | 2021-01-31 | Common Equipment/Other Equipment: Does this structure have equipment? | [Answer left blank] | There is equipment (a transformer) present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100296224 | PENINSULA D0811 POLES | Peninsula(C) | 2021-07-13 | 2021-08-19 | 2021-01-31 | Conductor: Conductor has splices tied in proximity to insulator preventing free movement of splice with conductor | [Answer left blank] | A splice appears to be tied within 2' of an insulator. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100296224 | PENINSULA D0811 POLES | Peninsula(C) | 2021-07-13 | 2021-08-19 | 2021-01-31 | Vegetation: Structure is overgrown with vegetation. | [Answer left blank] | The middle of the pole is overgrown with vegetation, preventing full inspection. | Disagree | Condition is not compelling | ELEC-1000 Training | Photos Attached to Inspection Record and photos in FM Report both appear to show vegetation around pole but does not appear to be preventing inspection. | N\A | N\A | N\A | N\A | N\A
100296224 | PENINSULA D0811 POLES | Peninsula(C) | 2021-07-13 | 2021-08-19 | 2021-01-31 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Structure with non-exempt open link fuses has dried ground vegetation within 10' of its base. | Agree | N/A | N¦A |  | Create "Other tag" | Yes | No | Yes | No
100296224 | PENINSULA D0811 POLES | Peninsula(C) | 2021-07-13 | 2021-08-19 | 2021-01-31 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | Open wire secondary is present at this location. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100296224 | PENINSULA D0811 POLES | Peninsula(C) | 2021-07-13 | 2021-08-19 | 2021-01-31 | Other Required Data: Is there non-exempt equipment at the inspection location (Universal or Open Link Fuse) | [Answer left blank] | Non-exempt open link fuses are present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100296224 | PENINSULA D0811 POLES | Peninsula(C) | 2021-07-13 | 2021-08-19 | 2021-01-31 | Other Required Data: 3 or more splices present in one phase of the span | [Answer left blank] | There are 3 phases on this pole. On the span west of the pole, there are 3 splices on the south phase. Span does not cross over a major roadway. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100296244 | PENINSULA D0811 POLES | Peninsula(C) | 2021-07-13 | 2021-08-19 | 2021-01-31 | Conductor: Open wire secondary conductor with rack construction has missing spreader brackets for spans> 135' | [Answer left blank] | An open wire secondary conductor span with rack construction appears to be over 135', without spreader brackets. | Agree | N/A | N¦A | 116881606 | Update a EC | Yes | No | Yes | No
100296244 | PENINSULA D0811 POLES | Peninsula(C) | 2021-07-13 | 2021-08-19 | 2021-01-31 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | Open wire secondary is present at this location. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100296244 | PENINSULA D0811 POLES | Peninsula(C) | 2021-07-13 | 2021-08-19 | 2021-01-31 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100296245 | PENINSULA D0811 POLES | Peninsula(C) | 2021-07-13 | 2021-08-19 | 2021-01-31 | Anchor and Guys: Necessary guys missing or loose | [Answer left blank] | Guy wires on the east side of the structure appear to be loose. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100312804 | PENINSULA D0811 POLES | Peninsula(C) | 2021-07-13 | 2021-08-19 | 2021-01-31 | Conductor: Conductor has splices tied in proximity to insulator preventing free movement of splice with conductor | [Answer left blank] | A splice appears to be tied within 2' of an insulator. | Agree | N/A | N¦A | 121723101 | Update a EC | Yes | No | Yes | No
100312804 | PENINSULA D0811 POLES | Peninsula(C) | 2021-07-13 | 2021-08-19 | 2021-01-31 | Common Equipment/Other Equipment: Does this structure have equipment? | Yes | There is no equipment on the structure. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100312804 | PENINSULA D0811 POLES | Peninsula(C) | 2021-07-13 | 2021-08-19 | 2021-01-31 | Non-Time-Dependent Issues: Pole steps are less than 8' 6" above the ground or any other accessible surface | [Answer left blank] | Pole step is at 7' 8" (92"). | Agree | N/A | N¦A | 121723101 | Update a EC | Yes | No | Yes | No
100312804 | PENINSULA D0811 POLES | Peninsula(C) | 2021-07-13 | 2021-08-19 | 2021-01-31 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | One of the high voltage signs is partially missing. | Agree | N/A | N¦A | 121723101 | Update a EC | Yes | No | Yes | No
100312811 | PENINSULA D0811 POLES | Peninsula(C) | 2021-07-13 | 2021-08-19 | 2021-01-31 | Anchor and Guys: Does or should this location have a Guy? | No | Anchor and Guys: Does or should this location have a Guy? | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100312811 | PENINSULA D0811 POLES | Peninsula(C) | 2021-07-13 | 2021-08-19 | 2021-01-31 | Hardware and Framing: Crossarm integrity compromised by any of the following; damaged, broken, burnt, decayed, rotten, loose, missing hardware or showing severe signs of bent bolts or brackets, damaged bracing, gun shots, insect damage or woodpecker damage, splitting, or fails to meet clearance requirements | [Answer left blank] | The crossarm brace appears to be loose. | Agree | N/A | N¦A | 121725684 | Update a EC | Yes | No | Yes | No
100312811 | PENINSULA D0811 POLES | Peninsula(C) | 2021-07-13 | 2021-08-19 | 2021-01-31 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Structure with non-exempt split bolt connectors has dried vegetation within 10' of its base. | Agree | N/A | N¦A |  | Create "Other tag" | Yes | No | Yes | No
100312811 | PENINSULA D0811 POLES | Peninsula(C) | 2021-07-13 | 2021-08-19 | 2021-01-31 | Other Required Data: Is there non-exempt equipment at the inspection location (Hot tap clamp or Split Bolt connector) | [Answer left blank] | Non-exempt split bolt connectors are present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100312811 | PENINSULA D0811 POLES | Peninsula(C) | 2021-07-13 | 2021-08-19 | 2021-01-31 | Other Required Data: Pole wrapped at ground-line at this location | Yes | Pole does not appear to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100474861 | DIABLO D0817 POLES | Diablo(C) | 2021-07-13 | 2021-08-17 | 2021-01-31 | Common Equipment/Other Equipment: Transformer shows signs of leaking, seeping, or weeping oil | [Answer left blank] | Transformer shows signs of seeping oil, as oil stains are present near the cap seal. | Agree | N/A | N¦A | 121721830 | Update a EC | Yes | No | Yes | No
100474886 | DIABLO D0817 POLES | Diablo(C) | 2021-07-13 | 2021-08-17 | 2021-01-31 | Non-Time-Dependent Issues: Visibility strips missing, broken, mismatched, or no longer reflective | [Answer left blank] | Visibility strips are missing. | Agree | N/A | N¦A |  | Update a EC | Yes | No | Yes | No
100525542 | DE ANZA I1423 POLES | De Anza(S) | 2021-07-13 | 2021-08-26 | 2021-01-31 | Vegetation: Tree causing strain or abrasion to secondary or service (2 or more services) | [Answer left blank] | Tree appears to be causing strain on the service conductor west of the pole. | Agree | N/A | N¦A |  | Update a EC | Yes | No | Yes | No
100525585 | DE ANZA I1423 POLES | De Anza(S) | 2021-07-13 | 2021-08-26 | 2021-01-31 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks in the pole near where hardware is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. | N\A | N\A | N\A | N\A | N\A
100525585 | DE ANZA I1423 POLES | De Anza(S) | 2021-07-13 | 2021-08-26 | 2021-01-31 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Structure with non-exempt solid blade disconnects has dried ground vegetation within a 10' radius of its base. | Agree | N/A | N¦A |  | Create "Other tag" | Yes | No | Yes | No
100526354 | DE ANZA I1423 POLES | De Anza(S) | 2021-07-13 | 2021-08-26 | 2021-01-31 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks in the pole near where hardware is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. | N\A | N\A | N\A | N\A | N\A
100526354 | DE ANZA I1423 POLES | De Anza(S) | 2021-07-13 | 2021-08-26 | 2021-01-31 | Conductor: Conductor has splices tied in proximity to insulator preventing free movement of splice with conductor | [Answer left blank] | A splice appears to be tied within 2' of an insulator. | Agree | N/A | N¦A | 117166250 | Update a EC | Yes | No | Yes | No
100526354 | DE ANZA I1423 POLES | De Anza(S) | 2021-07-13 | 2021-08-26 | 2021-01-31 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Structure with non-exempt equipment (split bolt connectors) has dried vegetation from ground to 8' above ground, within 10' of its base. | Agree | N/A | N¦A |  | Create "Other tag" | Yes | No | Yes | No
100526354 | DE ANZA I1423 POLES | De Anza(S) | 2021-07-13 | 2021-08-26 | 2021-01-31 | Vegetation: Support Structure with non-exempt equipment, has dried vegetation (dead branches) above 8' to top of conductors, within 10' radius of Support Structure | [Answer left blank] | Structure with non-exempt equipment (split bolt connectors) has dried vegetation above 8', within 10' of its base. | Agree | N/A | N¦A |  | Create "Other tag" | Yes | No | Yes | No
100526354 | DE ANZA I1423 POLES | De Anza(S) | 2021-07-13 | 2021-08-26 | 2021-01-31 | Other Required Data: 3 or more splices present in one phase of the span | [Answer left blank] | There are 3 phases on this pole. There are 9 splices on the span southeast of the pole, with 4 splices on the northeast phase, 3 splices on the center phase, and 2 splices on the southwest phase. Span does not cross over a major roadway. The monitor team also notes this potential exception to an adjacent asset (Equipment No. 100526355) | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100526355 | DE ANZA I1423 POLES | De Anza(S) | 2021-07-13 | 2021-08-26 | 2021-01-31 | Conductor: Conductor has splices tied in proximity to insulator preventing free movement of splice with conductor | [Answer left blank] | A splice appears to be tied within 2' of an insulator. | Agree | N/A | N¦A | 117166165 | Update a EC | Yes | No | Yes | No
100526355 | DE ANZA I1423 POLES | De Anza(S) | 2021-07-13 | 2021-08-26 | 2021-01-31 | Other Required Data: 3 or more splices present in one phase of the span | [Answer left blank] | There are 3 phases on this pole. There are 9 splices on the span northwest of the pole, with 4 splices on the northeast phase, 3 splices on the center phase, and 2 splices on the southwest phase. The monitor team also notes this potential exception to an adjacent asset (Equipment No. 100526355) There are 3 phases on the pole. There are 6 splices on the span south of the pole, with 5 splices on the east phase and 1 splice on the west phase.Neither span crosses over a major roadway. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101679366 | COAST M1321 POLES | Central Coast(S) | 2021-07-13 | 2021-08-17 | 2021-01-31 | Vegetation: Tree causing strain or abrasion to secondary or service (2 or more services) | [Answer left blank] | Vegetation appears to be causing strain on one of the service conductors. | Agree | N/A | N¦A | 116714966 | Update a EC | Yes | No | Yes | No
101679366 | COAST M1321 POLES | Central Coast(S) | 2021-07-13 | 2021-08-17 | 2021-01-31 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | High voltage sign is partially missing. | Agree | N/A | N¦A | 116714966 | Update a EC | Yes | No | Yes | No
101679366 | COAST M1321 POLES | Central Coast(S) | 2021-07-13 | 2021-08-17 | 2021-01-31 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101679368 | COAST M1321 POLES | Central Coast(S) | 2021-07-13 | 2021-08-17 | 2021-01-31 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | Open wire secondary is present at this location. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101679368 | COAST M1321 POLES | Central Coast(S) | 2021-07-13 | 2021-08-17 | 2021-01-31 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101679369 | COAST M1321 POLES | Central Coast(S) | 2021-07-13 | 2021-08-17 | 2/1/0201 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | Open wire secondary is present at this location. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101679371 | COAST M1321 POLES | Central Coast(S) | 2021-07-13 | 2021-08-17 | 2/1/0201 | Conductor: Conductor has splices tied in proximity to insulator preventing free movement of splice with conductor | [Answer left blank] | A splice appears to be tied within 2' of an insulator. | Agree | N/A | N¦A | 119697377 | Update a EC | Yes | No | Yes | No
101679408 | COAST M1321 POLES | Central Coast(S) | 2021-07-13 | 2021-08-17 | 2/1/0201 | Anchor and Guys: Anchor rod broken, damaged, corroded, covered by vegetation/overgrown, soil-eroded, graded, or buried | [Answer left blank] | Guy anchor is dislodged from the ground. PG&E inspector flagged a loose guy in connection with the damaged anchor. | Agree | N/A | N¦A | 119701686 | Update a EC | Yes | No | Yes | No
101679408 | COAST M1321 POLES | Central Coast(S) | 2021-07-13 | 2021-08-17 | 2/1/0201 | Non-Time-Dependent Issues: Visibility strips missing, broken, mismatched, or no longer reflective | [Answer left blank] | Visibility strips are missing. | Agree | N/A | N¦A | 119701686 | Update a EC | Yes | No | Yes | No
104027250 | DIABLO D0817 POLES | Diablo(C) | 2021-07-13 | 2021-08-17 | 2/1/0201 | Conductor: Primary, secondary, and/or service conductors broken, damaged, burnt, corroded, loose, frayed or bird caging | [Answer left blank] | A portion of the primary conductor on the east phase south of the pole appears to be bird caging. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100296230 | PENINSULA D0811 POLES | Peninsula(C) | 2021-07-14 | 2021-08-19 | 2/1/0201 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | Open wire secondary is present at this location. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100296231 | PENINSULA D0811 POLES | Peninsula(C) | 2021-07-14 | 2021-08-19 | 2/1/0201 | Conductor: Primary or secondary conductor has diminished clearance mid span or uneven conductor sag | [Answer left blank] | The secondary conductor appears to have diminished midspan clearance from the ground. | Agree | N/A | N¦A | 121605506 | Update a EC | Yes | No | Yes | No
100474847 | DIABLO D0817 POLES | Diablo(C) | 2021-07-14 | 2021-08-17 | 2/1/0201 | Anchor and Guys: Does or should this location have a Guy? | No | Guy wire is present. | Agree | N/A | N¦A | Not available on attainment report. | N\A | N\A | N\A | N\A | N\A
100474847 | DIABLO D0817 POLES | Diablo(C) | 2021-07-14 | 2021-08-17 | 2/1/0201 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Structure with non-exempt universal fuses has dried ground vegetation within 10' of its base. | Agree | N/A | N¦A | Not available on attainment report. | N\A | N\A | N\A | N\A | N\A
100474847 | DIABLO D0817 POLES | Diablo(C) | 2021-07-14 | 2021-08-17 | 2/1/0201 | Other Required Data: Is there non-exempt equipment at the inspection location (Universal or Open Link Fuse) | [Answer left blank] | Non-exempt universal fuses are present. | Agree | N/A | N¦A | Not available on attainment report. | N\A | N\A | N\A | N\A | N\A
100474852 | DIABLO D0817 POLES | Diablo(C) | 2021-07-14 | 2021-08-17 | 2/1/0201 | Other Required Data: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100526358 | DE ANZA I1423 POLES | De Anza(S) | 2021-07-14 | 2021-08-26 | 2/1/0201 | Anchor and Guys: Necessary guys missing or loose | [Answer left blank] | An overhead guy appears to be loose. The Monitor team also notes this potential exception in connection with an adjacent asset (Equipment No. 100557128). | Agree | N/A | N¦A |  | Update a EC | Yes | No | Yes | No
100557128 | DE ANZA I1423 POLES | De Anza(S) | 2021-07-14 | 2021-08-26 | 2/1/0201 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks on the pole near where hardware is attached. | Disagree | N/A | N¦A | Pole appears to have normal cracks and splits due to weather and ageing of pole. | N\A | N\A | N\A | N\A | N\A
100557128 | DE ANZA I1423 POLES | De Anza(S) | 2021-07-14 | 2021-08-26 | 2/1/0201 | Anchor and Guys: Necessary guys missing or loose | [Answer left blank] | An overhead guy appears to be loose. The Monitor team also notes this potential exception in connection with an adjacent asset (Equipment No. 100526358). | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101679407 | COAST M1321 POLES | Central Coast(S) | 2021-07-14 | 2021-08-17 | 2/1/0201 | Conductor: Conductor has splices tied in proximity to insulator preventing free movement of splice with conductor | [Answer left blank] | A splice appears to be tied within 2' of an insulator. | Agree | N/A | N¦A | 119693648 | Update a EC | Yes | No | Yes | No
101679407 | COAST M1321 POLES | Central Coast(S) | 2021-07-14 | 2021-08-17 | 2/1/0201 | Non-Time-Dependent Issues: Pole steps are less than 8' 6" above the ground or any other accessible surface | [Answer left blank] | Pole step is at 8' 3" (99"). | Agree | N/A | N¦A | 119693648 | Update a EC | Yes | No | Yes | No
101679407 | COAST M1321 POLES | Central Coast(S) | 2021-07-14 | 2021-08-17 | 2/1/0201 | Other Required Data: Tree anchor installed in tree by design | [Answer left blank] | There appears to be a tree anchor installed in tree by design. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101679407 | COAST M1321 POLES | Central Coast(S) | 2021-07-14 | 2021-08-17 | 2/1/0201 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101679407 | COAST M1321 POLES | Central Coast(S) | 2021-07-14 | 2021-08-17 | 2/1/0201 | Other Required Data: 3 or more splices present in one phase of the span | [Answer left blank] | There are 3 phases on the pole. On the span west of the pole, there are 3 splices on the north phase and 1 splice on the south phase. Span does not cross over a major roadway. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101801341 | COAST M1321 POLES | Central Coast(S) | 2021-07-14 | 2021-08-17 | 2/1/0201 | Other Required Data: Tree anchor installed in tree by design | [Answer left blank] | There appears to be a tree anchor installed in tree by design. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102346294 | DIABLO D0817 POLES | Diablo(C) | 2021-07-14 | 2021-08-17 | 2/1/0201 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Structure with non-exempt universal fuses has dried ground vegetation within 10' of its base. | Agree | N/A | N¦A |  | Create "Other tag" | Yes | No | Yes | No
100475049 | DIABLO D0822 POLES | Diablo(C) | 2021-07-15 | 2021-08-18 | 2/1/0201 | Anchor and Guys: Guy wire broken, damaged, clearance issues, corroded, covered by vegetation, overgrown, strain or abrasion | [Answer left blank] | Tree branch appears to be causing strain on span guy. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100566292 | SAN JOSE F2022 POLES | San Jose(S) | 2021-07-15 | 2021-08-19 | 2/1/0201 | Non-Time-Dependent Issues: Visibility strips missing, broken, mismatched, or no longer reflective | [Answer left blank] | Visibility strips are missing. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101673065 | COAST K1122 POLES | Central Coast(S) | 2021-07-15 | 2021-08-18 | 2/1/0201 | Anchor and Guys: Guy wire broken, damaged, clearance issues, corroded, covered by vegetation, overgrown, strain or abrasion | [Answer left blank] | Vegetation appears to be causing strain on the guy wire. | Agree | N/A | N¦A | 119618617 | Update a EC | Yes | No | Yes | No
103831221 | DIABLO D0822 POLES | Diablo(C) | 2021-07-15 | 2021-08-18 | 2/1/0201 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Structure with non-exempt universal fuses has dried ground vegetation within 10' of its base. | Agree | N/A | N¦A |  | Create "Other tag" | Yes | No | Yes | No
100475005 | DIABLO D0821 POLES | Diablo(C) | 2021-07-16 | 2021-08-18 | 2/1/0201 | Other Required Data: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100475005 | DIABLO D0821 POLES | Diablo(C) | 2021-07-16 | 2021-08-18 | 2/1/0201 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100475031 | DIABLO D0821 POLES | Diablo(C) | 2021-07-16 | 2021-08-18 | 2/1/0201 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Structure with non-exempt split bolt connectors has dried ground vegetation within 10' of its base. | Agree | N/A | N¦A |  | Create "Other tag" | Yes | No | Yes | No
100475102 | DIABLO D0822 POLES | Diablo(C) | 2021-07-17 | 2021-08-18 | 2/1/0201 | Vegetation: Tree causing strain or abrasion to secondary or service (only 1 service) | [Answer left blank] | Tree branch appears to be causing strain on service conductor. |  |  |  |  | Create a EC | Yes | No | Yes | No
100475102 | DIABLO D0822 POLES | Diablo(C) | 2021-07-17 | 2021-08-18 | 2/1/0201 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Structure with non-exempt universal fuses has dried ground vegetation within 10' of its base. | Agree | N/A | N¦A |  | Create "Other tag" | Yes | No | Yes | No
100475146 | DIABLO D0822 POLES | Diablo(C) | 2021-07-17 | 2021-08-17 | 2/1/0201 | Conductor: Conductor has splices tied in proximity to insulator preventing free movement of splice with conductor | [Answer left blank] | Splices appear to be tied within 2' of insulators. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100475091 | DIABLO D0822 POLES | Diablo(C) | 2021-07-18 | 2021-08-17 | 2/1/0201 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Structure with non-exempt split bolt connectors has dried ground vegetation within 10' of its base. | Agree | N/A | N¦A |  | Create "Other tag" | Yes | No | Yes | No
100475113 | DIABLO D0822 POLES | Diablo(C) | 2021-07-18 | 2021-08-17 | 2/1/0201 | Other Required Data: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100475126 | DIABLO D0822 POLES | Diablo(C) | 2021-07-18 | 2021-08-17 | 2/1/0201 | Other Required Data: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100475139 | DIABLO D0822 POLES | Diablo(C) | 2021-07-18 | 2021-08-17 | 2/1/0201 | Other Required Data: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100475075 | DIABLO D0822 POLES | Diablo(C) | 2021-07-19 | 2021-08-17 | 2/1/0201 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Structure with non-exempt universal fuses has dried vegetation within 10' of its base. | Agree | N/A | N¦A |  | Create "Other tag" | Yes | No | Yes | No
100475075 | DIABLO D0822 POLES | Diablo(C) | 2021-07-19 | 2021-08-17 | 2/1/0201 | Non-Time-Dependent Issues: Operating number missing, broken, illegible, not installed in field or incorrectly installed in field | [Answer left blank] | Operating number for non-exempt universal fuses appears to be missing. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101668673 | COAST L1217 POLES | Central Coast(S) | 2021-07-22 | 2021-08-25 | 2/1/0201 | Non-Time-Dependent Issues: Visibility strips missing, broken, mismatched, or no longer reflective | [Answer left blank] | Visibility strips are missing. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101668679 | COAST L1217 POLES | Central Coast(S) | 2021-07-22 | 2021-08-25 | 2/1/0201 | Conductor: Conductor has splices tied in proximity to insulator preventing free movement of splice with conductor | [Answer left blank] | Splices appear to be tied within 2' of an insulator. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101668679 | COAST L1217 POLES | Central Coast(S) | 2021-07-22 | 2021-08-25 | 2/1/0201 | Other Required Data: 3 or more splices present in one phase of the span | Energized Phases: 1, Splice Count: (3) for a total of 3 Splices. Span crosses over major roadway: No | There are 2 phases on this pole. There are 4 splices on the span southeast of the pole, with 3 splices on the northeast phase and 1 splice on the southwest phase. The monitor team also notes this observation with an adjacent asset (Equipment No. 103973756) There are 8 splices on the northwest span with 4 splices on the top phase and 4 splices on the bottom phase.Neither span crosses over a major roadway. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101668689 | COAST MAP L1216 POLES | Central Coast(S) | 2021-07-22 | 2021-08-25 | 2/1/0201 | Conductor: Conductor has splices tied in proximity to insulator preventing free movement of splice with conductor | [Answer left blank] | A splice appears to be tied within 2' of an insulator. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101668689 | COAST MAP L1216 POLES | Central Coast(S) | 2021-07-22 | 2021-08-25 | 2/1/0201 | Hardware and Framing: Tap clamps installed incorrectly | [Answer left blank] | A tap clamp appears to be installed on an armor rod rather than on a tap guard. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101668689 | COAST MAP L1216 POLES | Central Coast(S) | 2021-07-22 | 2021-08-25 | 2/1/0201 | Non-Time-Dependent Issues: Visibility strips missing, broken, mismatched, or no longer reflective | [Answer left blank] | Visibility strips are missing. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101668689 | COAST MAP L1216 POLES | Central Coast(S) | 2021-07-22 | 2021-08-25 | 2/1/0201 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | High voltage sign is missing from one side of the pole. | Disagree | Condition is not compelling | 1. High Voltage Sign Not Installed as Required - TD-2305M-JA02, Rev. 8 - Pg. 61 | The one high sign on the back of the pole satisfies the standard found in OH: Marking, Rev. #18: 11/01/18 022168 Page 3 of 35. Marking, Numbering, and Identification of Line Structures 3. Routine Inspection A. The requirement in 1, “Poles That Support Line Conductors,” must be satisfied with the following exceptions: 1. Sign the Pole: It is acceptable to have only one sign, or stacked pairs of signs, below the lowest line conductor energized above 750 V, except as noted in 4 “Special Locations.” B. The requirements in 2, Poles That Do Not Support Line Conductors,” must be satisfied with the following exceptions: 1. Risers: It is acceptable to have only one sign, or stacked pairs of signs, below risers energized above 750 V. 4. Special Locations: If the pole is signed, high-voltage signs are required on both sides of the pole in the following locations:  Near water areas suitable for sailboats.  Near established boat ramps and associated rigging areas.  Adjacent to swimming pools.  In agricultural areas with movable irrigation piping.  Locations, where in the judgement of the employee, high-voltage signs should be visible from all sides of the poles. | N\A | N\A | N\A | N\A | N\A
101801457 | COAST L1217 POLES | Central Coast(S) | 2021-07-22 | 2021-08-25 | 2/1/0201 | Conductor: Conductor has splices tied in proximity to insulator preventing free movement of splice with conductor | [Answer left blank] | A splice appears to be tied within 2' of an insulator. | Agree | N/A | N¦A | 116824645 | Update a EC | Yes | No | Yes | No
101801457 | COAST L1217 POLES | Central Coast(S) | 2021-07-22 | 2021-08-25 | 2/1/0201 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Structure with non-exempt universal fuses has dried ground vegetation within 10' of its base. | Agree | N/A | N¦A |  | Create "Other tag" | Yes | No | Yes | No
103826923 | COAST L1217 POLES | Central Coast(S) | 2021-07-22 | 2021-08-25 | 2/2/0201 | Hardware and Framing: Molding missing, broken, damaged, or loose | [Answer left blank] | There is a 6" gap in the molding at the ground level. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | Yes
103826923 | COAST L1217 POLES | Central Coast(S) | 2021-07-22 | 2021-08-25 | 2/2/0201 | Hardware and Framing: Grounds exposed, broken, damaged, disconnected, unsecured, or missing (if required) | [Answer left blank] | There is 6" of exposed ground wire at the ground level. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | Yes
103826923 | COAST L1217 POLES | Central Coast(S) | 2021-07-22 | 2021-08-25 | 2/2/0201 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Structure with non-exempt universal fuses has dried ground vegetation within 10' of its base. | Agree | N/A | N¦A |  | Create "Other tag" | Yes | No | Yes | No
104044369 | PENINSULA D0816 POLES | Peninsula(C) | 2021-07-22 | 2021-08-18 | 2/2/0201 | Anchor and Guys: Does or should this location have a Guy? | No | There is a span guy present at this location. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
104044369 | PENINSULA D0816 POLES | Peninsula(C) | 2021-07-22 | 2021-08-18 | 2/2/0201 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | Open wire secondary is present at this location. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
104044369 | PENINSULA D0816 POLES | Peninsula(C) | 2021-07-22 | 2021-08-18 | 2/2/0201 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | Pole number is visible. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
9.03 REPORT
102259135 | NORTH BAY MAP SS3020 POLES | North Bay(C) | 2021-06-26 | 2021-08-12 | 2021-12-07 | Other Required Data: Is there non-exempt equipment at the inspection location (Universal or Open Link Fuse) | Yes | Fuses are exempt. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102295516 | NORTH BAY MAP SS3020 POLES | North Bay(C) | 2021-06-26 | 2021-08-12 | 2021-12-07 | Anchor and Guys: Does or should this location have a Guy? | [Answer left blank] | Pole does not have a guy, and pole does not appear to need a guy because there is a support structure present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102295516 | NORTH BAY MAP SS3020 POLES | North Bay(C) | 2021-06-26 | 2021-08-12 | 2021-12-07 | Other Required Data: Support structure or stub present | [Answer left blank] | There is a wood support structure present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100707957 | FRESNO 14252 POLES | Fresno(S) | 2021-06-24 | 2021-08-10 | 2021-12-07 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks and signs of decay on the pole, including at the top near where hardware is attached. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100707957 | FRESNO 14252 POLES | Fresno(S) | 2021-06-24 | 2021-08-10 | 2021-12-07 | Hardware and Framing: Crossarm integrity compromised by any of the following; damaged, broken, burnt, decayed, rotten, loose, missing hardware or showing severe signs of bent bolts or brackets, damaged bracing, gun shots, insect damage or woodpecker damage, splitting, or fails to meet clearance requirements | [Answer left blank] | The top crossarm bolt appears to be loose. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100707957 | FRESNO 14252 POLES | Fresno(S) | 2021-06-24 | 2021-08-10 | 2021-12-07 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Structure with non-exempt lightning arresters appears to have dried ground vegetation within 10' of its base. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100707957 | FRESNO 14252 POLES | Fresno(S) | 2021-06-24 | 2021-08-10 | 2021-12-07 | Other Required Data: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100707957 | FRESNO 14252 POLES | Fresno(S) | 2021-06-24 | 2021-08-10 | 2021-12-07 | Other Required Data: Is there non-exempt equipment at the inspection location (Lightning or Surge Arrester) | [Answer left blank] | Non-exempt lightning arresters are present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100707957 | FRESNO 14252 POLES | Fresno(S) | 2021-06-24 | 2021-08-10 | 2021-12-07 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | High voltage sign is missing from one side of the pole. | Disagree | Condition is not compelling | 1. High Voltage Sign Not Installed as Required - TD-2305M-JA02, Rev. 8 - Pg. 61 | The one high sign on the back of the pole satisfies the standard found in OH: Marking, Rev. #18: 11/01/18 022168 Page 3 of 35. Marking, Numbering, and Identification of Line Structures 3. Routine Inspection A. The requirement in 1, “Poles That Support Line Conductors,” must be satisfied with the following exceptions: 1. Sign the Pole: It is acceptable to have only one sign, or stacked pairs of signs, below the lowest line conductor energized above 750 V, except as noted in 4 “Special Locations.” B. The requirements in 2, Poles That Do Not Support Line Conductors,” must be satisfied with the following exceptions: 1. Risers: It is acceptable to have only one sign, or stacked pairs of signs, below risers energized above 750 V. 4. Special Locations: If the pole is signed, high-voltage signs are required on both sides of the pole in the following locations: Near water areas suitable for sailboats. Near established boat ramps and associated rigging areas. Adjacent to swimming pools. In agricultural areas with movable irrigation piping. Locations, where in the judgement of the employee, high-voltage signs should be visible from all sides of the poles. | N\A | N\A | N\A | N\A | N\A
100707695 | FRESNO 14252 POLES | Fresno(S) | 2021-06-24 | 2021-08-10 | 2021-12-07 | Anchor and Guys: Does or should this location have a Guy? | No | Asset appears to have an overhead guy. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100707695 | FRESNO 14252 POLES | Fresno(S) | 2021-06-24 | 2021-08-10 | 2021-12-07 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100707671 | FRESNO 14252 POLES | Fresno(S) | 2021-06-24 | 2021-08-10 | 2021-12-07 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks along the length of the pole, including near where hardware is attached. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100707671 | FRESNO 14252 POLES | Fresno(S) | 2021-06-24 | 2021-08-10 | 2021-12-07 | Anchor and Guys: Does or should this location have a Guy? | Yes | The asset does not have or appear to need a guy. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100707671 | FRESNO 14252 POLES | Fresno(S) | 2021-06-24 | 2021-08-10 | 2021-12-07 | Other Required Data: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100707671 | FRESNO 14252 POLES | Fresno(S) | 2021-06-24 | 2021-08-10 | 2021-12-07 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100707715 | FRESNO 14252 POLES | Fresno(S) | 2021-06-24 | 2021-08-10 | 2021-12-07 | Other Required Data: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | Transformer may have PCB as there is no legible blue sticker present. | Disagree | Inspector Selected Correcly | 4. Transformer – Record keeping items - TD-2305M-JA02, Rev. 8 - Pg. 74 | Picture attached to FM report shows partial blue "Non-PCB" sticker. | N\A | N\A | N\A | N\A | N\A
100707715 | FRESNO 14252 POLES | Fresno(S) | 2021-06-24 | 2021-08-10 | 2021-12-07 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | The pole number is visible on the pole. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102258701 | NORTH BAY MAP SS3011 POLES | North Bay(C) | 2021-06-22 | 2021-08-11 | 2021-12-07 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Structure with non-exempt universal fuses has dried vegetation within 10' of its base. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100691950 | FRESNO 14261 POLES | Fresno(S) | 2021-06-23 | 2021-08-11 | 2021-12-07 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks and large woodpecker holes in the top third of the pole, including one woodpecker hole below the crossarm that appears to be at least 4" in diameter. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100685682 | FRESNO 14266 POLES | Fresno(S) | 2021-06-18 | 2021-08-12 | 2021-12-07 | Common Equipment/Other Equipment: Does this structure have equipment? | Yes | The structure does not have any equipment. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100684577 | FRESNO 14266 POLES | Fresno(S) | 2021-06-22 | 2021-08-12 | 2021-12-07 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks in the middle and top of the pole, including near where hardware is attached. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100684577 | FRESNO 14266 POLES | Fresno(S) | 2021-06-22 | 2021-08-12 | 2021-12-07 | Common Equipment/Other Equipment: Does this structure have equipment? | Yes | The structure does not have any equipment. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100685414 | FRESNO 14266 POLES | Fresno(S) | 2021-06-18 | 2021-08-12 | 2021-12-07 | Other Required Data: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100685414 | FRESNO 14266 POLES | Fresno(S) | 2021-06-18 | 2021-08-12 | 2021-12-07 | Other Required Data: Is there non-exempt equipment at the inspection location (Universal or Open Link Fuse) | [Answer left blank] | Non-exempt open link fuses are present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100691944 | FRESNO 14266 POLES | Fresno(S) | 2021-06-22 | 2021-08-11 | 2021-12-07 | Hardware and Framing: Animal mitigation broken, damaged, or missing (if required) | [Answer left blank] | Animal mitigation appears to be loose. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100691944 | FRESNO 14266 POLES | Fresno(S) | 2021-06-22 | 2021-08-11 | 2021-12-07 | Non-Time-Dependent Issues: Pole steps are less than 8' 6" above the ground or any other accessible surface | [Answer left blank] | Pole step is at 8' 0" (96"). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100684726 | FRESNO 14266 POLES | Fresno(S) | 2021-06-18 | 2021-08-12 | 2021-12-07 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks throughout the pole, including near where hardware is attached. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100684726 | FRESNO 14266 POLES | Fresno(S) | 2021-06-18 | 2021-08-12 | 2021-12-07 | Hardware and Framing: Tap clamps installed incorrectly | [Answer left blank] | Tap clamps are installed on armor rods rather than on tap guards. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100684726 | FRESNO 14266 POLES | Fresno(S) | 2021-06-18 | 2021-08-12 | 2021-12-07 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | The pole number is visible on the pole. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100706987 | FRESNO 14251 POLES | Fresno(S) | 2021-06-17 | 2021-08-10 | 2021-12-07 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are a number of woodpecker holes throughout the pole, including a hole that appears to be greater than 4" in diameter. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100706987 | FRESNO 14251 POLES | Fresno(S) | 2021-06-17 | 2021-08-10 | 2021-12-07 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Structure with non-exempt solid blade disconnects has dried ground vegetation within 10' of its base. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100706987 | FRESNO 14251 POLES | Fresno(S) | 2021-06-17 | 2021-08-10 | 2021-12-07 | Other Required Data: Is there non-exempt equipment at the inspection location (Solid Blade or In-line disconnect) | [Answer left blank] | Non-exempt solid blade disconnects are present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100684732 | FRESNO 14266 POLES | Fresno(S) | 2021-06-18 | 2021-08-12 | 2021-12-07 | Common Equipment/Other Equipment: Does this structure have equipment? | Yes | The structure does not have any equipment. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100684732 | FRESNO 14266 POLES | Fresno(S) | 2021-06-18 | 2021-08-12 | 2021-12-07 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | The pole number is visible on the pole. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102227836 | NORTH BAY MAP SS3116 POLES | North Bay(C) | 2021-06-16 | 2021-08-12 | 2021-12-07 | Non-Time-Dependent Issues: Visibility strips missing, broken, mismatched, or no longer reflective | [Answer left blank] | Visibility strips are no longer reflective, and one is missing. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102227836 | NORTH BAY MAP SS3116 POLES | North Bay(C) | 2021-06-16 | 2021-08-12 | 2021-12-07 | Other Required Data: Tree anchor installed in tree by design | [Answer left blank] | A tree anchor is installed in tree by design. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103848150 | NORTH BAY MAP SS3011 POLES | North Bay(C) | 2021-06-16 | 2021-08-11 | 2021-12-07 | Vegetation: Tree causing strain or abrasion to secondary or service (only 1 service) | [Answer left blank] | Tree appears to be causing strain on service conductor. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100691943 | FRESNO 14261 POLES | Fresno(S) | 2021-06-17 | 2021-08-11 | 2021-12-07 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks in the top third of the pole, including near where hardware is attached. | Agree | N/A | N¦A | 110491301 | Update a EC | Yes | No | Yes | No
100707251 | FRESNO 14251 POLES | Fresno(S) | 2021-06-15 | 2021-08-10 | 2021-12-07 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There appear to be 2 woodpecker holes greater than 4" in diameter. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100707251 | FRESNO 14251 POLES | Fresno(S) | 2021-06-15 | 2021-08-10 | 2021-12-07 | Hardware and Framing: Secondary connectors (mini wedge and Insulink) installed on primary conductor | [Answer left blank] | There appear to be Insulink connectors installed on the primary conductor. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100707251 | FRESNO 14251 POLES | Fresno(S) | 2021-06-15 | 2021-08-10 | 2021-12-07 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | The high voltage sign on the east side of the pole is broken. | Disagree | Condition is not compelling | 1. High Voltage Sign Not Installed as Required - TD-2305M-JA02, Rev. 8 - Pg. 61 | The one high sign in good condition on the opposite side of the pole satisfies the standard found in OH: Marking, Rev. #18: 11/01/18 022168 Page 3 of 35. Marking, Numbering, and Identification of Line Structures 3. Routine Inspection A. The requirement in 1, “Poles That Support Line Conductors,” must be satisfied with the following exceptions: 1. Sign the Pole: It is acceptable to have only one sign, or stacked pairs of signs, below the lowest line conductor energized above 750 V, except as noted in 4 “Special Locations.” B. The requirements in 2, Poles That Do Not Support Line Conductors,” must be satisfied with the following exceptions: 1. Risers: It is acceptable to have only one sign, or stacked pairs of signs, below risers energized above 750 V. 4. Special Locations: If the pole is signed, high-voltage signs are required on both sides of the pole in the following locations: Near water areas suitable for sailboats. Near established boat ramps and associated rigging areas. Adjacent to swimming pools. In agricultural areas with movable irrigation piping. Locations, where in the judgement of the employee, high-voltage signs should be visible from all sides of the poles. | N\A | N\A | N\A | N\A | N\A
102227845 | NORTH BAY MAP SS3116 POLES | North Bay(C) | 2021-06-15 | 2021-08-12 | 2021-12-08 | Anchor and Guys: Select if there are risks, hazards, or other maintenance conditions not previously captured in the checklist for Anchor & Guys section | [Answer left blank] | Down guy is located in a driveway. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102227845 | NORTH BAY MAP SS3116 POLES | North Bay(C) | 2021-06-15 | 2021-08-12 | 2021-12-08 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | Open wire secondary is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102227780 | NORTH BAY MAP SS3116 POLES | North Bay(C) | 2021-06-16 | 2021-08-12 | 2021-12-08 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Structure with non-exempt universal fuses has dried vegetation within 10' of its base. | Disagree | Inspector Selected Correcly | ELEC-1000 Training | ELEC-0342 Day 3 pg. 154. Pole is installed in a landscaped residential area. Vegetation on the ground is green and not dried. Inspect App question reads Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base. Inspector selected correctly. | N\A | N\A | N\A | N\A | N\A
102227780 | NORTH BAY MAP SS3116 POLES | North Bay(C) | 2021-06-16 | 2021-08-12 | 2021-12-08 | Other Required Data: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102227780 | NORTH BAY MAP SS3116 POLES | North Bay(C) | 2021-06-16 | 2021-08-12 | 2021-12-08 | Other Required Data: Is there non-exempt equipment at the inspection location (Universal or Open Link Fuse) | [Answer left blank] | Non-exempt universal fuses are present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100707213 | FRESNO 14251 POLES | Fresno(S) | 2021-06-15 | 2021-08-10 | 2021-12-08 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | The asset has a number of woodpecker holes, including at least 3 holes that appear to be more than 9” wide when measured as the sum of diameters within a 1’ vertical section. | Agree | N/A | N¦A | Condition is already attached to an EC Notification (116721523). Inspector did complete FSR to update Notification but did not indicate condition in Structure section of Inspection Record. | N\A | N\A | N\A | N\A | N\A
100707421 | FRESNO 14251 POLES | Fresno(S) | 2021-06-15 | 2021-08-10 | 2021-12-08 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are large woodpecker holes in the top half of the pole, including holes that appear to be larger than 4" in diameter. | Agree | N/A | N¦A | Condition is already attached to an EC Notification (116721293). Inspector did complete FSR to update Notification but did not indicate condition in Structure section of Inspection Record. | N\A | N\A | N\A | N\A | N\A
100707421 | FRESNO 14251 POLES | Fresno(S) | 2021-06-15 | 2021-08-10 | 2021-12-08 | Hardware and Framing: Tap clamps installed incorrectly | [Answer left blank] | Tap clamps are installed on armor rods rather than on tap guards. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100707421 | FRESNO 14251 POLES | Fresno(S) | 2021-06-15 | 2021-08-10 | 2021-12-08 | Non-Time-Dependent Issues: Visibility strips missing, broken, mismatched, or no longer reflective | [Answer left blank] | Visibility strips are no longer reflective, and one is missing. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100707421 | FRESNO 14251 POLES | Fresno(S) | 2021-06-15 | 2021-08-10 | 2021-12-08 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | High voltage sign on the south side of the pole is partially missing. | Disagree | Condition is not compelling | 1. High Voltage Sign Not Installed as Required - TD-2305M-JA02, Rev. 8 - Pg. 61 | The one high sign in good condition on the opposite side of the pole satisfies the standard found in OH: Marking, Rev. #18: 11/01/18 022168 Page 3 of 35. Marking, Numbering, and Identification of Line Structures 3. Routine Inspection A. The requirement in 1, “Poles That Support Line Conductors,” must be satisfied with the following exceptions: 1. Sign the Pole: It is acceptable to have only one sign, or stacked pairs of signs, below the lowest line conductor energized above 750 V, except as noted in 4 “Special Locations.” B. The requirements in 2, Poles That Do Not Support Line Conductors,” must be satisfied with the following exceptions: 1. Risers: It is acceptable to have only one sign, or stacked pairs of signs, below risers energized above 750 V. 4. Special Locations: If the pole is signed, high-voltage signs are required on both sides of the pole in the following locations: Near water areas suitable for sailboats. Near established boat ramps and associated rigging areas. Adjacent to swimming pools. In agricultural areas with movable irrigation piping. Locations, where in the judgement of the employee, high-voltage signs should be visible from all sides of the poles. | N\A | N\A | N\A | N\A | N\A
100707205 | FRESNO 14251 POLES | Fresno(S) | 2021-06-15 | 2021-08-10 | 2021-12-08 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks along the length of the pole, including at the top near where hardware is attached. | Agree | N/A | N¦A | Condition is already attached to an EC Notification (116719738). Inspector did complete FSR to update Notification but did not indicate condition in Structure section of Inspection Record. | N\A | N\A | N\A | N\A | N\A
100707247 | FRESNO 14251 POLES | Fresno(S) | 2021-06-15 | 2021-08-10 | 2021-12-08 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are large cracks along the length of the pole, including near where hardware is attached. | Agree | N/A | N¦A | Condition is already attached to an EC Notification (116720095). Inspector did complete FSR to update Notification but did not indicate condition in Structure section of Inspection Record. | N\A | N\A | N\A | N\A | N\A
100707247 | FRESNO 14251 POLES | Fresno(S) | 2021-06-15 | 2021-08-10 | 2021-12-08 | Equipment: Transformer flashed or corroded, e.g. integrity of the metal is breached – holes in metal, cover not securable, metal is damaged, separation, layering, bulging or bubbling | [Answer left blank] | The transformer appears to show signs of flashing. | Disagree | Inspector Selected Correcly | 2. Corrosion - TD-2305M-JA02, Rev. 8 - Pg. 71 | After reviewing photos, there is a stain on the SP transcormer below the switch that is possibly from an old leak. TX does not appear to have experienced an arc flash. | N\A | N\A | N\A | N\A | N\A
100707247 | FRESNO 14251 POLES | Fresno(S) | 2021-06-15 | 2021-08-10 | 2021-12-08 | Other Required Data: Support structure or stub present | [Answer left blank] | There is a steel truss connected to the pole. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100707247 | FRESNO 14251 POLES | Fresno(S) | 2021-06-15 | 2021-08-10 | 2021-12-08 | Other Required Data: Is there non-exempt equipment at the inspection location (Lightning or Surge Arrester) | [Answer left blank] | Non-exempt lightning arresters are present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100707247 | FRESNO 14251 POLES | Fresno(S) | 2021-06-15 | 2021-08-10 | 2021-12-08 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | High voltage sign is missing from the east side of the pole. | Disagree | Condition is not compelling | 1. High Voltage Sign Not Installed as Required - TD-2305M-JA02, Rev. 8 - Pg. 61 | The one high sign in good condition on the opposite side of the pole satisfies the standard found in OH: Marking, Rev. #18: 11/01/18 022168 Page 3 of 35. Marking, Numbering, and Identification of Line Structures 3. Routine Inspection A. The requirement in 1, “Poles That Support Line Conductors,” must be satisfied with the following exceptions: 1. Sign the Pole: It is acceptable to have only one sign, or stacked pairs of signs, below the lowest line conductor energized above 750 V, except as noted in 4 “Special Locations.” B. The requirements in 2, Poles That Do Not Support Line Conductors,” must be satisfied with the following exceptions: 1. Risers: It is acceptable to have only one sign, or stacked pairs of signs, below risers energized above 750 V. 4. Special Locations: If the pole is signed, high-voltage signs are required on both sides of the pole in the following locations: Near water areas suitable for sailboats. Near established boat ramps and associated rigging areas. Adjacent to swimming pools. In agricultural areas with movable irrigation piping. Locations, where in the judgement of the employee, high-voltage signs should be visible from all sides of the poles. | N\A | N\A | N\A | N\A | N\A
102224767 | NORTH BAY MAP SS3121 POLES | North Bay(C) | 2021-06-14 | 2021-08-12 | 2021-12-08 | Anchor and Guys: Guy wire broken, damaged, clearance issues, corroded, covered by vegetation, overgrown, strain or abrasion | [Answer left blank] | Tree appears to be causing strain on guy wire. | Agree | N/A | N¦A | 121532839 | Update a EC | Yes | No | Yes | No
102224767 | NORTH BAY MAP SS3121 POLES | North Bay(C) | 2021-06-14 | 2021-08-12 | 2021-12-08 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Structure with non-exempt split bolt connectors has dried ground vegetation within 10' of its base. | Agree | N/A | N¦A |  | Create "Other tag" | Yes | No | Yes | No
102224767 | NORTH BAY MAP SS3121 POLES | North Bay(C) | 2021-06-14 | 2021-08-12 | 2021-12-08 | Non-Time-Dependent Issues: Pole steps are less than 8' 6" above the ground or any other accessible surface | [Answer left blank] | Pole step is at 8' 0" (96"). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102224767 | NORTH BAY MAP SS3121 POLES | North Bay(C) | 2021-06-14 | 2021-08-12 | 2021-12-08 | Other Required Data: Is there non-exempt equipment at the inspection location (Hot tap clamp or Split Bolt connector) | [Answer left blank] | Non-exempt split bolt connectors are present. | Agree | N/A | N¦A | 121532839 | Update a EC | Yes | No | Yes | No
102253342 | NORTH BAY MAP UU3216 POLES | North Bay(C) | 2021-06-14 | 2021-08-10 | 2021-12-08 | Non-Time-Dependent Issues: Pole steps are less than 8' 6" above the ground or any other accessible surface | [Answer left blank] | Pole step is at 8' 3" (99"). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100707211 | FRESNO 14251 POLES | Fresno(S) | 2021-06-15 | 2021-08-10 | 2021-12-08 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks in the top third of the pole, including near where hardware is attached. | Disagree | N/A | N¦A | Condition is already attached to an EC Notification (116721391). Inspector did complete FSR to update Notification but did not indicate condition in Structure section of Inspection Record. | N\A | N\A | N\A | N\A | N\A
100707211 | FRESNO 14251 POLES | Fresno(S) | 2021-06-15 | 2021-08-10 | 2021-12-08 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102253414 | NORTH BAY MAP UU3216 POLES | North Bay(C) | 2021-06-13 | 2021-08-10 | 2021-12-08 | Common Equipment/Other Equipment: Does this structure have equipment? | No | Equipment (transformer) is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102253459 | NORTH BAY MAP UU3216 POLES | North Bay(C) | 2021-06-13 | 2021-08-10 | 2021-12-08 | Conductor: Service conductor has diminished clearance | [Answer left blank] | The service conductor appears to have diminished clearance from a structure on private property. | Agree | N/A | N¦A | Inspector identified this condition in Inspection Record | N\A | N\A | N\A | N\A | N\A
102253459 | NORTH BAY MAP UU3216 POLES | North Bay(C) | 2021-06-13 | 2021-08-10 | 2021-12-08 | Vegetation: Distribution Facility / Pole located in State Responsibility Area (SRA) / Federal Responsibility Area (FRA) / High Fire Threat District (HFTD) with vegetation within 4’ of primary conductor | [Answer left blank] | There appears to be vegetation within 4' of primary conductor on the span northwest of the pole. | Agree | N/A | N¦A |  | Create "Other tag" | Yes | No | Yes | No
103325219 | FRESNO 14251 POLES | Fresno(S) | 2021-06-13 | 2021-08-10 | 2021-12-08 | Non-Time-Dependent Issues: Pole steps are less than 8' 6" above the ground or any other accessible surface | [Answer left blank] | Pole step is at 8' 2" (98"). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102224757 | NORTH BAY MAP SS3121 POLES | North Bay(C) | 2021-06-14 | 2021-08-12 | 2021-12-08 | Anchor and Guys: Does or should this location have a Guy? | [Answer left blank] | There are down guys present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102224757 | NORTH BAY MAP SS3121 POLES | North Bay(C) | 2021-06-14 | 2021-08-12 | 2021-12-08 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Structure with non-exempt split bolt connectors appears to have dried ground vegetation within 10' of its base. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102224757 | NORTH BAY MAP SS3121 POLES | North Bay(C) | 2021-06-14 | 2021-08-12 | 2021-12-08 | Non-Time-Dependent Issues: Pole steps are less than 8' 6" above the ground or any other accessible surface | [Answer left blank] | Pole step is at 7' 4" (88"). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102224757 | NORTH BAY MAP SS3121 POLES | North Bay(C) | 2021-06-14 | 2021-08-12 | 2021-12-08 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | Secondary at this location[Answer left blank] | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102224757 | NORTH BAY MAP SS3121 POLES | North Bay(C) | 2021-06-14 | 2021-08-12 | 2021-12-08 | Other Required Data: Is there non-exempt equipment at the inspection location (Hot tap clamp or Split Bolt connector) | [Answer left blank] | Non-exempt split bolt connectors are present. | Agree | N/A | N¦A | 119289869 | Update a EC | Yes | No | Yes | No
102224757 | NORTH BAY MAP SS3121 POLES | North Bay(C) | 2021-06-14 | 2021-08-12 | 2021-12-08 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | High voltage sign is missing from one side of the pole. | Disagree | Condition is not compelling | 1. High Voltage Sign Not Installed as Required - TD-2305M-JA02, Rev. 8 - Pg. 61 | The one high sign in good condition on the opposite side of the pole satisfies the standard found in OH: Marking, Rev. #18: 11/01/18 022168 Page 3 of 35. Marking, Numbering, and Identification of Line Structures 3. Routine Inspection A. The requirement in 1, “Poles That Support Line Conductors,” must be satisfied with the following exceptions: 1. Sign the Pole: It is acceptable to have only one sign, or stacked pairs of signs, below the lowest line conductor energized above 750 V, except as noted in 4 “Special Locations.” B. The requirements in 2, Poles That Do Not Support Line Conductors,” must be satisfied with the following exceptions: 1. Risers: It is acceptable to have only one sign, or stacked pairs of signs, below risers energized above 750 V. 4. Special Locations: If the pole is signed, high-voltage signs are required on both sides of the pole in the following locations: Near water areas suitable for sailboats. Near established boat ramps and associated rigging areas. Adjacent to swimming pools. In agricultural areas with movable irrigation piping. Locations, where in the judgement of the employee, high-voltage signs should be visible from all sides of the poles. | N\A | N\A | N\A | N\A | N\A
100691902 | FRESNO 14261 POLES | Fresno(S) | 2021-06-13 | 2021-08-11 | 2021-12-08 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | The asset has several large woodpecker holes, including one that appears to be at least 4" in diameter. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100691902 | FRESNO 14261 POLES | Fresno(S) | 2021-06-13 | 2021-08-11 | 2021-12-08 | Other Required Data: 3 or more splices present in one phase of the span | [Answer left blank] | There are 2 phases on the pole. There are 5 splices on the span west of the pole, with 3 splices on the south phase and 2 splices on the north phase. Span does not cross over a major roadway.The Monitor team also notes this observation in connection with an adjacent asset (Equipment ID 100691901). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100691910 | FRESNO 14261 POLES | Fresno(S) | 2021-06-13 | 2021-08-11 | 2021-12-08 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100691910 | FRESNO 14261 POLES | Fresno(S) | 2021-06-13 | 2021-08-11 | 2021-12-08 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Structure with non-exempt equipment (universal fuses and lightning arresters) has dried ground vegetation within 10' of its base. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102227480 | NORTH BAY SS3117 POLE | North Bay(C) | 6/13/2021 | 2021-08-12 | 2021-12-08 | Hardware and Framing: Is Hardware Framing present on this structure? | [Answer left blank] | Crossarm and associated hardware are present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102227480 | NORTH BAY SS3117 POLE | North Bay(C) | 6/13/2021 | 2021-08-12 | 2021-12-08 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Structure with non-exempt universal fuses has dried ground vegetation within 10' of its base. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102227480 | NORTH BAY SS3117 POLE | North Bay(C) | 6/13/2021 | 2021-08-12 | 2021-12-08 | Other Required Data: Is there non-exempt equipment at the inspection location (Universal or Open Link Fuse) | [Answer left blank] | Universal fuses are present on this asset. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100691901 | FRESNO 14261 POLES | Fresno(S) | 2021-06-13 | 2021-08-11 | 2021-12-08 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | The pole is cracked/decaying, such that daylight can be seen through the pole. | Agree | N/A | ELEC-1000 Training | Pole was replaced on Emergency on 8/11/21 | N\A | N\A | N\A | N\A | N\A
100691901 | FRESNO 14261 POLES | Fresno(S) | 2021-06-13 | 2021-08-11 | 2021-12-08 | Other Required Data: 3 or more splices present in one phase of the span | [Answer left blank] | There are 2 phases on the pole. There are 5 splices on the span east of the pole, with 3 splices on the south phase and 2 splices on the north phase. Span does not cross over a major roadway.The Monitor team also notes this observation in connection with an adjacent asset (Equipment ID 100691902). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100691803 | FRESNO 14261 POLES | Fresno(S) | 2021-06-13 | 2021-08-11 | 2021-12-08 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100691803 | FRESNO 14261 POLES | Fresno(S) | 2021-06-13 | 2021-08-11 | 2021-12-08 | Vegetation: Support Structure with non-exempt equipment, has dried vegetation from ground to 8' above ground, within 10' radius of Support Structure base | [Answer left blank] | Structure with non-exempt equipment (open link fuses and lightning arresters) has dried vegetation from ground to 8' above ground, within 10' radius of its base. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100691879 | FRESNO 14261 POLES | Fresno(S) | 2021-06-13 | 2021-08-11 | 2021-12-08 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | The pole has cracks at the top, including near where hardware is attached. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100691879 | FRESNO 14261 POLES | Fresno(S) | 2021-06-13 | 2021-08-11 | 2021-12-08 | Hardware and Framing: Animal mitigation broken, damaged, or missing (if required) | [Answer left blank] | Animal mitigation appears to be loose. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100691879 | FRESNO 14261 POLES | Fresno(S) | 2021-06-13 | 2021-08-11 | 2021-12-08 | Other Required Data: Support structure or stub present | [Answer left blank] | There is a wood support structure present. | Disagree | Inspector Selected Correcly | ELEC-1000 Training | Push pole support structure is attached at commuications level, push pole does not appear to have any identifying PG&E markings and does not show on Webview map | N\A | N\A | N\A | N\A | N\A
100691881 | FRESNO 14261 POLES | Fresno(S) | 2021-06-13 | 2021-08-11 | 2021-12-09 | Other Required Data: Support structure or stub present | [Answer left blank] | There is a wood support structure present. | Disagree | Inspector Selected Correcly | ELEC-1000 Training | Push pole support structure is attached at commuications level, push pole does not appear to have any identifying PG&E markings and does not show on Webview map | N\A | N\A | N\A | N\A | N\A
102227416 | NORTH BAY SS3117 POLES | North Bay(C) | 2021-06-12 | 2021-08-12 | 2021-12-09 | Vegetation: Tree causing strain or abrasion to secondary or service (only 1 service) | [Answer left blank] | Tree appears to be causing strain on service drop. | Agree | N/A | N¦A | 119211253 | Update a EC | Yes | No | Yes | No
102227416 | NORTH BAY SS3117 POLES | North Bay(C) | 2021-06-12 | 2021-08-12 | 2021-12-09 | Non-Time-Dependent Issues: Pole steps are less than 8' 6" above the ground or any other accessible surface | [Answer left blank] | Pole step is at 7' 9" (93"). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102227416 | NORTH BAY SS3117 POLES | North Bay(C) | 2021-06-12 | 2021-08-12 | 2021-12-09 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | Open wire secondary is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103148046 | NORTH BAY SS3117 POLES | North Bay(C) | 2021-06-12 | 2021-08-12 | 2021-12-09 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | Pole number is visible. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103599283 | NORTH BAY MAP SS3121 POLES | North Bay(C) | 2021-06-12 | 2021-08-12 | 2021-12-09 | Anchor and Guys: Guy wire broken, damaged, clearance issues, corroded, covered by vegetation, overgrown, strain or abrasion | [Answer left blank] | Vegetation appears to be in contact with guy wire above guy insulator. | Agree | N/A | N¦A | Condition is already attached to an EC Notification (112407938). Inspector did complete FSR to update Notification but did not indicate condition in Anchor and Guy section of Inspection Record. | N\A | N\A | N\A | N\A | N\A
102227423 | NORTH BAY SS3117 POLES | North Bay(C) | 2021-06-12 | 2021-08-12 | 2021-12-09 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | Open wire secondary is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102253447 | NORTH BAY MAP UU3216 POLES | North Bay(C) | 2021-06-12 | 2021-08-10 | 2021-12-09 | Anchor and Guys: Guy wire broken, damaged, clearance issues, corroded, covered by vegetation, overgrown, strain or abrasion | [Answer left blank] | Broken tree limb appears to be causing strain on span guy. | Agree | N/A | N¦A | 119465293 | Update a EC | Yes | No | Yes | No
102253447 | NORTH BAY MAP UU3216 POLES | North Bay(C) | 2021-06-12 | 2021-08-10 | 2021-12-09 | Vegetation: Tree causing strain or abrasion to secondary or service (only 1 service) | [Answer left blank] | Broken tree limb appears to be causing strain on secondary conductor. | Agree | N/A | N¦A | 119465293 | Update a EC | Yes | No | Yes | No
100691905 | FRESNO 14261 POLES | Fresno(S) | 2021-06-12 | 2021-08-11 | 2021-12-09 | Vegetation: Does this structure have vegetation present? | [Answer left blank] | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100691905 | FRESNO 14261 POLES | Fresno(S) | 2021-06-12 | 2021-08-11 | 2021-12-09 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Structure with non-exempt lightning arrestors has dried vegetation within a 10' radius of its base. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102225821 | NORTH BAY MAP SS3121 POLES | North Bay(C) | 2021-06-12 | 2021-08-12 | 2021-12-09 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | Open wire secondary is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102225821 | NORTH BAY MAP SS3121 POLES | North Bay(C) | 2021-06-12 | 2021-08-12 | 2021-12-09 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102227397 | NORTH BAY SS3117 POLES | North Bay(C) | 2021-06-12 | 2021-08-12 | 2021-12-09 | Anchor and Guys: Does or should this location have a Guy? | [Answer left blank] | There are span guys present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102227397 | NORTH BAY SS3117 POLES | North Bay(C) | 2021-06-12 | 2021-08-12 | 2021-12-09 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Structure with non-exempt universal link fuses has dried vegetation within 10' of its base. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102227388 | NORTH BAY SS3117 POLES | North Bay(C) | 2021-06-11 | 2021-08-12 | 2021-12-09 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | Open wire secondary conductor is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102227389 | NORTH BAY SS3117 POLES | North Bay(C) | 2021-06-11 | 2021-08-12 | 2021-12-09 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | Open wire secondary is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102253252 | NORTH BAY MAP UU3216 POLES | North Bay(C) | 2021-06-11 | 2021-08-10 | 2021-12-09 | Vegetation: Distribution Facility / Pole located in State Responsibility Area (SRA) / Federal Responsibility Area (FRA) / High Fire Threat District (HFTD) with vegetation within 4’ of primary conductor | [Answer left blank] | There appears to be vegetation within 4' of primary conductor on south phase of the span east of the pole. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102253306 | NORTH BAY MAP UU3216 POLES | North Bay(C) | 2021-06-11 | 2021-08-10 | 2021-12-09 | Non-Time-Dependent Issues: Pole steps are less than 8' 6" above the ground or any other accessible surface | [Answer left blank] | Pole step is at 6' 8" (80"). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102253306 | NORTH BAY MAP UU3216 POLES | North Bay(C) | 2021-06-11 | 2021-08-10 | 2021-12-09 | Other Required Data: 3 or more splices present in one phase of the span | [Answer left blank] | The pole has 3 phases. The middle phase of the span northeast of the pole appears to have 3 splices. Span does not cross over a major roadway. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102227391 | NORTH BAY SS3117 POLES | North Bay(C) | 2021-06-11 | 2021-08-12 | 2021-12-09 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | Open wire secondary is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102259288 | NORTH BAY MAP SS3012 POLES | North Bay(C) | 2021-06-05 | 2021-08-11 | 2021-12-09 | Non-Time-Dependent Issues: Pole steps are less than 8' 6" above the ground or any other accessible surface | [Answer left blank] | Pole step is at 7' 9" (93"). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102225840 | NORTH BAY MAP SS3121 POLES | North Bay(C) | 2021-06-11 | 2021-08-12 | 2021-12-09 | Non-Time-Dependent Issues: Pole steps are less than 8' 6" above the ground or any other accessible surface | [Answer left blank] | Pole step is at 7' 7" (91"). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102225840 | NORTH BAY MAP SS3121 POLES | North Bay(C) | 2021-06-11 | 2021-08-12 | 2021-12-09 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | Open wire secondary is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102227282 | NORTH BAY SS3117 POLES | North Bay(C) | 2021-06-11 | 2021-08-12 | 2021-12-09 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | Open wire secondary is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102227286 | NORTH BAY SS3117 POLES | North Bay(C) | 2021-06-11 | 2021-08-12 | 2021-12-09 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | Open wire secondary is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102227286 | NORTH BAY SS3117 POLES | North Bay(C) | 2021-06-11 | 2021-08-12 | 2021-12-09 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | Pole number is visible. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100686605 | FRESNO 14266 POLES | Fresno(S) | 2021-06-04 | 2021-08-12 | 2021-12-09 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are several cracks along the length of the pole, including near where hardware is attached. | Agree | N/A | N¦A | 110535833 | Update a EC | Yes | No | Yes | No
100686605 | FRESNO 14266 POLES | Fresno(S) | 2021-06-04 | 2021-08-12 | 2021-12-09 | Hardware and Framing: Grounds exposed, broken, damaged, disconnected, unsecured, or missing (if required) | [Answer left blank] | Approximately 4" of ground wire is exposed where the molding is broken, approximately 2' from the ground. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | Yes
102259313 | NORTH BAY MAP SS3012 POLES | North Bay(C) | 2021-06-04 | 2021-08-11 | 2021-12-09 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | Open wire secondary is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102259229 | NORTH BAY MAP SS3012 POLES | North Bay(C) | 2021-06-05 | 2021-08-11 | 2021-12-09 | Vegetation: Distribution Facility / Pole located in State Responsibility Area (SRA) / Federal Responsibility Area (FRA) / High Fire Threat District (HFTD) with vegetation within 4’ of primary conductor | [Answer left blank] | East phase of primary conductor span north of the pole appears to be within 1' of tree trunk. | Disagree | Condition is not compelling | ELEC-1000 Training | Tree is allowed to be within minimum allowable distance and is exempted by the Major Woody Stem Exemption - Utility Procedure: TD-7102P-05 | N\A | N\A | N\A | N\A | N\A
102259145 | NORTH BAY MAP SS3012 POLES | North Bay(C) | 2021-06-04 | 2021-08-11 | 2021-12-09 | Vegetation: Tree causing strain or abrasion to secondary or service (only 1 service) | [Answer left blank] | Tree appears to be causing strain on service conductor connected to customer property. | Agree | N/A | N¦A | 120927297 | Update a EC | Yes | No | Yes | No
102259145 | NORTH BAY MAP SS3012 POLES | North Bay(C) | 2021-06-04 | 2021-08-11 | 2021-12-09 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | Pole number is visible. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102259197 | NORTH BAY MAP SS3012 POLES | North Bay(C) | 2021-06-05 | 2021-08-11 | 2021-12-09 | Non-Time-Dependent Issues: Pole steps are less than 8' 6" above the ground or any other accessible surface | [Answer left blank] | Pole step is at 7' 9" (93"). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102259197 | NORTH BAY MAP SS3012 POLES | North Bay(C) | 2021-06-05 | 2021-08-11 | 2021-12-09 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | Pole number is visible. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100685325 | FRESNO 14266 POLES | Fresno(S) | 2021-06-03 | 2021-08-12 | 2021-12-09 | Hardware and Framing: Animal mitigation broken, damaged, or missing (if required) | [Answer left blank] | Animal mitigation appears to be loose. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100685325 | FRESNO 14266 POLES | Fresno(S) | 2021-06-03 | 2021-08-12 | 2021-12-09 | Hardware and Framing: Insulators or King Pin chipped, cracked, corroded, contaminated, flashed, have signs of tracking, broken or damaged | [Answer left blank] | The insulators appear to show signs of flashing. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100685325 | FRESNO 14266 POLES | Fresno(S) | 2021-06-03 | 2021-08-12 | 2021-12-09 | Other Required Data: Is there non-exempt equipment at the inspection location (Universal or Open Link Fuse) | [Answer left blank] | Asset has non-exempt universal fuses. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102258692 | NORTH BAY MAP SS3011 POLES | North Bay(C) | 2021-06-23 | 2021-08-11 | 2021-12-09 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | High voltage sign on one side of the pole is missing. | Disagree | Condition is not compelling | 1. High Voltage Sign Not Installed as Required - TD-2305M-JA02, Rev. 8 - Pg. 61 | The one high sign in good condition on the opposite side of the pole satisfies the standard found in OH: Marking, Rev. #18: 11/01/18 022168 Page 3 of 35. Marking, Numbering, and Identification of Line Structures 3. Routine Inspection A. The requirement in 1, “Poles That Support Line Conductors,” must be satisfied with the following exceptions: 1. Sign the Pole: It is acceptable to have only one sign, or stacked pairs of signs, below the lowest line conductor energized above 750 V, except as noted in 4 “Special Locations.” B. The requirements in 2, Poles That Do Not Support Line Conductors,” must be satisfied with the following exceptions: 1. Risers: It is acceptable to have only one sign, or stacked pairs of signs, below risers energized above 750 V. 4. Special Locations: If the pole is signed, high-voltage signs are required on both sides of the pole in the following locations: Near water areas suitable for sailboats. Near established boat ramps and associated rigging areas. Adjacent to swimming pools. In agricultural areas with movable irrigation piping. Locations, where in the judgement of the employee, high-voltage signs should be visible from all sides of the poles. | N\A | N\A | N\A | N\A | N\A
100685092 | FRESNO 14266 POLES | Fresno(S) | 2021-06-04 | 2021-08-12 | 2021-12-09 | Other Required Data: Support structure or stub present | [Answer left blank] | There appears to be a steel truss on the pole. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103820535 | NORTH BAY MAP UU3216 POLES | North Bay(C) | 2021-06-13 | 2021-08-10 | 2021-12-09 | Other Required Data: 3 or more splices present in one phase of the span | [Answer left blank] | This pole has 2 phases. There are a total of 7 splices on the span north of the pole, with 3 splices on the west phase and 4 splices on the east phase. Span does not cross over a major roadway. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102258513 | NORTH BAY MAP SS30 POLES | North Bay(C) | 2021-06-08 | 2021-08-11 | 2021-12-09 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103352275 | NORTH BAY MAP UU3216 POLES | North Bay(C) | 2021-06-11 | 2021-08-10 | 2021-12-09 | Other Required Data: 3 or more splices present in one phase of the span | [Answer left blank] | The pole has 2 phases. The south phase of the span west of the pole appears to have 4 splices. Span does not cross over a major roadway. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102253359 | NORTH BAY MAP UU3216 POLES | North Bay(C) | 2021-06-13 | 2021-08-10 | 2021-12-09 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | High voltage signs are missing from both sides of the pole. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102259190 | NORTH BAY MAP SS3012 POLES | North Bay(C) | 2021-06-07 | 2021-08-11 | 2021-12-09 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | High voltage sign on one side of the pole is missing. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100685511 | FRESNO 14266 POLES | Fresno(S) | 2021-06-04 | 2021-08-12 | 2021-12-09 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100684515 | FRESNO 14266 POLES | Fresno(S) | 2021-06-05 | 2021-08-12 | 2021-12-09 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | High voltage sign appears to be missing from at least one side of the pole. | Agree | N/A | N¦A | 116876503 | Update a EC | Yes | No | Yes | No
8.30 REPORT
100097752 | NEVADA N1022 POLES | Sierra(N) | 2021-06-02 | 2021-07-29 | 2021-12-10 | Other Required Data: 3 or more splices present in one phase of the span | [Answer left blank] | The pole has 2 phases. The span west of the pole has 7 splices, with 4 splices on the south phase and 3 splices on the north phase. Span does not cross over a major roadway. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101387350 | EL DORADO H4214 POLES | Sierra(N) | 2021-06-02 | 8/3/2021 | 2021-12-10 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100080489 | NEVADA N1018 POLES | Sierra(N) | 2021-06-03 | 2021-07-29 | 2021-12-10 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100079351 | NEVADA MAP N1017 POLES | Sierra(N) | 2021-06-04 | 2021-07-29 | 2021-12-10 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101386747 | EL DORADO H4124 POLES | Sierra(N) | 2021-06-05 | 8/3/2021 | 2021-12-10 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101374901 | EL DORADO J3723 POLES | Sierra(N) | 2021-06-09 | 2021-08-04 | 2021-12-10 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101288074 | MARYSVILLE M2916 POLES | Sierra(N) | 2021-06-12 | 2021-07-28 | 2021-12-10 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100099193 | NEVADA MAP N1017 POLES | Sierra(N) | 2021-06-14 | 2021-07-29 | 2021-12-10 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101286698 | MARYSVILLE L2913 POLES | Sierra(N) | 2021-06-15 | 2021-07-27 | 2021-12-10 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101286718 | MARYSVILLE L2913 POLES | Sierra(N) | 2021-06-15 | 2021-07-27 | 2021-12-10 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101286746 | MARYSVILLE L2913 POLES | Sierra(N) | 2021-06-15 | 2021-07-27 | 2021-12-10 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101333682 | MARYSVILLE M2911 POLES | Sierra(N) | 2021-06-15 | 2021-07-28 | 2021-12-10 | Other Required Data: 3 or more splices present in one phase of the span | [Answer left blank] | The pole has 3 phases. The span north of the pole has 4 splices, with 3 splices on the east phase and 1 splice on the center phase. Span does not cross over a major roadway. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101335272 | MARYSVILLE L2913 POLES | Sierra(N) | 2021-06-15 | 2021-07-27 | 2021-12-10 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101340088 | MARYSVILLE L2913 POLES | Sierra(N) | 2021-06-15 | 2021-07-27 | 2021-12-10 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101375337 | EL DORADO K37 POLES | Sierra(N) | 2021-06-17 | 2021-08-04 | 2021-12-10 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101392122 | EL DORADO H4714 POLES | Sierra(N) | 2021-06-17 | 2021-07-29 | 2021-12-10 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101421001 | EL DORADO H4714 POLES | Sierra(N) | 2021-06-17 | 2021-07-29 | 2021-12-10 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
104014003 | EL DORADO H4714 POLES | Sierra(N) | 2021-06-17 | 2021-07-29 | 2021-12-10 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101374800 | EL DORADO K37 POLES | Sierra(N) | 2021-06-23 | 2021-08-05 | 2021-12-10 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | The high voltage sign on the west side of the pole is damaged/missing. | Disagree | Condition is not compelling | 1. High Voltage Sign Not Installed as Required - TD-2305M-JA02, Rev. 8 - Pg. 61 | The one high sign in good condition on the opposite side of the pole satisfies the standard found in OH: Marking, Rev. #18: 11/01/18 022168 Page 3 of 35. Marking, Numbering, and Identification of Line Structures 3. Routine Inspection A. The requirement in 1, “Poles That Support Line Conductors,” must be satisfied with the following exceptions: 1. Sign the Pole: It is acceptable to have only one sign, or stacked pairs of signs, below the lowest line conductor energized above 750 V, except as noted in 4 “Special Locations.” B. The requirements in 2, Poles That Do Not Support Line Conductors,” must be satisfied with the following exceptions: 1. Risers: It is acceptable to have only one sign, or stacked pairs of signs, below risers energized above 750 V. 4. Special Locations: If the pole is signed, high-voltage signs are required on both sides of the pole in the following locations: Near water areas suitable for sailboats. Near established boat ramps and associated rigging areas. Adjacent to swimming pools. In agricultural areas with movable irrigation piping. Locations, where in the judgement of the employee, high-voltage signs should be visible from all sides of the poles. | N\A | N\A | N\A | N\A | N\A
101375189 | EL DORADO K37 POLES | Sierra(N) | 2021-06-23 | 2021-08-05 | 2021-12-10 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | The high voltage sign on the east side of the pole is detached/partially missing. | Disagree | Condition is not compelling | 1. High Voltage Sign Not Installed as Required - TD-2305M-JA02, Rev. 8 - Pg. 61 | The one high sign in good condition on the opposite side of the pole satisfies the standard found in OH: Marking, Rev. #18: 11/01/18 022168 Page 3 of 35. Marking, Numbering, and Identification of Line Structures 3. Routine Inspection A. The requirement in 1, “Poles That Support Line Conductors,” must be satisfied with the following exceptions: 1. Sign the Pole: It is acceptable to have only one sign, or stacked pairs of signs, below the lowest line conductor energized above 750 V, except as noted in 4 “Special Locations.” B. The requirements in 2, Poles That Do Not Support Line Conductors,” must be satisfied with the following exceptions: 1. Risers: It is acceptable to have only one sign, or stacked pairs of signs, below risers energized above 750 V. 4. Special Locations: If the pole is signed, high-voltage signs are required on both sides of the pole in the following locations: Near water areas suitable for sailboats. Near established boat ramps and associated rigging areas. Adjacent to swimming pools. In agricultural areas with movable irrigation piping. Locations, where in the judgement of the employee, high-voltage signs should be visible from all sides of the poles. | N\A | N\A | N\A | N\A | N\A
101376030 | EL DORADO K3704 POLES | Sierra(N) | 2021-06-23 | 2021-08-04 | 2021-12-10 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101376060 | EL DORADO K3704 POLES | Sierra(N) | 2021-06-23 | 2021-08-04 | 2021-12-10 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101376068 | EL DORADO K3704 POLES | Sierra(N) | 2021-06-23 | 2021-08-04 | 2021-12-10 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101376035 | EL DORADO K3704 POLES | Sierra(N) | 2021-06-24 | 2021-08-04 | 2021-12-10 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101376105 | EL DORADO K3704 POLES | Sierra(N) | 2021-06-24 | 2021-08-04 | 2021-12-10 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101376127 | EL DORADO K3704 POLES | Sierra(N) | 2021-06-24 | 2021-08-04 | 2021-12-10 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101410889 | EL DORADO K3704 POLES | Sierra(N) | 2021-06-24 | 2021-08-04 | 2021-12-10 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101410896 | EL DORADO K3704 POLES | Sierra(N) | 2021-06-24 | 2021-08-04 | 2021-12-10 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101374972 | EL DORADO K3804 POLES | Sierra(N) | 2021-06-25 | 2021-08-05 | 2021-12-10 | Other Required Data: 3 or more splices present in one phase of the span | Energized Phases: 2, Splice Count: (1, 4) for a total of 5 Splices. Span crosses over major roadway: No | There are 2 phases on this pole. There are 7 splices on the span west of the pole, with 5 splices on the south phase and 2 splices on the north phase. There are 4 splices on the span east of the pole, with 3 splices on the south phase and 1 splice on the north phase. Neither span crosses over a major roadway.Span west of the pole: 4 | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101376357 | EL DORADO K36 POLES | Sierra(N) | 2021-06-26 | 2021-08-04 | 2021-12-10 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101376367 | EL DORADO K36 POLES | Sierra(N) | 2021-06-27 | 2021-08-04 | 2021-12-10 | Other Required Data: 3 or more splices present in one phase of the span | [Answer left blank] | There are 2 phases on the pole. There are 5 splices on the span west of the pole, with 3 splices on the south phase and 2 splices on the north phase. Span does not cross over a major roadway. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101408984 | EL DORADO K36 POLES | Sierra(N) | 2021-06-27 | 2021-08-04 | 2021-12-10 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101378720 | EL DORADO K3814 POLES | Sierra(N) | 2021-06-29 | 2021-08-05 | 2021-12-10 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101400383 | EL DORADO I46 POLES | Sierra(N) | 2021-06-29 | 2021-07-27 | 2021-12-10 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101411758 | EL DORADO K3814 POLES | Sierra(N) | 2021-06-29 | 2021-08-05 | 2021-12-10 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101411759 | EL DORADO K3814 POLES | Sierra(N) | 2021-06-29 | 2021-08-05 | 2021-12-10 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | High voltage sign appears to be partially detached. | Disagree | Condition is not compelling | 1. High Voltage Sign Not Installed as Required - TD-2305M-JA02, Rev. 8 - Pg. 61 | The one high sign in good condition on the opposite side of the pole satisfies the standard found in OH: Marking, Rev. #18: 11/01/18 022168 Page 3 of 35. Marking, Numbering, and Identification of Line Structures 3. Routine Inspection A. The requirement in 1, “Poles That Support Line Conductors,” must be satisfied with the following exceptions: 1. Sign the Pole: It is acceptable to have only one sign, or stacked pairs of signs, below the lowest line conductor energized above 750 V, except as noted in 4 “Special Locations.” B. The requirements in 2, Poles That Do Not Support Line Conductors,” must be satisfied with the following exceptions: 1. Risers: It is acceptable to have only one sign, or stacked pairs of signs, below risers energized above 750 V. 4. Special Locations: If the pole is signed, high-voltage signs are required on both sides of the pole in the following locations: Near water areas suitable for sailboats. Near established boat ramps and associated rigging areas. Adjacent to swimming pools. In agricultural areas with movable irrigation piping. Locations, where in the judgement of the employee, high-voltage signs should be visible from all sides of the poles. | N\A | N\A | N\A | N\A | N\A
101422337 | EL DORADO I46 POLES | Sierra(N) | 2021-06-29 | 2021-07-27 | 2021-12-10 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101422338 | EL DORADO I46 POLES | Sierra(N) | 2021-06-29 | 2021-07-27 | 2021-12-10 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103965151 | EL DORADO MAP I4614 POLES | Sierra(N) | 2021-06-29 | 2021-07-27 | 2021-12-10 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103965153 | EL DORADO MAP I4614 POLES | Sierra(N) | 2021-06-29 | 2021-07-27 | 2021-12-10 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100110447 | NEVADA N1016 POLES | Sierra(N) | 2021-06-02 | 2021-07-29 | 2021-12-10 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100110447 | NEVADA N1016 POLES | Sierra(N) | 2021-06-02 | 2021-07-29 | 2021-12-10 | Other Required Data: Is there non-exempt equipment at the inspection location (Lightning or Surge Arrester) | Yes | Lightning (surge) arrester appears to be exempt. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100110447 | NEVADA N1016 POLES | Sierra(N) | 2021-06-02 | 2021-07-29 | 2021-12-10 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100073321 | NEVADA N1016 POLES | Sierra(N) | 2021-06-03 | 2021-07-29 | 2021-12-10 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks in middle and top sections of the pole, including near where hardware is attached. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100073321 | NEVADA N1016 POLES | Sierra(N) | 2021-06-03 | 2021-07-29 | 2021-12-10 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100080438 | NEVADA N1018 POLES | Sierra(N) | 2021-06-03 | 2021-07-29 | 2021-12-10 | Conductor: Conductor has splices tied in proximity to insulator preventing free movement of splice with conductor | [Answer left blank] | Splices appear to be tied within 2' of insulators. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100080773 | NEVADA N1018 POLES | Sierra(N) | 2021-06-03 | 2021-07-29 | 2021-12-10 | Common Equipment/Other Equipment: Does this structure have equipment? | Yes | Structure does not appear to have equipment. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100067273 | NEVADA MAP N1023 POLES | Sierra(N) | 2021-06-04 | 2021-07-29 | 2021-12-10 | Hardware and Framing: Select if there are risks, hazards or other maintenance conditions not previously captured in the checklist for Hardware Framing at this location | [Answer left blank] | Secondary bracket hardware appears to be loose. | Agree | N/A | N¦A | 121473194 | Update a EC | Yes | No | Yes | No
101386795 | EL DORADO H4124 POLES | Sierra(N) | 2021-06-05 | 2021-08-03 | 2021-12-10 | Anchor and Guys: Does or should this location have a Guy? | No | A down guy and overhead guy are present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101386795 | EL DORADO H4124 POLES | Sierra(N) | 2021-06-05 | 2021-08-03 | 2021-12-10 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | Open wire secondary is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101386795 | EL DORADO H4124 POLES | Sierra(N) | 2021-06-05 | 2021-08-03 | 2021-12-10 | Other Required Data: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101386797 | EL DORADO H4124 POLES | Sierra(N) | 2021-06-05 | 2021-08-03 | 2021-12-10 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Support structure with non-exempt equipment (lightning arresters) has dried ground vegetation within 10' of its base. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101386797 | EL DORADO H4124 POLES | Sierra(N) | 2021-06-05 | 2021-08-03 | 2021-12-10 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | Open wire secondary is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101386797 | EL DORADO H4124 POLES | Sierra(N) | 2021-06-05 | 2021-08-03 | 2021-12-10 | Other Required Data: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101386797 | EL DORADO H4124 POLES | Sierra(N) | 2021-06-05 | 2021-08-03 | 2021-12-10 | Other Required Data: Is there non-exempt equipment at the inspection location (Lightning or Surge Arrester) | [Answer left blank] | Non-exempt lightning arresters are present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101374886 | EL DORADO J3723 POLES | Sierra(N) | 2021-06-09 | 2021-08-04 | 2021-12-10 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Support structure with non-exempt equipment (lightning arresters) has dried ground vegetation within 10' of its base. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101374886 | EL DORADO J3723 POLES | Sierra(N) | 2021-06-09 | 2021-08-04 | 2021-12-10 | Other Required Data: Is there non-exempt equipment at the inspection location (Lightning or Surge Arrester) | [Answer left blank] | Non-exempt lightning arresters are present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101386855 | EL DORADO H4124 POLES | Sierra(N) | 2021-06-10 | 2021-08-03 | 2021-12-10 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | Open wire secondary is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101414377 | EL DORADO H4124 POLES | Sierra(N) | 2021-06-10 | 2021-08-03 | 2021-12-10 | Other Required Data: Is there non-exempt equipment at the inspection location (Lightning or Surge Arrester) | [Answer left blank] | Non-exempt lightning arresters are present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101386910 | EL DORADO H4124 POLES | Sierra(N) | 2021-06-11 | 2021-08-03 | 2021-12-10 | Other Required Data: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101333676 | MARYSVILLE M2916 POLES | Sierra(N) | 2021-06-12 | 2021-07-28 | 2021-12-10 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | The bottom half of the pole has a deep crack. In the middle section of the pole, there are several woodpecker holes, including one approximately 4" in diameter. | Agree | N/A | N¦A | Condition is already attached to an EC Notification (116814645). Inspector did complete FSR to update Notification but did not indicate condition in Structure section of Inspection Record. | N\A | N\A | N\A | N\A | N\A
101333676 | MARYSVILLE M2916 POLES | Sierra(N) | 2021-06-12 | 2021-07-28 | 2021-12-10 | Anchor and Guys: Does or should this location have a Guy? | No | A guy is present at this location. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101387245 | EL DORADO H4213 POLES | Sierra(N) | 2021-06-12 | 2021-08-03 | 2021-12-10 | Conductor: Conductor has splices tied in proximity to insulator preventing free movement of splice with conductor | [Answer left blank] | A splice appears to be tied within 2' of the insulator. | Agree | N/A | N¦A | Condition is already attached to an EC Notification (119145581). Inspector did complete FSR to update Notification but did not indicate condition in Conductor section of Inspection Record. | N\A | N\A | N\A | N\A | N\A
101387245 | EL DORADO H4213 POLES | Sierra(N) | 2021-06-12 | 2021-08-03 | 2021-12-10 | Other Required Data: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101387320 | EL DORADO H4213 POLES | Sierra(N) | 2021-06-12 | 2021-08-03 | 2021-12-10 | Vegetation: Tree causing strain or abrasion to secondary or service (only 1 service) | [Answer left blank] | The service conductor west of the pole appears to be strained by vegetation. | Disagree | N/A | N¦A | Condition was identified by Inspector and FSR was completed to update Notification. | N\A | N\A | N\A | N\A | N\A
101412916 | EL DORADO H4213 POLES | Sierra(N) | 2021-06-12 | 2021-08-03 | 2021-12-13 | Anchor and Guys: Does or should this location have a Guy? | Yes | Pole does not have or appear to need a guy. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100099192 | NEVADA MAP N1017 POLES | Sierra(N) | 2021-06-14 | 2021-07-29 | 2021-12-13 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Structure with non-exempt lightning arresters appears to have dried vegetation within 10' of its base. | Disagree | Inspector Selected Correcly | ELEC-1000 Training | Photos provided by both the Compliance Inspector and the Federal Monitor Inspector both appear to show an adequate 10' radius of cleared vegetation around the base of the pole in accordance with ELEC-0342 | N\A | N\A | N\A | N\A | N\A
100099192 | NEVADA MAP N1017 POLES | Sierra(N) | 2021-06-14 | 2021-07-29 | 2021-12-13 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | Pole number is visible on pole. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100099192 | NEVADA MAP N1017 POLES | Sierra(N) | 2021-06-14 | 2021-07-29 | 2021-12-13 | Other Required Data: Is there non-exempt equipment at the inspection location (Lightning or Surge Arrester) | [Answer left blank] | Non-exempt lightning arresters are present on the structure. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101288097 | MARYSVILLE M2921 POLES | Sierra(N) | 2021-06-14 | 2021-07-28 | 2021-12-13 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks from the middle to the top of the pole, including near where crossarm hardware is attached. | Agree | N/A | N¦A | Condition is already attached to an EC Notification (116817935). Inspector did complete FSR to update Notification but did not indicate condition in Structure section of Inspection Record. | N\A | N\A | N\A | N\A | N\A
101288097 | MARYSVILLE M2921 POLES | Sierra(N) | 2021-06-14 | 2021-07-28 | 2021-12-13 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101336523 | MARYSVILLE M2921 POLES | Sierra(N) | 2021-06-14 | 2021-07-28 | 2021-12-13 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks and holes throughout the pole, including near where hardware is attached. | Agree | N/A | N¦A | Condition is already attached to an EC Notification (116823032). Inspector did complete FSR to update Notification but did not indicate condition in Structure section of Inspection Record. | N\A | N\A | N\A | N\A | N\A
101336523 | MARYSVILLE M2921 POLES | Sierra(N) | 2021-06-14 | 2021-07-28 | 2021-12-13 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | High voltage signs appear to be missing from at least one side of the pole. | Agree | N/A | N¦A | 116823032 | Update a EC | Yes | No | Yes | No
101387236 | EL DORADO H4213 POLES | Sierra(N) | 2021-06-14 | 2021-08-03 | 2021-12-13 | Anchor and Guys: Guy wire broken, damaged, clearance issues, corroded, covered by vegetation, overgrown, strain or abrasion | [Answer left blank] | Vegetation appears to be causing strain on the down guy. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101387251 | EL DORADO H4213 POLES | Sierra(N) | 2021-06-14 | 2021-08-03 | 2021-12-13 | Conductor: Conductor has splices tied in proximity to insulator preventing free movement of splice with conductor | [Answer left blank] | The middle phase of the span east of the pole appears to have a splice tied within 2' of the insulator. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101387251 | EL DORADO H4213 POLES | Sierra(N) | 2021-06-14 | 2021-08-03 | 2021-12-13 | Non-Time-Dependent Issues: Visibility strips missing, broken, mismatched, or no longer reflective | [Answer left blank] | Pole is missing one visibility strip. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101387251 | EL DORADO H4213 POLES | Sierra(N) | 2021-06-14 | 2021-08-03 | 2021-12-13 | Non-Time-Dependent Issues: Pole steps are less than 8' 6" above the ground or any other accessible surface | [Answer left blank] | Pole step is at 7' 8" (92"). | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101387270 | EL DORADO H4213 POLES | Sierra(N) | 2021-06-14 | 2021-08-03 | 2021-12-13 | Conductor: Conductor has splices tied in proximity to insulator preventing free movement of splice with conductor | [Answer left blank] | The east phase on the span north of the pole appears to have a splice tied within 2' of the insulator. | Agree | N/A | N¦A | Location has existing EC Notification (119995511). Inspector did not identify condition and did not add condition to Notification. | Update a EC | Yes | No | Yes | No
101387415 | EL DORADO H42 POLES | Sierra(N) | 2021-06-14 | 2021-08-03 | 2021-12-13 | Conductor: Conductor has splices tied in proximity to insulator preventing free movement of splice with conductor | [Answer left blank] | A splice appears to be tied within 2' of the insulator. | Agree | N/A | N¦A | Condition is already attached to an EC Notification (116823032). Inspector did complete FSR to update Notification but did not indicate condition in Structure section of Inspection Record. | N\A | N\A | N\A | N\A | N\A
101412921 | EL DORADO H4213 POLES | Sierra(N) | 2021-06-14 | 2021-08-03 | 2021-12-13 | Other Required Data: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101416360 | EL DORADO H42 POLES | Sierra(N) | 2021-06-14 | 2021-08-03 | 2021-12-13 | Common Equipment/Other Equipment: Does this structure have equipment? | No | There is equipment (a transformer) present on the structure. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103029418 | MARYSVILLE M2921 POLES | Sierra(N) | 2021-06-14 | 2021-07-28 | 2021-12-13 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Structure with non-exempt lightning arresters appears to have dried vegetation within 10' of its base. | Disagree | Inspector Selected Correcly | ELEC-1000 Training | Photos provided by both the Compliance Inspector and the Federal Monitor Inspector both appear to show an adequate 10' radius of cleared vegetation around the base of the pole in accordance with ELEC-0342 | N\A | N\A | N\A | N\A | N\A
103029418 | MARYSVILLE M2921 POLES | Sierra(N) | 2021-06-14 | 2021-07-28 | 2021-12-13 | Other Required Data: Is there non-exempt equipment at the inspection location (Lightning or Surge Arrester) | [Answer left blank] | Non-exempt lightning arresters are present on the structure. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
104003081 | EL DORADO H4719 POLES | Sierra(N) | 2021-06-14 | 2021-07-29 | 2021-12-13 | Conductor: Service conductor has diminished clearance | [Answer left blank] | One of the service conductors appears to have diminished clearance, running less than 12' from the ground. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101286728 | MARYSVILLE L2913 POLES | Sierra(N) | 2021-06-15 | 2021-07-27 | 2021-12-14 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Structure with non-exempt solid blade disconnects appears to have dried vegetation within 10' of its base. | Agree | N/A | N¦A |  | Create "Other tag" | Yes | No | Yes | No
101286728 | MARYSVILLE L2913 POLES | Sierra(N) | 2021-06-15 | 2021-07-27 | 2021-12-14 | Other Required Data: Is there non-exempt equipment at the inspection location (Solid Blade or In-line disconnect) | [Answer left blank] | Non-exempt solid blade disconnects are present on the structure. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101390012 | JUNK YARD FL TO HOLD DELETED DATA | Sierra(N) | 2021-06-15 | 2021-07-28 | 2021-12-14 | Anchor and Guys: Does or should this location have a Guy? | [Answer left blank] | Pole does not have or appear to need a guy. Guys are associated with adjacent structures. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101390012 | JUNK YARD FL TO HOLD DELETED DATA | Sierra(N) | 2021-06-15 | 2021-07-28 | 2021-12-14 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole does not appear to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101390034 | EL DORADO H4701 POLES | Sierra(N) | 2021-06-15 | 2021-07-28 | 2021-12-14 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | Yes | Pole number is visible on pole. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101390034 | EL DORADO H4701 POLES | Sierra(N) | 2021-06-15 | 2021-07-28 | 2021-12-14 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101390036 | EL DORADO H4701 POLES | Sierra(N) | 2021-06-15 | 2021-07-28 | 2021-12-14 | Conductor: Primary, secondary, and/or service conductors broken, damaged, burnt, corroded, loose, frayed or bird caging | [Answer left blank] | Conductor appears to be frayed on the middle phase of the northwest span. | Agree | N/A | N¦A | 110590401 | Update a EC | Yes | No | Yes | No
101390036 | EL DORADO H4701 POLES | Sierra(N) | 2021-06-15 | 2021-07-28 | 2021-12-14 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | Pole number is visible on pole. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101390036 | EL DORADO H4701 POLES | Sierra(N) | 2021-06-15 | 2021-07-28 | 2021-12-14 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101390108 | EL DORADO H4701 POLES | Sierra(N) | 2021-06-15 | 2021-07-28 | 2021-12-14 | Common Equipment/Other Equipment: Does this structure have equipment? | No | Structure has equipment (transformer). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101390108 | EL DORADO H4701 POLES | Sierra(N) | 2021-06-15 | 2021-07-28 | 2021-12-14 | Anchor and Guys: Does or should this location have a Guy? | No | Structure has three guy wires. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101390108 | EL DORADO H4701 POLES | Sierra(N) | 2021-06-15 | 2021-07-28 | 2021-12-14 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | Pole number is visible on pole. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101390108 | EL DORADO H4701 POLES | Sierra(N) | 2021-06-15 | 2021-07-28 | 2021-12-14 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101419380 | EL DORADO H4701 POLES | Sierra(N) | 2021-06-15 | 2021-07-28 | 2021-12-14 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | Pole number is visible on pole. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101419380 | EL DORADO H4701 POLES | Sierra(N) | 2021-06-15 | 2021-07-28 | 2021-12-14 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101419805 | EL DORADO H4701 POLES | Sierra(N) | 2021-06-15 | 2021-07-28 | 2021-12-14 | Conductor: Conductor has splices tied in proximity to insulator preventing free movement of splice with conductor | [Answer left blank] | Three splices appear to be tied within 2' of insulators. | Agree | N/A | N¦A | 119174395 | Update a EC | Yes | No | Yes | No
101419805 | EL DORADO H4701 POLES | Sierra(N) | 2021-06-15 | 2021-07-28 | 2021-12-14 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | Pole number is visible on pole. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101419805 | EL DORADO H4701 POLES | Sierra(N) | 2021-06-15 | 2021-07-28 | 2021-12-14 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101419810 | JUNK YARD FL TO HOLD DELETED DATA | Sierra(N) | 2021-06-15 | 2021-07-28 | 2021-12-14 | Conductor: Service conductor has diminished clearance | [Answer left blank] | The service conductor appears to have diminished clearance from a structure on private property. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
103029433 | MARYSVILLE M2911 POLES | Sierra(N) | 2021-06-15 | 2021-07-28 | 2021-12-14 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Structure with non-exempt lightning arresters appears to have dried vegetation within 10' of its base. | Disagree | Inspector Selected Correcly | ELEC-1000 Training | Photos provided by both the Compliance Inspector and the Federal Monitor Inspector both appear to show an adequate 10' radius of cleared vegetation around the base of the pole in accordance with ELEC-0342 Debris on ground is leaves that have fallen to the ground. | N\A | N\A | N\A | N\A | N\A
103029433 | MARYSVILLE M2911 POLES | Sierra(N) | 2021-06-15 | 2021-07-28 | 2021-12-14 | Other Required Data: Is there non-exempt equipment at the inspection location (Lightning or Surge Arrester) | [Answer left blank] | Non-exempt lightning arresters are present on the structure. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103673809 | MARYSVILLE L2913 POLES | Sierra(N) | 2021-06-15 | 2021-07-27 | 2021-12-14 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks throughout the pole, including near where hardware is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Pole top had wood crossarm bolts and anti-split bolt. | N\A | N\A | N\A | N\A | N\A
103673814 | MARYSVILLE L2913 POLES | Sierra(N) | 2021-06-15 | 2021-07-27 | 2021-12-14 | Vegetation: Support Structure with non-exempt equipment, has dried vegetation from ground to 8' above ground, within 10' radius of Support Structure base | [Answer left blank] | Structure with non-exempt lightning arresters appears to have dried vegetation present from ground to 8' above ground. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103673814 | MARYSVILLE L2913 POLES | Sierra(N) | 2021-06-15 | 2021-07-27 | 2021-12-14 | Other Required Data: Is there non-exempt equipment at the inspection location (Lightning or Surge Arrester) | [Answer left blank] | Non-exempt lightning arresters are present on the structure. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101286759 | MARYSVILLE L29 POLES | Sierra(N) | 2021-06-16 | 2021-07-27 | 2021-12-14 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | Pole number is visible on pole. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
104006128 | EL DORADO H4713 POLES | Sierra(N) | 2021-06-16 | 2021-07-29 | 2021-12-14 | Common Equipment/Other Equipment: Does this structure have equipment? | No | Structure has equipment (sectionalizing devices). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
104006128 | EL DORADO H4713 POLES | Sierra(N) | 2021-06-16 | 2021-07-29 | 2021-12-14 | Hardware and Framing: Animal mitigation broken, damaged, or missing (if required) | [Answer left blank] | Animal mitigation on the north/road-side phase of the east span is upside down. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101286831 | MARYSVILLE MAP L2914 POLES | Sierra(N) | 2021-06-17 | 2021-07-27 | 2021-12-14 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks throughout the pole, including near where hardware is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Pole top had wood crossarm bolts and anti-split bolt. | N\A | N\A | N\A | N\A | N\A
101375407 | EL DORADO K37 POLES | Sierra(N) | 2021-06-17 | 2021-08-04 | 2021-12-14 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101375416 | EL DORADO K37 POLES | Sierra(N) | 2021-06-17 | 2021-08-04 | 2021-12-14 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101410060 | EL DORADO K37 POLES | Sierra(N) | 2021-06-17 | 2021-08-04 | 2021-12-14 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103672474 | MARYSVILLE MAP L2914 POLES | Sierra(N) | 2021-06-17 | 2021-07-27 | 2021-12-14 | Common Equipment/Other Equipment: Does this structure have equipment? | No | Structure has equipment (exempt in-line fuses). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103986559 | EL DORADO K37 POLES | Sierra(N) | 2021-06-17 | 2021-08-04 | 2021-12-14 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
104001894 | EL DORADO H4713 POLES | Sierra(N) | 2021-06-17 | 2021-07-29 | 2021-12-14 | Vegetation: Distribution Facility / Pole located in State Responsibility Area (SRA) / Federal Responsibility Area (FRA) / High Fire Threat District (HFTD) with vegetation within 4’ of primary conductor | [Answer left blank] | A tree trunk appears to be within 4' of the east phase of primary conductor. | Disagree | Condition is not compelling | ELEC-1000 Training | Tree is allowed to be within minimum allowable distance and is exempted by the Major Woody Stem Exemption - Utility Procedure: TD-7102P-05 | N\A | N\A | N\A | N\A | N\A
101375307 | EL DORADO K37 POLES | Sierra(N) | 2021-06-18 | 2021-08-04 | 2021-12-14 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101410073 | EL DORADO K37 POLES | Sierra(N) | 2021-06-18 | 2021-08-04 | 2021-12-14 | Conductor: Primary, secondary, and/or service conductors broken, damaged, burnt, corroded, loose, frayed or bird caging | [Answer left blank] | There is bird-caging on the road-side phase south of the pole. | Agree | N/A | N¦A | 117093253 | Update a EC | Yes | No | Yes | No
101410073 | EL DORADO K37 POLES | Sierra(N) | 2021-06-18 | 2021-08-04 | 2021-12-14 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101374914 | EL DORADO K37 POLES | Sierra(N) | 2021-06-22 | 2021-08-05 | 2021-12-14 | Hardware and Framing: Secondary connectors (mini wedge and Insulink) installed on primary conductor | [Answer left blank] | There is a secondary connector installed on the primary jumper. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101374914 | EL DORADO K37 POLES | Sierra(N) | 2021-06-22 | 2021-08-05 | 2021-12-14 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101374939 | EL DORADO K37 POLES | Sierra(N) | 2021-06-22 | 2021-08-05 | 2021-12-14 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101375199 | EL DORADO K37 POLES | Sierra(N) | 2021-06-22 | 2021-08-05 | 2021-12-14 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101375215 | EL DORADO K37 POLES | Sierra(N) | 2021-06-22 | 2021-08-05 | 2021-12-14 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101391942 | EL DORADO H4718 POLES | Sierra(N) | 2021-06-22 | 2021-07-29 | 2021-12-14 | Conductor: Primary or secondary conductor has diminished clearance mid span or uneven conductor sag | [Answer left blank] | The span northeast of the pole (going downhill) appears to have a diminished clearance mid-span on both phases. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101391942 | EL DORADO H4718 POLES | Sierra(N) | 2021-06-22 | 2021-07-29 | 2021-12-14 | Common Equipment/Other Equipment: Does this structure have equipment? | No | Structure has equipment (fuse disconnects). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101375077 | EL DORADO K37 POLES | Sierra(N) | 2021-06-23 | 2021-08-05 | 2021-12-14 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101376145 | EL DORADO K3704 POLES | Sierra(N) | 2021-06-23 | 2021-08-04 | 2021-12-14 | Conductor: Primary or secondary conductor has diminished clearance mid span or uneven conductor sag | [Answer left blank] | The phases on the span west of the pole have uneven sag. | Agree | N/A | N¦A | 119518866 | Update a EC | Yes | No | Yes | No
101376145 | EL DORADO K3704 POLES | Sierra(N) | 2021-06-23 | 2021-08-04 | 2021-12-14 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101376157 | EL DORADO K3704 POLES | Sierra(N) | 2021-06-23 | 2021-08-04 | 2021-12-14 | Hardware and Framing: Tap clamps installed incorrectly | [Answer left blank] | Tap clamps are installed on armor rods rather than on tap guards. | Agree | N/A | N¦A | 119518882 | Update a EC | Yes | No | Yes | No
101376157 | EL DORADO K3704 POLES | Sierra(N) | 2021-06-23 | 2021-08-04 | 2021-12-14 | Hardware and Framing: Animal mitigation broken, damaged, or missing (if required) | [Answer left blank] | Animal mitigation is missing on one transformer bushing. | Agree | N/A | N¦A | 119518882 | Update a EC | Yes | No | Yes | No
101376429 | EL DORADO K36 POLES | Sierra(N) | 2021-06-23 | 2021-08-04 | 2021-12-14 | Anchor and Guys: Anchor rod broken, damaged, corroded, covered by vegetation/overgrown, soil-eroded, graded, or buried | [Answer left blank] | The anchor rod is buried. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101409682 | EL DORADO K37 POLES | Sierra(N) | 2021-06-23 | 2021-08-05 | 2021-12-14 | Hardware and Framing: Grounds exposed, broken, damaged, disconnected, unsecured, or missing (if required) | [Answer left blank] | There is exposed ground wire approximately 6' from the ground. The uninsulated wire is exposed for approximately 6" before returning behind the molding. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | Yes
101409683 | EL DORADO K37 POLES | Sierra(N) | 2021-06-23 | 2021-08-05 | 2021-12-14 | Non-Time-Dependent Issues: Visibility strips missing, broken, mismatched, or no longer reflective | [Answer left blank] | Visibility strips are no longer reflective, and one is missing. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101410894 | EL DORADO K3704 POLES | Sierra(N) | 2021-06-23 | 2021-08-04 | 2021-12-14 | Anchor and Guys: Guy wire broken, damaged, clearance issues, corroded, covered by vegetation, overgrown, strain or abrasion | [Answer left blank] | Vegetation appears to be causing strain on the guy wire. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101410894 | EL DORADO K3704 POLES | Sierra(N) | 2021-06-23 | 2021-08-04 | 2021-12-14 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101419616 | EL DORADO K3704 POLES | Sierra(N) | 2021-06-23 | 2021-08-04 | 2021-12-14 | Conductor: Does this structure have PG&E owned conductor? | Yes | Structure does not have a power conductor. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103806554 | EL DORADO K37 POLES | Sierra(N) | 2021-06-23 | 2021-08-05 | 2021-12-15 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103986635 | EL DORADO K3704 POLES | Sierra(N) | 2021-06-23 | 2021-08-04 | 2021-12-15 | Non-Time-Dependent Issues: Pole steps are less than 8' 6" above the ground or any other accessible surface | [Answer left blank] | Pole step is at 7' 11" (95") | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
103986635 | EL DORADO K3704 POLES | Sierra(N) | 2021-06-23 | 2021-08-04 | 2021-12-15 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101375054 | EL DORADO K37 POLES | Sierra(N) | 2021-06-24 | 2021-08-05 | 2021-12-15 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101376111 | EL DORADO K3704 POLES | Sierra(N) | 2021-06-24 | 2021-08-04 | 2021-12-15 | Conductor: Conductor has splices tied in proximity to insulator preventing free movement of splice with conductor | [Answer left blank] | Splice appears to be tied within 2' of the insulator. | Agree | N/A | N¦A | Condition is already attached to an EC Notification (119523940). Inspector did complete FSR to update Notification but did not indicate condition in Conductor section of Inspection Record. | N\A | N\A | N\A | N\A | N\A
101376111 | EL DORADO K3704 POLES | Sierra(N) | 2021-06-24 | 2021-08-04 | 2021-12-15 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101376148 | EL DORADO K36 POLES | Sierra(N) | 2021-06-24 | 2021-08-04 | 2021-12-15 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks along the length of the pole, including near where hardware is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. | N\A | N\A | N\A | N\A | N\A
101376148 | EL DORADO K36 POLES | Sierra(N) | 2021-06-24 | 2021-08-04 | 2021-12-15 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101393793 | EL DORADO H4605 POLES | Sierra(N) | 2021-06-24 | 2021-07-28 | 2021-12-15 | Conductor: Conductor has splices tied in proximity to insulator preventing free movement of splice with conductor | [Answer left blank] | A splice appears to be tied within 2' of an insulator on the west/road-side phase of the south span. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101393793 | EL DORADO H4605 POLES | Sierra(N) | 2021-06-24 | 2021-07-28 | 2021-12-15 | Common Equipment/Other Equipment: IFD (aka "Turkey Popper") has activated on the transformer (orange band is visible) | [Answer left blank] | The IFD appears to have been activated. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101393793 | EL DORADO H4605 POLES | Sierra(N) | 2021-06-24 | 2021-07-28 | 2021-12-15 | Hardware and Framing: Molding missing, broken, damaged, or loose | [Answer left blank] | There is a gap in the molding approximately 10' from the ground. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101393793 | EL DORADO H4605 POLES | Sierra(N) | 2021-06-24 | 2021-07-28 | 2021-12-15 | Hardware and Framing: Grounds exposed, broken, damaged, disconnected, unsecured, or missing (if required) | [Answer left blank] | Ground is exposed approximately 10' from the ground. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101393793 | EL DORADO H4605 POLES | Sierra(N) | 2021-06-24 | 2021-07-28 | 2021-12-15 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101393793 | EL DORADO H4605 POLES | Sierra(N) | 2021-06-24 | 2021-07-28 | 2021-12-15 | Other Required Data: 3 or more splices present in one phase of the span | [Answer left blank] | The structure has 2 phases. The span south of the pole has 5 splices, with 2 splices on the east phase and 3 splices on the west/road-side phase. Span does not cross over a major roadway. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101410093 | EL DORADO K37 POLES | Sierra(N) | 2021-06-24 | 2021-08-05 | 2021-12-15 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101286875 | MARYSVILLE MAP L2919 POLES | Sierra(N) | 2021-06-25 | 2021-07-27 | 2021-12-15 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101286875 | MARYSVILLE MAP L2919 POLES | Sierra(N) | 2021-06-25 | 2021-07-27 | 2021-12-15 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101286879 | MARYSVILLE MAP L2919 POLES | Sierra(N) | 2021-06-25 | 2021-07-27 | 2021-12-15 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101286901 | MARYSVILLE MAP L2919 POLES | Sierra(N) | 2021-06-25 | 2021-07-27 | 2021-12-15 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101286915 | MARYSVILLE MAP L2919 POLES | Sierra(N) | 2021-06-25 | 2021-07-27 | 2021-12-15 | Common Equipment/Other Equipment: Does this structure have equipment? | No | Structure has equipment (transformer). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101286915 | MARYSVILLE MAP L2919 POLES | Sierra(N) | 2021-06-25 | 2021-07-27 | 2021-12-15 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101286915 | MARYSVILLE MAP L2919 POLES | Sierra(N) | 2021-06-25 | 2021-07-27 | 2021-12-15 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101340075 | MARYSVILLE MAP L2919 POLES | Sierra(N) | 2021-06-25 | 2021-07-27 | 2021-12-15 | Hardware and Framing: Tap clamps installed incorrectly | [Answer left blank] | Tap clamps are not installed on tap guards. | Agree | N/A | N¦A | Condition is already attached to an EC Notification (121602122). Inspector did complete FSR to update Notification but did not indicate condition in Hardware & Framing section of Inspection Record. | N\A | N\A | N\A | N\A | N\A
101340075 | MARYSVILLE MAP L2919 POLES | Sierra(N) | 2021-06-25 | 2021-07-27 | 2021-12-15 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101340081 | MARYSVILLE MAP L2919 POLES | Sierra(N) | 2021-06-25 | 2021-07-27 | 2021-12-15 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101340081 | MARYSVILLE MAP L2919 POLES | Sierra(N) | 2021-06-25 | 2021-07-27 | 2021-12-15 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101374943 | EL DORADO K3804 POLES | Sierra(N) | 2021-06-25 | 2021-08-05 | 2021-12-15 | Structure: Pole leaning or out of plumb by more than 10% of its height above the ground | [Answer left blank] | Pole appears to be leaning more than 10% of its height above the ground. | Agree | N/A | N¦A | Condition is already attached to an EC Notification (119557089). Inspector did complete FSR to update Notification but did not indicate condition in Structure section of Inspection Record. | N\A | N\A | N\A | N\A | N\A
101376052 | EL DORADO K36 POLES | Sierra(N) | 2021-06-25 | 2021-08-04 | 2021-12-15 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | The asset has a large crack at the top of the pole, near where hardware is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Pole has steel arm and Down guy which is acting as an anti-split bolt. | N\A | N\A | N\A | N\A | N\A
101376236 | EL DORADO K36 POLES | Sierra(N) | 2021-06-25 | 2021-08-04 | 2021-12-15 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are large cracks near the top of the pole, including near where hardware is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Pole has steel 9" brackets and anti-split bolt installed. | N\A | N\A | N\A | N\A | N\A
101376236 | EL DORADO K36 POLES | Sierra(N) | 2021-06-25 | 2021-08-04 | 2021-12-15 | Hardware and Framing: Tap clamps installed incorrectly | [Answer left blank] | Tap clamp is installed on armor rod rather than on a tap guard. | Agree | N/A | N¦A | 117685458 | Update a EC | Yes | No | Yes | No
101409357 | EL DORADO K36 POLES | Sierra(N) | 2021-06-25 | 2021-08-04 | 2021-12-15 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103960548 | MARYSVILLE MAP L2919 POLES | Sierra(N) | 2021-06-25 | 2021-07-27 | 2021-12-15 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101286887 | MARYSVILLE MAP L2919 POLES | Sierra(N) | 2021-06-26 | 2021-07-27 | 2021-12-15 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101286889 | MARYSVILLE MAP L2919 POLES | Sierra(N) | 2021-06-26 | 2021-07-27 | 2021-12-15 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101286889 | MARYSVILLE MAP L2919 POLES | Sierra(N) | 2021-06-26 | 2021-07-27 | 2021-12-15 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101286890 | MARYSVILLE MAP L2919 POLES | Sierra(N) | 2021-06-26 | 2021-07-27 | 2021-12-15 | Hardware and Framing: Tap clamps installed incorrectly | [Answer left blank] | Tap clamps are not installed on tap guards. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101286890 | MARYSVILLE MAP L2919 POLES | Sierra(N) | 2021-06-26 | 2021-07-27 | 2021-12-15 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101286890 | MARYSVILLE MAP L2919 POLES | Sierra(N) | 2021-06-26 | 2021-07-27 | 2021-12-15 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101340079 | MARYSVILLE MAP L2919 POLES | Sierra(N) | 2021-06-26 | 2021-07-27 | 2021-12-15 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101340079 | MARYSVILLE MAP L2919 POLES | Sierra(N) | 2021-06-26 | 2021-07-27 | 2021-12-15 | Non-Time-Dependent Issues: Visibility strips missing, broken, mismatched, or no longer reflective | [Answer left blank] | Visibility strips are missing. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
103920127 | MARYSVILLE MAP L2919 POLES | Sierra(N) | 2021-06-26 | 2021-07-27 | 2021-12-15 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103999749 | EL DORADO I4607 POLES | Sierra(N) | 2021-06-26 | 2021-07-27 | 2021-12-15 | Common Equipment/Other Equipment: Transformer flashed or corroded, e.g. integrity of the metal is breached – holes in metal, cover not securable, metal is damaged, separation, layering, bulging or bubblin | [Answer left blank] | The transformer appears to be flashed around the road-side bushing. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
103999749 | EL DORADO I4607 POLES | Sierra(N) | 2021-06-26 | 2021-07-27 | 2021-12-15 | Common Equipment/Other Equipment: Transformer shows signs of leaking, seeping, or weeping oil | [Answer left blank] | Transformer appears to show signs of seeping oil, as oil stains are present. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101286908 | MARYSVILLE MAP L2919 POLES | Sierra(N) | 2021-06-27 | 2021-07-27 | 2021-12-15 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101286908 | MARYSVILLE MAP L2919 POLES | Sierra(N) | 2021-06-27 | 2021-07-27 | 2021-12-15 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | High voltage sign on one side of the pole is broken/partially missing. | Disagree | Condition is not compelling | 1. High Voltage Sign Not Installed as Required - TD-2305M-JA02, Rev. 8 - Pg. 61 | The one high sign in good condition on the opposite side of the pole satisfies the standard found in OH: Marking, Rev. #18: 11/01/18 022168 Page 3 of 35. Marking, Numbering, and Identification of Line Structures 3. Routine Inspection A. The requirement in 1, “Poles That Support Line Conductors,” must be satisfied with the following exceptions: 1. Sign the Pole: It is acceptable to have only one sign, or stacked pairs of signs, below the lowest line conductor energized above 750 V, except as noted in 4 “Special Locations.” B. The requirements in 2, Poles That Do Not Support Line Conductors,” must be satisfied with the following exceptions: 1. Risers: It is acceptable to have only one sign, or stacked pairs of signs, below risers energized above 750 V. 4. Special Locations: If the pole is signed, high-voltage signs are required on both sides of the pole in the following locations: Near water areas suitable for sailboats. Near established boat ramps and associated rigging areas. Adjacent to swimming pools. In agricultural areas with movable irrigation piping. Locations, where in the judgement of the employee, high-voltage signs should be visible from all sides of the poles. | N\A | N\A | N\A | N\A | N\A
101286958 | MARYSVILLE MAP L2918 POLES | Sierra(N) | 2021-06-27 | 2021-07-27 | 2021-12-15 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101286958 | MARYSVILLE MAP L2918 POLES | Sierra(N) | 2021-06-27 | 2021-07-27 | 2021-12-15 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101286963 | MARYSVILLE MAP L2918 POLES | Sierra(N) | 2021-06-27 | 2021-07-27 | 2021-12-15 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101286969 | MARYSVILLE MAP L2918 POLES | Sierra(N) | 2021-06-27 | 2021-07-27 | 2021-12-15 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101286971 | MARYSVILLE MAP L2918 POLES | Sierra(N) | 2021-06-27 | 2021-07-27 | 2021-12-15 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101286971 | MARYSVILLE MAP L2918 POLES | Sierra(N) | 2021-06-27 | 2021-07-27 | 2021-12-15 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101286972 | MARYSVILLE MAP L2918 POLES | Sierra(N) | 2021-06-27 | 2021-07-27 | 2021-12-15 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101286972 | MARYSVILLE MAP L2918 POLES | Sierra(N) | 2021-06-27 | 2021-07-27 | 2021-12-15 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101286980 | MARYSVILLE MAP L2918 POLES | Sierra(N) | 2021-06-27 | 2021-07-27 | 2021-12-15 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101286980 | MARYSVILLE MAP L2918 POLES | Sierra(N) | 2021-06-27 | 2021-07-27 | 2021-12-15 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101334287 | MARYSVILLE MAP L2918 POLES | Sierra(N) | 2021-06-27 | 2021-07-27 | 2021-12-15 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101334287 | MARYSVILLE MAP L2918 POLES | Sierra(N) | 2021-06-27 | 2021-07-27 | 2021-12-15 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101340306 | MARYSVILLE MAP L2918 POLES | Sierra(N) | 2021-06-27 | 2021-07-27 | 2021-12-15 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101376393 | EL DORADO K36 POLES | Sierra(N) | 2021-06-27 | 2021-08-04 | 2021-12-15 | Conductor: Conductor has splices tied in proximity to insulator preventing free movement of splice with conductor | [Answer left blank] | The south phase on the span west of the pole appears to have a splice tied within 2' of the insulator. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101376396 | EL DORADO K36 POLES | Sierra(N) | 2021-06-27 | 2021-08-04 | 2021-12-15 | Anchor and Guys: Anchor rod broken, damaged, corroded, covered by vegetation/overgrown, soil-eroded, graded, or buried | [Answer left blank] | The anchor rod has pulled loose from the ground. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101376396 | EL DORADO K36 POLES | Sierra(N) | 2021-06-27 | 2021-08-04 | 2021-12-15 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101400386 | EL DORADO I46 POLES | Sierra(N) | 2021-06-29 | 2021-07-27 | 2021-12-15 | Hardware and Framing: Molding missing, broken, damaged, or loose | [Answer left blank] | Molding is loose/disconnected 7' 9" from the ground. | Agree | N/A | N¦A | 119508170 | Update a EC | Yes | No | Yes | No
101400386 | EL DORADO I46 POLES | Sierra(N) | 2021-06-29 | 2021-07-27 | 2021-12-15 | Hardware and Framing: Grounds exposed, broken, damaged, disconnected, unsecured, or missing (if required) | [Answer left blank] | Uninsulated ground is exposed 7' 9" from the ground. | Agree | N/A | N¦A | 119508170 | Update a EC | Yes | No | Yes | Yes
101418456 | EL DORADO K3814 POLES | Sierra(N) | 2021-06-29 | 2021-08-05 | 2021-12-15 | Common Equipment/Other Equipment: Does this structure have equipment? | Yes | Structure does not have equipment. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101418456 | EL DORADO K3814 POLES | Sierra(N) | 2021-06-29 | 2021-08-05 | 2021-12-15 | Anchor and Guys: Does or should this location have a Guy? | Yes | Pole does not have or appear to need a guy. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103687324 | EL DORADO MAP I4614 POLES | Sierra(N) | 2021-06-29 | 2021-07-27 | 2021-12-15 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103965155 | EL DORADO MAP I4614 POLES | Sierra(N) | 2021-06-29 | 2021-07-27 | 2021-12-15 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103672059 | MARYSVILLE MAP M2819 POLES | Sierra(N) | 2021-07-01 | 2021-07-28 | 2021-12-15 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103672059 | MARYSVILLE MAP M2819 POLES | Sierra(N) | 2021-07-01 | 2021-07-28 | 2021-12-15 | Other Required Data: Is there non-exempt equipment at the inspection location (Lightning or Surge Arrester) | [Answer left blank] | Non-exempt lighting arresters are present on the structure | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101327255 | MARYSVILLE MAP M2819 POLES | Sierra(N) | 2021-07-07 | 2021-07-28 | 2021-12-15 | Conductor: Primary or secondary conductor has diminished clearance mid span or uneven conductor sag | [Answer left blank] | The service conductor appears to have diminished clearance from the ground | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100056857 | PLACER MAP V0512 POLES | Sierra(N) | 2020-07-12 | 2021-07-29 | 2021-12-15 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | Pole appears to be bowed starting at the communication level. | Agree | N/A | N¦A | 121713629 | Update a EC | Yes | No | Yes | No
100056857 | PLACER MAP V0512 POLES | Sierra(N) | 2020-07-12 | 2021-07-29 | 2021-12-15 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101304840 | MARYSVILLE N2803 POLES | Sierra(N) | 2021-07-19 | 2021-07-28 | 2021-12-15 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks throughout the pole. The top of the pole appears to show signs of cracking/damage, including near where hardware is attached. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101304840 | MARYSVILLE N2803 POLES | Sierra(N) | 2021-07-19 | 2021-07-28 | 2021-12-15 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101330425 | MARYSVILLE M28 POLES | Sierra(N) | 2021-07-22 | 2021-07-28 | 2021-12-15 | Anchor and Guys: Does or should this location have a Guy? | Yes | Pole does not have or appear to need a guy. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101330430 | MARYSVILLE M2823 POLES | Sierra(N) | 2021-07-22 | 2021-07-28 | 2021-12-15 | Other Required Data: Is there non-exempt equipment at the inspection location (Solid Blade or In-line disconnect) | [Answer left blank] | Non-exempt solid blade disconnects are present on the structure. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
8.24 REPORT
103906625 | SHASTA MAP Q4008 POLES | North Valley(N) | 2021-05-07 | 2021-06-30 | 2021-12-16 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101484541 | SHASTA Q4004 POLES | North Valley(N) | 2021-05-10 | 2021-06-30 | 2021-12-16 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101484546 | SHASTA Q4004 POLES | North Valley(N) | 2021-05-10 | 2021-06-30 | 2021-12-16 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101484549 | SHASTA Q4004 POLES | North Valley(N) | 2021-05-10 | 2021-06-30 | 2021-12-16 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101484550 | SHASTA Q4004 POLES | North Valley(N) | 2021-05-10 | 2021-06-30 | 2021-12-16 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101251756 | MOTHER LODE L31 POLES | North Valley(N) | 2021-05-11 | 2021-07-08 | 2021-12-16 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101251785 | MOTHER LODE L31 POLES | North Valley(N) | 2021-05-11 | 2021-07-08 | 2021-12-16 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101484515 | SHASTA Q4004 POLES | North Valley(N) | 2021-05-12 | 2021-06-30 | 2021-12-16 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101484519 | SHASTA Q4004 POLES | North Valley(N) | 2021-05-12 | 2021-06-30 | 2021-12-16 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103384007 | MOTHER LODE MAP LL29 POLES | North Valley(N) | 2021-05-12 | 7/6/2021 | 2021-12-16 | Other Required Data: 3 or more splices present in one phase of the span | [Answer left blank] | There are 3 phases on the asset. There are 7 splices on the south span, with 3 splices on the southeast phase, 3 splices on the center phase, and 1 splice on the southwest phase. Span does not cross over a major roadway. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101251789 | MOTHER LODE L31 POLES | North Valley(N) | 2021-05-12 | 7/6/2021 | 2021-12-16 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101247742 | MOTHER LODE N28 POLES | North Valley(N) | 2021-05-14 | 7/9/2021 | 2021-12-16 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | High voltage sign on one side of the pole has faded and is difficult to read. | Disagree | Condition is not compelling | 1. High Voltage Sign Not Installed as Required - TD-2305M-JA02, Rev. 8 - Pg. 61 | The one high sign in good condition on the opposite side of the pole satisfies the standard found in OH: Marking, Rev. #18: 11/01/18 022168 Page 3 of 35. Marking, Numbering, and Identification of Line Structures 3. Routine Inspection A. The requirement in 1, “Poles That Support Line Conductors,” must be satisfied with the following exceptions: 1. Sign the Pole: It is acceptable to have only one sign, or stacked pairs of signs, below the lowest line conductor energized above 750 V, except as noted in 4 “Special Locations.” B. The requirements in 2, Poles That Do Not Support Line Conductors,” must be satisfied with the following exceptions: 1. Risers: It is acceptable to have only one sign, or stacked pairs of signs, below risers energized above 750 V. 4. Special Locations: If the pole is signed, high-voltage signs are required on both sides of the pole in the following locations: Near water areas suitable for sailboats. Near established boat ramps and associated rigging areas. Adjacent to swimming pools. In agricultural areas with movable irrigation piping. Locations, where in the judgement of the employee, high-voltage signs should be visible from all sides of the poles. | N\A | N\A | N\A | N\A | N\A
101465669 | SHASTA R2804 POLES | North Valley(N) | 2021-05-15 | 7/1/2021 | 2021-12-16 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103951102 | SHASTA R2804 POLES | North Valley(N) | 2021-05-15 | 7/1/2021 | 2021-12-16 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | The high voltage sign on one side of the pole appears to be damaged. | Disagree | Condition is not compelling | 1. High Voltage Sign Not Installed as Required - TD-2305M-JA02, Rev. 8 - Pg. 61 | The one high sign in good condition on the opposite side of the pole satisfies the standard found in OH: Marking, Rev. #18: 11/01/18 022168 Page 3 of 35. Marking, Numbering, and Identification of Line Structures 3. Routine Inspection A. The requirement in 1, “Poles That Support Line Conductors,” must be satisfied with the following exceptions: 1. Sign the Pole: It is acceptable to have only one sign, or stacked pairs of signs, below the lowest line conductor energized above 750 V, except as noted in 4 “Special Locations.” B. The requirements in 2, Poles That Do Not Support Line Conductors,” must be satisfied with the following exceptions: 1. Risers: It is acceptable to have only one sign, or stacked pairs of signs, below risers energized above 750 V. 4. Special Locations: If the pole is signed, high-voltage signs are required on both sides of the pole in the following locations: Near water areas suitable for sailboats. Near established boat ramps and associated rigging areas. Adjacent to swimming pools. In agricultural areas with movable irrigation piping. Locations, where in the judgement of the employee, high-voltage signs should be visible from all sides of the poles. | N\A | N\A | N\A | N\A | N\A
103951102 | SHASTA R2804 POLES | North Valley(N) | 2021-05-15 | 7/1/2021 | 2021-12-16 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101465550 | SHASTA MAP R2803 POLES | North Valley(N) | 2021-05-17 | 7/1/2021 | 2021-12-20 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101465520 | SHASTA MAP R2803 POLES | North Valley(N) | 2021-05-18 | 7/1/2021 | 2021-12-20 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | Thehigh voltage sign on the south side of the pole appears to be missing. | Disagree | Condition is not compelling | 1. High Voltage Sign Not Installed as Required - TD-2305M-JA02, Rev. 8 - Pg. 61 | The one high sign in good condition on the opposite side of the pole satisfies the standard found in OH: Marking, Rev. #18: 11/01/18 022168 Page 3 of 35. Marking, Numbering, and Identification of Line Structures 3. Routine Inspection A. The requirement in 1, “Poles That Support Line Conductors,” must be satisfied with the following exceptions: 1. Sign the Pole: It is acceptable to have only one sign, or stacked pairs of signs, below the lowest line conductor energized above 750 V, except as noted in 4 “Special Locations.” B. The requirements in 2, Poles That Do Not Support Line Conductors,” must be satisfied with the following exceptions: 1. Risers: It is acceptable to have only one sign, or stacked pairs of signs, below risers energized above 750 V. 4. Special Locations: If the pole is signed, high-voltage signs are required on both sides of the pole in the following locations: Near water areas suitable for sailboats. Near established boat ramps and associated rigging areas. Adjacent to swimming pools. In agricultural areas with movable irrigation piping. Locations, where in the judgement of the employee, high-voltage signs should be visible from all sides of the poles. | N\A | N\A | N\A | N\A | N\A
101465520 | SHASTA MAP R2803 POLES | North Valley(N) | 2021-05-18 | 7/1/2021 | 2021-12-20 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101465523 | SHASTA MAP R2803 POLES | North Valley(N) | 2021-05-18 | 7/1/2021 | 2021-12-20 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101465526 | SHASTA MAP R2803 POLES | North Valley(N) | 2021-05-18 | 7/1/2021 | 2021-12-20 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101465527 | SHASTA MAP R2803 POLES | North Valley(N) | 2021-05-18 | 7/1/2021 | 2021-12-20 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101247498 | MOTHER LODE N28 POLES | Stockton(N) | 2021-05-18 | 7/1/2021 | 2021-12-20 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | High voltage sign is illegible. | Disagree | Condition is not compelling | 1. High Voltage Sign Not Installed as Required - TD-2305M-JA02, Rev. 8 - Pg. 61 | The one high sign in good condition on the opposite side of the pole satisfies the standard found in OH: Marking, Rev. #18: 11/01/18 022168 Page 3 of 35. Marking, Numbering, and Identification of Line Structures 3. Routine Inspection A. The requirement in 1, “Poles That Support Line Conductors,” must be satisfied with the following exceptions: 1. Sign the Pole: It is acceptable to have only one sign, or stacked pairs of signs, below the lowest line conductor energized above 750 V, except as noted in 4 “Special Locations.” B. The requirements in 2, Poles That Do Not Support Line Conductors,” must be satisfied with the following exceptions: 1. Risers: It is acceptable to have only one sign, or stacked pairs of signs, below risers energized above 750 V. 4. Special Locations: If the pole is signed, high-voltage signs are required on both sides of the pole in the following locations: Near water areas suitable for sailboats. Near established boat ramps and associated rigging areas. Adjacent to swimming pools. In agricultural areas with movable irrigation piping. Locations, where in the judgement of the employee, high-voltage signs should be visible from all sides of the poles. | N\A | N\A | N\A | N\A | N\A
101511803 | TEHEMA U29 POLES | North Valley(N) | 2021-05-18 | 2021-06-29 | 2021-12-20 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | The high voltage sign on the northwest side of the poleappears to be damaged. | Disagree | Condition is not compelling | 1. High Voltage Sign Not Installed as Required - TD-2305M-JA02, Rev. 8 - Pg. 61 | The one high sign in good condition on the opposite side of the pole satisfies the standard found in OH: Marking, Rev. #18: 11/01/18 022168 Page 3 of 35. Marking, Numbering, and Identification of Line Structures 3. Routine Inspection A. The requirement in 1, “Poles That Support Line Conductors,” must be satisfied with the following exceptions: 1. Sign the Pole: It is acceptable to have only one sign, or stacked pairs of signs, below the lowest line conductor energized above 750 V, except as noted in 4 “Special Locations.” B. The requirements in 2, Poles That Do Not Support Line Conductors,” must be satisfied with the following exceptions: 1. Risers: It is acceptable to have only one sign, or stacked pairs of signs, below risers energized above 750 V. 4. Special Locations: If the pole is signed, high-voltage signs are required on both sides of the pole in the following locations: Near water areas suitable for sailboats. Near established boat ramps and associated rigging areas. Adjacent to swimming pools. In agricultural areas with movable irrigation piping. Locations, where in the judgement of the employee, high-voltage signs should be visible from all sides of the poles. | N\A | N\A | N\A | N\A | N\A
103581252 | MOTHER LODE MAP KK31 POLES | Stockton(N) | 2021-05-19 | 2021-07-08 | 2021-12-20 | Other Required Data: 3 or more splices present in one phase of the span | [Answer left blank] | There are 3 phases on the asset. There are 11 splices on the north span, with 6 splices on the east phase, 2 splices on the west phase, and 3 splices on the center phase. Span does not cross over a major roadway. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101465508 | SHASTA R2802 POLES | North Valley(N) | 2021-05-26 | 7/1/2021 | 2021-12-20 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100937752 | MISSION L15 POLES | Mission(C) | 2021-06-02 | 2021-07-13 | 2021-12-20 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101890568 | PASO ROBLES JJ38 POLES | Los Padres(S) | 2021-06-02 | 2021-07-14 | 2021-12-20 | Other Required Data: 3 or more splices present in one phase of the span | [Answer left blank] | There are 2 phases on the asset. There are 7 splices on the span east of the pole, with 4 on the south phase and 3 on the north phase. Span does not cross over a major roadway. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102259146 | NORTH BAY MAP SS3012 POLES | North Bay(C) | 2021-06-02 | 2021-07-21 | 2021-12-20 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | There is only one high voltage sign on the pole. | Disagree | Condition is not compelling | 1. High Voltage Sign Not Installed as Required - TD-2305M-JA02, Rev. 8 - Pg. 61 | The one high sign in good condition on the opposite side of the pole satisfies the standard found in OH: Marking, Rev. #18: 11/01/18 022168 Page 3 of 35. Marking, Numbering, and Identification of Line Structures 3. Routine Inspection A. The requirement in 1, “Poles That Support Line Conductors,” must be satisfied with the following exceptions: 1. Sign the Pole: It is acceptable to have only one sign, or stacked pairs of signs, below the lowest line conductor energized above 750 V, except as noted in 4 “Special Locations.” B. The requirements in 2, Poles That Do Not Support Line Conductors,” must be satisfied with the following exceptions: 1. Risers: It is acceptable to have only one sign, or stacked pairs of signs, below risers energized above 750 V. 4. Special Locations: If the pole is signed, high-voltage signs are required on both sides of the pole in the following locations: Near water areas suitable for sailboats. Near established boat ramps and associated rigging areas. Adjacent to swimming pools. In agricultural areas with movable irrigation piping. Locations, where in the judgement of the employee, high-voltage signs should be visible from all sides of the poles. | N\A | N\A | N\A | N\A | N\A
100937748 | MISSION L15 POLES | Mission(C) | 2021-06-06 | 2021-07-13 | 2021-12-20 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102254263 | NORTH BAY MAP SS2809 POLES | North Bay(C) | 2021-06-06 | 2021-07-21 | 2021-12-20 | Other Required Data: 3 or more splices present in one phase of the span | [Answer left blank] | There are 2 phases on this asset. There are 10 splices on the span east of the asset, with 5 splices on the south phase and 5 splices on the north phase. Span does not cross over a major roadway. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103923076 | NORTH BAY MAP SS2809 POLES | North Bay(C) | 2021-06-06 | 2021-07-21 | 2021-12-20 | Other Required Data: 3 or more splices present in one phase of the span | [Answer left blank] | There are 2 phases on this asset. There are 5 splices on the span east of the asset, with 3 splices on the north phase and 2 splices on the south phase. Span does not cross over a major roadway. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100933853 | MISSION K1521 POLES | Mission(C) | 2021-06-07 | 2021-07-13 | 2021-12-20 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100937213 | MISSION K1521 POLES | Mission(C) | 2021-06-07 | 2021-07-13 | 2021-12-20 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100937753 | MISSION L1501 POLES | Mission(C) | 2021-06-07 | 2021-07-13 | 2021-12-20 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101882563 | SAN LUIS OBISPO II29 POLES | Los Padres(S) | 2021-06-16 | 2021-07-13 | 2021-12-20 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101936846 | SAN LUIS OBISPO II29 POLES | Los Padres(S) | 2021-06-16 | 2021-07-13 | 2021-12-20 | Other Required Data: 3 or more splices present in one phase of the span | [Answer left blank] | There are 2 phases on the asset. There are 6 splices on the southeast span, with 4 on the south phase and 2 on the north phase. Span does not cross over a major roadway. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101882554 | SAN LUIS OBISPO II29 POLES | Los Padres(S) | 2021-06-17 | 2021-07-13 | 2021-12-20 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101900732 | PASO ROBLES GG29 POLES | Los Padres(S) | 2021-06-27 | 2021-07-14 | 2021-12-20 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | High voltage sign is missing from one side of pole. | Disagree | Condition is not compelling | 1. High Voltage Sign Not Installed as Required - TD-2305M-JA02, Rev. 8 - Pg. 61 | The one high sign in good condition on the opposite side of the pole satisfies the standard found in OH: Marking, Rev. #18: 11/01/18 022168 Page 3 of 35. Marking, Numbering, and Identification of Line Structures 3. Routine Inspection A. The requirement in 1, “Poles That Support Line Conductors,” must be satisfied with the following exceptions: 1. Sign the Pole: It is acceptable to have only one sign, or stacked pairs of signs, below the lowest line conductor energized above 750 V, except as noted in 4 “Special Locations.” B. The requirements in 2, Poles That Do Not Support Line Conductors,” must be satisfied with the following exceptions: 1. Risers: It is acceptable to have only one sign, or stacked pairs of signs, below risers energized above 750 V. 4. Special Locations: If the pole is signed, high-voltage signs are required on both sides of the pole in the following locations: Near water areas suitable for sailboats. Near established boat ramps and associated rigging areas. Adjacent to swimming pools. In agricultural areas with movable irrigation piping. Locations, where in the judgement of the employee, high-voltage signs should be visible from all sides of the poles. | N\A | N\A | N\A | N\A | N\A
101900745 | PASO ROBLES GG29 POLES | Los Padres(S) | 2021-06-27 | 2021-07-14 | 2021-12-20 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | One of the high voltage signs appears to be broken. | Disagree | Condition is not compelling | 1. High Voltage Sign Not Installed as Required - TD-2305M-JA02, Rev. 8 - Pg. 61 | The one high sign in good condition on the opposite side of the pole satisfies the standard found in OH: Marking, Rev. #18: 11/01/18 022168 Page 3 of 35. Marking, Numbering, and Identification of Line Structures 3. Routine Inspection A. The requirement in 1, “Poles That Support Line Conductors,” must be satisfied with the following exceptions: 1. Sign the Pole: It is acceptable to have only one sign, or stacked pairs of signs, below the lowest line conductor energized above 750 V, except as noted in 4 “Special Locations.” B. The requirements in 2, Poles That Do Not Support Line Conductors,” must be satisfied with the following exceptions: 1. Risers: It is acceptable to have only one sign, or stacked pairs of signs, below risers energized above 750 V. 4. Special Locations: If the pole is signed, high-voltage signs are required on both sides of the pole in the following locations: Near water areas suitable for sailboats. Near established boat ramps and associated rigging areas. Adjacent to swimming pools. In agricultural areas with movable irrigation piping. Locations, where in the judgement of the employee, high-voltage signs should be visible from all sides of the poles. | N\A | N\A | N\A | N\A | N\A
102252105 | NORTH BAY MAP SS2810 POLES | Los Padres(S) | 2021-06-27 | 2021-07-20 | 2021-12-20 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102164144 | UKIAH T2414 POLES | Humboldt(N) | 2021-05-03 | 2021-07-08 | 2021-12-20 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | The pole number is visible on the pole. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101481728 | SHASTA P40 POLES | North Valley(N) | 2021-05-04 | 2021-06-30 | 2021-12-20 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101481728 | SHASTA P40 POLES | North Valley(N) | 2021-05-04 | 2021-06-30 | 2021-12-20 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | Pole number is visible. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101481579 | SHASTA P40 POLES | North Valley(N) | 2021-05-05 | 2021-06-30 | 2021-12-20 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks throughout the pole, including near where hardware is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Pole top has steel crossarm bolts and down guy which acts as an anti-split bolt. | N\A | N\A | N\A | N\A | N\A
101481579 | SHASTA P40 POLES | North Valley(N) | 2021-05-05 | 2021-06-30 | 2021-12-20 | Other Required Data: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101481579 | SHASTA P40 POLES | North Valley(N) | 2021-05-05 | 2021-06-30 | 2021-12-20 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | High voltage sign on one side of pole is missing. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101481579 | SHASTA P40 POLES | North Valley(N) | 2021-05-05 | 2021-06-30 | 2021-12-20 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102163913 | UKIAH T2415 POLES | Humboldt(N) | 2021-05-05 | 2021-07-08 | 2021-12-20 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are multiple cracks at the top of the pole near where hardware is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Pole is Deadend Line & Buck framing and has steel crossarms & bolts and down guys which act as an anti-split bolt. | N\A | N\A | N\A | N\A | N\A
102163913 | UKIAH T2415 POLES | Humboldt(N) | 2021-05-05 | 2021-07-08 | 2021-12-20 | Anchor and Guys: Guy wire broken, damaged, clearance issues, corroded, covered by vegetation, overgrown, strain or abrasion | [Answer left blank] | Vegetation is in contact with both down guys above the insulator. | Agree | N/A | N¦A | Condition is already attached to an EC Notification (111432051). Inspector did complete FSR to update Notification for another condition but did not indicate this condition on FSR or Vegetation section of Inspection Record. | Update a EC | Yes | No | Yes | No
102163913 | UKIAH T2415 POLES | Humboldt(N) | 2021-05-05 | 2021-07-08 | 2021-12-20 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | The pole number is visible on the pole. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102163916 | UKIAH T2415 POLES | Humboldt(N) | 2021-05-05 | 2021-07-08 | 2021-12-20 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | The top third of the pole has several cracks, including near where hardware is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Pole is tangent framing with wood crossarm & bolts, King pin and down guy which acts as an anti-split bolt. | N\A | N\A | N\A | N\A | N\A
102163916 | UKIAH T2415 POLES | Humboldt(N) | 2021-05-05 | 2021-07-08 | 2021-12-20 | Non-Time-Dependent Issues: Visibility strips missing, broken, mismatched, or no longer reflective | [Answer left blank] | Sign is obstructing one of the visibility strips. | Agree | N/A | N¦A | Third party Non-Utility needs to be created | Create "Other tag" | Yes | No | Yes | No
102163916 | UKIAH T2415 POLES | Humboldt(N) | 2021-05-05 | 2021-07-08 | 2021-12-20 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | The pole number is visible on the pole. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102163918 | UKIAH T2415 POLES | Humboldt(N) | 2021-05-05 | 2021-07-08 | 2021-12-20 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | The pole number is visible on the pole. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102163919 | UKIAH T2415 POLES | Humboldt(N) | 2021-05-05 | 2021-07-08 | 2021-12-20 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | The top third of the pole has several cracks, including near where hardware is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Pole is tangent framing with wood crossarm & bolts, King pin and down guy which acts as an anti-split bolt. | N\A | N\A | N\A | N\A | N\A
102163919 | UKIAH T2415 POLES | Humboldt(N) | 2021-05-05 | 2021-07-08 | 2021-12-20 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | The pole number is visible on the pole. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102163920 | UKIAH T2415 POLES | Humboldt(N) | 2021-05-05 | 2021-07-08 | 2021-12-20 | Hardware and Framing: Molding missing, broken, damaged, or loose | [Answer left blank] | Molding for the transformer ground is not attached to the pole until approximately 10' from the ground. | Agree | N/A | N¦A | Condition is already attached to an EC Notification (111432051). Inspector did complete FSR to update Notification but did not indicate condition on Hardware section of Inspection Record. | N\A | N\A | N\A | N\A | N\A
102163920 | UKIAH T2415 POLES | Humboldt(N) | 2021-05-05 | 2021-07-08 | 2021-12-20 | Vegetation: Tree causing strain or abrasion to secondary or service (only 1 service) | [Answer left blank] | A tree limb appears to be causing strain on one phase of the service triplex conductor. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
102163920 | UKIAH T2415 POLES | Humboldt(N) | 2021-05-05 | 2021-07-08 | 2021-12-20 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | The pole number is visible on the pole. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102163920 | UKIAH T2415 POLES | Humboldt(N) | 2021-05-05 | 2021-07-08 | 2021-12-20 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | High voltage sign is missing from one side of pole. | Disagree | Condition is not compelling | 1. High Voltage Sign Not Installed as Required - TD-2305M-JA02, Rev. 8 - Pg. 61 | The one high sign in good condition on the opposite side of the pole satisfies the standard found in OH: Marking, Rev. #18: 11/01/18 022168 Page 3 of 35. Marking, Numbering, and Identification of Line Structures 3. Routine Inspection A. The requirement in 1, “Poles That Support Line Conductors,” must be satisfied with the following exceptions: 1. Sign the Pole: It is acceptable to have only one sign, or stacked pairs of signs, below the lowest line conductor energized above 750 V, except as noted in 4 “Special Locations.” B. The requirements in 2, Poles That Do Not Support Line Conductors,” must be satisfied with the following exceptions: 1. Risers: It is acceptable to have only one sign, or stacked pairs of signs, below risers energized above 750 V. 4. Special Locations: If the pole is signed, high-voltage signs are required on both sides of the pole in the following locations: Near water areas suitable for sailboats. Near established boat ramps and associated rigging areas. Adjacent to swimming pools. In agricultural areas with movable irrigation piping. Locations, where in the judgement of the employee, high-voltage signs should be visible from all sides of the poles. | N\A | N\A | N\A | N\A | N\A
102163923 | UKIAH T2415 POLES | Humboldt(N) | 2021-05-05 | 2021-07-08 | 2021-12-20 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | The pole number is visible on the pole. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102163926 | UKIAH T2415 POLES | Humboldt(N) | 2021-05-05 | 2021-07-08 | 2021-12-20 | Common Equipment/Other Equipment: Transformer flashed or corroded, e.g. integrity of the metal is breached – holes in metal, cover not securable, metal is damaged, separation, layering, bulging or bubbling | [Answer left blank] | Transformer appears to be flashed at the secondary bushing. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
102163926 | UKIAH T2415 POLES | Humboldt(N) | 2021-05-05 | 2021-07-08 | 2021-12-20 | Common Equipment/Other Equipment: Transformer shows signs of leaking, seeping, or weeping oil | [Answer left blank] | Transformer appears to show signs of seeping oil, as oil stains are present. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
102163926 | UKIAH T2415 POLES | Humboldt(N) | 2021-05-05 | 2021-07-08 | 2021-12-20 | Common Equipment/Other Equipment: IFD (aka "Turkey Popper") has activated on the transformer (orange band is visible) | [Answer left blank] | Transformer IFD appears to have activated on both transformers. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
102163926 | UKIAH T2415 POLES | Humboldt(N) | 2021-05-05 | 2021-07-08 | 2021-12-20 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | The pole number is visible on the pole. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102163926 | UKIAH T2415 POLES | Humboldt(N) | 2021-05-05 | 2021-07-08 | 2021-12-20 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101481649 | SHASTA P40 POLES | North Valley(N) | 2021-05-06 | 2021-06-30 | 2021-12-20 | Conductor: Conductor has splices tied in proximity to insulator preventing free movement of splice with conductor | [Answer left blank] | Splice appears to be tied within 2' of insulator. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101481649 | SHASTA P40 POLES | North Valley(N) | 2021-05-06 | 2021-06-30 | 2021-12-20 | Hardware and Framing: Tap clamps installed incorrectly | [Answer left blank] | Tap clamps appear to be installed on armor rod instead of on tap guards. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101481662 | SHASTA P40 POLES | North Valley(N) | 2021-05-06 | 2021-06-30 | 2021-12-20 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102163946 | UKIAH T2415 POLES | Humboldt(N) | 2021-05-06 | 2021-07-08 | 2021-12-20 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | The pole number is visible on the pole. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102163949 | UKIAH T2415 POLES | Humboldt(N) | 2021-05-06 | 2021-07-08 | 2021-12-20 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks on the top third of the pole, including near where the transformer is attached. There appears to be cracking and reduced pole circumference near the service stand-off brackets. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Pole is Deadend Line & Buck framing and has steel crossarms & bolts and down guys which act as an anti-split bolt. | N\A | N\A | N\A | N\A | N\A
102163949 | UKIAH T2415 POLES | Humboldt(N) | 2021-05-06 | 2021-07-08 | 2021-12-20 | Common Equipment/Other Equipment: Transformer shows signs of leaking, seeping, or weeping oil | [Answer left blank] | Transformer appears to show signs of seeping oil, as oil stains are present. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
102163949 | UKIAH T2415 POLES | Humboldt(N) | 2021-05-06 | 2021-07-08 | 2021-12-20 | Other Required Data: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102163949 | UKIAH T2415 POLES | Humboldt(N) | 2021-05-06 | 2021-07-08 | 2021-12-20 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | The pole number is visible on the pole. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102163952 | UKIAH T2415 POLES | Humboldt(N) | 2021-05-06 | 2021-07-08 | 2021-12-20 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | The pole number is visible on the pole. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102163996 | UKIAH T2415 POLES | Humboldt(N) | 2021-05-06 | 2021-07-08 | 2021-12-20 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | The pole number is visible on the pole. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102163996 | UKIAH T2415 POLES | Humboldt(N) | 2021-05-06 | 2021-07-08 | 2021-12-20 | Other Required Data: Pole wrapped at ground-line at this location | Yes | The pole does not appear to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102163999 | UKIAH T2415 POLES | Humboldt(N) | 2021-05-06 | 2021-07-08 | 2021-12-20 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | The pole number is visible on the pole. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102164019 | UKIAH T2415 POLES | Humboldt(N) | 2021-05-06 | 2021-07-08 | 2021-12-20 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | The pole number is visible on the pole. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102164022 | UKIAH T2415 POLES | Humboldt(N) | 2021-05-06 | 2021-07-08 | 2021-12-21 | Anchor and Guys: Necessary guys missing or loose | [Answer left blank] | The guy is loose. | Agree | N/A | N¦A | Pole has open EC Notification for anchor to be replaced (111430426). Inspector did update Notification for another condition but did not indicate this condition in FSR or in Anchor and Guy section of Inspection Record. | Update a EC | Yes | No | Yes | No
102164022 | UKIAH T2415 POLES | Humboldt(N) | 2021-05-06 | 2021-07-08 | 2021-12-21 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | The pole number is visible on the pole. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101245824 | MOTHER LODE MAP KK31 POLES | Stockton(N) | 2021-05-07 | 2021-07-08 | 2021-12-21 | Anchor and Guys: Guy wire broken, damaged, clearance issues, corroded, covered by vegetation, overgrown, strain or abrasion | [Answer left blank] | Vegetation appears to be in contact with both guys above the guy insulator. | Agree | N/A | N¦A | Condition was identified by inspector during FSR in 2020 inspection cycle. Gatekeeper has not yet added this FDA to EC Notification (117324512). Inspector did update Notification but did not update this condition in FSR or indicate this condition in Vegetation section of Inspection Record on the 2021 inspection cycle. | Update a EC | Yes | No | Yes | No
101245824 | MOTHER LODE MAP KK31 POLES | Stockton(N) | 2021-05-07 | 2021-07-08 | 2021-12-21 | Hardware and Framing: Tap clamps installed incorrectly | [Answer left blank] | The tap clamps do not appear to be installed on tap guards. | Agree | N/A | N¦A | Condition was identified by inspector during FSR in 2020 inspection cycle. Gatekeeper has not yet added this FDA to EC Notification (117324512). Inspector did update Notification but did not update this condition in FSR or indicate this condition in Hardware section of Inspection Record on the 2021 inspection cycle. | Update a EC | Yes | No | Yes | No
101484858 | SHASTA MAP Q4008 POLES | North Valley(N) | 2021-05-07 | 2021-06-30 | 2021-12-21 | Anchor and Guys: Does or should this location have a Guy? | No | This location has a guy. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
102164002 | UKIAH T2415 POLES | Humboldt(N) | 2021-05-07 | 2021-07-08 | 2021-12-21 | Vegetation: Tree causing strain or abrasion to secondary or service (only 1 service) | [Answer left blank] | Tree appears to be causing strain on the service conductor. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
102164002 | UKIAH T2415 POLES | Humboldt(N) | 2021-05-07 | 2021-07-08 | 2021-12-21 | Other Required Data: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102164002 | UKIAH T2415 POLES | Humboldt(N) | 2021-05-07 | 2021-07-08 | 2021-12-21 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | The pole number is visible on the pole. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102164029 | UKIAH T2415 POLES | Humboldt(N) | 2021-05-07 | 2021-07-08 | 2021-12-21 | ardware and Framing: Crossarm integrity compromised by any of the following; damaged, broken, burnt, decayed, rotten, loose, missing hardware or showing severe signs of bent bolts or brackets, damaged bracing, gun shots, insect damage or woodpecker damage, splitting, or fails to meet clearance requirements | [Answer left blank] | The primary crossarm appears to be cracked on the west side of the pole where the insulator pin is connected. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
102164029 | UKIAH T2415 POLES | Humboldt(N) | 2021-05-07 | 2021-07-08 | 2021-12-21 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | The pole number is visible on the pole. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103906471 | SHASTA MAP Q4008 POLES | North Valley(N) | 2021-05-07 | 2021-06-30 | 2021-12-21 | Anchor and Guys: Does or should this location have a Guy? | No | This location has a guy. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103906471 | SHASTA MAP Q4008 POLES | North Valley(N) | 2021-05-07 | 2021-06-30 | 2021-12-21 | Other Required Data: Pole wrapped at ground-line at this location | Yes | The pole does not appear to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101249204 | MOTHER LODE MAP LL29 POLES | Stockton(N) | 2021-05-08 | 2021-07-06 | 2021-12-21 | Non-Time-Dependent Issues: Visibility strips missing, broken, mismatched, or no longer reflective | [Answer left blank] | Visibility strips appear to be missing. | Disagree | Condition does not exist | ELEC-1000 Training | The Compliance Inspector was correct. The pole is located on private property and the photos attached to the inspection record do show visibility strips attached to the pole on the driveway side of the pole. It also appears that the Federal Monitor Inspector did not gain access to the pole to perform an adequate assessment of the pole due to the FM photos all being taken from one side of the pole at a distance. | N\A | N\A | N\A | N\A | N\A
101249227 | MOTHER LODE MAP LL29 POLES | Stockton(N) | 2021-05-08 | 2021-07-06 | 2021-12-21 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Structure with non-exempt fuses has dried ground vegetation within 10' of its base. | Agree | N/A | N¦A |  | Create "Other tag" | Yes | No | Yes | No
101249227 | MOTHER LODE MAP LL29 POLES | Stockton(N) | 2021-05-08 | 2021-07-06 | 2021-12-21 | Other Required Data: Is there non-exempt equipment at the inspection location (Universal or Open Link Fuse) | [Answer left blank] | Non-exempt universal fuses are present on structure. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101249227 | MOTHER LODE MAP LL29 POLES | Stockton(N) | 2021-05-08 | 2021-07-06 | 2021-12-21 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101249242 | MOTHER LODE MAP LL29 POLES | Stockton(N) | 2021-05-08 | 2021-07-06 | 2021-12-22 | Anchor and Guys: Guy wire broken, damaged, clearance issues, corroded, covered by vegetation, overgrown, strain or abrasion | [Answer left blank] | Vegetation appears to be in contact with the guy wire above the insulator. | Agree | N/A | N¦A | Pole has open EC Notification (117021709). Inspector did update Notification for another condition but did not indicate this condition in FSR or in Anchor anf Guy section of Inspection Record. | Update a EC | Yes | No | Yes | No
101249259 | MOTHER LODE MAP LL29 POLES | Stockton(N) | 2021-05-08 | 2021-07-06 | 2021-12-22 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Structure with non-exempt fuses has dried ground vegetation within 10' of base. | Agree | N/A | N¦A |  | Create "Other tag" | Yes | No | Yes | No
101249259 | MOTHER LODE MAP LL29 POLES | Stockton(N) | 2021-05-08 | 2021-07-06 | 2021-12-22 | Other Required Data: Is there non-exempt equipment at the inspection location (Universal or Open Link Fuse) | [Answer left blank] | Structure has non-exempt fuses. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101249259 | MOTHER LODE MAP LL29 POLES | Stockton(N) | 2021-05-08 | 2021-07-06 | 2021-12-22 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101484892 | SHASTA Q4009 POLES | North Valley(N) | 2021-05-08 | 2021-06-30 | 2021-12-22 | Conductor: Conductor has splices tied in proximity to insulator preventing free movement of splice with conductor | [Answer left blank] | Splice appears to be tied within 2' of insulator. | Agree | N/A | N¦A | Pole has open EC Notification (117073903). Inspector did update Notification for another condition but did not indicate this condition in FSR or in Conductor section of Inspection Record. | Update a EC | Yes | No | Yes | No
101484900 | SHASTA Q4009 POLES | North Valley(N) | 2021-05-08 | 2021-06-30 | 2021-12-22 | Anchor and Guys: Does or should this location have a Guy? | No | This location has a guy. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101251739 | MOTHER LODE L31 POLES | Stockton(N) | 2021-05-10 | 2021-07-08 | 2021-12-22 | Hardware and Framing: Molding missing, broken, damaged, or loose | [Answer left blank] | Molding appears to be damaged a little more than halfway up the pole. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101251739 | MOTHER LODE L31 POLES | Stockton(N) | 2021-05-10 | 2021-07-08 | 2021-12-22 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101484539 | SHASTA Q4004 POLES | North Valley(N) | 2021-05-10 | 2021-06-30 | 2021-12-22 | damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | The top of the pole has cracks where the crossarm and down guy are attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Corner pole is Deadend Line & Buck framing and has wood crossarms & bolts and down guy which act as an anti-split bolt. | N\A | N\A | N\A | N\A | N\A
101484543 | SHASTA Q4004 POLES | North Valley(N) | 2021-05-10 | 2021-06-30 | 2021-12-22 | Common Equipment/Other Equipment: Transformer shows signs of leaking, seeping, or weeping oil | [Answer left blank] | Transformer appears to show signs of seeping oil, as oil stains are present. | Agree | N/A | N¦A | Pole has open EC Notification (119094042). Inspector did update Notification for another condition but did not indicate this condition in FSR or in Equipment section of Inspection Record. | Update a EC | Yes | No | Yes | No
101484543 | SHASTA Q4004 POLES | North Valley(N) | 2021-05-10 | 2021-06-30 | 2021-12-22 | Non-Time-Dependent Issues: Visibility strips missing, broken, mismatched, or no longer reflective | [Answer left blank] | One visibility strip is loose. | Agree | N/A | N¦A | Pole has open EC Notification (119094042). Inspector did update Notification for another condition but did not indicate this condition in FSR or in Non-Time-Dependent section of Inspection Record. | Update a EC | Yes | No | Yes | No
101484543 | SHASTA Q4004 POLES | North Valley(N) | 2021-05-10 | 2021-06-30 | 2021-12-22 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | High voltage sign is missing on one side of pole. | Disagree | Condition is not compelling | 1. High Voltage Sign Not Installed as Required - TD-2305M-JA02, Rev. 8 - Pg. 61 | The one high sign in good condition on the opposite side of the pole satisfies the standard found in OH: Marking, Rev. #18: 11/01/18 022168 Page 3 of 35. Marking, Numbering, and Identification of Line Structures 3. Routine Inspection A. The requirement in 1, “Poles That Support Line Conductors,” must be satisfied with the following exceptions: 1. Sign the Pole: It is acceptable to have only one sign, or stacked pairs of signs, below the lowest line conductor energized above 750 V, except as noted in 4 “Special Locations.” B. The requirements in 2, Poles That Do Not Support Line Conductors,” must be satisfied with the following exceptions: 1. Risers: It is acceptable to have only one sign, or stacked pairs of signs, below risers energized above 750 V. 4. Special Locations: If the pole is signed, high-voltage signs are required on both sides of the pole in the following locations: Near water areas suitable for sailboats. Near established boat ramps and associated rigging areas. Adjacent to swimming pools. In agricultural areas with movable irrigation piping. Locations, where in the judgement of the employee, high-voltage signs should be visible from all sides of the poles. | N\A | N\A | N\A | N\A | N\A
101484551 | SHASTA Q4004 POLES | North Valley(N) | 2021-05-10 | 2021-06-30 | 2021-12-22 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There is a crack at the top of the pole near where hardware is attached. | Agree | N/A | N¦A | Incorrect wardware used on composite crossarm. | Create a EC | Yes | No | Yes | No
101484551 | SHASTA Q4004 POLES | North Valley(N) | 2021-05-10 | 2021-06-30 | 2021-12-22 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103694142 | SOLANO Q1113 POLES | Sacramento(N) | 2021-05-10 | 2021-07-01 | 2021-12-22 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are woodpecker holes throughout the pole, including several holes that appear to be over 3" in diameter just above the communications level and one hole that appears to be over 4" in diameter. | Disagree | N/A | N¦A | Inspector selected "Select if there are risks, hazards or other maintenance conditions not previously captured in the checklist above for the pole" which would cover woodpecker damage to pole. Inspector also completed FSR to update existing EC Notification (117017845) | N\A | N\A | N\A | N\A | N\A
101484505 | SHASTA Q4004 POLES | North Valley(N) | 2021-05-11 | 2021-06-30 | 2021-12-22 | Anchor and Guys: Does or should this location have a Guy? | No | This location has a guy. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101484505 | SHASTA Q4004 POLES | North Valley(N) | 2021-05-11 | 2021-06-30 | 2021-12-22 | Hardware and Framing: Molding missing, broken, damaged, or loose | [Answer left blank] | Molding is damaged approximately 10' from the ground line. | Agree | N/A | N¦A | Pole has open EC Notification (117016654). Inspector did update Notification for another condition but did not indicate this condition in FSR or in Hardware section of Inspection Record. | Update a EC | Yes | No | Yes | No
101484505 | SHASTA Q4004 POLES | North Valley(N) | 2021-05-11 | 2021-06-30 | 2021-12-22 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | High voltage sign is missing on one side of the pole. | Disagree | Condition is not compelling | 1. High Voltage Sign Not Installed as Required - TD-2305M-JA02, Rev. 8 - Pg. 61 | The one high sign in good condition on the opposite side of the pole satisfies the standard found in OH: Marking, Rev. #18: 11/01/18 022168 Page 3 of 35. Marking, Numbering, and Identification of Line Structures 3. Routine Inspection A. The requirement in 1, “Poles That Support Line Conductors,” must be satisfied with the following exceptions: 1. Sign the Pole: It is acceptable to have only one sign, or stacked pairs of signs, below the lowest line conductor energized above 750 V, except as noted in 4 “Special Locations.” B. The requirements in 2, Poles That Do Not Support Line Conductors,” must be satisfied with the following exceptions: 1. Risers: It is acceptable to have only one sign, or stacked pairs of signs, below risers energized above 750 V. 4. Special Locations: If the pole is signed, high-voltage signs are required on both sides of the pole in the following locations: Near water areas suitable for sailboats. Near established boat ramps and associated rigging areas. Adjacent to swimming pools. In agricultural areas with movable irrigation piping. Locations, where in the judgement of the employee, high-voltage signs should be visible from all sides of the poles. | N\A | N\A | N\A | N\A | N\A
101570096 | SOLANO Q1113 POLES | Sacramento(N) | 2021-05-11 | 2021-07-01 | 2021-12-22 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There is a woodpecker hole that appears to be 4" in diameter at the top of the pole, near where the king pin is attached. | Agree | N/A | N¦A | Pole has open EC Notification (117016654). Inspector did create Notification for another condition but did not indicate in Structure section of Inspection Record. | Update a EC | Yes | No | Yes | No
101570096 | SOLANO Q1113 POLES | Sacramento(N) | 2021-05-11 | 2021-07-01 | 2021-12-22 | Hardware and Framing: Molding missing, broken, damaged, or loose | [Answer left blank] | Wood molding covering the ground wire is broken at 7'9" (93") from the ground. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | Yes
101570096 | SOLANO Q1113 POLES | Sacramento(N) | 2021-05-11 | 2021-07-01 | 2021-12-22 | Hardware and Framing: Grounds exposed, broken, damaged, disconnected, unsecured, or missing (if required) | [Answer left blank] | Ground is exposed at 7'9" (93") from the ground. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | Yes
101570106 | SOLANO Q1113 POLES | Sacramento(N) | 2021-05-11 | 2021-07-01 | 2021-12-22 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | Pole number is visible on pole. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101570119 | SOLANO Q1113 POLES | Sacramento(N) | 2021-05-11 | 2021-07-01 | 2021-12-22 | Hardware and Framing: Tap clamps installed incorrectly | [Answer left blank] | The tap clamps do not appear to be installed on tap guards. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101570121 | SOLANO Q1113 POLES | Sacramento(N) | 2021-05-11 | 2021-07-01 | 2021-12-22 | Anchor and Guys: Anchor rod broken, damaged, corroded, covered by vegetation/overgrown, soil-eroded, graded, or buried | [Answer left blank] | Anchor rod is buried. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101570121 | SOLANO Q1113 POLES | Sacramento(N) | 2021-05-11 | 2021-07-01 | 2021-12-22 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101570122 | SOLANO Q1113 POLES | Sacramento(N) | 2021-05-11 | 2021-07-01 | 2021-12-22 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are several cracks at the top of pole near where hardware is attached, and the pole appears to show signs of decay. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Angle pole is Deadend slack span framing and has steel crossarm, king pin & bolts and down guy which act as an anti-split bolt. | N\A | N\A | N\A | N\A | N\A
101570122 | SOLANO Q1113 POLES | Sacramento(N) | 2021-05-11 | 2021-07-01 | 2021-12-22 | Conductor: Conductor has splices tied in proximity to insulator preventing free movement of splice with conductor | [Answer left blank] | Splices are tied within 2' of insulators. | Disagree | Condition is not compelling | ELEC-1000 Training | Splices are within 2' of slack span shoe. Conductor is bolted into shoe and therefore does not need room to allow free monement of splice with conductor. | N\A | N\A | N\A | N\A | N\A
101570122 | SOLANO Q1113 POLES | Sacramento(N) | 2021-05-11 | 2021-07-01 | 2021-12-22 | Hardware and Framing: Insulators or King Pin chipped, cracked, corroded, contaminated, flashed, have signs of tracking, broken or damaged | [Answer left blank] | King pin hardware appears to be loose. | Agree | N/A | N¦A | Pole has open EC Notification (117037879). Inspector did update Notification for another condition but did not indicate this condition in FSR or in Hardware section of Inspection Record. | Update a EC | Yes | No | Yes | No
101570122 | SOLANO Q1113 POLES | Sacramento(N) | 2021-05-11 | 2021-07-01 | 2021-12-22 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103060360 | SOLANO Q1113 POLES | Sacramento(N) | 2021-05-11 | 2021-07-01 | 2021-12-22 | Hardware and Framing: Tap clamps installed incorrectly | [Answer left blank] | The tap clamps do not appear to be installed on tap guards. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
103060360 | SOLANO Q1113 POLES | Sacramento(N) | 2021-05-11 | 2021-07-01 | 2021-12-22 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103060360 | SOLANO Q1113 POLES | Sacramento(N) | 2021-05-11 | 2021-07-01 | 2021-12-22 | Vegetation: Support Structure with non-exempt equipment, has dried vegetation (dead branches) above 8' to top of conductors, within 10' radius of Support Structure | [Answer left blank] | There is non-exempt equipment on the pole and dried vegetation present between 10 and 20 feet from the ground, within a 10' radius of the pole. | Agree | N/A | N¦A |  | Create "Other tag" | Yes | No | Yes | No
103060360 | SOLANO Q1113 POLES | Sacramento(N) | 2021-05-11 | 2021-07-01 | 2021-12-22 | Other Required Data: Is there non-exempt equipment at the inspection location (Universal or Open Link Fuse) | [Answer left blank] | Universal or open link fuse is present on the pole. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
104013562 | SHASTA Q4004 POLES | North Valley(N) | 2021-05-11 | 2021-06-30 | 2021-12-22 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | Pole number is visible on pole. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101249217 | MOTHER LODE MAP LL29 POLES | Stockton(N) | 2021-05-12 | 2021-07-06 | 2021-12-22 | Other Required Data: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101276994 | MOTHER LODE M29 POLES | Stockton(N) | 2021-05-13 | 2021-07-07 | 2021-12-22 | Conductor: Primary, secondary, and/or service conductors broken, damaged, burnt, corroded, loose, frayed or bird caging | [Answer left blank] | Conductor shows signs of bird caging/damage (i) near the crossarm and (ii) at midspan of southeast span. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101277008 | MOTHER LODE M29 POLES | Stockton(N) | 2021-05-13 | 2021-07-07 | 2021-12-22 | Conductor: Primary, secondary, and/or service conductors broken, damaged, burnt, corroded, loose, frayed or bird caging | [Answer left blank] | Conductor shows signs of bird caging. | Agree | N/A | N¦A | Pole has open EC Notification (113011573). Inspector did update Notification for another condition but did not indicate this condition in FSR or in Conductor section of Inspection Record. | Update a EC | Yes | No | Yes | No
103992059 | SOLANO Q1113 POLES | Sacramento(N) | 2021-05-13 | 2021-07-01 | 2021-12-22 | Hardware and Framing: Tap clamps installed incorrectly | [Answer left blank] | The tap clamps do not appear to be installed on tap guards. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101247724 | MOTHER LODE N28 POLES | Stockton(N) | 2021-05-14 | 2021-07-09 | 2021-12-22 | Structure: Pole leaning or out of plumb by more than 10% of its height above the ground | [Answer left blank] | Pole appears to be out of plumb by more than 10% of its height above the ground. | Agree | N/A | N¦A | Inspector did update the existing EC Notification (117267676) with this condition but did not indicate this condition in Structure section of Inspection Record. He marked Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay. | N\A | N\A | N\A | N\A | N\A
101247724 | MOTHER LODE N28 POLES | Stockton(N) | 2021-05-14 | 2021-07-09 | 2021-12-22 | Common Equipment/Other Equipment: Does this structure have equipment? | No | Operating equipment (exempt in-line fuses) appears to be present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101247724 | MOTHER LODE N28 POLES | Stockton(N) | 2021-05-14 | 2021-07-09 | 2021-12-22 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | Pole number is visible. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101247757 | MOTHER LODE N28 POLES | Stockton(N) | 2021-05-14 | 2021-07-09 | 2021-12-22 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | Cracks are present at the top of pole, including where hardware is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Pole is single phase tangent framing and has wood crossarm & bolts and anti-split bolt. | N\A | N\A | N\A | N\A | N\A
101570127 | SOLANO Q11 POLES | Sacramento(N) | 2021-05-14 | 2021-07-01 | 2021-12-22 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are several cracks near the top of the pole, including near where hardware is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Pole is line & buck tangent framing and has 9" steel brackets, king pin & bolts and steel buck arm. | N\A | N\A | N\A | N\A | N\A
101570127 | SOLANO Q11 POLES | Sacramento(N) | 2021-05-14 | 2021-07-01 | 2021-12-22 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101570127 | SOLANO Q11 POLES | Sacramento(N) | 2021-05-14 | 2021-07-01 | 2021-12-22 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101570136 | SOLANO Q11 POLES | Sacramento(N) | 2021-05-14 | 2021-07-01 | 2021-12-22 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There is a deep crack in the midsection of the pole, and several cracks near the top of the pole where hardware is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Corner pole is has steel crossarms & bolts and down guy combination of bolts act as anti-split bolt. | N\A | N\A | N\A | N\A | N\A
101570136 | SOLANO Q11 POLES | Sacramento(N) | 2021-05-14 | 2021-07-01 | 2021-12-22 | Hardware and Framing: Molding missing, broken, damaged, or loose | [Answer left blank] | Molding is loose just below transformer and about 15' from the ground level, exposing insulated conductor. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101570136 | SOLANO Q11 POLES | Sacramento(N) | 2021-05-14 | 2021-07-01 | 2021-12-22 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101662271 | SOLANO Q11 POLES | Sacramento(N) | 2021-05-14 | 2021-07-01 | 2021-12-22 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | At the top of the pole near where hardware is attached, there are several cracks and two woodpecker holes that appear to be over 4" in diameter. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101662271 | SOLANO Q11 POLES | Sacramento(N) | 2021-05-14 | 2021-07-01 | 2021-12-22 | Anchor and Guys: Guy wire broken, damaged, clearance issues, corroded, covered by vegetation, overgrown, strain or abrasion | [Answer left blank] | Tree appears to be in contact with down guy above insulator. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101662271 | SOLANO Q11 POLES | Sacramento(N) | 2021-05-14 | 2021-07-01 | 2021-12-22 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | Yes | Pole number is not visible. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103060325 | SOLANO Q11 POLES | Sacramento(N) | 2021-05-14 | 2021-07-01 | 2021-12-22 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101465657 | SHASTA R2804 POLES | North Valley(N) | 2021-05-15 | 2021-07-01 | 2021-12-22 | Hardware and Framing: Tap clamps installed incorrectly | [Answer left blank] | Tap clamps appear to be installed on armor rodinstead of a tap guard. | Agree | N/A | N¦A | Pole has open EC Notification (122228390). Inspector did not indicate condition in Hardware section of Inspection Record. | Update a EC | Yes | No | Yes | No
101465657 | SHASTA R2804 POLES | North Valley(N) | 2021-05-15 | 2021-07-01 | 2021-12-22 | Vegetation: Tree causing strain or abrasion to secondary or service (only 1 service) | [Answer left blank] | A tree appears to be causing strain to the secondary service conductor. | Agree | N/A | N¦A | Pole has open EC Notification (122228390). Inspector did not indicate condition in Vegetation section of Inspection Record. | Update a EC | Yes | No | Yes | No
101465657 | SHASTA R2804 POLES | North Valley(N) | 2021-05-15 | 2021-07-01 | 2021-12-22 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101465666 | SHASTA R2804 POLES | North Valley(N) | 2021-05-15 | 2021-07-01 | 2021-12-22 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are deep cracks along the length of the pole. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. | N\A | N\A | N\A | N\A | N\A
101465666 | SHASTA R2804 POLES | North Valley(N) | 2021-05-15 | 2021-07-01 | 2021-12-22 | Vegetation: Tree causing strain or abrasion to secondary or service (2 or more services) | [Answer left blank] | The service conductor running north across the road appears to be strained by vegetation. | Agree | N/A | N¦A | Pole has open EC Notification (112879124). Inspector did update Notification for primary FDA but did not indicate vegetation condition in FSR or in Vegetation section of Inspection Record. | Update a EC | Yes | No | Yes | No
101465666 | SHASTA R2804 POLES | North Valley(N) | 2021-05-15 | 2021-07-01 | 2021-12-22 | Other Required Data: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101465666 | SHASTA R2804 POLES | North Valley(N) | 2021-05-15 | 2021-07-01 | 2021-12-22 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101465551 | SHASTA R2804 POLES | North Valley(N) | 2021-05-17 | 2021-07-01 | 2021-12-22 | Anchor and Guys: Does or should this location have a Guy? | No | This location has a guy. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101465551 | SHASTA R2804 POLES | North Valley(N) | 2021-05-17 | 2021-07-01 | 2021-12-22 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101465556 | SHASTA R2803 POLES | North Valley(N) | 2021-05-17 | 2021-07-01 | 2021-12-22 | Common Equipment/Other Equipment: IFD (aka "Turkey Popper") has activated on the transformer (orange band is visible) | [Answer left blank] | The IFD appears to have been activated. | Agree | N/A | N¦A | Pole has open EC Notification (116751497). Inspector did update Notification for primary FDA but did not indicate transformer condition in FSR or on Structure section of Inspection Record. | Update a EC | Yes | No | Yes | No
101465556 | SHASTA R2803 POLES | North Valley(N) | 2021-05-17 | 2021-07-01 | 2021-12-22 | Other Required Data: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101465556 | SHASTA R2803 POLES | North Valley(N) | 2021-05-17 | 2021-07-01 | 2021-12-22 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | The asset does not appear to have high voltage signs. | Disagree | Condition does not exist | ELEC-1000 Training | Photos attached to Inspection Record and photos in FM Report both appear to show at least one High Voltage sign attached to back of pole per the construction standard. | N\A | N\A | N\A | N\A | N\A
101510908 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-17 | 2021-06-30 | 2021-12-22 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are deep cracks in the pole, including at the top near where hardware is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Single phase tangent pole has 9" brackets and anti-split bolt installed | N\A | N\A | N\A | N\A | N\A
101510908 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-17 | 2021-06-30 | 2021-12-22 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101510908 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-17 | 2021-06-30 | 2021-12-22 | Non-Time-Dependent Issues: Visibility strips missing, broken, mismatched, or no longer reflective | [Answer left blank] | Visibility strips are no longer reflective, and one is missing. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101510910 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-17 | 2021-06-30 | 2021-12-22 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks along the length of the pole and a woodpecker hole that appears to be 4" in diameter under the high voltage sign. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101510910 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-17 | 2021-06-30 | 2021-12-22 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101510910 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-17 | 2021-06-30 | 2021-12-22 | Non-Time-Dependent Issues: Visibility strips missing, broken, mismatched, or no longer reflective | [Answer left blank] | Visibility strips are no longer reflective, and one is missing. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
103644584 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-17 | 2021-06-30 | 2021-12-22 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103855167 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-17 | 2021-06-30 | 2021-12-22 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103856873 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-17 | 2021-06-30 | 2021-12-22 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101247332 | MOTHER LODE N28 POLES | Stockton(N) | 2021-05-18 | 2021-07-09 | 2021-12-22 | Anchor and Guys: Does or should this location have a Guy? | No | This location has a guy. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101247332 | MOTHER LODE N28 POLES | Stockton(N) | 2021-05-18 | 2021-07-09 | 2021-12-22 | Hardware and Framing: Tap clamps installed incorrectly | [Answer left blank] | The tap clamps do not appear to be installed on tap guards. | Agree | N/A | N¦A | Inspector did update the existing EC Notification (117245880) with this condition but did not indicate condition on Hardware section of Inspection Record. | N\A | N\A | N\A | N\A | N\A
101465519 | SHASTA MAP R2803 POLES | North Valley(N) | 2021-05-18 | 2021-07-01 | 2021-12-22 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks throughout the pole, including near where hardware is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Pole also has some signs of shell rot above ground level. Single phase tangent pole has 9" brackets and anti-split bolt installed at pole top and steel arm and hardware installed below for slack span. | N\A | N\A | N\A | N\A | N\A
101465519 | SHASTA MAP R2803 POLES | North Valley(N) | 2021-05-18 | 2021-07-01 | 2021-12-22 | Hardware and Framing: Tap clamps installed incorrectly | [Answer left blank] | Tap clamps appear to be installed on armor rodinstead of a tap guard. | Agree | N/A | N¦A | Pole has open EC Notification (122214592). Inspector did not indicate condition in Hardware section of Inspection Record. | N\A | N\A | N\A | N\A | N\A
101465522 | SHASTA MAP R2803 POLES | North Valley(N) | 2021-05-18 | 2021-07-01 | 2021-12-22 | Hardware and Framing: Tap clamps installed incorrectly | [Answer left blank] | The tap clamps do not appear to be installed on tap guards. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101465522 | SHASTA MAP R2803 POLES | North Valley(N) | 2021-05-18 | 2021-07-01 | 2021-12-22 | Other Required Data: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101465522 | SHASTA MAP R2803 POLES | North Valley(N) | 2021-05-18 | 2021-07-01 | 2021-12-22 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101465570 | SHASTA MAP R2803 POLES | North Valley(N) | 2021-05-18 | 2021-07-01 | 2021-12-22 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks throughout the pole, including near where hardware is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. | N\A | N\A | N\A | N\A | N\A
101465570 | SHASTA MAP R2803 POLES | North Valley(N) | 2021-05-18 | 2021-07-01 | 2021-12-22 | Hardware and Framing: Tap clamps installed incorrectly | [Answer left blank] | Tap clamps appear to be installed on armor rod instead of a tap guard. | Agree | N/A | N¦A | Pole has open EC Notification (116752241). Inspector did update Notification in FSR but did not indicate condition in Hardware section of Inspection Record. | Update a EC | Yes | No | Yes | No
101465570 | SHASTA MAP R2803 POLES | North Valley(N) | 2021-05-18 | 2021-07-01 | 2021-12-22 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101510933 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-18 | 2021-06-30 | 2021-12-23 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks along the length of the pole, including at the top near where hardware is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Single phase tangent pole has 9" brackets and anti-split bolt installed at pole top. | N\A | N\A | N\A | N\A | N\A
101510933 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-18 | 2021-06-30 | 2021-12-23 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101510936 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-18 | 2021-06-30 | 2021-12-23 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101510936 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-18 | 2021-06-30 | 2021-12-23 | Other Required Data: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101510938 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-18 | 2021-06-30 | 2021-12-23 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks in the middle and top sections of the pole, including near where hardware is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Single phase tangent pole has 9" brackets and hardware. | N\A | N\A | N\A | N\A | N\A
101510938 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-18 | 2021-06-30 | 2021-12-23 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101510938 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-18 | 2021-06-30 | 2021-12-23 | Non-Time-Dependent Issues: Visibility strips missing, broken, mismatched, or no longer reflective | [Answer left blank] | Visibility strips are no longer fully reflective, and one is missing. | Agree | N/A | N¦A | Pole does not need visibility strips due to it's location. Faded vis strips can be removed. | Create a EC | Yes | No | Yes | No
101510938 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-18 | 2021-06-30 | 2021-12-23 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101510940 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-18 | 2021-06-30 | 2021-12-23 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks in the bottom and top sections of the pole, including near where hardware is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Single phase corner pole has steel cross arms & hardware and down guy fixture. | N\A | N\A | N\A | N\A | N\A
101510940 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-18 | 2021-06-30 | 2021-12-23 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101510940 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-18 | 2021-06-30 | 2021-12-23 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101510949 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-18 | 2021-06-30 | 2021-12-23 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101510951 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-18 | 2021-06-30 | 2021-12-23 | damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks along the length of the front of the pole, including at the top near where hardware is attached | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Single phase tangent pole has 9" brackets and hardware. | N\A | N\A | N\A | N\A | N\A
101510951 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-18 | 2021-06-30 | 2021-12-23 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101510952 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-18 | 2021-06-30 | 2021-12-23 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101510955 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-18 | 2021-06-30 | 2021-12-23 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101510958 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-18 | 2021-06-30 | 2021-12-23 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks along the length of the pole and several large woodpecker holes near the top of the pole. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Single phase tangent pole has 9" brackets and hardware. | N\A | N\A | N\A | N\A | N\A
101510958 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-18 | 2021-06-30 | 2021-12-23 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101510958 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-18 | 2021-06-30 | 2021-12-23 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | High voltage sign on one side of the pole is missing. | Disagree | Condition is not compelling | 1. High Voltage Sign Not Installed as Required - TD-2305M-JA02, Rev. 8 - Pg. 61 | The one high sign in good condition on the opposite side of the pole satisfies the standard found in OH: Marking, Rev. #18: 11/01/18 022168 Page 3 of 35. Marking, Numbering, and Identification of Line Structures 3. Routine Inspection A. The requirement in 1, “Poles That Support Line Conductors,” must be satisfied with the following exceptions: 1. Sign the Pole: It is acceptable to have only one sign, or stacked pairs of signs, below the lowest line conductor energized above 750 V, except as noted in 4 “Special Locations.” B. The requirements in 2, Poles That Do Not Support Line Conductors,” must be satisfied with the following exceptions: 1. Risers: It is acceptable to have only one sign, or stacked pairs of signs, below risers energized above 750 V. 4. Special Locations: If the pole is signed, high-voltage signs are required on both sides of the pole in the following locations: Near water areas suitable for sailboats. Near established boat ramps and associated rigging areas. Adjacent to swimming pools. In agricultural areas with movable irrigation piping. Locations, where in the judgement of the employee, high-voltage signs should be visible from all sides of the poles. | N\A | N\A | N\A | N\A | N\A
101510959 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-18 | 2021-06-30 | 2021-12-23 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks along the length of the pole, including at the top near where hardware is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Single phase line & buck pole has 9" brackets & hardware and steel buck arm for slack span. | N\A | N\A | N\A | N\A | N\A
101510959 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-18 | 2021-06-30 | 2021-12-23 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101510959 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-18 | 2021-06-30 | 2021-12-23 | Non-Time-Dependent Issues: Visibility strips missing, broken, mismatched, or no longer reflective | [Answer left blank] | Visibility strips are no longer reflective, and one is missing. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101510962 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-18 | 2021-06-30 | 2021-12-23 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks at both the bottom and top sections of the pole, including near where the hardware is attached. The top third of the pole also appears to be damaged. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101510962 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-18 | 2021-06-30 | 2021-12-23 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101510962 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-18 | 2021-06-30 | 2021-12-23 | Non-Time-Dependent Issues: Visibility strips missing, broken, mismatched, or no longer reflective | [Answer left blank] | Visibility strips are no longer fully reflective. | Agree | N/A | N¦A | Pole does not need visibility strips due to it's location. Faded vis strips can be removed. | Create a EC | Yes | No | Yes | No
101510962 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-18 | 2021-06-30 | 2021-12-23 | CommentsOther Required Data: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101510963 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-18 | 2021-06-30 | 2021-12-23 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks along the length of the pole, including at the top near where the hardware is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Single phase pole has 9" brackets & hardware and anti-split bolt installed. | N\A | N\A | N\A | N\A | N\A
101510963 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-18 | 2021-06-30 | 2021-12-23 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101510963 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-18 | 2021-06-30 | 2021-12-23 | Non-Time-Dependent Issues: Visibility strips missing, broken, mismatched, or no longer reflective | [Answer left blank] | Visibility strips are no longer reflective, and one is missing. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101510963 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-18 | 2021-06-30 | 2021-12-23 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | High voltage sign on one side of the pole is missing. | Disagree | Condition is not compelling | 1. High Voltage Sign Not Installed as Required - TD-2305M-JA02, Rev. 8 - Pg. 61 | The one high sign in good condition on the opposite side of the pole satisfies the standard found in OH: Marking, Rev. #18: 11/01/18 022168 Page 3 of 35. Marking, Numbering, and Identification of Line Structures 3. Routine Inspection A. The requirement in 1, “Poles That Support Line Conductors,” must be satisfied with the following exceptions: 1. Sign the Pole: It is acceptable to have only one sign, or stacked pairs of signs, below the lowest line conductor energized above 750 V, except as noted in 4 “Special Locations.” B. The requirements in 2, Poles That Do Not Support Line Conductors,” must be satisfied with the following exceptions: 1. Risers: It is acceptable to have only one sign, or stacked pairs of signs, below risers energized above 750 V. 4. Special Locations: If the pole is signed, high-voltage signs are required on both sides of the pole in the following locations: Near water areas suitable for sailboats. Near established boat ramps and associated rigging areas. Adjacent to swimming pools. In agricultural areas with movable irrigation piping. Locations, where in the judgement of the employee, high-voltage signs should be visible from all sides of the poles. | N\A | N\A | N\A | N\A | N\A
101510963 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-18 | 2021-06-30 | 2021-12-23 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101510964 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-18 | 2021-06-30 | 2021-12-23 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks along the length of the pole, including at the top near where hardware is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Single phase pole has 9" brackets & hardware and anti-split bolt installed. | N\A | N\A | N\A | N\A | N\A
101510964 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-18 | 2021-06-30 | 2021-12-23 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101510964 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-18 | 2021-06-30 | 2021-12-23 | Non-Time-Dependent Issues: Visibility strips missing, broken, mismatched, or no longer reflective | [Answer left blank] | Visibility strips are no longer reflective, and one is missing. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101510965 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-18 | 2021-06-30 | 2021-12-23 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101510965 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-18 | 2021-06-30 | 2021-12-23 | Non-Time-Dependent Issues: Visibility strips missing, broken, mismatched, or no longer reflective | [Answer left blank] | Visibility strips are no longer reflective, and one is missing. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101510965 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-18 | 2021-06-30 | 2021-12-23 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | The high voltage sign appears to be missing on one side of the pole. | Disagree | Condition is not compelling | 1. High Voltage Sign Not Installed as Required - TD-2305M-JA02, Rev. 8 - Pg. 61 | The one high sign in good condition on the opposite side of the pole satisfies the standard found in OH: Marking, Rev. #18: 11/01/18 022168 Page 3 of 35. Marking, Numbering, and Identification of Line Structures 3. Routine Inspection A. The requirement in 1, “Poles That Support Line Conductors,” must be satisfied with the following exceptions: 1. Sign the Pole: It is acceptable to have only one sign, or stacked pairs of signs, below the lowest line conductor energized above 750 V, except as noted in 4 “Special Locations.” B. The requirements in 2, Poles That Do Not Support Line Conductors,” must be satisfied with the following exceptions: 1. Risers: It is acceptable to have only one sign, or stacked pairs of signs, below risers energized above 750 V. 4. Special Locations: If the pole is signed, high-voltage signs are required on both sides of the pole in the following locations: Near water areas suitable for sailboats. Near established boat ramps and associated rigging areas. Adjacent to swimming pools. In agricultural areas with movable irrigation piping. Locations, where in the judgement of the employee, high-voltage signs should be visible from all sides of the poles. | N\A | N\A | N\A | N\A | N\A
101510966 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-18 | 2021-06-30 | 2021-12-23 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks along the length of the pole, including at the top near where hardware is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Single phase line & buck pole has 9" brackets & hardware, anti-split bolt and steel buck arm for slack span. | N\A | N\A | N\A | N\A | N\A
101510966 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-18 | 2021-06-30 | 2021-12-23 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101510969 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-18 | 2021-06-30 | 2021-12-23 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks along the length of the pole, including at the top near where hardware is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Single phase line & buck pole has 9" brackets & hardware, anti-split bolt and steel buck arm for slack span. | N\A | N\A | N\A | N\A | N\A
101510969 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-18 | 2021-06-30 | 2021-12-23 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101510969 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-18 | 2021-06-30 | 2021-12-23 | Non-Time-Dependent Issues: Visibility strips missing, broken, mismatched, or no longer reflective | [Answer left blank] | Visibility strips are no longer reflective, and one is missing. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101510969 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-18 | 2021-06-30 | 2021-12-23 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | High voltage sign on one side of the pole is missing. | Disagree | Condition is not compelling | 1. High Voltage Sign Not Installed as Required - TD-2305M-JA02, Rev. 8 - Pg. 61 | The one high sign in good condition on the opposite side of the pole satisfies the standard found in OH: Marking, Rev. #18: 11/01/18 022168 Page 3 of 35. Marking, Numbering, and Identification of Line Structures 3. Routine Inspection A. The requirement in 1, “Poles That Support Line Conductors,” must be satisfied with the following exceptions: 1. Sign the Pole: It is acceptable to have only one sign, or stacked pairs of signs, below the lowest line conductor energized above 750 V, except as noted in 4 “Special Locations.” B. The requirements in 2, Poles That Do Not Support Line Conductors,” must be satisfied with the following exceptions: 1. Risers: It is acceptable to have only one sign, or stacked pairs of signs, below risers energized above 750 V. 4. Special Locations: If the pole is signed, high-voltage signs are required on both sides of the pole in the following locations: Near water areas suitable for sailboats. Near established boat ramps and associated rigging areas. Adjacent to swimming pools. In agricultural areas with movable irrigation piping. Locations, where in the judgement of the employee, high-voltage signs should be visible from all sides of the poles. | N\A | N\A | N\A | N\A | N\A
101510970 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-18 | 2021-06-30 | 2021-12-23 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101510975 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-18 | 2021-06-30 | 2021-12-23 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks along the length of the pole, including at the top near where hardware is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Single phase tangent pole has wood cross arm & hardware. | N\A | N\A | N\A | N\A | N\A
101510975 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-18 | 2021-06-30 | 2021-12-23 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101510975 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-18 | 2021-06-30 | 2021-12-23 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101510976 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-18 | 2021-06-30 | 2021-12-23 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks along the length of the pole, including at the top near where hardware is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Single phase tangent pole has wood cross arm & hardware and anti-split bolt installed. | N\A | N\A | N\A | N\A | N\A
101510976 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-18 | 2021-06-30 | 2021-12-23 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103782332 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-18 | 2021-06-30 | 2021-12-23 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101245859 | MOTHER LODE MAP KK31 POLES | Stockton(N) | 2021-05-19 | 2021-07-08 | 2021-12-23 | Anchor and Guys: Guy wire broken, damaged, clearance issues, corroded, covered by vegetation, overgrown, strain or abrasion | [Answer left blank] | Vegetation appears to be in contact with guy above the guy insulator. | Agree | N/A | N¦A | Pole has open EC Notification (117363890). Inspector did update Notification but did not indicate condition in FSR or on Structure section of Inspection Record. | Update a EC | Yes | No | Yes | No
101245859 | MOTHER LODE MAP KK31 POLES | Stockton(N) | 2021-05-19 | 2021-07-08 | 2021-12-23 | Non-Time-Dependent Issues: Visibility strips missing, broken, mismatched, or no longer reflective | [Answer left blank] | Visibility strips are missing. | Agree | N/A | N¦A | Pole has open EC Notification (117363890). Inspector did update Notification but did not indicate condition in FSR or on Structure section of Inspection Record. | Update a EC | Yes | No | Yes | No
101247543 | MOTHER LODE N28 POLES | Stockton(N) | 2021-05-19 | 2021-07-09 | 2021-12-23 | Non-Time-Dependent Issues: Visibility strips missing, broken, mismatched, or no longer reflective | [Answer left blank] | Visibility strips are missing. | Agree | N/A | N¦A | Pole has open EC Notification (117267627). Inspector did update Notification but did not indicate condition in FSR or on Structure section of Inspection Record. | Update a EC | Yes | No | Yes | No
101247543 | MOTHER LODE N28 POLES | Stockton(N) | 2021-05-19 | 2021-07-09 | 2021-12-23 | Non-Time-Dependent Issues: Pole steps are less than 8' 6" above the ground or any other accessible surface | [Answer left blank] | Pole step is at 8' 4" (100"). | Agree | N/A | N¦A | Pole has open EC Notification (117267627). Inspector did update Notification but did not indicate condition in FSR or on Structure section of Inspection Record. | Update a EC | Yes | No | Yes | No
101247543 | MOTHER LODE N28 POLES | Stockton(N) | 2021-05-19 | 2021-07-09 | 2021-12-23 | Other Required Data: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101247582 | MOTHER LODE N28 POLES | Stockton(N) | 2021-05-19 | 2021-07-09 | 2021-12-23 | Conductor: Conductor has splices tied in proximity to insulator preventing free movement of splice with conductor | [Answer left blank] | Two splices on the northwest span appear to be within 2' of the insulator. | Agree | N/A | N¦A | Pole has open EC Notification (117271538). Inspector did update Notification but did not indicate condition in FSR or on Conductor section of Inspection Record. | Update a EC | Yes | No | Yes | No
101247582 | MOTHER LODE N28 POLES | Stockton(N) | 2021-05-19 | 2021-07-09 | 2021-12-23 | Other Required Data: 3 or more splices present in one phase of the span. | [Answer left blank] | There are 3 phases on the asset. There are 11 splices on the northwest span. There are 2 splices on the north phase, 5 splices on the center phase, and 4 splices on the south phase. Span does not cross over a major roadway. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101511804 | TEHEMA U29 POLES | North Valley(N) | 2021-05-19 | 2021-06-29 | 2021-12-23 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There is a deep crack (approximately 4”) running the length of the pole, including near the top where hardware is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Single phase tangent pole 9" brackets & hardware. | N\A | N\A | N\A | N\A | N\A
101511804 | TEHEMA U29 POLES | North Valley(N) | 2021-05-19 | 2021-06-29 | 2021-12-23 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102002438 | SANTA ROSA HH2205 POLES | Sonoma(N) | 2021-05-19 | 2021-07-07 | 2021-12-23 | Common Equipment/Other Equipment: Does this structure have equipment? | Yes | This is a service pole. There is no equipment. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102002439 | SANTA ROSA HH2205 POLES | Sonoma(N) | 2021-05-19 | 2021-07-07 | 2021-12-23 | Vegetation: Tree causing strain or abrasion to secondary or service (2 or more services) | [Answer left blank] | Vegetation appears to be causing strain on two service conductors. | Agree | N/A | N¦A |  | Create "Other tag" | Yes | No | Yes | No
103925169 | SANTA ROSA HH2205 POLES | Sonoma(N) | 2021-05-19 | 2021-07-07 | 2021-12-23 | Other Required Data: Tree anchor installed in tree by design | [Answer left blank] | Tree anchors appear to be installed in tree by design | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103925169 | SANTA ROSA HH2205 POLES | Sonoma(N) | 2021-05-19 | 2021-07-07 | 2021-12-23 | Other Required Data: 3 or more splices present in one phase of the span | [Answer left blank] | There are 2 phases on the asset. On the span north of the pole, there are 3 splices on the phase nearest the roadand 1 splice on the phasenearest the field. Span does not cross over a major roadway. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103975841 | SANTA ROSA HH2205 POLES | Sonoma(N) | 2021-05-19 | 2021-07-07 | 2021-12-23 | Vegetation: Tree causing strain or abrasion to secondary or service (only 1 service) | [Answer left blank] | Trees are is causing strain on service conductor. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
103975841 | SANTA ROSA HH2205 POLES | Sonoma(N) | 2021-05-19 | 2021-07-07 | 2021-12-23 | Vegetation: Branches are broken and can strike facilities and/or Tree is dead and can strike facilities | [Answer left blank] | Large tree has fallen on service conductor. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101247693 | MOTHER LODE N28 POLES | Stockton(N) | 2021-05-20 | 2021-07-09 | 2021-12-23 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Structure with non-exempt equipment (universal fuse cutouts and lightning arresters) has a stump within 10' of its base. | Agree | N/A | N¦A |  | Create "Other tag" | Yes | No | Yes | No
101247693 | MOTHER LODE N28 POLES | Stockton(N) | 2021-05-20 | 2021-07-09 | 2021-12-23 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101510766 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-20 | 2021-06-30 | 2021-12-23 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101510769 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-20 | 2021-06-30 | 2021-12-23 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks along the length of the pole. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Single phase dead end pole has steel arm & hardware. | N\A | N\A | N\A | N\A | N\A
101510769 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-20 | 2021-06-30 | 2021-12-23 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101510772 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-20 | 2021-06-30 | 2021-12-23 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks along the length of the pole, including at the top near where the hardware is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Single phase dead end corner pole has steel arms & hardware and down guys. | N\A | N\A | N\A | N\A | N\A
101510772 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-20 | 2021-06-30 | 2021-12-23 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101510773 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-20 | 2021-06-30 | 2021-12-23 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101510773 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-20 | 2021-06-30 | 2021-12-23 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103644586 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-20 | 2021-06-30 | 2021-12-23 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | The pole number appears to be visible on the pole. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103644587 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-20 | 2021-06-30 | 2021-12-23 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | There are cracks along the length of the pole, including at the top near where the hardware is attached. | There are cracks along the length of the pole, including at the top near where the hardware is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Single phase tangent pole has 9" brackets & hardware, down guy and anti-split bolt installed. | N\A | N\A | N\A | N\A | N\A
103644587 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-20 | 2021-06-30 | 2021-12-23 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103644587 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-20 | 2021-06-30 | 2021-12-23 | Non-Time-Dependent Issues: Visibility strips missing, broken, mismatched, or no longer reflective | [Answer left blank] | Visibility strips are no longer reflective, and one is missing. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101973653 | SANTA ROSA II2225 POLES | Sonoma(N) | 2021-05-21 | 2021-07-06 | 2021-12-23 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | There are cracks along the length of the pole, including at the top near where the hardware is attached. | There are several cracks at the top of the pole, including near where hardware is attached. | Agree | N/A | N¦A | Condition is already attached to an EC Notification (116862057). Inspector did update Notification but did not indicate condition on Structure section of Inspection Record. | N\A | N\A | N\A | N\A | N\A
101973653 | SANTA ROSA II2225 POLES | Sonoma(N) | 2021-05-21 | 2021-07-06 | 2021-12-23 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101973653 | SANTA ROSA II2225 POLES | Sonoma(N) | 2021-05-21 | 2021-07-06 | 2021-12-23 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | The pole number appears to be visible on the pole. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102002446 | SANTA ROSA HH2205 POLES | Sonoma(N) | 2021-05-21 | 2021-07-07 | 2021-12-23 | Conductor: Conductor has splices tied in proximity to insulator preventing free movement of splice with conductor | [Answer left blank] | Splice appears to be tied within 2' of the insulator. | Agree | N/A | N¦A | Condition is already attached to an EC Notification (119086281). Inspector did update Notification but did not indicate condition on Conductor section of Inspection Record. | N\A | N\A | N\A | N\A | N\A
102004800 | SANTA ROSA HH2301 POLES | Sonoma(N) | 2021-05-21 | 2021-07-07 | 2021-12-23 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | Open wire secondary is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102008227 | SANTA ROSA II2225 POLES | Sonoma(N) | 2021-05-21 | 2021-07-06 | 2021-12-23 | Anchor and Guys: Does or should this location have a Guy? | No | There is an overhead guy. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102008227 | SANTA ROSA II2225 POLES | Sonoma(N) | 2021-05-21 | 2021-07-06 | 2021-12-23 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Structure with non-exempt universal fuse cutouts has dried ground vegetation present within 10' of its base. | Agree | N/A | N¦A |  | Create "Other tag" | Yes | No | Yes | No
102008227 | SANTA ROSA II2225 POLES | Sonoma(N) | 2021-05-21 | 2021-07-06 | 2021-12-23 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | Pole step is at 7' 8" (92"). | Agree | N/A | N¦A | Condition was identified by inspector during FSR in 2020 inspection cycle. Gatekeeper has not yet added this FDA to EC Notification (119191880). Inspector did update Notification but did not indicate condition on Hardware section of Inspection Record on the 2021 inspection cycle. | N\A | N\A | N\A | N\A | N\A
102008227 | SANTA ROSA II2225 POLES | Sonoma(N) | 2021-05-21 | 2021-07-06 | 2021-12-23 | Open wire secondary is present. | [Answer left blank] | Open wire secondary is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102008227 | SANTA ROSA II2225 POLES | Sonoma(N) | 2021-05-21 | 2021-07-06 | 2021-12-23 | Other Required Data: Is there non-exempt equipment at the inspection location (Universal or Open Link Fuse) | [Answer left blank] | Non-Exempt universal fuse cutouts are present at this location. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102008227 | SANTA ROSA II2225 POLES | Sonoma(N) | 2021-05-21 | 2021-07-06 | 2021-12-23 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102008230 | SANTA ROSA II2225 POLES | Sonoma(N) | 2021-05-21 | 2021-07-06 | 2021-12-23 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks at the top of the pole, including near where hardware is attached | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Three phase tangent pole has king pin, 9" brackets & hardware and steel slackspan arm. | N\A | N\A | N\A | N\A | N\A
102008230 | SANTA ROSA II2225 POLES | Sonoma(N) | 2021-05-21 | 2021-07-06 | 2021-12-23 | Hardware and Framing: Secondary connectors (mini wedge and Insulink) installed on primary conductor | [Answer left blank] | There are Insulink connectors on the primary jumpers. | Agree | N/A | N¦A | Condition is already attached to an EC Notification (116863309). Inspector did not indicate condition on Hardware section of Inspection Record. | N\A | N\A | N\A | N\A | N\A
102008230 | SANTA ROSA II2225 POLES | Sonoma(N) | 2021-05-21 | 2021-07-06 | 2021-12-23 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101282436 | MOTHER LODE M3001 POLES | Stockton(N) | 2021-05-22 | 2021-07-07 | 2021-12-23 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Structure with non-exempt universal fuses has dried ground vegetation within 10' radius of its base. | Agree | N/A | N¦A |  | Create "Other tag" | Yes | No | Yes | No
101282437 | MOTHER LODE M3001 POLES | Stockton(N) | 2021-05-22 | 2021-07-07 | 2021-12-23 | Hardware and Framing: Molding missing, broken, damaged, or loose | [Answer left blank] | Molding is damaged at 8'8" (104"). | Agree | N/A | N¦A | Condition was identified by inspector during FSR in 2020 inspection cycle. Gatekeeper has not yet added this FDA to EC Notification (117229412). Inspector did update Notification but did not indicate condition on Hardware section of Inspection Record on the 2021 inspection cycle. | Update a EC | Yes | No | Yes | No
101282437 | MOTHER LODE M3001 POLES | Stockton(N) | 2021-05-22 | 2021-07-07 | 2021-12-23 | Hardware and Framing: Grounds exposed, broken, damaged, disconnected, unsecured, or missing (if required) | [Answer left blank] | Ground is exposed at 8'8" (104"). | Agree | N/A | N¦A | Condition is already attached to an EC Notification (117229412). Inspector did update Notification but did not indicate condition on Hardware section of Inspection Record. | N\A | N\A | N\A | N\A | N\A
101511752 | TEHEMA U2907 POLES | North Valley(N) | 2021-05-22 | 2021-06-29 | 2021-12-23 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | There are cracks along the length of the pole, including at the top near where the hardware is attached. | There are cracks along the length of the pole, including at the top near where the hardware is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Three phase tangent pole has king pin, 9" brackets & hardware and steel slack span arm. | N\A | N\A | N\A | N\A | N\A
101511752 | TEHEMA U2907 POLES | North Valley(N) | 2021-05-22 | 2021-06-29 | 2021-12-23 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101511753 | TEHEMA U2907 POLES | North Valley(N) | 2021-05-22 | 2021-06-29 | 2021-12-27 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | There are cracks along the length of the pole, including at the top near where the hardware is attached. | There are cracks along the length of the pole, including near where hardware is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Three phase tangent pole has king pin, 9" brackets & hardware. | N\A | N\A | N\A | N\A | N\A
101511753 | TEHEMA U2907 POLES | North Valley(N) | 2021-05-22 | 2021-06-29 | 2021-12-27 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | High voltage sign on one side of the pole is loose. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101511756 | TEHEMA U2907 POLES | North Valley(N) | 2021-05-22 | 2021-06-29 | 2021-12-27 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101511758 | TEHEMA U2907 POLES | North Valley(N) | 2021-05-22 | 2021-06-29 | 2021-12-27 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There is a crack at the top of the pole near where a bolt is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Single phase double dead-end pole has steel arm & hardware and anti-split bolt installed. | N\A | N\A | N\A | N\A | N\A
101511758 | TEHEMA U2907 POLES | North Valley(N) | 2021-05-22 | 2021-06-29 | 2021-12-27 | Hardware and Framing: Crossarm integrity compromised by any of the following; damaged, broken, burnt, decayed, rotten, loose, missing hardware or showing severe signs of bent bolts or brackets, damaged bracing, gun shots, insect damage or woodpecker damage, splitting, or fails to meet clearance requirements | [Answer left blank] | Crossarm hardware appears to be loose. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101511759 | TEHEMA U2907 POLES | North Valley(N) | 2021-05-22 | 2021-06-29 | 2021-12-27 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks along the length of the pole, including near where hardware is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Secondary pole has clevis & hardware installed. | N\A | N\A | N\A | N\A | N\A
101511762 | TEHEMA U2907 POLES | North Valley(N) | 2021-05-22 | 2021-06-29 | 2021-12-27 | Other Required Data: Transformer is suspect ofhaving PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101511768 | TEHEMA U2907 POLES | North Valley(N) | 2021-05-22 | 2021-06-29 | 2021-12-27 | Non-Time-Dependent Issues: Visibility strips missing, broken, mismatched, or no longer reflective | [Answer left blank] | Visibility strips are no longer reflective, and one is missing. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101511786 | TEHEMA U2907 POLES | North Valley(N) | 2021-05-22 | 2021-06-29 | 2021-12-28 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks along the west side of the pole, including near where hardware is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Three phase tangent pole has king pin, 9" brackets & hardware. | N\A | N\A | N\A | N\A | N\A
101511786 | TEHEMA U2907 POLES | North Valley(N) | 2021-05-22 | 2021-06-29 | 2021-12-28 | Other Required Data: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101955896 | SANTA ROSA II2225 POLES | Sonoma(N) | 2021-05-22 | 2021-07-06 | 2021-12-28 | Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | Open wire secondary is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101955900 | SANTA ROSA II2225 POLES | Sonoma(N) | 2021-05-22 | 2021-07-06 | 2021-12-28 | Conductor: Conductor has splices tied in proximity to insulator preventing free movement of splice with conductor | [Answer left blank] | Splice appears to be tied within 2' of insulator. | Agree | N/A | N¦A | 116871186 | Update a EC | Yes | No | Yes | No
101955900 | SANTA ROSA II2225 POLES | Sonoma(N) | 2021-05-22 | 2021-07-06 | 2021-12-28 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Structure with non-exempt split bolt connectors on primary jumpers has dried vegetation within 10' of its base. | Agree | N/A | N¦A |  | Create "Other tag" | Yes | No | Yes | No
101955900 | SANTA ROSA II2225 POLES | Sonoma(N) | 2021-05-22 | 2021-07-06 | 2021-12-28 | Other Required Data: Is there non-exempt equipment at the inspection location (Hot tap clamp or Split Bolt connector) | [Answer left blank] | There are non-exempt split bolt connectors on both primary jumpers. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101955900 | SANTA ROSA II2225 POLES | Sonoma(N) | 2021-05-22 | 2021-07-06 | 2021-12-28 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | High voltage sign on one side of the pole is missing. | Disagree | Condition is not compelling | 1. High Voltage Sign Not Installed as Required - TD-2305M-JA02, Rev. 8 - Pg. 61 | The one high sign in good condition on the opposite side of the pole satisfies the standard found in OH: Marking, Rev. #18: 11/01/18 022168 Page 3 of 35. Marking, Numbering, and Identification of Line Structures 3. Routine Inspection A. The requirement in 1, “Poles That Support Line Conductors,” must be satisfied with the following exceptions: 1. Sign the Pole: It is acceptable to have only one sign, or stacked pairs of signs, below the lowest line conductor energized above 750 V, except as noted in 4 “Special Locations.” B. The requirements in 2, Poles That Do Not Support Line Conductors,” must be satisfied with the following exceptions: 1. Risers: It is acceptable to have only one sign, or stacked pairs of signs, below risers energized above 750 V. 4. Special Locations: If the pole is signed, high-voltage signs are required on both sides of the pole in the following locations: Near water areas suitable for sailboats. Near established boat ramps and associated rigging areas. Adjacent to swimming pools. In agricultural areas with movable irrigation piping. Locations, where in the judgement of the employee, high-voltage signs should be visible from all sides of the poles. | N\A | N\A | N\A | N\A | N\A
101955900 | SANTA ROSA II2225 POLES | Sonoma(N) | 2021-05-22 | 2021-07-06 | 2021-12-28 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101955900 | SANTA ROSA II2225 POLES | Sonoma(N) | 2021-05-22 | 2021-07-06 | 2021-12-28 | Other Required Data: 3 or more splices present in one phase of the span | [Answer left blank] | There are 2 phases on this asset. On the span heading east, there are 4 splices on the phase closest to the field and 2 splices on the phase closest to the road. Span does not cross over a major roadway. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101511773 | TEHEMA U2907 POLES | North Valley(N) | 2021-05-24 | 2021-06-29 | 2021-12-28 | Other Required Data: Transformer is suspect ofhaving PCB" (guidance: look for blue sticker or indicator for no PCB) | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101511997 | TEHEMA MAP U2908 POLES | North Valley(N) | 2021-05-24 | 2021-06-29 | 2021-12-28 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks along the north side of the pole and at the top of the pole, including near where hardware is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Single phase dead-end pole has steel arm, & hardware, transformer and dow guy. | N\A | N\A | N\A | N\A | N\A
101465467 | SHASTA R2802 POLES | North Valley(N) | 2021-05-25 | 2021-07-01 | 2021-12-28 | Hardware and Framing: Crossarm integrity compromised by any of the following; damaged, broken, burnt, decayed, rotten, loose, missing hardware or showing severe signs of bent bolts or brackets, damaged bracing, gun shots, insect damage or woodpecker damage, splitting, or fails to meet clearance requirements | [Answer left blank] | The hardware on the crossarm appears to be loose. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101465467 | SHASTA R2802 POLES | North Valley(N) | 2021-05-25 | 2021-07-01 | 2021-12-28 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101465475 | SHASTA R2802 POLES | North Valley(N) | 2021-05-25 | 2021-07-01 | 2021-12-28 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101465475 | SHASTA R2802 POLES | North Valley(N) | 2021-05-25 | 2021-07-01 | 2021-12-28 | Other Required Data: Transformer is suspect ofhaving PCB" (guidance: look for blue sticker or indicator for no PCB) | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101465475 | SHASTA R2802 POLES | North Valley(N) | 2021-05-25 | 2021-07-01 | 2021-12-28 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101465514 | SHASTA R2802 POLES | North Valley(N) | 2021-05-25 | 2021-07-01 | 2021-12-28 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There is a crack at the top of the pole near where hardware is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Secondary pole has back to back secondary extension brackets with part 6 spool & clevis and anti-split bolt installed at pole top. | N\A | N\A | N\A | N\A | N\A
101465515 | SHASTA R2802 POLES | North Valley(N) | 2021-05-25 | 2021-07-01 | 2021-12-28 | Other Required Data: Transformer is suspect ofhaving PCB" (guidance: look for blue sticker or indicator for no PCB) | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101465515 | SHASTA R2802 POLES | North Valley(N) | 2021-05-25 | 2021-07-01 | 2021-12-28 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101510944 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-25 | 2021-06-30 | 2021-12-28 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101510945 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-25 | 2021-06-30 | 2021-12-28 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks along the length of the pole, including at the top near where hardware is attached. | Agree | N/A | N¦A | 121395169 | Update a EC | Yes | No | Yes | No
101510945 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-25 | 2021-06-30 | 2021-12-28 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101510945 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-25 | 2021-06-30 | 2021-12-28 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | The high voltage sign appears to be loose. | Agree | N/A | N¦A | 121395169 | Update a EC | Yes | No | Yes | No
101510946 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-25 | 2021-06-30 | 2021-12-29 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There is a crack in the middle section of the pole and a woodpecker hole that appears to be 4" in diameter near the top of the pole. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101510946 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-25 | 2021-06-30 | 2021-12-29 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101510948 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-25 | 2021-06-30 | 2021-12-29 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101511968 | TEHEMA MAP U2908 POLES | North Valley(N) | 2021-05-25 | 2021-06-29 | 2021-12-29 | Other Required Data: Transformer is suspect ofhaving PCB" (guidance: look for blue sticker or indicator for no PCB) | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101511972 | TEHEMA MAP U2908 POLES | North Valley(N) | 2021-05-25 | 2021-06-29 | 2021-12-29 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks at the top of the pole, including near where hardware is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Three phase tangent pole has king pin, 9" brackets & hardware. | N\A | N\A | N\A | N\A | N\A
101511972 | TEHEMA MAP U2908 POLES | North Valley(N) | 2021-05-25 | 2021-06-29 | 2021-12-29 | Other Required Data: Transformer is suspect ofhaving PCB" (guidance: look for blue sticker or indicator for no PCB) | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101511973 | TEHEMA MAP U2908 POLES | North Valley(N) | 2021-05-25 | 2021-06-29 | 2021-12-29 | Conductor: Select if there are risks, hazards or other maintenance conditions not previously captured in the checklist for this conductor | [Answer left blank] | The lashing on the secondary conductor appears to be broken or loose in multiple places. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101511975 | TEHEMA MAP U2908 POLES | North Valley(N) | 2021-05-25 | 2021-06-29 | 2021-12-29 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks at the top of the pole, including where a bolt is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Three phase tangent pole has king pin, composite arm & hardware. | N\A | N\A | N\A | N\A | N\A
101511975 | TEHEMA MAP U2908 POLES | North Valley(N) | 2021-05-25 | 2021-06-29 | 2021-12-29 | Anchor and Guys: Does or should this location have a Guy? | No | There appears to be guy running north across the road. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101511978 | TEHEMA MAP U2908 POLES | North Valley(N) | 2021-05-25 | 2021-06-29 | 2021-12-29 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks along the length of the pole, including near where hardware is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Three phase tangent pole has king pin, 9" brackets & hardware. | N\A | N\A | N\A | N\A | N\A
101511978 | TEHEMA MAP U2908 POLES | North Valley(N) | 2021-05-25 | 2021-06-29 | 2021-12-29 | Other Required Data: Transformer is suspect ofhaving PCB" (guidance: look for blue sticker or indicator for no PCB) | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101511981 | TEHEMA MAP U2908 POLES | North Valley(N) | 2021-05-25 | 2021-06-29 | 2021-12-29 | Non-Time-Dependent Issues: Visibility strips missing, broken, mismatched, or no longer reflective | [Answer left blank] | Visibility strips are no longer reflective, and one is missing. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101511981 | TEHEMA MAP U2908 POLES | North Valley(N) | 2021-05-25 | 2021-06-29 | 2021-12-29 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101512100 | TEHEMA MAP U2909 POLES | North Valley(N) | 2021-05-25 | 2021-06-29 | 2021-12-29 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks along the length of the pole, including near where hardware is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Single phase dead end cormer pole has steel arms & hardware. | N\A | N\A | N\A | N\A | N\A
101545806 | TEHEMA MAP U2908 POLES | North Valley(N) | 2021-05-25 | 2021-06-29 | 2021-12-29 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks along the length of the pole, including near where hardware is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Secondary pole has back to back figure 4 and secondary extension bracket with part 6 spool & clevis installed at pole top. | N\A | N\A | N\A | N\A | N\A
103984208 | SHASTA R2802 POLES | North Valley(N) | 2021-05-25 | 2021-07-01 | 2021-12-29 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | Pole number is visible on pole. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101465497 | SHASTA R2802 POLES | North Valley(N) | 2021-05-26 | 2021-07-01 | 2021-12-29 | Anchor and Guys: Guy wire broken, damaged, clearance issues, corroded, covered by vegetation, overgrown, strain or abrasion | [Answer left blank] | Vegetationhas overgrown the base of the guy. | Agree | N/A | N¦A | 121400703 | Update a EC | Yes | No | Yes | No
101465503 | SHASTA R2802 POLES | North Valley(N) | 2021-05-26 | 2021-07-01 | 2021-12-29 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101465505 | SHASTA R2802 POLES | North Valley(N) | 2021-05-26 | 2021-07-01 | 2021-12-29 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101465506 | SHASTA R2802 POLES | North Valley(N) | 2021-05-26 | 2021-07-01 | 2021-12-29 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101465506 | SHASTA R2802 POLES | North Valley(N) | 2021-05-26 | 2021-07-01 | 2021-12-29 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101471226 | SHASTA MAP O3220 POLES | North Valley(N) | 2021-05-26 | 2021-06-29 | 2021-12-29 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks at the top of the pole near where a hardware is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Single phase tangent pole has composite arm & hardware and anti-split bolt installed. | N\A | N\A | N\A | N\A | N\A
101471226 | SHASTA MAP O3220 POLES | North Valley(N) | 2021-05-26 | 2021-06-29 | 2021-12-29 | Hardware and Framing: Animal mitigation broken, damaged, or missing (if required) | [Answer left blank] | Animal mitigation is loose. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101471226 | SHASTA MAP O3220 POLES | North Valley(N) | 2021-05-26 | 2021-06-29 | 2021-12-29 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101471228 | SHASTA MAP O3220 POLES | North Valley(N) | 2021-05-26 | 2021-06-29 | 2021-12-29 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks at the top of the pole near where a hardware is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Three phase line & buck pole has king pin, 9" brackets & hardware and double wood buck arms. | N\A | N\A | N\A | N\A | N\A
101471228 | SHASTA MAP O3220 POLES | North Valley(N) | 2021-05-26 | 2021-06-29 | 2021-12-29 | Hardware and Framing: Insulators or King Pin chipped, cracked, corroded, contaminated, flashed, have signs of tracking, broken or damaged | [Answer left blank] | King pin hardware appears to be loose. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101471228 | SHASTA MAP O3220 POLES | North Valley(N) | 2021-05-26 | 2021-06-29 | 2021-12-29 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101471229 | SHASTA MAP O3220 POLES | North Valley(N) | 2021-05-26 | 2021-06-29 | 2021-12-29 | Conductor: Primary, secondary, and/or service conductors broken, damaged, burnt, corroded, loose, frayed or bird caging | [Answer left blank] | Primary conductor appears to be damaged/bird caging. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101471229 | SHASTA MAP O3220 POLES | North Valley(N) | 2021-05-26 | 2021-06-29 | 2021-12-29 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101471231 | SHASTA MAP O3220 POLES | North Valley(N) | 2021-05-26 | 2021-06-29 | 2021-12-29 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | High voltage sign on one side of the pole is broken. | Agree | N/A | N¦A | 116971152 | Update a EC | Yes | No | Yes | No
101471242 | SHASTA MAP O3220 POLES | North Valley(N) | 2021-05-26 | 2021-06-29 | 2021-12-29 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101471244 | SHASTA MAP O3220 POLES | North Valley(N) | 2021-05-26 | 2021-06-29 | 2021-12-29 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks at the top of the pole near cross arm hardware. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Single phase dead end slack-span pole with steel crossarm & hardware. | N\A | N\A | N\A | N\A | N\A
101471244 | SHASTA MAP O3220 POLES | North Valley(N) | 2021-05-26 | 2021-06-29 | 2021-12-29 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101471244 | SHASTA MAP O3220 POLES | North Valley(N) | 2021-05-26 | 2021-06-29 | 2021-12-29 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101471253 | SHASTA MAP O3220 POLES | North Valley(N) | 2021-05-26 | 2021-06-29 | 2021-12-29 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks on the top of the pole near where hardware is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Three phase tangent pole has king pin, 9" brackets & hardware with single phase with steel crossarm & hardware. | N\A | N\A | N\A | N\A | N\A
101471253 | SHASTA MAP O3220 POLES | North Valley(N) | 2021-05-26 | 2021-06-29 | 2021-12-29 | Conductor: Conductor has splices tied in proximity to insulator preventing free movement of splice with conductor | [Answer left blank] | Splice appears to be tied within 2' of insulator. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101471253 | SHASTA MAP O3220 POLES | North Valley(N) | 2021-05-26 | 2021-06-29 | 2021-12-29 | Hardware and Framing: Animal mitigation broken, damaged, or missing (if required) | [Answer left blank] | Animal mitigation is loose. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101471253 | SHASTA MAP O3220 POLES | North Valley(N) | 2021-05-26 | 2021-06-29 | 2021-12-29 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101471255 | SHASTA MAP O3220 POLES | North Valley(N) | 2021-05-26 | 2021-06-29 | 2021-12-29 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There is damage near the bottom of the pole. | Agree | N/A | N¦A | Condition is already attached to an EC Notification (116973045). Inspector did updste complete FSR to update Notification but did not indicate condition on Structure section of Inspection Record. | N\A | N\A | N\A | N\A | N\A
101471255 | SHASTA MAP O3220 POLES | North Valley(N) | 2021-05-26 | 2021-06-29 | 2021-12-29 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101471256 | SHASTA MAP O3220 POLES | North Valley(N) | 2021-05-26 | 2021-06-29 | 2021-12-29 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101471256 | SHASTA MAP O3220 POLES | North Valley(N) | 2021-05-26 | 2021-06-29 | 2021-12-29 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101471330 | SHASTA MAP O3220 POLES | North Valley(N) | 2021-05-26 | 2021-06-29 | 2021-12-29 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks at the top of the pole near where hardware is attached. | Agree | N/A | N¦A | Pole appears to have woodpecker damage in addition to the cracks at phone level cracks. | Create a EC | Yes | No | Yes | No
101471330 | SHASTA MAP O3220 POLES | North Valley(N) | 2021-05-26 | 2021-06-29 | 2021-12-29 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101471330 | SHASTA MAP O3220 POLES | North Valley(N) | 2021-05-26 | 2021-06-29 | 2021-12-29 | Other Required Data: Transformer is suspect ofhaving PCB" (guidance: look for blue sticker or indicator for no PCB) | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101471331 | SHASTA MAP O3220 POLES | North Valley(N) | 2021-05-26 | 2021-06-29 | 2021-12-29 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101471333 | SHASTA MAP O3220 POLES | North Valley(N) | 2021-05-26 | 2021-06-29 | 2021-12-29 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101510956 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-25 | 2021-06-30 | 2021-12-29 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101510956 | TEHEMA MAP V31 POLES | North Valley(N) | 2021-05-25 | 2021-06-30 | 2021-12-29 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | The high voltage sign appears to be partially missing on one side of the pole. | Agree | N/A | N¦A | Condition is already attached to an EC Notification (117297187). Inspector did complete FSR to update Notification but did not indicate condition on Non-Time Dependent section of Inspection Record. | N\A | N\A | N\A | N\A | N\A
103567676 | SHASTA MAP O3220 POLES | North Valley(N) | 2021-05-26 | 2021-06-29 | 2021-12-29 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103567678 | SHASTA MAP O3220 POLES | North Valley(N) | 2021-05-26 | 2021-06-29 | 2021-12-29 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
104000356 | SHASTA MAP O3220 POLES | North Valley(N) | 2021-05-26 | 2021-06-29 | 2021-12-29 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101471712 | SHASTA MAP O3215 POLES | North Valley(N) | 2021-05-27 | 2021-06-29 | 2021-12-29 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | rotten or decay [Answer left blank]There are cracks at the top of the pole where cross arm bolt is attached. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101471712 | SHASTA MAP O3215 POLES | North Valley(N) | 2021-05-27 | 2021-06-29 | 2021-12-29 | Conductor: Conductor has splices tied in proximity to insulator preventing free movement of splice with conductor | [Answer left blank] | Splice appears to be tied within 2' of insulator. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101471712 | SHASTA MAP O3215 POLES | North Valley(N) | 2021-05-27 | 2021-06-29 | 2021-12-29 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101471722 | SHASTA MAP O3215 POLES | North Valley(N) | 2021-05-27 | 2021-06-29 | 2021-12-29 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks at the top of the pole near where hardware is attached | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Single phase tangent pole has 9" brackets & hardware and anti-split bolt installed. | N\A | N\A | N\A | N\A | N\A
101471722 | SHASTA MAP O3215 POLES | North Valley(N) | 2021-05-27 | 2021-06-29 | 2021-12-29 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101471722 | SHASTA MAP O3215 POLES | North Valley(N) | 2021-05-27 | 2021-06-29 | 2021-12-29 | Non-Time-Dependent Issues: Visibility strips missing, broken, mismatched, or no longer reflective | [Answer left blank] | A visibility strip is missing. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101471722 | SHASTA MAP O3215 POLES | North Valley(N) | 2021-05-27 | 2021-06-29 | 2021-12-29 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101471733 | SHASTA MAP O3215 POLES | North Valley(N) | 2021-05-27 | 2021-06-29 | 2021-12-29 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks at the top of the pole near where hardware is attached | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Single phase tangent pole has 9" brackets & hardware and anti-split bolt installed. | N\A | N\A | N\A | N\A | N\A
101471733 | SHASTA MAP O3215 POLES | North Valley(N) | 2021-05-27 | 2021-06-29 | 2021-12-29 | Hardware and Framing: Molding missing, broken, damaged, or loose | [Answer left blank] | Molding has come loose from the pole at the ground level. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101471733 | SHASTA MAP O3215 POLES | North Valley(N) | 2021-05-27 | 2021-06-29 | 2021-12-29 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101471733 | SHASTA MAP O3215 POLES | North Valley(N) | 2021-05-27 | 2021-06-29 | 2021-12-29 | Non-Time-Dependent Issues: Pole steps are less than 8' 6" above the ground or any other accessible surface | [Answer left blank] | Pole step is at 8' 1" (97"). | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101471733 | SHASTA MAP O3215 POLES | North Valley(N) | 2021-05-27 | 2021-06-29 | 2021-12-29 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | High voltage sign on one side of the pole is loose. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101471735 | SHASTA MAP O3215 POLES | North Valley(N) | 2021-05-27 | 2021-06-29 | 2021-12-30 | Common Equipment/Other Equipment: Transformer shows signs of leaking, seeping, or weeping oil | [Answer left blank] | Transformer appears to show signs of seeping oil, as oil stains are present. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101471735 | SHASTA MAP O3215 POLES | North Valley(N) | 2021-05-27 | 2021-06-29 | 2021-12-30 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101471735 | SHASTA MAP O3215 POLES | North Valley(N) | 2021-05-27 | 2021-06-29 | 2021-12-30 | Other Required Data: Transformer is suspect ofhaving PCB" (guidance: look for blue sticker or indicator for no PCB) | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101471735 | SHASTA MAP O3215 POLES | North Valley(N) | 2021-05-27 | 2021-06-29 | 2021-12-30 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | High voltage sign is missing on one side of the pole. | Disagree | Condition is not compelling | 1. High Voltage Sign Not Installed as Required - TD-2305M-JA02, Rev. 8 - Pg. 61 | The one high sign in good condition on the opposite side of the pole satisfies the standard found in OH: Marking, Rev. #18: 11/01/18 022168 Page 3 of 35. Marking, Numbering, and Identification of Line Structures 3. Routine Inspection A. The requirement in 1, “Poles That Support Line Conductors,” must be satisfied with the following exceptions: 1. Sign the Pole: It is acceptable to have only one sign, or stacked pairs of signs, below the lowest line conductor energized above 750 V, except as noted in 4 “Special Locations.” B. The requirements in 2, Poles That Do Not Support Line Conductors,” must be satisfied with the following exceptions: 1. Risers: It is acceptable to have only one sign, or stacked pairs of signs, below risers energized above 750 V. 4. Special Locations: If the pole is signed, high-voltage signs are required on both sides of the pole in the following locations: Near water areas suitable for sailboats. Near established boat ramps and associated rigging areas. Adjacent to swimming pools. In agricultural areas with movable irrigation piping. Locations, where in the judgement of the employee, high-voltage signs should be visible from all sides of the poles. | N\A | N\A | N\A | N\A | N\A
101471735 | SHASTA MAP O3215 POLES | North Valley(N) | 2021-05-27 | 2021-06-29 | 2021-12-30 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101471741 | SHASTA MAP O3215 POLES | North Valley(N) | 2021-05-27 | 2021-06-29 | 2021-12-30 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks at the top of the pole near where hardware is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Single phase dead end pole with slackspan has steel arms & hardware and anti-split bolt installed. | N\A | N\A | N\A | N\A | N\A
101471741 | SHASTA MAP O3215 POLES | North Valley(N) | 2021-05-27 | 2021-06-29 | 2021-12-30 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101471741 | SHASTA MAP O3215 POLES | North Valley(N) | 2021-05-27 | 2021-06-29 | 2021-12-30 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101471743 | SHASTA MAP O3215 POLES | North Valley(N) | 2021-05-27 | 2021-06-29 | 2021-12-30 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks at the top of the pole near where hardware is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Single phase dead end pole with slackspan has steel arm & hardware and anti-split bolt installed. | N\A | N\A | N\A | N\A | N\A
101471743 | SHASTA MAP O3215 POLES | North Valley(N) | 2021-05-27 | 2021-06-29 | 2021-12-30 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101471743 | SHASTA MAP O3215 POLES | North Valley(N) | 2021-05-27 | 2021-06-29 | 2021-12-30 | Other Required Data: Transformer is suspect ofhaving PCB" (guidance: look for blue sticker or indicator for no PCB) | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101471744 | SHASTA MAP O3215 POLES | North Valley(N) | 2021-05-27 | 2021-06-29 | 2021-12-30 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks at the top of the pole near where hardware is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Single phase tangent pole with 9" brackets & hardware and anti-split bolt installed. | N\A | N\A | N\A | N\A | N\A
101471744 | SHASTA MAP O3215 POLES | North Valley(N) | 2021-05-27 | 2021-06-29 | 2021-12-30 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101471746 | SHASTA MAP O3215 POLES | North Valley(N) | 2021-05-27 | 2021-06-29 | 2021-12-30 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101471746 | SHASTA MAP O3215 POLES | North Valley(N) | 2021-05-27 | 2021-06-29 | 2021-12-30 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | High voltage sign is broken on one side of the pole. | Disagree | Condition is not compelling | 1. High Voltage Sign Not Installed as Required - TD-2305M-JA02, Rev. 8 - Pg. 61 | The one high sign in good condition on the opposite side of the pole satisfies the standard found in OH: Marking, Rev. #18: 11/01/18 022168 Page 3 of 35. Marking, Numbering, and Identification of Line Structures 3. Routine Inspection A. The requirement in 1, “Poles That Support Line Conductors,” must be satisfied with the following exceptions: 1. Sign the Pole: It is acceptable to have only one sign, or stacked pairs of signs, below the lowest line conductor energized above 750 V, except as noted in 4 “Special Locations.” B. The requirements in 2, Poles That Do Not Support Line Conductors,” must be satisfied with the following exceptions: 1. Risers: It is acceptable to have only one sign, or stacked pairs of signs, below risers energized above 750 V. 4. Special Locations: If the pole is signed, high-voltage signs are required on both sides of the pole in the following locations: Near water areas suitable for sailboats. Near established boat ramps and associated rigging areas. Adjacent to swimming pools. In agricultural areas with movable irrigation piping. Locations, where in the judgement of the employee, high-voltage signs should be visible from all sides of the poles. | N\A | N\A | N\A | N\A | N\A
101471749 | SHASTA MAP O3215 POLES | North Valley(N) | 2021-05-27 | 2021-06-29 | 2021-12-30 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks at the top of the pole near where hardware is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Single phase dead end pole with steel & hardware and anti-split bolt installed. | N\A | N\A | N\A | N\A | N\A
101471749 | SHASTA MAP O3215 POLES | North Valley(N) | 2021-05-27 | 2021-06-29 | 2021-12-30 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101471749 | SHASTA MAP O3215 POLES | North Valley(N) | 2021-05-27 | 2021-06-29 | 2021-12-30 | Other Required Data: Transformer is suspect ofhaving PCB" (guidance: look for blue sticker or indicator for no PCB) | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101471750 | SHASTA MAP O3215 POLES | North Valley(N) | 2021-05-27 | 2021-06-29 | 2021-12-30 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101471754 | SHASTA MAP O3215 POLES | North Valley(N) | 2021-05-27 | 2021-06-29 | 2021-12-30 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks at the top of the pole near where hardware is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Single phase tangent pole with 9" brackets & hardware and anti-split bolt installed and slackspan with steel arn & hardware. | N\A | N\A | N\A | N\A | N\A
101471754 | SHASTA MAP O3215 POLES | North Valley(N) | 2021-05-27 | 2021-06-29 | 2021-12-30 | Structure: Pole leaning or out of plumb by more than 10% of its height above the ground | [Answer left blank] | Pole appears to be leaning by more than 10% of its height above the ground. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101471754 | SHASTA MAP O3215 POLES | North Valley(N) | 2021-05-27 | 2021-06-29 | 2021-12-30 | Hardware and Framing: Select if there are risks, hazards or other maintenance conditions not previously captured in the checklist for Hardware Framing at this location | [Answer left blank] | Primary stand-off bracket on the top phase appears to be loose. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101471754 | SHASTA MAP O3215 POLES | North Valley(N) | 2021-05-27 | 2021-06-29 | 2021-12-30 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103571360 | TEHEMA U2906 POLES | North Valley(N) | 2021-05-27 | 2021-06-29 | 2021-12-30 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are deep cracks in the bottom half of the east side of the pole, including one that is approximately 4”. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Single phase dead end corner pole with composite arms & hardware and anti-split bolt installed. | N\A | N\A | N\A | N\A | N\A
101512106 | TEHEMA MAP U2909 POLES | North Valley(N) | 2021-05-28 | 2021-06-29 | 2021-12-30 | Anchor and Guys: Necessary guys missing or loose | [Answer left blank] | Guy wire at communications level is loose. | Agree | N/A | N¦A | Third Party Utility Notification needs to be created. | Create "Other tag" | Yes | No | Yes | No
100955625 | MISSION I1112 POLES | Mission(C) | 2021-06-02 | 2021-07-15 | 2021-12-30 | Anchor and Guys: Guy wire broken, damaged, clearance issues, corroded, covered by vegetation, overgrown, strain or abrasion | [Answer left blank] | Large tree limbs appear to be causing strain on the down guy; additionally, vegetation appears to be in contact with guy wire above insulator. | Agree | N/A | N¦A | Condition is already attached to an EC Notification (119024563). Inspector did complete FSR to update Notification but did not indicate condition on Anchor and Guys section of Inspection Record. | N\A | N\A | N\A | N\A | N\A
103780867 | MISSION L15 POLES | Mission(C) | 2021-06-02 | 2021-07-13 | 2021-12-30 | Vegetation: Support Structure with non-exempt equipment, has dried vegetation from ground to 8' above ground, within 10' radius of Support Structure base | [Answer left blank] | There are non-exempt universal fuses on the structure, with dried vegetation within a 10' radius of the pole from the base of the pole to 8' above ground level. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100909355 | MISSION I1112 POLES | Mission(C) | 2021-06-03 | 2021-07-15 | 2021-12-30 | Non-Time-Dependent Issues: Pole steps are less than 8' 6" above the ground or any other accessible surface | [Answer left blank] | Pole step is at 7' 9" (93"). | Agree | N/A | N¦A | Condition is already attached to an EC Notification (119026356). Inspector did complete FSR to update Notification but did not indicate condition on Anchor and Guys section of Inspection Record. | N\A | N\A | N\A | N\A | N\A
101890560 | PASO ROBLES JJ38 POLES | Los Padres(S) | 2021-06-03 | 2021-07-14 | 2021-12-30 | Other Required Data: Transformer is suspect ofhaving PCB" (guidance: look for blue sticker or indicator for no PCB) | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101945995 | PASO ROBLES JJ38 POLES | Los Padres(S) | 2021-06-03 | 2021-07-14 | 2021-12-30 | Other Required Data: Transformer is suspect ofhaving PCB" (guidance: look for blue sticker or indicator for no PCB) | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101945995 | PASO ROBLES JJ38 POLES | Los Padres(S) | 2021-06-03 | 2021-07-14 | 2021-12-30 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103042581 | MISSION I1112 POLES | Mission(C) | 2021-06-03 | 2021-07-15 | 2021-12-30 | Anchor and Guys: Necessary guys missing or loose | [Answer left blank] | Overhead guy supporting dead end and secondary on adjacent asset appears loose. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
103042581 | MISSION I1112 POLES | Mission(C) | 2021-06-03 | 2021-07-15 | 2021-12-30 | Other Required Data: 3 or more splices present in one phase of the span | [Answer left blank] | There are 3 phases on the asset. On the span north of the pole, there are 3 splices on the center phase. Span does not cross over a major roadway. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103042600 | MISSION I1112 POLES | Mission(C) | 2021-06-03 | 2021-07-15 | 2021-12-30 | Conductor: Conductor has splices tied in proximity to insulator preventing free movement of splice with conductor | [Answer left blank] | A splice appears to be tied within 2' of insulators. | Disagree | Condition is not compelling | ELEC-1000 Training | Splice is within 2' of dead end shoe therefore does not need room to allow free monement of splice with conductor. | N\A | N\A | N\A | N\A | N\A
100909364 | MISSION I1112 POLES | Mission(C) | 2021-06-04 | 2021-07-15 | 2021-12-30 | Anchor and Guys: Necessary guys missing or loose | [Answer left blank] | The span guy appears loose. | Agree | N/A | N¦A | Condition is already attached to an EC Notification (111650778). Inspector did complete FSR to update Notification but did not indicate condition on Anchor and Guys section of Inspection Record. | N\A | N\A | N\A | N\A | N\A
101890536 | PASO ROBLES JJ38 POLES | Los Padres(S) | 2021-06-04 | 2021-07-14 | 2021-12-30 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | Pole number is visible on pole. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101890536 | PASO ROBLES JJ38 POLES | Los Padres(S) | 2021-06-04 | 2021-07-14 | 2021-12-30 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102259143 | NORTH BAY MAP SS3012 POLES | North Bay(C) | 2021-06-04 | 2021-07-21 | 2021-12-30 | Hardware and Framing: Molding missing, broken, damaged, or loose | [Answer left blank] | Molding is broken at the base of the pole. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
102259143 | NORTH BAY MAP SS3012 POLES | North Bay(C) | 2021-06-04 | 2021-07-21 | 2021-12-30 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | Open wire secondary is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102259149 | NORTH BAY MAP SS3012 POLES | North Bay(C) | 2021-06-04 | 2021-07-21 | 2021-12-30 | Hardware and Framing: Is Hardware Framing present on this structure? | No | Yes, hardware framing is present at the top of the pole. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102259161 | NORTH BAY MAP SS3012 POLES | North Bay(C) | 2021-06-04 | 2021-07-21 | 2021-12-30 | Vegetation: Tree causing strain or abrasion to secondary or service (only 1 service) | [Answer left blank] | Vegetation appears to be causing strain on the secondary conductor. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
102259314 | NORTH BAY MAP SS3012 POLES | North Bay(C) | 2021-06-04 | 2021-07-21 | 2021-12-30 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | Open wire secondary is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100909334 | MISSION I1111 POLES | Mission(C) | 2021-06-04 | 2021-07-21 | 2021-12-30 | Anchor and Guys: Does or should this location have a Guy? | No | There is an overhead guy on the asset. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | No
100909334 | MISSION I1111 POLES | Mission(C) | 2021-06-05 | 2021-07-15 | 2021-12-30 | Anchor and Guys: Necessary guys missing or loose | [Answer left blank] | The overhead guy appears to be loose. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | N\A
102259308 | NORTH BAY MAP SS3012 POLES | North Bay(C) | 2021-06-05 | 2021-07-21 | 2021-12-30 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Structure with non-exempt equipment (split bolt connector) has dried ground vegetation within 10' of its base. | Agree | N/A | N¦A |  | Create "Other tag" | Yes | No | Yes | No
102259308 | NORTH BAY MAP SS3012 POLES | North Bay(C) | 2021-06-05 | 2021-07-21 | 2021-12-30 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103413835 | PASO ROBLES JJ38 POLES | Los Padres(S) | 2021-06-05 | 2021-07-14 | 2021-12-30 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | Pole number is visible on pole. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102254206 | NORTH BAY MAP SS2809 POLES | North Bay(C) | 2021-06-06 | 2021-07-20 | 2021-12-30 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Structure with non-exempt universal fuse cutouts has dried ground vegetation within 10' radius of its base. | Agree | N/A | N¦A |  | Create "Other tag" | Yes | No | Yes | No
102254262 | NORTH BAY MAP SS2809 POLES | North Bay(C) | 2021-06-06 | 2021-07-20 | 2021-12-30 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | Open wire secondary is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102254262 | NORTH BAY MAP SS2809 POLES | North Bay(C) | 2021-06-06 | 2021-07-20 | 2021-12-30 | Other Required Data: 3 or more splices present in one phase of the span | [Answer left blank] | There are 2 phases on the asset. There are 11 splices on the span east of the asset, with 6 splices on the north phase and 5 splices on the south phase. Span does not cross over a major roadway. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100937212 | MISSION K1521 POLES | Mission(C) | 2021-06-07 | 2021-07-13 | 2022-01-03 | Vegetation: Support Structure with non-exempt equipment, has dried vegetation from ground to 8' above ground, within 10' radius of Support Structure base | [Answer left blank] | There are non-exempt fuse cutouts on the pole with dried vegetation within a 10' radius of the pole. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100937212 | MISSION K1521 POLES | Mission(C) | 2021-06-07 | 2021-07-13 | 2022-01-03 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102259296 | NORTH BAY MAP SS3012 POLES | North Bay(C) | 2021-06-07 | 2021-07-21 | 2022-01-03 | Anchor and Guys: Does or should this location have a Guy? | No | There appears to be a pole-to-pole guy present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102259174 | NORTH BAY MAP SS3012 POLES | North Bay(C) | 2021-06-08 | 2021-07-21 | 2022-01-03 | Anchor and Guys: Does or should this location have a Guy? | No | There appears to be a pole-to-pole guy present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102259174 | NORTH BAY MAP SS3012 POLES | North Bay(C) | 2021-06-08 | 2021-07-21 | 2022-01-03 | Hardware and Framing: Tap clamps installed incorrectly | [Answer left blank] | The tap clamps do not appear to be installed on tap guards. | Agree | N/A | N¦A | 117092649 | Update a EC | Yes | No | Yes | No
102259174 | NORTH BAY MAP SS3012 POLES | North Bay(C) | 2021-06-08 | 2021-07-21 | 2022-01-03 | Hardware and Framing: Crossarm integrity compromised by any of the following; damaged, broken, burnt, decayed, rotten, loose, missing hardware or showing severe signs of bent bolts or brackets, damaged bracing, gun shots, insect damage or woodpecker damage, splitting, or fails to meet clearance requirements | [Answer left blank] | The ends of the primary crossarm are cracked, near where hardware is attached. | Agree | N/A | N¦A | 117092649 | Update a EC | Yes | No | Yes | No
102259175 | NORTH BAY MAP SS3012 POLES | North Bay(C) | 2021-06-08 | 2021-07-21 | 2022-01-03 | Other Required Data: Is there non-exempt equipment at the inspection location (Hot tap clamp or Split Bolt connector) | Yes | There does not appear to be non-exempt equipment on this pole. Because the split bolt connectors appear idle, they are exempt. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103982991 | DIABLO E0605 POLES | Diablo(C) | 2021-06-10 | 2021-07-14 | 2022-01-03 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | Pole number is visible on pole. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102275407 | NORTH BAY MAP VV3209 POLES | North Bay(C) | 2021-06-11 | 2021-07-22 | 2022-01-03 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | Open wire secondary is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102275512 | NORTH BAY MAP VV3209 POLES | North Bay(C) | 2021-06-13 | 2021-07-22 | 2022-01-03 | Common Equipment/Other Equipment: IFD (aka "Turkey Popper") has activated on the transformer (orange band is visible) | [Answer left blank] | The turkey popper appears to have been activated. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
102275512 | NORTH BAY MAP VV3209 POLES | North Bay(C) | 2021-06-13 | 2021-07-22 | 2022-01-03 | Vegetation: Structure is overgrown with vegetation | [Answer left blank] | The middle third of the pole is overgrown with vegetation, preventing a full inspection. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
102275529 | NORTH BAY MAP VV3209 POLES | North Bay(C) | 2021-06-13 | 2021-07-22 | 2022-01-03 | Vegetation: Structure is overgrown with vegetation | [Answer left blank] | Bottom third of the pole is overgrown with vegetation, preventing full inspection. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
102275532 | NORTH BAY MAP VV3209 POLES | North Bay(C) | 2021-06-13 | 2021-07-22 | 2022-01-03 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Structure with non-exempt equipment (solid blade disconnects) has dried vegetation within 10' of its base. | Agree | N/A | N¦A |  | Create "Other tag" | Yes | No | Yes | No
102275540 | NORTH BAY MAP VV3209 POLES | North Bay(C) | 2021-06-13 | 2021-07-22 | 2022-01-03 | Vegetation: Structure is overgrown with vegetation | [Answer left blank] | Pole is overgrown by vegetation, preventing full inspection. | Agree | N/A | N¦A | 121528654 | Update a EC | Yes | No | Yes | No
102275540 | NORTH BAY MAP VV3209 POLES | North Bay(C) | 2021-06-13 | 2021-07-22 | 2022-01-03 | Vegetation: Tree causing strain or abrasion to secondary or service (2 or more services) | [Answer left blank] | Vegetation appears to be causing strain on the service line south of the pole. | Agree | N/A | N¦A | 121528654 | Update a EC | Yes | No | Yes | No
102275540 | NORTH BAY MAP VV3209 POLES | North Bay(C) | 2021-06-13 | 2021-07-22 | 2022-01-03 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102295822 | NORTH BAY MAP VV3209 POLES | North Bay(C) | 2021-06-13 | 2021-07-22 | 2022-01-03 | Conductor: Primary, secondary, and/or service conductors broken, damaged, burnt, corroded, loose, frayed or bird caging | [Answer left blank] | Conductor shows signs of bird caging near the splice. | Agree | N/A | N¦A | 119068175 | Update a EC | Yes | No | Yes | No
102295822 | NORTH BAY MAP VV3209 POLES | North Bay(C) | 2021-06-13 | 2021-07-22 | 2022-01-03 | Conductor: Conductor has splices tied in proximity to insulator preventing free movement of splice with conductor | [Answer left blank] | Splices on both phases on the span south of the pole (up the hill) appear to be within 2' of insulators. | Agree | N/A | N¦A | 119068175 | Update a EC | Yes | No | Yes | No
102295822 | NORTH BAY MAP VV3209 POLES | North Bay(C) | 2021-06-13 | 2021-07-22 | 2022-01-03 | Hardware and Framing: Tap clamps installed incorrectly | [Answer left blank] | The tap clamps appear to be installed on armor rods rather than tap guards. | Agree | N/A | N¦A | 119068175 | Update a EC | Yes | No | Yes | No
102295822 | NORTH BAY MAP VV3209 POLES | North Bay(C) | 2021-06-13 | 2021-07-22 | 2022-01-03 | Vegetation: Tree causing strain or abrasion to secondary or service (only 1 service) | [Answer left blank] | A tree limb appears to be straining the service conductor. | Agree | N/A | N¦A | 119068175 | Update a EC | Yes | No | Yes | No
102295822 | NORTH BAY MAP VV3209 POLES | North Bay(C) | 2021-06-13 | 2021-07-22 | 2022-01-03 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | Open wire secondary is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102295822 | NORTH BAY MAP VV3209 POLES | North Bay(C) | 2021-06-13 | 2021-07-22 | 2022-01-03 | Other Required Data: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101882533 | SAN LUIS OBISPO II29 POLES | Los Padres(S) | 2021-06-16 | 2021-07-13 | 2022-01-03 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101882534 | SAN LUIS OBISPO II29 POLES | Los Padres(S) | 2021-06-16 | 2021-07-13 | 2022-01-03 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101882535 | SAN LUIS OBISPO II29 POLES | Los Padres(S) | 2021-06-16 | 2021-07-13 | 2022-01-03 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101882535 | SAN LUIS OBISPO II29 POLES | Los Padres(S) | 2021-06-16 | 2021-07-13 | 2022-01-03 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101882537 | SAN LUIS OBISPO II29 POLES | Los Padres(S) | 2021-06-16 | 2021-07-13 | 2022-01-03 | Anchor and Guys: Guy wire broken, damaged, clearance issues, corroded, covered by vegetation, overgrown, strain or abrasion | [Answer left blank] | Vegetation appears to be in contact with guy above the guy insulator. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101882537 | SAN LUIS OBISPO II29 POLES | Los Padres(S) | 2021-06-16 | 2021-07-13 | 2022-01-03 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101882538 | SAN LUIS OBISPO II29 POLES | Los Padres(S) | 2021-06-16 | 2021-07-13 | 2022-01-03 | Anchor and Guys: Guy wire broken, damaged, clearance issues, corroded, covered by vegetation, overgrown, strain or abrasion | [Answer left blank] | Vegetation appears to be in contact with guy above the guy insulator. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101882540 | SAN LUIS OBISPO II29 POLES | Los Padres(S) | 2021-06-16 | 2021-07-13 | 2022-01-03 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101882543 | SAN LUIS OBISPO II29 POLES | Los Padres(S) | 2021-06-16 | 2021-07-13 | 2022-01-03 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101936849 | SAN LUIS OBISPO II29 POLES | Los Padres(S) | 2021-06-16 | 2021-07-13 | 2022-01-03 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101936849 | SAN LUIS OBISPO II29 POLES | Los Padres(S) | 2021-06-16 | 2021-07-13 | 2022-01-03 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103012253 | SAN LUIS OBISPO II29 POLES | Los Padres(S) | 2021-06-16 | 2021-07-13 | 2022-01-03 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103012253 | SAN LUIS OBISPO II29 POLES | Los Padres(S) | 2021-06-16 | 2021-07-13 | 2022-01-03 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101882551 | SAN LUIS OBISPO II29 POLES | Los Padres(S) | 2021-06-17 | 2021-07-13 | 2022-01-03 | Anchor and Guys: Necessary guys missing or loose | [Answer left blank] | Pole-to-pole guy is loose. | Agree | N/A | N¦A | 119112166 | Update a EC | Yes | No | Yes | No
101882555 | SAN LUIS OBISPO II29 POLES | Los Padres(S) | 2021-06-17 | 2021-07-13 | 2022-01-03 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101936841 | SAN LUIS OBISPO II29 POLES | Los Padres(S) | 2021-06-17 | 2021-07-13 | 2022-01-03 | Anchor and Guys: Necessary guys missing or loose | [Answer left blank] | Guy appears to be loose. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101936842 | SAN LUIS OBISPO II29 POLES | Los Padres(S) | 2021-06-17 | 2021-07-13 | 2022-01-03 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101936842 | SAN LUIS OBISPO II29 POLES | Los Padres(S) | 2021-06-17 | 2021-07-13 | 2022-01-03 | Non-Time-Dependent Issues: Visibility strips missing, broken, mismatched, or no longer reflective | [Answer left blank] | Visibility strips are missing. | Agree | N/A | N¦A | 117190064 | Update a EC | Yes | No | Yes | No
101936842 | SAN LUIS OBISPO II29 POLES | Los Padres(S) | 2021-06-17 | 2021-07-13 | 2022-01-03 | Non-Time-Dependent Issues: Pole steps are less than 8' 6" above the ground or any other accessible surface | [Answer left blank] | Pole step is at 7' 8" (92"). | Agree | N/A | N¦A | 117190064 | Update a EC | Yes | No | Yes | No
101936843 | SAN LUIS OBISPO II29 POLES | Los Padres(S) | 2021-06-17 | 2021-07-13 | 2022-01-03 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101936843 | SAN LUIS OBISPO II29 POLES | Los Padres(S) | 2021-06-17 | 2021-07-13 | 2022-01-03 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103922096 | SAN LUIS OBISPO II29 POLES | Los Padres(S) | 2021-06-17 | 2021-07-13 | 2022-01-03 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103930713 | SAN LUIS OBISPO II29 POLES | Los Padres(S) | 2021-06-17 | 2021-07-13 | 2022-01-03 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
104012522 | SAN LUIS OBISPO II29 POLES | Los Padres(S) | 2021-06-17 | 2021-07-13 | 2022-01-03 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101864938 | SANTA MARIA AA4824 POLES | Los Padres(S) | 2021-06-22 | 2021-07-15 | 2022-01-03 | Common Equipment/Other Equipment: IFD (aka "Turkey Popper") has activated on the transformer (orange band is visible) | [Answer left blank] | Transformer IFD appears to have been activated. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101864938 | SANTA MARIA AA4824 POLES | Los Padres(S) | 2021-06-22 | 2021-07-15 | 2022-01-03 | Hardware and Framing: Animal mitigation broken, damaged, or missing (if required) | [Answer left blank] | Animal protection on transformer bushings appear to be damaged. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101864938 | SANTA MARIA AA4824 POLES | Los Padres(S) | 2021-06-22 | 2021-07-15 | 2022-01-03 | Other Required Data: Is there non-exempt equipment at the inspection location (Universal or Open Link Fuse) | [Answer left blank] | Non-exempt universal fuse appears to be present at the location. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101864940 | SANTA MARIA AA4824 POLES | Los Padres(S) | 2021-06-22 | 2021-07-15 | 2022-01-03 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | The top of the pole shows signs of decay near where hardware is attached. There are cracks along the middle and bottom of the pole. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Single phase tangent pole with 9" brackets & hardware installed. | N\A | N\A | N\A | N\A | N\A
101864940 | SANTA MARIA AA4824 POLES | Los Padres(S) | 2021-06-22 | 2021-07-15 | 2022-01-03 | Common Equipment/Other Equipment: Does this structure have equipment? | No | Structure appears to have equipment (riser fuses). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101864940 | SANTA MARIA AA4824 POLES | Los Padres(S) | 2021-06-22 | 2021-07-15 | 2022-01-03 | Anchor and Guys: Does or should this location have a Guy? | No | A guy wire is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101864940 | SANTA MARIA AA4824 POLES | Los Padres(S) | 2021-06-22 | 2021-07-15 | 2022-01-03 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101864944 | SANTA MARIA AA4824 POLES | Los Padres(S) | 2021-06-22 | 2021-07-15 | 2022-01-03 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks at the middle and top of pole, including near where the hardware is attached. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101864990 | SANTA MARIA AA4819 POLES | Los Padres(S) | 2021-06-22 | 2021-07-15 | 2022-01-03 | Non-Time-Dependent Issues: Pole steps are less than 8' 6" above the ground or any other accessible surface | [Answer left blank] | Pole step is at 7' 4" (88"). | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101914689 | SANTA MARIA AA4819 POLES | Los Padres(S) | 2021-06-22 | 2021-07-15 | 2022-01-03 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are woodpecker holes that appear to have a diameter greater than 4". There are cracks along the bottom and middle of the pole | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101915552 | SANTA MARIA AA4824 POLES | Los Padres(S) | 2021-06-22 | 2021-07-15 | 2022-01-03 | Equipment: Does this structure have equipment? | [Answer left blank] | This structure has equipment (fuses and lightning arrestors). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101915552 | SANTA MARIA AA4824 POLES | Los Padres(S) | 2021-06-22 | 2021-07-15 | 2022-01-03 | Other Required Data: Is there non-exempt equipment at the inspection location (Lightning or Surge Arrester) | [Answer left blank] | Non-exempt lightning arrestors are present at this location. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101915555 | SANTA MARIA AA4824 POLES | Los Padres(S) | 2021-06-22 | 2021-07-15 | 2022-01-03 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks in the middle and top of pole, including near where the hardware is attached. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101915559 | SANTA MARIA AA4824 POLES | Los Padres(S) | 2021-06-22 | 2021-07-15 | 2022-01-03 | Common Equipment/Other Equipment: Does this structure have equipment? | No | The structure has equipment (fuses and lightning arrestors). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101915559 | SANTA MARIA AA4824 POLES | Los Padres(S) | 2021-06-22 | 2021-07-15 | 2022-01-03 | Other Required Data: Is there non-exempt equipment at the inspection location (Lightning or Surge Arrester) | [Answer left blank] | Non-exempt lightning arrestors are present at this location. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103760149 | SANTA MARIA AA4824 POLES | Los Padres(S) | 2021-06-22 | 2021-07-15 | 2022-01-03 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | Pole number is visible on pole. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103847473 | SANTA MARIA AA4824 POLES | Los Padres(S) | 2021-06-22 | 2021-07-15 | 2022-01-03 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | Pole number is visible on pole. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103847473 | SANTA MARIA AA4824 POLES | Los Padres(S) | 2021-06-22 | 2021-07-15 | 2022-01-03 | Other Required Data: Is there non-exempt equipment at the inspection location (Universal or Open Link Fuse) | [Answer left blank] | Non-exempt universal fuses are present at the location. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103854572 | SANTA MARIA AA4824 POLES | Los Padres(S) | 2021-06-22 | 2021-07-15 | 2022-01-03 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | Pole number is visible on pole. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101864947 | SANTA MARIA AA4824 POLES | Los Padres(S) | 2021-06-22 | 2021-07-15 | 2022-01-03 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There is a woodpecker hole at the top of the pole that appears to be greater than 4" in diameter. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101864966 | SANTA MARIA AA4825 POLES | Los Padres(S) | 2021-06-23 | 2021-07-15 | 2022-01-03 | Common Equipment/Other Equipment: Does this structure have equipment? | No | Structure appears to have equipment (in-line fuses). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101864966 | SANTA MARIA AA4825 POLES | Los Padres(S) | 2021-06-23 | 2021-07-15 | 2022-01-03 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | Pole number is visible on pole. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101914695 | SANTA MARIA AA4825 POLES | Los Padres(S) | 2021-06-23 | 2021-07-15 | 2022-01-03 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks along the length of pole, including at the top near where hardware is attached. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101914699 | SANTA MARIA AA4825 POLES | Los Padres(S) | 2021-06-23 | 2021-07-15 | 2022-01-03 | Common Equipment/Other Equipment: Does this structure have equipment? | No | The structure has equipment (in-line fuses). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102275163 | NORTH BAY MAP VV3208 POLES | North Bay(C) | 2021-06-23 | 2021-07-15 | 2022-01-03 | Non-Time-Dependent Issues: Visibility strips missing, broken, mismatched, or no longer reflective | [Answer left blank] | Visibility strips consist of small sections on the molding only. | Agree | N/A | N¦A | 121589526 | Update a EC | Yes | No | Yes | No
102275163 | NORTH BAY MAP VV3208 POLES | North Bay(C) | 2021-06-23 | 2021-07-15 | 2022-01-03 | Non-Time-Dependent Issues: Pole steps are less than 8' 6" above the ground or any other accessible surface | [Answer left blank] | Pole step is at 8' 4" (100"). | Agree | N/A | N¦A | 121589526 | Update a EC | Yes | No | Yes | No
103523655 | SANTA MARIA AA4825 POLES | Los Padres(S) | 2021-06-23 | 2021-07-15 | 2022-01-03 | Common Equipment/Other Equipment: Does this structure have equipment? | No | The structure has equipment (fuses and lightning arrestors). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103523655 | SANTA MARIA AA4825 POLES | Los Padres(S) | 2021-06-23 | 2021-07-15 | 2022-01-03 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Structure with non-exempt equipment (solid blade disconnects and lightning arresters) appears to have dried ground vegetation within 10' of its base. | Agree | N/A | N¦A |  | Create "Other tag" | Yes | No | Yes | No
103523655 | SANTA MARIA AA4825 POLES | Los Padres(S) | 2021-06-23 | 2021-07-15 | 2022-01-03 | Other Required Data: Is there non-exempt equipment at the inspection location (Solid Blade or In-line disconnect) | [Answer left blank] | Non-exempt solid blade disconnects are present at the location. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103523655 | SANTA MARIA AA4825 POLES | Los Padres(S) | 2021-06-23 | 2021-07-15 | 2022-01-03 | Other Required Data: Is there non-exempt equipment at the inspection location (Lightning or Surge Arrester) | [Answer left blank] | Non-exempt lightning arresters are present at the location. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101864984 | SANTA MARIA AA4820 POLES | Los Padres(S) | 2021-06-24 | 2021-07-15 | 2022-01-04 | Other Required Data: Is there non-exempt equipment at the inspection location (Lightning or Surge Arrester) | [Answer left blank] | There are non-exempt lightning arrestors at the location. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102275290 | NORTH BAY MAP VV3208 POLES | North Bay(C) | 2021-06-25 | 2021-07-22 | 2022-01-04 | Common Equipment/Other Equipment: Does this structure have equipment? | No | There are line fuses on the asset. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102252548 | NORTH BAY MAP SS2810 POLES | North Bay(C) | 2021-06-26 | 2021-07-20 | 2022-01-04 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks atthe top of the pole, near where hardware is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Single phase line & Buck pole with wood arms & hardware installed. | N\A | N\A | N\A | N\A | N\A
102252548 | NORTH BAY MAP SS2810 POLES | North Bay(C) | 2021-06-26 | 2021-07-20 | 2022-01-04 | Hardware and Framing: Crossarm integrity compromised by any of the following; damaged, broken, burnt, decayed, rotten, loose, missing hardware or showing severe signs of bent bolts or brackets, damaged bracing, gun shots, insect damage or woodpecker damage, splitting, or fails to meet clearance requirements | [Answer left blank] | Some hardware appears to be loose, and the lower primary crossarm appears to be decayed near where the insulator is attached. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
102252548 | NORTH BAY MAP SS2810 POLES | North Bay(C) | 2021-06-26 | 2021-07-20 | 2022-01-04 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Structure with non-exempt equipment (split bolt connectors) appears to have dried vegetation and partially dry bushes within 10' of its base. | Agree | N/A | N¦A |  | Create "Other tag" | Yes | No | Yes | No
102252548 | NORTH BAY MAP SS2810 POLES | North Bay(C) | 2021-06-26 | 2021-07-20 | 2022-01-04 | Other Required Data: Is there non-exempt equipment at the inspection location (Hot tap clamp or Split Bolt connector) | [Answer left blank] | There appearto be split bolt connectors on the primary conductor. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102252572 | NORTH BAY MAP SS2810 POLES | North Bay(C) | 2021-06-26 | 2021-07-20 | 2022-01-04 | Conductor: Conductor has splices tied in proximity to insulator preventing free movement of splice with conductor | [Answer left blank] | On the east phase of the primary conductor (i.e., the road-side phase), a splice appears to be within 2' of the insulator. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
102252572 | NORTH BAY MAP SS2810 POLES | North Bay(C) | 2021-06-26 | 2021-07-20 | 2022-01-04 | Hardware and Framing: Molding missing, broken, damaged, or loose | [Answer left blank] | Molding is broken/disconnected at 8' 4" (100"). | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
102252572 | NORTH BAY MAP SS2810 POLES | North Bay(C) | 2021-06-26 | 2021-07-20 | 2022-01-04 | Hardware and Framing: Grounds exposed, broken, damaged, disconnected, unsecured, or missing (if required) | [Answer left blank] | Ground is partially exposed at 8' 4" (100"). | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
102252572 | NORTH BAY MAP SS2810 POLES | North Bay(C) | 2021-06-26 | 2021-07-20 | 2022-01-04 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Structure with non-exempt equipment (split bolt connectors) appears to have dried vegetation within a 10' radius of its base. | Agree | N/A | N¦A |  | Create "Other tag" | Yes | No | Yes | No
102252572 | NORTH BAY MAP SS2810 POLES | North Bay(C) | 2021-06-26 | 2021-07-20 | 2022-01-04 | Other Required Data: Is there non-exempt equipment at the inspection location (Hot tap clamp or Split Bolt connector) | [Answer left blank] | Both transformer jumpers appear to be connected to the primary conductor with split bolt connectors, which are considered non-exempt. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102252577 | NORTH BAY MAP SS2810 POLES | North Bay(C) | 2021-06-26 | 2021-07-20 | 2022-01-04 | Conductor: Conductor has splices tied in proximity to insulator preventing free movement of splice with conductor | [Answer left blank] | There appear to be two splices tied within 2' of the insulators. The splices are on the span west of the pole | Agree | N/A | N¦A | 121607205 | Update a EC | Yes | No | Yes | No
103978432 | DIABLO E0605 POLES | Diablo(C) | 2021-06-26 | 2021-07-14 | 2022-01-04 | Anchor and Guys: Does or should this location have a Guy? | No | There is a guy at this location. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103978440 | DIABLO E0605 POLES | Diablo(C) | 2021-06-26 | 2021-07-14 | 2022-01-04 | Hardware and Framing: Animal mitigation broken, damaged, or missing (if required) | [Answer left blank] | Animal mitigations appear to be damaged/out of place on west phase, both north and south of the pole. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
103978441 | DIABLO E0605 POLES | Diablo(C) | 2021-06-26 | 2021-07-14 | 2022-01-04 | Hardware and Framing: Animal mitigation broken, damaged, or missing (if required) | [Answer left blank] | Animal mitigation appears to be damaged/out of place on the east phase, south of the pole. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
103978640 | DIABLO E0610 POLES | Diablo(C) | 2021-06-26 | 2021-07-14 | 2022-01-04 | Conductor: Select if there are risks, hazards or other maintenance conditions not previously captured in the checklist for this conductor | [Answer left blank] | Tape on primary jumper connectors appears loose, exposing conductor. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
103978640 | DIABLO E0610 POLES | Diablo(C) | 2021-06-26 | 2021-07-14 | 2022-01-04 | Common Equipment/Other Equipment: Does this structure have equipment? | No | This structure has equipment (transformer). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101900734 | PASO ROBLES GG29 POLES | Los Padres(S) | 2021-06-27 | 2021-07-14 | 2022-01-04 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101900738 | PASO ROBLES GG29 POLES | Los Padres(S) | 2021-06-27 | 2021-07-14 | 2022-01-04 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are deep cracks in the middle and top of the pole, including near where hardware is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Single phase double deadend pole with steel arm & hardware installed. | N\A | N\A | N\A | N\A | N\A
101900738 | PASO ROBLES GG29 POLES | Los Padres(S) | 2021-06-27 | 2021-07-14 | 2022-01-04 | Common Equipment/Other Equipment: Does this structure have equipment? | No | Equipment (universal fuses) are present on the structure | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101900738 | PASO ROBLES GG29 POLES | Los Padres(S) | 2021-06-27 | 2021-07-14 | 2022-01-04 | Non-Time-Dependent Issues: Operating number missing, broken, illegible, not installed in field or incorrectly installed in field | [Answer left blank] | Some digits in the operating number are illegible. | Agree | N/A | N¦A | 119049719 | Update a EC | Yes | No | Yes | No
101900738 | PASO ROBLES GG29 POLES | Los Padres(S) | 2021-06-27 | 2021-07-14 | 2022-01-04 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101900740 | PASO ROBLES GG29 POLES | Los Padres(S) | 2021-06-27 | 2021-07-14 | 2022-01-04 | Anchor and Guys: Guy wire broken, damaged, clearance issues, corroded, covered by vegetation, overgrown, strain or abrasion | [Answer left blank] | Vegetation appears to be in contact with guy wire above the guy insulator. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101900741 | PASO ROBLES GG29 POLES | Los Padres(S) | 2021-06-27 | 2021-07-14 | 2022-01-04 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101900743 | PASO ROBLES GG29 POLES | Los Padres(S) | 2021-06-27 | 2021-07-14 | 2022-01-04 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101900744 | PASO ROBLES GG29 POLES | Los Padres(S) | 2021-06-27 | 2021-07-14 | 2022-01-04 | Vegetation: Tree causing strain or abrasion to secondary or service (only 1 service) | [Answer left blank] | Vegetation appears to be causing strain on a service conductor. The service conductor appears to be de-energized. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101900782 | PASO ROBLES GG29 POLES | Los Padres(S) | 2021-06-27 | 2021-07-14 | 2022-01-04 | Common Equipment/Other Equipment: Does this structure have equipment? | No | Equipment (universal fuses) are present on this structure. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101900782 | PASO ROBLES GG29 POLES | Los Padres(S) | 2021-06-27 | 2021-07-14 | 2022-01-04 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101900782 | PASO ROBLES GG29 POLES | Los Padres(S) | 2021-06-27 | 2021-07-14 | 2022-01-04 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | The structure has non-exempt universal fuses and a stump within 10' of its base. | Agree | N/A | N¦A |  | Create "Other tag" | Yes | No | Yes | No
101939141 | PASO ROBLES GG29 POLES | Los Padres(S) | 2021-06-27 | 2021-07-14 | 2022-01-04 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101939141 | PASO ROBLES GG29 POLES | Los Padres(S) | 2021-06-27 | 2021-07-14 | 2022-01-04 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | High voltage sign is missing from one side of pole. | Disagree | Condition is not compelling | 1. High Voltage Sign Not Installed as Required - TD-2305M-JA02, Rev. 8 - Pg. 61 | The one high sign in good condition on the opposite side of the pole satisfies the standard found in OH: Marking, Rev. #18: 11/01/18 022168 Page 3 of 35. Marking, Numbering, and Identification of Line Structures 3. Routine Inspection A. The requirement in 1, “Poles That Support Line Conductors,” must be satisfied with the following exceptions: 1. Sign the Pole: It is acceptable to have only one sign, or stacked pairs of signs, below the lowest line conductor energized above 750 V, except as noted in 4 “Special Locations.” B. The requirements in 2, Poles That Do Not Support Line Conductors,” must be satisfied with the following exceptions: 1. Risers: It is acceptable to have only one sign, or stacked pairs of signs, below risers energized above 750 V. 4. Special Locations: If the pole is signed, high-voltage signs are required on both sides of the pole in the following locations: Near water areas suitable for sailboats. Near established boat ramps and associated rigging areas. Adjacent to swimming pools. In agricultural areas with movable irrigation piping. Locations, where in the judgement of the employee, high-voltage signs should be visible from all sides of the poles. | N\A | N\A | N\A | N\A | N\A
101939143 | PASO ROBLES GG29 POLES | Los Padres(S) | 2021-06-27 | 2021-07-14 | 2022-01-04 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101947418 | PASO ROBLES GG29 POLES | Los Padres(S) | 2021-06-27 | 2021-07-14 | 2022-01-04 | Vegetation: Tree causing strain or abrasion to secondary or service (only 1 service) | [Answer left blank] | A tree branch appears to be causing strain on the secondary conductor. | Agree | N/A | N¦A | Condition is already attached to an EC Notification (117136945). Inspector did complete FSR to update Notification but did not indicate condition in Vegetation section of Inspection Record. | N\A | N\A | N\A | N\A | N\A
102252022 | NORTH BAY MAP SS2810 POLES | North Bay(C) | 2021-06-27 | 2021-07-20 | 2022-01-04 | Conductor: Conductor has splices tied in proximity to insulator preventing free movement of splice with conductor | [Answer left blank] | There appears to be a splice under the tie wire and within 2' of insulator. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
102252022 | NORTH BAY MAP SS2810 POLES | North Bay(C) | 2021-06-27 | 2021-07-20 | 2022-01-04 | Other Required Data: 3 or more splices present in one phase of the span | Energized Phases: 2, Splice Count: (4, 1) for a total of 5 Splices. Span crosses over major roadway: No | There are 2 phases on this asset. There are 7 splices on the span south of the asset, with 4 splices on the west phase and 3 splices on the east phase. Span does not cross over a major roadway. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102252025 | NORTH BAY MAP SS2810 POLES | North Bay(C) | 2021-06-27 | 2021-07-20 | 2022-01-04 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks at the top of the pole, near where hardware is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Three phase line & buck pole with wood arms & hardware installed. | N\A | N\A | N\A | N\A | N\A
103534050 | PASO ROBLES GG29 POLES | Los Padres(S) | 2021-06-27 | 2021-07-20 | 2022-01-04 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103534050 | PASO ROBLES GG29 POLES | Los Padres(S) | 2021-06-27 | 2021-07-20 | 2022-01-04 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103891893 | PASO ROBLES GG29 POLES | Los Padres(S) | 2021-06-27 | 2021-07-20 | 2022-01-04 | Conductor: Primary or secondary conductor has diminished clearance mid span or uneven conductor sag | [Answer left blank] | Three phases of primary conductor show uneven sag. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
103891893 | PASO ROBLES GG29 POLES | Los Padres(S) | 2021-06-27 | 2021-07-20 | 2022-01-04 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103891893 | PASO ROBLES GG29 POLES | Los Padres(S) | 2021-06-27 | 2021-07-20 | 2022-01-04 | Other Required Data: 3 or more splices present in one phase of the span | [Answer left blank] | There are 3 phases on the asset. There are 7 splices on the southwest span, with 4 splices on the northwest phase and 3 splices on the center phase. Span does not cross over a major roadway. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103943412 | PASO ROBLES GG29 POLES | Los Padres(S) | 2021-06-27 | 2021-07-20 | 2022-01-04 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103978439 | DIABLO E0610 POLES | Diablo(C) | 2021-06-27 | 2021-07-20 | 2022-01-04 | Common Equipment/Other Equipment: Does this structure have equipment? | No | Structure has equipment (transformer) present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
8.12 REPORT
102268174 | SILVERADO GG33 POLES | North Bay(C) | 2021-04-03 | 6/4/2021 | 2022-01-04 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | High voltage sign on one side of the pole appears loose. | Disagree | Condition is not compelling | 1. High Voltage Sign Not Installed as Required - TD-2305M-JA02, Rev. 8 - Pg. 61 | The one high sign in good condition on the opposite side of the pole satisfies the standard found in OH: Marking, Rev. #18: 11/01/18 022168 Page 3 of 35. Marking, Numbering, and Identification of Line Structures 3. Routine Inspection A. The requirement in 1, “Poles That Support Line Conductors,” must be satisfied with the following exceptions: 1. Sign the Pole: It is acceptable to have only one sign, or stacked pairs of signs, below the lowest line conductor energized above 750 V, except as noted in 4 “Special Locations.” B. The requirements in 2, Poles That Do Not Support Line Conductors,” must be satisfied with the following exceptions: 1. Risers: It is acceptable to have only one sign, or stacked pairs of signs, below risers energized above 750 V. 4. Special Locations: If the pole is signed, high-voltage signs are required on both sides of the pole in the following locations: Near water areas suitable for sailboats. Near established boat ramps and associated rigging areas. Adjacent to swimming pools. In agricultural areas with movable irrigation piping. Locations, where in the judgement of the employee, high-voltage signs should be visible from all sides of the poles. | N\A | N\A | N\A | N\A | N\A
101967889 | SANTA ROSA KK2721 POLES | Sonoma(N) | 2021-04-17 | 6/4/2021 | 2022-01-04 | Vegetation: Does this structure have vegetation present? | No | Vegetation is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101967894 | SANTA ROSA KK2721 POLES | Sonoma(N) | 2021-04-17 | 6/4/2021 | 2022-01-04 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | Part of high voltage sign is missing from one side of the pole. | Disagree | Condition is not compelling | 1. High Voltage Sign Not Installed as Required - TD-2305M-JA02, Rev. 8 - Pg. 61 | The one high sign in good condition on the opposite side of the pole satisfies the standard found in OH: Marking, Rev. #18: 11/01/18 022168 Page 3 of 35. Marking, Numbering, and Identification of Line Structures 3. Routine Inspection A. The requirement in 1, “Poles That Support Line Conductors,” must be satisfied with the following exceptions: 1. Sign the Pole: It is acceptable to have only one sign, or stacked pairs of signs, below the lowest line conductor energized above 750 V, except as noted in 4 “Special Locations.” B. The requirements in 2, Poles That Do Not Support Line Conductors,” must be satisfied with the following exceptions: 1. Risers: It is acceptable to have only one sign, or stacked pairs of signs, below risers energized above 750 V. 4. Special Locations: If the pole is signed, high-voltage signs are required on both sides of the pole in the following locations: Near water areas suitable for sailboats. Near established boat ramps and associated rigging areas. Adjacent to swimming pools. In agricultural areas with movable irrigation piping. Locations, where in the judgement of the employee, high-voltage signs should be visible from all sides of the poles. | N\A | N\A | N\A | N\A | N\A
101987238 | SANTA ROSA MM26 POLES | Sonoma(N) | 2021-04-19 | 6/3/2021 | 2022-01-04 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102008448 | SANTA ROSA MM26 POLES | Sonoma(N) | 2021-04-19 | 6/3/2021 | 2022-01-04 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102008628 | SANTA ROSA MM26 POLES | Sonoma(N) | 2021-04-19 | 6/3/2021 | 2022-01-04 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101998355 | SANTA ROSA MM26 POLES | Sonoma(N) | 2021-04-19 | 6/3/2021 | 2022-01-04 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101998373 | SANTA ROSA MM25 POLES | Sonoma(N) | 2021-04-20 | 6/3/2021 | 2022-01-04 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101998379 | SANTA ROSA MM25 POLES | Sonoma(N) | 2021-04-20 | 6/3/2021 | 2022-01-04 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102014734 | SANTA ROSA MM25 POLES | Sonoma(N) | 2021-04-20 | 6/3/2021 | 2022-01-04 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102014754 | SANTA ROSA MM25 POLES | Sonoma(N) | 2021-04-20 | 6/3/2021 | 2022-01-04 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101998326 | SANTA ROSA MM25 POLES | Sonoma(N) | 2021-04-21 | 6/3/2021 | 2022-01-04 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101998333 | SANTA ROSA MM25 POLES | Sonoma(N) | 2021-04-21 | 6/3/2021 | 2022-01-04 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101998344 | SANTA ROSA MM25 POLES | Sonoma(N) | 2021-04-21 | 6/3/2021 | 2022-01-04 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101998354 | SANTA ROSA MM25 POLES | Sonoma(N) | 2021-04-21 | 6/3/2021 | 2022-01-04 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102014727 | SANTA ROSA MM25 POLES | Sonoma(N) | 2021-04-21 | 6/3/2021 | 2022-01-04 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102014732 | SANTA ROSA MM25 POLES | Sonoma(N) | 2021-04-21 | 6/3/2021 | 2022-01-04 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102015256 | SANTA ROSA MM25 POLES | Sonoma(N) | 2021-04-21 | 6/3/2021 | 2022-01-04 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101998331 | SANTA ROSA MM25 POLES | Sonoma(N) | 2021-04-21 | 6/3/2021 | 2022-01-04 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100411022 | OROVILLE J26 POLES | North Valley(N) | 2021-05-05 | 6/24/2021 | 2022-01-04 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | Portion of high voltage sign on one side of the pole is missing. | Disagree | Condition is not compelling | 1. High Voltage Sign Not Installed as Required - TD-2305M-JA02, Rev. 8 - Pg. 61 | The one high sign in good condition on the opposite side of the pole satisfies the standard found in OH: Marking, Rev. #18: 11/01/18 022168 Page 3 of 35. Marking, Numbering, and Identification of Line Structures 3. Routine Inspection A. The requirement in 1, “Poles That Support Line Conductors,” must be satisfied with the following exceptions: 1. Sign the Pole: It is acceptable to have only one sign, or stacked pairs of signs, below the lowest line conductor energized above 750 V, except as noted in 4 “Special Locations.” B. The requirements in 2, Poles That Do Not Support Line Conductors,” must be satisfied with the following exceptions: 1. Risers: It is acceptable to have only one sign, or stacked pairs of signs, below risers energized above 750 V. 4. Special Locations: If the pole is signed, high-voltage signs are required on both sides of the pole in the following locations: Near water areas suitable for sailboats. Near established boat ramps and associated rigging areas. Adjacent to swimming pools. In agricultural areas with movable irrigation piping. Locations, where in the judgement of the employee, high-voltage signs should be visible from all sides of the poles. | N\A | N\A | N\A | N\A | N\A
100381158 | OROVILLE J26 POLES | North Valley(N) | 2021-05-06 | 6/24/2021 | 2022-01-04 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100411467 | OROVILLE J26 POLES | North Valley(N) | 2021-05-06 | 6/24/2021 | 2022-01-04 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100381165 | OROVILLE J26 POLES | North Valley(N) | 2021-05-07 | 6/24/2021 | 2022-01-05 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100411018 | OROVILLE J26 POLES | North Valley(N) | 2021-05-07 | 6/24/2021 | 2022-01-05 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | High voltage sign on one side of the pole is partially missing. | Disagree | Condition is not compelling | 1. High Voltage Sign Not Installed as Required - TD-2305M-JA02, Rev. 8 - Pg. 61 | The one high sign in good condition on the opposite side of the pole satisfies the standard found in OH: Marking, Rev. #18: 11/01/18 022168 Page 3 of 35. Marking, Numbering, and Identification of Line Structures 3. Routine Inspection A. The requirement in 1, “Poles That Support Line Conductors,” must be satisfied with the following exceptions: 1. Sign the Pole: It is acceptable to have only one sign, or stacked pairs of signs, below the lowest line conductor energized above 750 V, except as noted in 4 “Special Locations.” B. The requirements in 2, Poles That Do Not Support Line Conductors,” must be satisfied with the following exceptions: 1. Risers: It is acceptable to have only one sign, or stacked pairs of signs, below risers energized above 750 V. 4. Special Locations: If the pole is signed, high-voltage signs are required on both sides of the pole in the following locations: Near water areas suitable for sailboats. Near established boat ramps and associated rigging areas. Adjacent to swimming pools. In agricultural areas with movable irrigation piping. Locations, where in the judgement of the employee, high-voltage signs should be visible from all sides of the poles. | N\A | N\A | N\A | N\A | N\A
100381195 | OROVILLE J26 POLES | North Valley(N) | 2021-05-08 | 6/24/2021 | 2022-01-05 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103935741 | MERCED MAP 07214D POLES | Yosemite(S) | 2021-05-10 | 2021-06-17 | 2022-01-05 | Other Required Data: 3 or more splices present in one phase of the span | [Answer left blank] | There are three splices on the east span, all of which are on the north/field-side phase. Span does not cross over a major roadway. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101017845 | MERCED MAP 07214D POLES | Yosemite(S) | 2021-05-12 | 2021-06-17 | 2022-01-05 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101066067 | MERCED MAP 06191 POLES | Yosemite(S) | 2021-05-13 | 2021-06-16 | 2022-01-05 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100353234 | PARADISE R3304 POLES | North Valley(N) | 2021-05-15 | 2021-06-22 | 2022-01-05 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | High voltage sign is missing on one side of pole. | Disagree | Condition is not compelling | 1. High Voltage Sign Not Installed as Required - TD-2305M-JA02, Rev. 8 - Pg. 61 | The one high sign in good condition on the opposite side of the pole satisfies the standard found in OH: Marking, Rev. #18: 11/01/18 022168 Page 3 of 35. Marking, Numbering, and Identification of Line Structures 3. Routine Inspection A. The requirement in 1, “Poles That Support Line Conductors,” must be satisfied with the following exceptions: 1. Sign the Pole: It is acceptable to have only one sign, or stacked pairs of signs, below the lowest line conductor energized above 750 V, except as noted in 4 “Special Locations.” B. The requirements in 2, Poles That Do Not Support Line Conductors,” must be satisfied with the following exceptions: 1. Risers: It is acceptable to have only one sign, or stacked pairs of signs, below risers energized above 750 V. 4. Special Locations: If the pole is signed, high-voltage signs are required on both sides of the pole in the following locations: Near water areas suitable for sailboats. Near established boat ramps and associated rigging areas. Adjacent to swimming pools. In agricultural areas with movable irrigation piping. Locations, where in the judgement of the employee, high-voltage signs should be visible from all sides of the poles. | N\A | N\A | N\A | N\A | N\A
100353236 | PARADISE R3304 POLES | North Valley(N) | 2021-05-15 | 2021-06-22 | 2022-01-05 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | High voltage sign on one side of the pole is missing. | Disagree | Condition is not compelling | 1. High Voltage Sign Not Installed as Required - TD-2305M-JA02, Rev. 8 - Pg. 61 | The one high sign in good condition on the opposite side of the pole satisfies the standard found in OH: Marking, Rev. #18: 11/01/18 022168 Page 3 of 35. Marking, Numbering, and Identification of Line Structures 3. Routine Inspection A. The requirement in 1, “Poles That Support Line Conductors,” must be satisfied with the following exceptions: 1. Sign the Pole: It is acceptable to have only one sign, or stacked pairs of signs, below the lowest line conductor energized above 750 V, except as noted in 4 “Special Locations.” B. The requirements in 2, Poles That Do Not Support Line Conductors,” must be satisfied with the following exceptions: 1. Risers: It is acceptable to have only one sign, or stacked pairs of signs, below risers energized above 750 V. 4. Special Locations: If the pole is signed, high-voltage signs are required on both sides of the pole in the following locations: Near water areas suitable for sailboats. Near established boat ramps and associated rigging areas. Adjacent to swimming pools. In agricultural areas with movable irrigation piping. Locations, where in the judgement of the employee, high-voltage signs should be visible from all sides of the poles. | N\A | N\A | N\A | N\A | N\A
100353290 | PARADISE R3304 POLES | North Valley(N) | 2021-05-15 | 2021-06-22 | 2022-01-05 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | High voltage sign on one side of the pole is missing. | Disagree | Condition is not compelling | 1. High Voltage Sign Not Installed as Required - TD-2305M-JA02, Rev. 8 - Pg. 61 | The one high sign in good condition on the opposite side of the pole satisfies the standard found in OH: Marking, Rev. #18: 11/01/18 022168 Page 3 of 35. Marking, Numbering, and Identification of Line Structures 3. Routine Inspection A. The requirement in 1, “Poles That Support Line Conductors,” must be satisfied with the following exceptions: 1. Sign the Pole: It is acceptable to have only one sign, or stacked pairs of signs, below the lowest line conductor energized above 750 V, except as noted in 4 “Special Locations.” B. The requirements in 2, Poles That Do Not Support Line Conductors,” must be satisfied with the following exceptions: 1. Risers: It is acceptable to have only one sign, or stacked pairs of signs, below risers energized above 750 V. 4. Special Locations: If the pole is signed, high-voltage signs are required on both sides of the pole in the following locations: Near water areas suitable for sailboats. Near established boat ramps and associated rigging areas. Adjacent to swimming pools. In agricultural areas with movable irrigation piping. Locations, where in the judgement of the employee, high-voltage signs should be visible from all sides of the poles. | N\A | N\A | N\A | N\A | N\A
103987969 | PARADISE T3406 POLES | North Valley(N) | 2021-05-15 | 2021-06-23 | 2022-01-05 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100353483 | PARADISE R3309 POLES | North Valley(N) | 2021-05-17 | 2021-06-22 | 2022-01-05 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100353484 | PARADISE R3309 POLES | North Valley(N) | 2021-05-17 | 2021-06-22 | 2022-01-05 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101065913 | MERCED MAP 06191 POLES | Yosemite(S) | 2021-05-17 | 2021-06-16 | 2022-01-05 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | High voltage sign is missing from one side of pole. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
103967771 | PARADISE T3309 POLES | North Valley(N) | 2021-05-18 | 2021-06-24 | 2022-01-05 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | High voltage sign on one side of the pole is missing. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100325555 | PARADISE T3406 POLES | North Valley(N) | 2021-05-20 | 2021-06-23 | 2022-01-05 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101017817 | MERCED MAP 07214D POLES | Yosemite(S) | 2021-05-20 | 2021-06-23 | 2022-01-05 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103954126 | PARADISE T3310 POLES | North Valley(N) | 2021-05-20 | 2021-06-23 | 2022-01-05 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101020136 | MERCED MAP 07214D POLES | Yosemite(S) | 2021-05-24 | 2021-06-17 | 2022-01-05 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101020137 | MERCED MAP 07214D POLES | Yosemite(S) | 2021-05-24 | 2021-06-17 | 2022-01-05 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103932559 | MERCED MAP 07214D POLES | Yosemite(S) | 2021-05-24 | 2021-06-17 | 2022-01-05 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | High voltage sign is broken. | Disagree | Condition is not compelling | 1. High Voltage Sign Not Installed as Required - TD-2305M-JA02, Rev. 8 - Pg. 61 | The one high sign in good condition on the opposite side of the pole satisfies the standard found in OH: Marking, Rev. #18: 11/01/18 022168 Page 3 of 35. Marking, Numbering, and Identification of Line Structures 3. Routine Inspection A. The requirement in 1, “Poles That Support Line Conductors,” must be satisfied with the following exceptions: 1. Sign the Pole: It is acceptable to have only one sign, or stacked pairs of signs, below the lowest line conductor energized above 750 V, except as noted in 4 “Special Locations.” B. The requirements in 2, Poles That Do Not Support Line Conductors,” must be satisfied with the following exceptions: 1. Risers: It is acceptable to have only one sign, or stacked pairs of signs, below risers energized above 750 V. 4. Special Locations: If the pole is signed, high-voltage signs are required on both sides of the pole in the following locations: Near water areas suitable for sailboats. Near established boat ramps and associated rigging areas. Adjacent to swimming pools. In agricultural areas with movable irrigation piping. Locations, where in the judgement of the employee, high-voltage signs should be visible from all sides of the poles. | N\A | N\A | N\A | N\A | N\A
100326256 | PARADISE T3407 POLES | North Valley(N) | 2021-05-25 | 2021-06-23 | 2022-01-05 | Other Required Data: 3 or more splices present in one phase of the span | [Answer left blank] | On the south phase of the east-west line, there are 5 splices. Span does not cross over a major roadway. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101020094 | MERCED MAP 07214D POLES | Yosemite(S) | 2021-05-25 | 2021-06-17 | 2022-01-05 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101020096 | MERCED MAP 07214D POLES | Yosemite(S) | 2021-05-25 | 2021-06-17 | 2022-01-05 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101020112 | MERCED MAP 07214D POLES | Yosemite(S) | 2021-05-25 | 2021-06-17 | 2022-01-05 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
104030383 | PARADISE T3407 POLES | North Valley(N) | 2021-05-25 | 2021-06-23 | 2022-01-05 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102268163 | SILVERADO MAP GG3303 POLES | North Bay(C) | 2021-03-27 | 2021-06-04 | 2022-01-05 | Other Required Data: Is there non-exempt equipment at the inspection location (Universal or Open Link Fuse) | [Answer left blank] | There are non-exempt universal fuses on the asset. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102268163 | SILVERADO MAP GG3303 POLES | North Bay(C) | 2021-03-27 | 2021-06-04 | 2022-01-05 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Structure has non-exempt universal fuses and dried grass at the base. | Disagree | N/A | ELEC-1000 Training | PG&E Inspection was completed Prior to the start of the 2021 fire season. Questions in the Inspect app related to vegetation in proximity to pole with Non-Exempt Equipment would not have been available for the inspector to answer until May 1st. | N\A | N\A | N\A | N\A | N\A
102248414 | SILVERADO MAP EE3117 POLES | North Bay(C) | 2021-03-30 | 2021-06-02 | 2022-01-05 | Non-Time-Dependent Issues: Visibility strips missing, broken, mismatched, or no longer reflective | [Answer left blank] | Visibility strips are missing. | Agree | N/A | N¦A | 119308685 | Update a EC | Yes | No | Yes | No
102248419 | SILVERADO MAP EE3117 POLES | North Bay(C) | 2021-03-30 | 2021-06-02 | 2022-01-05 | Hardware and Framing: Tap clamps installed incorrectly | [Answer left blank] | Tap clamps appear to be installed directly on the conductors instead of on tap guards. | Disagree | Condition is not compelling | N¦A | Not needed, conductor is 2 copper. OH: Conductors 028852 Page 5 of 11 Rev. #15: 08−15-17 Tap Clamps Application 1. Tap clamps shall only be used to connect overhead transformers directly serving customers on overhead primary distribution lines, or for connecting jumpers on minor overhead tap lines serving two or less transformer banks. Note: An open delta bank counts as one transformer. To meet required load and reliability criteria, use tap guards for #6 through #4 copper, and #4 through #2 aluminum or ACSR conductors. Tighten all clamps to the recommended torque. | N\A | N\A | N\A | N\A | N\A
102248424 | SILVERADO MAP EE3117 POLES | North Bay(C) | 2021-03-30 | 2021-06-02 | 2022-01-05 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There appear to be multiple cracks running vertically along the length of the pole, including near the equipment. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Three phase tangent pole with king pin and 9" brackets & hardware installed. | N\A | N\A | N\A | N\A | N\A
102248424 | SILVERADO MAP EE3117 POLES | North Bay(C) | 2021-03-30 | 2021-06-02 | 2022-01-05 | Hardware and Framing: Tap clamps installed incorrectly | [Answer left blank] | Tap clamps appear to be installed directly on the conductors instead of on tap guards. | Disagree | Condition is not compelling | N¦A | Not needed, conductor is 2 copper. OH: Conductors 028852 Page 5 of 11 Rev. #15: 08−15-17 Tap Clamps Application 1. Tap clamps shall only be used to connect overhead transformers directly serving customers on overhead primary distribution lines, or for connecting jumpers on minor overhead tap lines serving two or less transformer banks. Note: An open delta bank counts as one transformer. To meet required load and reliability criteria, use tap guards for #6 through #4 copper, and #4 through #2 aluminum or ACSR conductors. Tighten all clamps to the recommended torque. | N\A | N\A | N\A | N\A | N\A
102248845 | SILVERADO MAP EE3117 POLES | North Bay(C) | 2021-03-30 | 2021-06-02 | 2022-01-05 | Hardware and Framing: Is Hardware Framing present on this structure? | No | Yes, hardware is present on this pole. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102248845 | SILVERADO MAP EE3117 POLES | North Bay(C) | 2021-03-30 | 2021-06-02 | 2022-01-05 | Hardware and Framing: Secondary connectors (mini wedge and Insulink) installed on primary conductor | [Answer left blank] | There appear to be two Insulink connectors installed on the primary jumpers. | Agree | N/A | N¦A | Condition is already attached to an EC Notification (119301013). Inspector did complete FSR to update Notification but did not indicate condition in Hardware section of Inspection Record. | N\A | N\A | N\A | N\A | N\A
102248849 | SILVERADO MAP EE3117 POLES | North Bay(C) | 2021-03-30 | 2021-06-02 | 2022-01-05 | Hardware and Framing: Secondary connectors (mini wedge and Insulink) installed on primary conductor | [Answer left blank] | There appear to be two Insulink connectors installed on the primary jumpers. | Agree | N/A | N¦A | Condition is already attached to an EC Notification (119301044). Inspector did complete FSR to update Notification but did not indicate condition in Hardware section of Inspection Record. | N\A | N\A | N\A | N\A | N\A
103115803 | SILVERADO MAP EE3117 POLES | North Bay(C) | 2021-03-30 | 2021-06-02 | 2022-01-05 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There appear to be multiple large cracks along the length of the pole, including at the crossarm level. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Single phase tangent pole with wood crossarm & hardware installed. | N\A | N\A | N\A | N\A | N\A
102248436 | SILVERADO MAP EE3117 POLES | North Bay(C) | 2021-03-31 | 2021-06-02 | 2022-01-05 | Anchor and Guys: Does or should this location have a Guy? | No | This location has a guy. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102248436 | SILVERADO MAP EE3117 POLES | North Bay(C) | 2021-03-31 | 2021-06-02 | 2022-01-05 | Non-Time-Dependent Issues: Visibility strips missing, broken, mismatched, or no longer reflective | [Answer left blank] | Visibility strips are missing. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
102025710 | SANTA ROSA HH2802 POLES | Sonoma(N) | 2021-04-02 | 2021-06-01 | 2022-01-05 | Conductor: Conductor has splices tied in proximity to insulator preventing free movement of splice with conductor | [Answer left blank] | There appear to be 4 splices tied within 2' of the insulators. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
102025710 | SANTA ROSA HH2802 POLES | Sonoma(N) | 2021-04-02 | 2021-06-01 | 2022-01-05 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | There appears to be an open wire secondary at this location. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103633585 | SANTA ROSA HH2802 POLES | Sonoma(N) | 2021-04-02 | 2021-06-01 | 2022-01-05 | Vegetation: Tree causing strain or abrasion to secondary or service (only 1 service) | [Answer left blank] | A tree limb appears to be causing strain to the secondary conductor. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101967893 | SANTA ROSA KK2721 POLES | Sonoma(N) | 2021-04-17 | 6/4/2021 | 2022-01-05 | Other Required Data: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101967893 | SANTA ROSA KK2721 POLES | Sonoma(N) | 2021-04-17 | 6/4/2021 | 2022-01-05 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101967902 | SANTA ROSA KK2721 POLES | Sonoma(N) | 2021-04-17 | 6/4/2021 | 2022-01-05 | Anchor and Guys: Guy wire broken, damaged, clearance issues, corroded, covered by vegetation, overgrown, strain or abrasion | [Answer left blank] | Vegetation appears to be in contact with the guy above the insulator. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101967902 | SANTA ROSA KK2721 POLES | Sonoma(N) | 2021-04-17 | 6/4/2021 | 2022-01-05 | Vegetation: Tree causing strain or abrasion to secondary or service (2 or more services) | [Answer left blank] | Tree branch appears to be causing strain on the service conductor. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
102017008 | SANTA ROSA KK2721 POLES | Sonoma(N) | 2021-04-17 | 6/4/2021 | 2022-01-05 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | The base and top of the pole are cracked and broken. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
102017008 | SANTA ROSA KK2721 POLES | Sonoma(N) | 2021-04-17 | 6/4/2021 | 2022-01-05 | Anchor and Guys: Does or should this location have a Guy? | No | There are two span guys, one on each side of the pole parallel to the road. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102017008 | SANTA ROSA KK2721 POLES | Sonoma(N) | 2021-04-17 | 6/4/2021 | 2022-01-05 | Anchor and Guys: Guy wire broken, damaged, clearance issues, corroded, covered by vegetation, overgrown, strain or abrasion | [Answer left blank] | Vegetation appears to be in contact with the guy above the insulator. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
102017008 | SANTA ROSA KK2721 POLES | Sonoma(N) | 2021-04-17 | 6/4/2021 | 2022-01-05 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | There appear to be open wire secondary at this location. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102017008 | SANTA ROSA KK2721 POLES | Sonoma(N) | 2021-04-17 | 6/4/2021 | 2022-01-05 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102017017 | SANTA ROSA KK2721 POLES | Sonoma(N) | 2021-04-17 | 6/4/2021 | 2022-01-05 | Common Equipment/Other Equipment: IFD (aka "Turkey Popper") has activated on the transformer (orange band is visible) | [Answer left blank] | The transformer IFD appears to have been activated as the orange band is visible and the cap is off. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
102017017 | SANTA ROSA KK2721 POLES | Sonoma(N) | 2021-04-17 | 6/4/2021 | 2022-01-05 | Hardware and Framing: Tap clamps installed incorrectly | [Answer left blank] | There are two tap clamps installed on armor rod rather than on tap guards. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
102017017 | SANTA ROSA KK2721 POLES | Sonoma(N) | 2021-04-17 | 6/4/2021 | 2022-01-05 | Other Required Data: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102017019 | SANTA ROSA KK2721 POLES | Sonoma(N) | 2021-04-17 | 6/4/2021 | 2022-01-05 | Other Required Data: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101967904 | SANTA ROSA KK2721 POLES | Sonoma(N) | 2021-04-17 | 6/4/2021 | 2022-01-05 | Structure: Pole leaning or out of plumb by more than 10% of its height above the ground | [Answer left blank] | The pole appears to be leaning by at least 10% of its height above the ground. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101967911 | SANTA ROSA KK2721 POLES | Sonoma(N) | 2021-04-19 | 6/4/2021 | 2022-01-06 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There appears to be a crack at the base of the pole, and several cracks at the middle of the pole. A portion of the pole top is missing. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Secondary pole with clevis' & hardware installed. | N\A | N\A | N\A | N\A | N\A
101967911 | SANTA ROSA KK2721 POLES | Sonoma(N) | 2021-04-19 | 6/4/2021 | 2022-01-06 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102008478 | SANTA ROSA MM26 POLES | Sonoma(N) | 2021-04-19 | 6/3/2021 | 2022-01-06 | Other Required Data: Support structure or stub present | [Answer left blank] | There is a steel truss supporting the structure. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102008478 | SANTA ROSA MM26 POLES | Sonoma(N) | 2021-04-19 | 6/3/2021 | 2022-01-06 | Other Required Data: Is there non-exempt equipment at the inspection location (Switch (grasshopper)) | Yes | The switch appears to be exempt. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101998356 | SANTA ROSA MM25 POLES | Sonoma(N) | 2021-04-20 | 6/3/2021 | 2022-01-06 | Conductor: Conductor has splices tied in proximity to insulator preventing free movement of splice with conductor | [Answer left blank] | There appears to be a splice on each phase that is tied within 2' of the insulator. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101998374 | SANTA ROSA MM25 POLES | Sonoma(N) | 2021-04-20 | 6/3/2021 | 2022-01-06 | Common Equipment/Other Equipment: Transformer flashed or corroded, e.g. integrity of the metal is breached – holes in metal, cover not securable, metal is damaged, separation, layering, bulging or bubbling | [Answer left blank] | The transformer appears to have areas of corrosion, especially around the popoff valve and one secondary bushing. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101998374 | SANTA ROSA MM25 POLES | Sonoma(N) | 2021-04-20 | 6/3/2021 | 2022-01-06 | Other Required Data: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101998374 | SANTA ROSA MM25 POLES | Sonoma(N) | 2021-04-20 | 6/3/2021 | 2022-01-06 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101998386 | SANTA ROSA MM25 POLES | Sonoma(N) | 2021-04-20 | 6/3/2021 | 2022-01-06 | Conductor: Conductor has splices tied in proximity to insulator preventing free movement of splice with conductor | [Answer left blank] | There appear to be two splices on the west span (one on the north phase and one on the south phase) that appear to be within 2' of the insulators. There is one splice on the south span (east phase) that appears to be within 2' of the insulator. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101998386 | SANTA ROSA MM25 POLES | Sonoma(N) | 2021-04-20 | 6/3/2021 | 2022-01-06 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101998386 | SANTA ROSA MM25 POLES | Sonoma(N) | 2021-04-20 | 6/3/2021 | 2022-01-06 | Other Required Data: 3 or more splices present in one phase of the span | [Answer left blank] | There are four splices on the south span, all on the west phase. Span does not cross over a major roadway. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101998392 | SANTA ROSA MM25 POLES | Sonoma(N) | 2021-04-20 | 6/3/2021 | 2022-01-06 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | The pole number appears to be visible on pole. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101998392 | SANTA ROSA MM25 POLES | Sonoma(N) | 2021-04-20 | 6/3/2021 | 2022-01-06 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102014744 | SANTA ROSA MM25 POLES | Sonoma(N) | 2021-04-20 | 6/3/2021 | 2022-01-06 | Hardware and Framing: Is Hardware Framing present on this structure? | No | Yes, hardware is present on this pole. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102014746 | SANTA ROSA MM25 POLES | Sonoma(N) | 2021-04-20 | 6/3/2021 | 2022-01-06 | Conductor: Conductor has splices tied in proximity to insulator preventing free movement of splice with conductor | [Answer left blank] | There appears to be one splice within 2' of the insulator on the west (roadside) phase of the structure. | Agree | N/A | N¦A | 120854030 | Update a EC | Yes | No | Yes | No
102014746 | SANTA ROSA MM25 POLES | Sonoma(N) | 2021-04-20 | 6/3/2021 | 2022-01-06 | Common Equipment/Other Equipment: Does this structure have equipment? | No | There appear to be line fuse cutouts. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102014746 | SANTA ROSA MM25 POLES | Sonoma(N) | 2021-04-20 | 6/3/2021 | 2022-01-06 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102014758 | SANTA ROSA MM25 POLES | Sonoma(N) | 2021-04-20 | 6/3/2021 | 2022-01-06 | Anchor and Guys: Guy wire broken, damaged, clearance issues, corroded, covered by vegetation, overgrown, strain or abrasion | [Answer left blank] | The base of the guy wire is covered in dense and thorny vegetation. | Disagree | Inspector Selected Correcly | ELEC-1000 Training | Inspector indicated the down guy and base of pole were covered in vegetation in the both the Anchor & Guy's section and Vegetation section of the Inspection Record. Inspector also created an EC Notification (120854033) for these conditions | N\A | N\A | N\A | N\A | N\A
102014758 | SANTA ROSA MM25 POLES | Sonoma(N) | 2021-04-20 | 6/3/2021 | 2022-01-06 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | There appear to be open wire secondary at this location. | Disagree | Inspector Selected Correcly | ELEC-1000 Training | There is no secondary conductor on the pole. The other cables on the pole are at telecom level and run down the pole to a telecom junction box attachet at bottom 1/3 of pole. | N\A | N\A | N\A | N\A | N\A
101998345 | SANTA ROSA MM25 POLES | Sonoma(N) | 2021-04-21 | 6/3/2021 | 2022-01-06 | Structure: Pole leaning or out of plumb by more than 10% of its height above the ground | [Answer left blank] | The pole appears to be leaning by at least 10% of its height above the ground. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101998345 | SANTA ROSA MM25 POLES | Sonoma(N) | 2021-04-21 | 6/3/2021 | 2022-01-06 | Conductor: Conductor has splices tied in proximity to insulator preventing free movement of splice with conductor | [Answer left blank] | There appear to be splices tied within 2' of the insulators on the property-side and center phases on the north span. | Disagree | Condition is not compelling | ELEC-1000 Training | Splice is within 2' of dead end shoe therefore does not need room to allow free monement of splice with conductor. | N\A | N\A | N\A | N\A | N\A
101998345 | SANTA ROSA MM25 POLES | Sonoma(N) | 2021-04-21 | 6/3/2021 | 2022-01-06 | Hardware and Framing: Secondary connectors (mini wedge and Insulink) installed on primary conductor | [Answer left blank] | There appear to be mini wedge connectors on the primary conductors. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101998345 | SANTA ROSA MM25 POLES | Sonoma(N) | 2021-04-21 | 6/3/2021 | 2022-01-06 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102014733 | SANTA ROSA MM25 POLES | Sonoma(N) | 2021-04-21 | 6/3/2021 | 2022-01-06 | Conductor: Conductor has splices tied in proximity to insulator preventing free movement of splice with conductor | [Answer left blank] | The northeast phase appears to have two splices within 2' of the insulator. | Agree | N/A | N¦A | 120861933 | Update a EC | Yes | No | Yes | No
102014733 | SANTA ROSA MM25 POLES | Sonoma(N) | 2021-04-21 | 6/3/2021 | 2022-01-06 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101998329 | SANTA ROSA MM25 POLES | Sonoma(N) | 2021-04-22 | 6/3/2021 | 2022-01-06 | Conductor: Conductor has splices tied in proximity to insulator preventing free movement of splice with conductor | [Answer left blank] | The center phase of the south span has a splice that appears to be tied within 2' of the insulator. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101998329 | SANTA ROSA MM25 POLES | Sonoma(N) | 2021-04-22 | 6/3/2021 | 2022-01-06 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | There appears to be an open wire secondary at this location. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101998329 | SANTA ROSA MM25 POLES | Sonoma(N) | 2021-04-22 | 6/3/2021 | 2022-01-06 | Other Required Data: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101998329 | SANTA ROSA MM25 POLES | Sonoma(N) | 2021-04-22 | 6/3/2021 | 2022-01-06 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101998330 | SANTA ROSA MM25 POLES | Sonoma(N) | 2021-04-22 | 6/3/2021 | 2022-01-06 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | There appears to be an open wire secondary at this location. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101970195 | SANTA ROSA KK2625 POLES | Sonoma(N) | 2021-04-28 | 6/4/2021 | 2022-01-06 | Other Required Data: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101970197 | SANTA ROSA KK2625 POLES | Sonoma(N) | 2021-04-28 | 6/4/2021 | 2022-01-06 | Other Required Data: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | One transformer may contain PCB as there is no blue sticker. The other transformer has a blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101970197 | SANTA ROSA KK2625 POLES | Sonoma(N) | 2021-04-28 | 6/4/2021 | 2022-01-06 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100382459 | OROVILLE E26 POLES | North Valley(N) | 2021-05-01 | 2021-06-23 | 2022-01-06 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | The pole number is visible. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100382462 | OROVILLE E26 POLES | North Valley(N) | 2021-05-01 | 2021-06-23 | 2022-01-06 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | The pole number is visible. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103649674 | OROVILLE E26 POLES | North Valley(N) | 2021-05-01 | 2021-06-23 | 2022-01-06 | Vegetation: Does this structure have vegetation present? | No | There is vegetation near the base of the pole. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103649674 | OROVILLE E26 POLES | North Valley(N) | 2021-05-01 | 2021-06-23 | 2022-01-06 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | The pole number is visible. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103932599 | OROVILLE E26 POLES | North Valley(N) | 2021-05-01 | 2021-06-23 | 2022-01-06 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | The pole number is visible. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103984602 | OROVILLE E26 POLES | North Valley(N) | 2021-05-01 | 2021-06-23 | 2022-01-06 | Vegetation: Does this structure have vegetation present? | No | There is vegetation near the base of the pole. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103984602 | OROVILLE E26 POLES | North Valley(N) | 2021-05-01 | 2021-06-23 | 2022-01-06 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | The pole number is visible. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103995210 | OROVILLE E26 POLES | North Valley(N) | 2021-05-01 | 2021-06-23 | 2022-01-06 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | The pole number is visible. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
104009883 | OROVILLE E26 POLES | North Valley(N) | 2021-05-01 | 2021-06-23 | 2022-01-06 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | The pole number is visible. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
104007082 | OROVILLE E26 POLES | North Valley(N) | 2021-05-04 | 2021-06-23 | 2022-01-06 | Vegetation: Does this structure have vegetation present? | No | There is vegetation near the base of the asset. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
104007082 | OROVILLE E26 POLES | North Valley(N) | 2021-05-04 | 2021-06-23 | 2022-01-06 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | The pole number is visible. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
104007082 | OROVILLE E26 POLES | North Valley(N) | 2021-05-04 | 2021-06-23 | 2022-01-06 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
104007083 | OROVILLE E26 POLES | North Valley(N) | 2021-05-04 | 2021-06-23 | 2022-01-06 | Common Equipment/Other Equipment: Other equipment Inoperable (not operable) or Offline | [Answer left blank] | There appear to be idle cutouts on the pole. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
104007083 | OROVILLE E26 POLES | North Valley(N) | 2021-05-04 | 2021-06-23 | 2022-01-06 | Vegetation: Does this structure have vegetation present? | No | There is vegetation near the base of the pole. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
104007083 | OROVILLE E26 POLES | North Valley(N) | 2021-05-04 | 2021-06-23 | 2022-01-06 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | The pole number is visible. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
104007083 | OROVILLE E26 POLES | North Valley(N) | 2021-05-04 | 2021-06-23 | 2022-01-06 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
104007084 | OROVILLE E26 POLES | North Valley(N) | 2021-05-04 | 2021-06-23 | 2022-01-06 | Vegetation: Does this structure have vegetation present? | No | There is vegetation near the base of the pole. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
104007084 | OROVILLE E26 POLES | North Valley(N) | 2021-05-04 | 2021-06-23 | 2022-01-06 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | The pole number is visible. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
104008027 | OROVILLE E26 POLES | North Valley(N) | 2021-05-04 | 2021-06-23 | 2022-01-06 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | The pole number is visible. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
104008027 | OROVILLE E26 POLES | North Valley(N) | 2021-05-04 | 2021-06-23 | 2022-01-06 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
104008028 | OROVILLE E26 POLES | North Valley(N) | 2021-05-04 | 2021-06-23 | 2022-01-06 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | The pole number is visible. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100411023 | OROVILLE J26 POLES | North Valley(N) | 2021-05-05 | 2021-06-24 | 2022-01-06 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | The asset appears to have large cracks, including near where the hardware is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Single phase tangent pole with 9" brackets & hardware installed. | N\A | N\A | N\A | N\A | N\A
100411023 | OROVILLE J26 POLES | North Valley(N) | 2021-05-05 | 2021-06-24 | 2022-01-06 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100411014 | OROVILLE J26 POLES | North Valley(N) | 2021-05-06 | 2021-06-24 | 2022-01-06 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | The top of the pole appears to be deformed (twisted) and has large cracks. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100411014 | OROVILLE J26 POLES | North Valley(N) | 2021-05-06 | 2021-06-24 | 2022-01-06 | Structure: Pole leaning or out of plumb by more than 10% of its height above the ground | [Answer left blank] | The asset appears to be leaning more than 10% of its height. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100411014 | OROVILLE J26 POLES | North Valley(N) | 2021-05-06 | 2021-06-24 | 2022-01-06 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103021695 | OROVILLE J26 POLES | North Valley(N) | 2021-05-06 | 2021-06-24 | 2022-01-06 | Hardware and Framing: Tap clamps installed incorrectly | [Answer left blank] | The tap clamps do not appear to be installed on tap guards. | Agree | N/A | N¦A | 120947198 | Update a EC | Yes | No | Yes | No
100381176 | OROVILLE J26 POLES | North Valley(N) | 2021-05-07 | 2021-06-24 | 2022-01-06 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | The asset appears to have deep cracks along the entire length of the pole, including near where the hardware is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Single phase tangent pole with 9" brackets & hardware installed. | N\A | N\A | N\A | N\A | N\A
100381193 | OROVILLE J26 POLES | North Valley(N) | 2021-05-08 | 2021-06-24 | 2022-01-06 | Anchor and Guys: Does or should this location have a Guy? | No | The asset has a guy. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100381193 | OROVILLE J26 POLES | North Valley(N) | 2021-05-08 | 2021-06-24 | 2022-01-06 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100381196 | OROVILLE J26 POLES | North Valley(N) | 2021-05-08 | 2021-06-24 | 2022-01-06 | Hardware and Framing: Crossarm integrity compromised by any of the following; damaged, broken, burnt, decayed, rotten, loose, missing hardware or showing severe signs of bent bolts or brackets, damaged bracing, gun shots, insect damage or woodpecker damage, splitting, or fails to meet clearance requirements | [Answer left blank] | The crossarm hardware appears to be loose. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100411472 | OROVILLE J26 POLES | North Valley(N) | 2021-05-08 | 2021-06-24 | 2022-01-06 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | The pole has reduced circumference at the bottom 4 feet. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101017898 | MERCED MAP 07214D POLES | Yosemite(S) | 2021-05-10 | 2021-06-17 | 2022-01-06 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | Top of pole has several cracks around secondary bracket, and appears to show signs of decay. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101017898 | MERCED MAP 07214D POLES | Yosemite(S) | 2021-05-10 | 2021-06-17 | 2022-01-06 | Hardware and Framing: Select if there are risks, hazards or other maintenance conditions not previously captured in the checklist for Hardware Framing at this location | [Answer left blank] | Hardware for secondary bracket is loose. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101017898 | MERCED MAP 07214D POLES | Yosemite(S) | 2021-05-10 | 2021-06-17 | 2022-01-06 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100382453 | OROVILLE E26 POLES | North Valley(N) | 2021-05-11 | 2021-06-23 | 2022-01-06 | Vegetation: Does this structure have vegetation present? | No | There is vegetation near the base of the asset. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100403629 | OROVILLE E26 POLES | North Valley(N) | 2021-05-11 | 2021-06-23 | 2022-01-06 | Vegetation: Does this structure have vegetation present? | No | There is vegetation near the base of the asset. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
104007950 | OROVILLE E26 POLES | North Valley(N) | 2021-05-11 | 2021-06-23 | 2022-01-06 | Vegetation: Does this structure have vegetation present? | No | There is vegetation near the base of the asset. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
104007953 | OROVILLE E26 POLES | North Valley(N) | 2021-05-11 | 2021-06-23 | 2022-01-06 | Vegetation: Does this structure have vegetation present? | No | There is vegetation near the base of the asset. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101017836 | MERCED MAP 07214D POLES | Yosemite(S) | 2021-05-12 | 2021-06-17 | 2022-01-06 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Structure base[Answer left blank] | Agree | N/A | N¦A |  | Create "Other tag" | Yes | No | Yes | No
101017836 | MERCED MAP 07214D POLES | Yosemite(S) | 2021-05-17 | 2021-06-17 | 2022-01-06 | Other Required Data: Is there non-exempt equipment at the inspection location (Universal or Open Link Fuse) | [Answer left blank] | Non-exempt open link fuses are present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101017858 | MERCED MAP 07214D POLES | Yosemite(S) | 2021-05-12 | 2021-06-17 | 2022-01-06 | Other Required Data: Is there non-exempt equipment at the inspection location (Lightning or Surge Arrester) | [Answer left blank] | Non-exempt lightning arrestors appear to be present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101017858 | MERCED MAP 07214D POLES | Yosemite(S) | 2021-05-12 | 2021-06-17 | 2022-01-06 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101065978 | MERCED MAP 06191 POLES | Yosemite(S) | 2021-05-12 | 2021-06-16 | 2022-01-06 | Non-Time-Dependent Issues: Visibility strips missing, broken, mismatched, or no longer reflective | [Answer left blank] | Visibility strips are missing. | Agree | N/A | N¦A | 116760762 | Update a EC | Yes | No | Yes | No
101066048 | MERCED MAP 06191 POLES | Yosemite(S) | 2021-05-13 | 2021-06-16 | 2022-01-06 | Hardware and Framing: Tap clamps installed incorrectly | [Answer left blank] | Tap clamps are installed on primary conductor without tap guards. | Agree | N/A | N¦A | Condition is already attached to an EC Notification (116763152). Inspector did complete FSR to update Notification but did not indicate condition in Hardware section of Inspection Record. | N\A | N\A | N\A | N\A | N\A
101066074 | MERCED MAP 06191 POLES | Yosemite(S) | 2021-05-13 | 2021-06-16 | 2022-01-06 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | Top of pole has several cracks near where hardware is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Single phase tangent pole with 9" brackets & hardware and anti-split bolt installed. | N\A | N\A | N\A | N\A | N\A
101066076 | MERCED MAP 06191 POLES | Yosemite(S) | 2021-05-13 | 2021-06-16 | 2022-01-06 | Common Equipment/Other Equipment: Does this structure have equipment? | Yes | This pole does not have any equipment. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101066076 | MERCED MAP 06191 POLES | Yosemite(S) | 2021-05-13 | 2021-06-16 | 2022-01-06 | Anchor and Guys: Guy wire broken, damaged, clearance issues, corroded, covered by vegetation, overgrown, strain or abrasion | [Answer left blank] | Vegetation appears to be in contact with the guy above the guy insulator. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101066076 | MERCED MAP 06191 POLES | Yosemite(S) | 2021-05-13 | 2021-06-16 | 2022-01-06 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | Part of high voltage sign is not fully connected to the crossarm. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101066080 | MERCED MAP 06191 POLES | Yosemite(S) | 2021-05-13 | 2021-06-16 | 2022-01-06 | Hardware and Framing: Crossarm integrity compromised by any of the following; damaged, broken, burnt, decayed, rotten, loose, missing hardware or showing severe signs of bent bolts or brackets, damaged bracing, gun shots, insect damage or woodpecker damage, splitting, or fails to meet clearance requirements | [Answer left blank] | There is a loose bolt and washer on the crossarm. | Agree | N/A | N¦A | 121338106 | Update a EC | Yes | No | Yes | No
101074542 | MERCED MAP 04184 POLES | Yosemite(S) | 2021-05-13 | 2021-06-15 | 2022-01-06 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | Cracking is present throughout the pole, including near where the hardware is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Secondary pole with spool & clevis installed. | N\A | N\A | N\A | N\A | N\A
101074548 | MERCED MAP 04184 POLES | Yosemite(S) | 2021-05-13 | 2021-06-15 | 2022-01-06 | Vegetation: Tree causing strain or abrasion to secondary or service (only 1 service) | [Answer left blank] | Tree branch appears to be causing strain on service conductor | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101074548 | MERCED MAP 04184 POLES | Yosemite(S) | 2021-05-13 | 2021-06-15 | 2022-01-06 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103854401 | MERCED MAP 06191 POLES | Yosemite(S) | 2021-05-13 | 2021-06-15 | 2022-01-06 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | Cracks are present throughout the pole, including near where transformer hardware is attached. Top of pole shows signs of decay. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
103854401 | MERCED MAP 06191 POLES | Yosemite(S) | 2021-05-13 | 2021-06-15 | 2022-01-06 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | High voltage sign on one side of the pole appears to be loose. | Disagree | Condition is not compelling | 1. High Voltage Sign Not Installed as Required - TD-2305M-JA02, Rev. 8 - Pg. 61 | The one high sign in good condition on the opposite side of the pole satisfies the standard found in OH: Marking, Rev. #18: 11/01/18 022168 Page 3 of 35. Marking, Numbering, and Identification of Line Structures 3. Routine Inspection A. The requirement in 1, “Poles That Support Line Conductors,” must be satisfied with the following exceptions: 1. Sign the Pole: It is acceptable to have only one sign, or stacked pairs of signs, below the lowest line conductor energized above 750 V, except as noted in 4 “Special Locations.” B. The requirements in 2, Poles That Do Not Support Line Conductors,” must be satisfied with the following exceptions: 1. Risers: It is acceptable to have only one sign, or stacked pairs of signs, below risers energized above 750 V. 4. Special Locations: If the pole is signed, high-voltage signs are required on both sides of the pole in the following locations: Near water areas suitable for sailboats. Near established boat ramps and associated rigging areas. Adjacent to swimming pools. In agricultural areas with movable irrigation piping. Locations, where in the judgement of the employee, high-voltage signs should be visible from all sides of the poles. | N\A | N\A | N\A | N\A | N\A
101074176 | MERCED MAP 04184 POLES | Yosemite(S) | 2021-05-14 | 2021-06-15 | 2022-01-06 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are large cracks at the top of the pole, near where hardware is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Single phase tangent pole with 9" brackets & hardware and anti-split bolt installed. | N\A | N\A | N\A | N\A | N\A
101074176 | MERCED MAP 04184 POLES | Yosemite(S) | 2021-05-14 | 2021-06-15 | 2022-01-06 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101074508 | MERCED MAP 04184 POLES | Yosemite(S) | 2021-05-14 | 2021-06-15 | 2022-01-06 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are large cracks at the top of the pole, near where hardware is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Single phase tangent pole with 9" brackets & hardware and anti-split bolt installed. | N\A | N\A | N\A | N\A | N\A
101074508 | MERCED MAP 04184 POLES | Yosemite(S) | 2021-05-14 | 2021-06-15 | 2022-01-06 | Other Required Data: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | Yes | "Non-PCB" sticker is present on transformer. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101074508 | MERCED MAP 04184 POLES | Yosemite(S) | 2021-05-14 | 2021-06-15 | 2022-01-06 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | High voltage sign is missing from one side of the pole. Part of high voltage sign is missing from other side of the pole. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100353229 | PARADISE R3304 POLES | North Valley(N) | 2021-05-15 | 2021-06-22 | 2022-01-06 | Non-Time-Dependent Issues: Visibility strips missing, broken, mismatched, or no longer reflective | [Answer left blank] | There are only two visibility strips (instead of three), and they are no longer reflective. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100353231 | PARADISE R3304 POLES | North Valley(N) | 2021-05-15 | 2021-06-22 | 2022-01-06 | Hardware and Framing: Tap clamps installed incorrectly | [Answer left blank] | Tap clamps are installed without tap guards. | Agree | N/A | N¦A | Condition is already attached to an EC Notification (117085624). Inspector did complete FSR to update Notification but did not indicate condition in Hardware section of Inspection Record. | N\A | N\A | N\A | N\A | N\A
100353231 | PARADISE R3304 POLES | North Valley(N) | 2021-05-15 | 2021-06-22 | 2022-01-06 | Vegetation: Does this structure have vegetation present? | No | There is vegetation present surrounding the base of the pole. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100353231 | PARADISE R3304 POLES | North Valley(N) | 2021-05-15 | 2021-06-22 | 2022-01-06 | Other Required Data: Pole wrapped at ground-line at this location | Yes | Pole does not appear to be wrapped at ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100353233 | PARADISE R3304 POLES | North Valley(N) | 2021-05-15 | 2021-06-22 | 2022-01-06 | Vegetation: Does this structure have vegetation present? | No | There is vegetation present at the base of the pole. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100353274 | PARADISE R3304 POLES | North Valley(N) | 2021-05-15 | 2021-06-22 | 2022-01-06 | Non-Time-Dependent Issues: Pole steps are less than 8' 6" above the ground or any other accessible surface | [Answer left blank] | Pole step is at 7' 10" (94 inches). | Agree | N/A | N¦A | 111191580 | Update a EC | Yes | No | Yes | No
100353274 | PARADISE R3304 POLES | North Valley(N) | 2021-05-15 | 2021-06-22 | 2022-01-06 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | High voltage sign is missing on one side of the pole. | Disagree | Condition is not compelling | 1. High Voltage Sign Not Installed as Required - TD-2305M-JA02, Rev. 8 - Pg. 61 | The one high sign in good condition on the opposite side of the pole satisfies the standard found in OH: Marking, Rev. #18: 11/01/18 022168 Page 3 of 35. Marking, Numbering, and Identification of Line Structures 3. Routine Inspection A. The requirement in 1, “Poles That Support Line Conductors,” must be satisfied with the following exceptions: 1. Sign the Pole: It is acceptable to have only one sign, or stacked pairs of signs, below the lowest line conductor energized above 750 V, except as noted in 4 “Special Locations.” B. The requirements in 2, Poles That Do Not Support Line Conductors,” must be satisfied with the following exceptions: 1. Risers: It is acceptable to have only one sign, or stacked pairs of signs, below risers energized above 750 V. 4. Special Locations: If the pole is signed, high-voltage signs are required on both sides of the pole in the following locations: Near water areas suitable for sailboats. Near established boat ramps and associated rigging areas. Adjacent to swimming pools. In agricultural areas with movable irrigation piping. Locations, where in the judgement of the employee, high-voltage signs should be visible from all sides of the poles. | N\A | N\A | N\A | N\A | N\A
100353284 | PARADISE R3304 POLES | North Valley(N) | 2021-05-15 | 2021-06-22 | 2022-01-07 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There is a large crack at the top of the pole near where hardware is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Single phase dead end pole with steel crossarm & hardware and anti-split bolt installed. | N\A | N\A | N\A | N\A | N\A
100353284 | PARADISE R3304 POLES | North Valley(N) | 2021-05-15 | 2021-06-22 | 2022-01-07 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | High voltage sign on one side of the pole is missing. | Disagree | Condition is not compelling | 1. High Voltage Sign Not Installed as Required - TD-2305M-JA02, Rev. 8 - Pg. 61 | The one high sign in good condition on the opposite side of the pole satisfies the standard found in OH: Marking, Rev. #18: 11/01/18 022168 Page 3 of 35. Marking, Numbering, and Identification of Line Structures 3. Routine Inspection A. The requirement in 1, “Poles That Support Line Conductors,” must be satisfied with the following exceptions: 1. Sign the Pole: It is acceptable to have only one sign, or stacked pairs of signs, below the lowest line conductor energized above 750 V, except as noted in 4 “Special Locations.” B. The requirements in 2, Poles That Do Not Support Line Conductors,” must be satisfied with the following exceptions: 1. Risers: It is acceptable to have only one sign, or stacked pairs of signs, below risers energized above 750 V. 4. Special Locations: If the pole is signed, high-voltage signs are required on both sides of the pole in the following locations: Near water areas suitable for sailboats. Near established boat ramps and associated rigging areas. Adjacent to swimming pools. In agricultural areas with movable irrigation piping. Locations, where in the judgement of the employee, high-voltage signs should be visible from all sides of the poles. | N\A | N\A | N\A | N\A | N\A
100353287 | PARADISE R3304 POLES | North Valley(N) | 2021-05-15 | 2021-06-22 | 2022-01-07 | Non-Time-Dependent Issues: Pole steps are less than 8' 6" above the ground or any other accessible surface | [Answer left blank] | Pole step is at 8'1" (97 inches). | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100353294 | PARADISE R3304 POLES | North Valley(N) | 2021-05-15 | 2021-06-22 | 2022-01-07 | Common Equipment/Other Equipment: IFD (aka "Turkey Popper") has activated on the transformer (orange band is visible) | [Answer left blank] | The turkey popper appears to have been activated as the orange band is visible. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100353294 | PARADISE R3304 POLES | North Valley(N) | 2021-05-15 | 2021-06-22 | 2022-01-07 | Non-Time-Dependent Issues: Visibility strips missing, broken, mismatched, or no longer reflective | [Answer left blank] | Visibility strips are missing. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100353294 | PARADISE R3304 POLES | North Valley(N) | 2021-05-15 | 2021-06-22 | 2022-01-07 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | High voltage sign on one side of the pole is missing. | Disagree | Condition is not compelling | 1. High Voltage Sign Not Installed as Required - TD-2305M-JA02, Rev. 8 - Pg. 61 | The one high sign in good condition on the opposite side of the pole satisfies the standard found in OH: Marking, Rev. #18: 11/01/18 022168 Page 3 of 35. Marking, Numbering, and Identification of Line Structures 3. Routine Inspection A. The requirement in 1, “Poles That Support Line Conductors,” must be satisfied with the following exceptions: 1. Sign the Pole: It is acceptable to have only one sign, or stacked pairs of signs, below the lowest line conductor energized above 750 V, except as noted in 4 “Special Locations.” B. The requirements in 2, Poles That Do Not Support Line Conductors,” must be satisfied with the following exceptions: 1. Risers: It is acceptable to have only one sign, or stacked pairs of signs, below risers energized above 750 V. 4. Special Locations: If the pole is signed, high-voltage signs are required on both sides of the pole in the following locations: Near water areas suitable for sailboats. Near established boat ramps and associated rigging areas. Adjacent to swimming pools. In agricultural areas with movable irrigation piping. Locations, where in the judgement of the employee, high-voltage signs should be visible from all sides of the poles. | N\A | N\A | N\A | N\A | N\A
101074487 | MERCED MAP 04184 POLES | Yosemite(S) | 2021-05-15 | 2021-06-15 | 2022-01-07 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | A deep crack is present at top of pole near where hardware is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Single phase tangent pole with 9" brackets & hardware installed. | N\A | N\A | N\A | N\A | N\A
103363880 | MERCED MAP 06191 POLES | Yosemite(S) | 2021-05-15 | 2021-06-16 | 2022-01-07 | Hardware and Framing: Animal mitigation broken, damaged, or missing (if required) | [Answer left blank] | Animal mitigation is not closed. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
103574870 | PARADISE R3304 POLES | North Valley(N) | 2021-05-15 | 2021-06-22 | 2022-01-07 | Conductor: Primary, secondary, and/or service conductors broken, damaged, burnt, corroded, loose, frayed or bird caging | [Answer left blank] | On the primary conductor span traveling south, both the east and west phases appear to have bird caging. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101066098 | MERCED MAP 06191 POLES | Yosemite(S) | 2021-05-17 | 2021-06-16 | 2022-01-07 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | Several cracks are present throughout the pole, including around transformer and bracket hardware. Pole top also appears to show signs of decay. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Single phase tangent pole with 9" brackets & hardware and anti-split bolt installed. | N\A | N\A | N\A | N\A | N\A
101066098 | MERCED MAP 06191 POLES | Yosemite(S) | 2021-05-17 | 2021-06-16 | 2022-01-07 | Hardware and Framing: Tap clamps installed incorrectly | [Answer left blank] | Tap clamps are attached to armor rod rather than tap guards. | Agree | N/A | N¦A | 116756896 | Update a EC | Yes | No | Yes | No
101074555 | MERCED MAP 04184 POLES | Yosemite(S) | 2021-05-17 | 2021-06-16 | 2022-01-07 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | Top third of the pole has several cracks, including near where crossarm is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Single phase tangent pole with 9" brackets & hardware and anti-split bolt installed. | N\A | N\A | N\A | N\A | N\A
101074555 | MERCED MAP 04184 POLES | Yosemite(S) | 2021-05-17 | 2021-06-15 | 2022-01-07 | Anchor and Guys: Necessary guys missing or loose | [Answer left blank] | Down guy is loose and not under tension. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101074560 | MERCED MAP 04184 POLES | Yosemite(S) | 2021-05-17 | 2021-06-15 | 2022-01-07 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | Top third of pole has several cracks, including near where hardware is attached. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101074564 | MERCED MAP 04184 POLES | Yosemite(S) | 2021-05-17 | 2021-06-15 | 2022-01-07 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | Middle third and top third of pole have deep cracks. A woodpecker hole greater than 4” is located in middle of pole. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101074567 | MERCED MAP 04184 POLES | Yosemite(S) | 2021-05-17 | 2021-06-15 | 2022-01-07 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | Top third of pole has several cracks, including near where hardware is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Single phase tangent pole with 9" brackets & hardware installed. | N\A | N\A | N\A | N\A | N\A
104007955 | OROVILLE E27 POLES | North Valley(N) | 2021-05-18 | 2021-06-23 | 2022-01-07 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | The pole number is visible. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
104008173 | OROVILLE E27 POLES | North Valley(N) | 2021-05-18 | 2021-06-23 | 2022-01-07 | Conductor: Does this structure have PG&E owned conductor? | No | There appear to be two PG&E owned conductors on the structure. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
104008173 | OROVILLE E27 POLES | North Valley(N) | 2021-05-18 | 2021-06-23 | 2022-01-07 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | The pole number is visible. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
104008174 | OROVILLE E27 POLES | North Valley(N) | 2021-05-18 | 2021-06-23 | 2022-01-07 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | The pole number is visible. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
104008175 | OROVILLE E27 POLES | North Valley(N) | 2021-05-18 | 2021-06-23 | 2022-01-07 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | The pole number is visible. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
104008176 | OROVILLE E27 POLES | North Valley(N) | 2021-05-18 | 2021-06-23 | 2022-01-07 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | The pole number is visible. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103964095 | PARADISE T3406 POLES | North Valley(N) | 2021-05-19 | 2021-06-23 | 2022-01-07 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | The pole number is visible. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103964098 | PARADISE T3406 POLES | North Valley(N) | 2021-05-19 | 2021-06-23 | 2022-01-07 | Common Equipment/Other Equipment: Does this structure have equipment? | Yes | The pole does not appear to have equipment. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100329314 | PARADISE T3310 POLES | North Valley(N) | 2021-05-20 | 2021-06-23 | 2022-01-07 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | Top third of pole has several cracks, including near where hardware is attached. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101020130 | MERCED MAP 07214D POLES | Yosemite(S) | 2021-05-20 | 2021-06-17 | 2022-01-07 | Hardware and Framing: Animal mitigation broken, damaged, or missing (if required) | [Answer left blank] | Animal mitigation is not closed. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
103932586 | MERCED MAP 07214D POLES | Yosemite(S) | 2021-05-20 | 2021-06-17 | 2022-01-07 | Hardware and Framing: Animal mitigation broken, damaged, or missing (if required) | [Answer left blank] | Animal mitigation is not closed. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
103953664 | PARADISE T3406 POLES | North Valley(N) | 2021-05-20 | 2021-06-23 | 2022-01-07 | Anchor and Guys: Does or should this location have a Guy? | No | This location has guys anchored to the ground and overhead. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101020139 | MERCED MAP 07214D POLES | Yosemite(S) | 2021-05-24 | 2021-06-17 | 2022-01-07 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | Top of the pole has deep cracks and appears to show signs of decay. | Agree | N/A | N¦A | Condition is already attached to an EC Notification (117208424). Inspector did complete FSR to update Notification but did not indicate condition in Structure section of Inspection Record. | Update a EC | Yes | No | Yes | No
101020139 | MERCED MAP 07214D POLES | Yosemite(S) | 2021-05-24 | 2021-06-17 | 2022-01-07 | Hardware and Framing: Secondary connectors (mini wedge and Insulink) installed on primary conductor | [Answer left blank] | Secondary Insulink connectors are present on primary jumpers. | Agree | N/A | N¦A | Condition is already attached to an EC Notification (117208424). Inspector did complete FSR to update Notification but did not indicate condition in Hardware section of Inspection Record. | Update a EC | Yes | No | Yes | No
101020139 | MERCED MAP 07214D POLES | Yosemite(S) | 2021-05-24 | 2021-06-17 | 2022-01-07 | Hardware and Framing: Tap clamps installed incorrectly | [Answer left blank] | Tap clamps are installed without tap guards. | Agree | N/A | N¦A | Condition is already attached to an EC Notification (117208424). Inspector did complete FSR to update Notification but did not indicate condition in Hardware section of Inspection Record. | Update a EC | Yes | No | Yes | No
101020139 | MERCED MAP 07214D POLES | Yosemite(S) | 2021-05-24 | 2021-06-17 | 2022-01-07 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | Pole appears to be wrapped at the ground-line | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103343085 | MERCED MAP 07214D POLES | Yosemite(S) | 2021-05-24 | 2021-06-17 | 2022-01-07 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There is a woodpecker hole greater than 4” near the transformer brackets. | Agree | N/A | N¦A | Condition is already attached to an EC Notification (117210216). Inspector did complete FSR to update Notification but did not indicate condition in Structure section of Inspection Record. | Update a EC | Yes | No | Yes | No
103343085 | MERCED MAP 07214D POLES | Yosemite(S) | 2021-05-24 | 2021-06-17 | 2022-01-07 | Hardware and Framing: Animal mitigation broken, damaged, or missing (if required) | [Answer left blank] | Animal mitigation is not closed. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100326429 | PARADISE T3407 POLES | North Valley(N) | 2021-05-28 | 2021-06-17 | 2022-01-07 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are several large woodpecker holes at the top of the pole. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100326429 | PARADISE T3407 POLES | North Valley(N) | 2021-05-28 | 2021-06-17 | 2022-01-07 | Anchor and Guys: Necessary guys missing or loose | [Answer left blank] | The guy wire appears to be loose. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100326429 | PARADISE T3407 POLES | North Valley(N) | 2021-05-28 | 2021-06-17 | 2022-01-07 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | Pole appears to be wrapped at the ground-line | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103935030 | PARADISE T3407 POLES | North Valley(N) | 2021-05-28 | 2021-06-17 | 2022-01-07 | Anchor and Guys: Necessary guys missing or loose | [Answer left blank] | The guy wire appears to be loose. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
7.20 REPORT
100085429 | PLACER T0923 POLES | Sierra(N) | 2021-04-06 | 2021-05-17 | 2022-01-07 | Other Required Data: 3 or more splices present in one phase of the span | [Answer left blank] | Other Required Data: 3 or more splices present in one phase of the span | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101409775 | EL DORADO I3915 POLES | Sierra(N) | 2021-04-06 | 2021-05-25 | 2022-01-07 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | High voltage sign missing on one side of the pole. | Disagree | Condition is not compelling | 1. High Voltage Sign Not Installed as Required - TD-2305M-JA02, Rev. 8 - Pg. 61 | The one high sign in good condition on the opposite side of the pole satisfies the standard found in OH: Marking, Rev. #18: 11/01/18 022168 Page 3 of 35. Marking, Numbering, and Identification of Line Structures 3. Routine Inspection A. The requirement in 1, “Poles That Support Line Conductors,” must be satisfied with the following exceptions: 1. Sign the Pole: It is acceptable to have only one sign, or stacked pairs of signs, below the lowest line conductor energized above 750 V, except as noted in 4 “Special Locations.” B. The requirements in 2, Poles That Do Not Support Line Conductors,” must be satisfied with the following exceptions: 1. Risers: It is acceptable to have only one sign, or stacked pairs of signs, below risers energized above 750 V. 4. Special Locations: If the pole is signed, high-voltage signs are required on both sides of the pole in the following locations: Near water areas suitable for sailboats. Near established boat ramps and associated rigging areas. Adjacent to swimming pools. In agricultural areas with movable irrigation piping. Locations, where in the judgement of the employee, high-voltage signs should be visible from all sides of the poles. | N\A | N\A | N\A | N\A | N\A
100263416 | PENINSULA B0617 POLES | Peninsula(C) | 2021-04-07 | 2021-05-12 | 2022-01-07 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Dried vegetation is present within 10 feet of pole with non-exempt line fuses on it. | Disagree | N/A | ELEC-1000 Training | PG&E Inspection was completed Prior to the start of the 2021 fire season. Questions in the Inspect app related to vegetation in proximity to pole with Non-Exempt Equipment would not have been available for the inspector to answer until May 1st. | N\A | N\A | N\A | N\A | N\A
100263416 | PENINSULA B0617 POLES | Peninsula(C) | 2021-04-07 | 2021-05-12 | 2022-01-07 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground-line | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100313758 | PENINSULA B0617 POLES | Peninsula(C) | 2021-04-08 | 2021-05-12 | 2022-01-07 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground-line | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101383829 | EL DORADO I3909 POLES | Sierra(N) | 2021-04-08 | 2021-05-25 | 2022-01-07 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | High voltage sign is missing on one side of the pole. | Disagree | Condition is not compelling | 1. High Voltage Sign Not Installed as Required - TD-2305M-JA02, Rev. 8 - Pg. 61 | The one high sign in good condition on the opposite side of the pole satisfies the standard found in OH: Marking, Rev. #18: 11/01/18 022168 Page 3 of 35. Marking, Numbering, and Identification of Line Structures 3. Routine Inspection A. The requirement in 1, “Poles That Support Line Conductors,” must be satisfied with the following exceptions: 1. Sign the Pole: It is acceptable to have only one sign, or stacked pairs of signs, below the lowest line conductor energized above 750 V, except as noted in 4 “Special Locations.” B. The requirements in 2, Poles That Do Not Support Line Conductors,” must be satisfied with the following exceptions: 1. Risers: It is acceptable to have only one sign, or stacked pairs of signs, below risers energized above 750 V. 4. Special Locations: If the pole is signed, high-voltage signs are required on both sides of the pole in the following locations: Near water areas suitable for sailboats. Near established boat ramps and associated rigging areas. Adjacent to swimming pools. In agricultural areas with movable irrigation piping. Locations, where in the judgement of the employee, high-voltage signs should be visible from all sides of the poles. | N\A | N\A | N\A | N\A | N\A
100030384 | PLACER S1023 POLES | Sierra(N) | 2021-04-14 | 2021-05-19 | 2022-01-07 | Other Required Data: 3 or more splices present in one phase of the span | [Answer left blank] | There appear to be 6 splices on the west span, with 3 on the north phase and 3 on the south phase. Span does not cross over a major roadway.The Monitor team also notes this potential exception to an adjacent asset (Equipment No. 100030385). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100030385 | PLACER S1023 POLES | Sierra(N) | 2021-04-14 | 2021-05-19 | 2022-01-07 | Other Required Data: 3 or more splices present in one phase of the span | [Answer left blank] | There appear to be 6 splices on the west span, with 3 on the north phase and 3 on the south phase. Span does not cross over a major roadway.The Monitor team also notes this potential exception to an adjacent asset (Equipment No. 100030384). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100276316 | PENINSULA E0709 POLES | Peninsula(C) | 2021-04-14 | 2021-05-13 | 2022-01-07 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground-line | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100276316 | PENINSULA E0709 POLES | Peninsula(C) | 2021-04-14 | 2021-05-13 | 2022-01-07 | Other Required Data: 3 or more splices present in one phase of the span | [Answer left blank] | There are 3 splices on the north span, with all 3 splices on the west phase. Span does not cross over a major roadway. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101378947 | EL DORADO I3807 POLES | Sierra(N) | 2021-04-14 | 2021-05-24 | 2022-01-10 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground-line | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100276303 | PENINSULA E0709 POLES | Peninsula(C) | 2021-04-15 | 2021-05-13 | 2022-01-10 | Other Required Data: 3 or more splices present in one phase of the span | [Answer left blank] | There are 3 splices on the north span, with all 3 splices on the west phase. Span does not cross over a major roadway. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100030380 | PLACER S1023 POLES | Sierra(N) | 2021-04-17 | 2021-05-19 | 2022-01-10 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | One of the high voltage signs is missing the word “high.” | Disagree | Condition is not compelling | 1. High Voltage Sign Not Installed as Required - TD-2305M-JA02, Rev. 8 - Pg. 61 | The one high sign in good condition on the opposite side of the pole satisfies the standard found in OH: Marking, Rev. #18: 11/01/18 022168 Page 3 of 35. Marking, Numbering, and Identification of Line Structures 3. Routine Inspection A. The requirement in 1, “Poles That Support Line Conductors,” must be satisfied with the following exceptions: 1. Sign the Pole: It is acceptable to have only one sign, or stacked pairs of signs, below the lowest line conductor energized above 750 V, except as noted in 4 “Special Locations.” B. The requirements in 2, Poles That Do Not Support Line Conductors,” must be satisfied with the following exceptions: 1. Risers: It is acceptable to have only one sign, or stacked pairs of signs, below risers energized above 750 V. 4. Special Locations: If the pole is signed, high-voltage signs are required on both sides of the pole in the following locations: Near water areas suitable for sailboats. Near established boat ramps and associated rigging areas. Adjacent to swimming pools. In agricultural areas with movable irrigation piping. Locations, where in the judgement of the employee, high-voltage signs should be visible from all sides of the poles. | N\A | N\A | N\A | N\A | N\A
100073147 | PLACER S1023 POLES | Sierra(N) | 2021-04-17 | 2021-05-19 | 2022-01-10 | Other Required Data: 3 or more splices present in one phase of the span | [Answer left blank] | There are 3 splices on the north span, all on the west phase. Span does not cross over a major roadway. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103975319 | PLACER T0612 POLES | Sierra(N) | 2021-04-20 | 2021-05-20 | 2022-01-10 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground-line | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100029188 | PLACER S0911 POLES | Sierra(N) | 2021-04-22 | 2021-05-19 | 2022-01-10 | Other Required Data: 3 or more splices present in one phase of the span | [Answer left blank] | There are 4 splices on the south span, with 3 splices on the west phase and 1 splice on the east phase. Span does not cross over a major roadway. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100273492 | PENINSULA F0806 POLES | Peninsula(C) | 2021-04-23 | 2021-05-11 | 2022-01-10 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | One of the high voltage signs is missing the word “high.” | Agree | N/A | N¦A | 120876962 | Update a EC | Yes | No | Yes | No
100273957 | PENINSULA E0710 POLES | Peninsula(C) | 2021-04-27 | 2021-05-13 | 2022-01-10 | Other Required Data: 3 or more splices present in one phase of the span | [Answer left blank] | There are 10 splices on the east span, with 2 splices on the south phase, 4 splices on the center phase, and 4 splices on the north phase. Span does not cross over a major roadway. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103034261 | EL DORADO J3812 POLES | Sierra(N) | 2021-04-30 | 2021-05-27 | 2022-01-10 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole does not appear to be wrapped at the ground-line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101374613 | EL DORADO MAP K3805 POLES | Sierra(N) | 2021-03-24 | 2021-05-26 | 2022-01-10 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | here appear to be deep cracks (approximately 4 to 5") in pole from base to approximately 15' up the pole. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Single phase dead end line & buck pole with wood crossarm & hardware installed. | N\A | N\A | N\A | N\A | N\A
103914522 | EL DORADO MAP K3805 POLES | Sierra(N) | 2021-03-24 | 2021-05-26 | 2022-01-10 | Hardware and Framing: Animal mitigation broken, damaged, or missing (if required) | [Answer left blank] | Wildlife mitigation on top of transformer bushings appears loose. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
103914522 | EL DORADO MAP K3805 POLES | Sierra(N) | 2021-03-24 | 2021-05-26 | 2022-01-10 | Vegetation: Does this structure have vegetation present? | No | Yes, there appears to be vegetation at the base of the structure within a ten foot radius. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101374462 | EL DORADO MAP K3805 POLES | Sierra(N) | 2021-03-25 | 2021-05-26 | 2022-01-10 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There appears to be a deep crack (approximately 4") from ground to about halfway up the pole. There are also cracks at the top of the pole near the crossarm hardware attachment. | Agree | N/A | N¦A | 117108062 | Update a EC | Yes | No | Yes | No
101374462 | EL DORADO MAP K3805 POLES | Sierra(N) | 2021-03-25 | 2021-05-26 | 2022-01-10 | Vegetation: Tree causing strain or abrasion to secondary or service (only 1 service) | [Answer left blank] | Vegetation appears to be causing strain on service conductor in two locations. | Agree | N/A | N¦A | 117108062 | Update a EC | Yes | No | Yes | No
101384474 | EL DORADO J3812 POLES | Sierra(N) | 2021-03-30 | 2021-05-27 | 2022-01-10 | Hardware and Framing: Animal mitigation broken, damaged, or missing (if required) | [Answer left blank] | Animal mitigation is missing. | Agree | N/A | N¦A | 120712153 | Update a EC | Yes | No | Yes | No
101384474 | EL DORADO J3812 POLES | Sierra(N) | 2021-03-30 | 2021-05-27 | 2022-01-10 | Other Required Data: Is there non-exempt equipment at the inspection location (Universal or Open Link Fuse) | [Answer left blank] | There is a non-exempt universal link fuse on the asset. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101384474 | EL DORADO J3812 POLES | Sierra(N) | 2021-03-30 | 2021-05-27 | 2022-01-10 | Other Required Data: Is there non-exempt equipment at the inspection location (Lightning or Surge Arrester) | [Answer left blank] | There is a non-exempt lightning arrester on the asset. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101384474 | EL DORADO J3812 POLES | Sierra(N) | 2021-03-30 | 2021-05-27 | 2022-01-10 | Vegetation: Support Structure with non-exempt equipment, has dried vegetation from ground to 8' above ground, within 10' radius of Support Structure base | [Answer left blank] | Dried vegetation is present within 10 feet of pole with non-exempt universal link fuse on it. | Disagree | N/A | ELEC-1000 Training | PG&E Inspection was completed Prior to the start of the 2021 fire season. Questions in the Inspect app related to vegetation in proximity to pole with Non-Exempt Equipment would not have been available for the inspector to answer until May 1st. | N\A | N\A | N\A | N\A | N\A
101384477 | EL DORADO J3812 POLES | Sierra(N) | 2021-03-30 | 2021-05-27 | 2022-01-10 | Anchor and Guys: Does or should this location have a Guy? | No | Yes, there is an overhead guy on the pole. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101384477 | EL DORADO J3812 POLES | Sierra(N) | 2021-03-30 | 2021-05-27 | 2022-01-10 | Other Required Data: Is there non-exempt equipment at the inspection location (Universal or Open Link Fuse) | [Answer left blank] | There is a non-exempt universal link fuse present on the asset. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101384477 | EL DORADO J3812 POLES | Sierra(N) | 2021-03-30 | 2021-05-27 | 2022-01-10 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Dried vegetation is present within 10 feet of pole with non-exempt universal link fuse on it. | Disagree | N/A | ELEC-1000 Training | PG&E Inspection was completed Prior to the start of the 2021 fire season. Questions in the Inspect app related to vegetation in proximity to pole with Non-Exempt Equipment would not have been available for the inspector to answer until May 1st. | N\A | N\A | N\A | N\A | N\A
100295585 | PENINSULA F0802 POLES | Peninsula(C) | 2021-03-31 | 2021-05-11 | 2022-01-10 | Anchor and Guys: Does or should this location have a Guy? | No | Yes, this location has a guy. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100304570 | PENINSULA F0802 POLES | Peninsula(C) | 2021-03-31 | 2021-05-11 | 2022-01-10 | Other Required Data: Is there non-exempt equipment at the inspection location (Universal or Open Link Fuse) | Yes | The fuse cutout on the asset is exempt. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101413973 | EL DORADO J3824 POLES | Sierra(N) | 2021-03-31 | 2021-05-26 | 2022-01-10 | PromptPG&E Inspection Form ResponseMonitor Team CommentsStructure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There is a large crack from the top of the pole to where the lower crossarm hardware is attached, as well as large cracks along the entire length of the pole. | Agree | N/A | N¦A | 119710960 | Update a EC | Yes | No | Yes | No
101384617 | EL DORADO J3811 POLES | Sierra(N) | 2021-04-01 | 2021-05-27 | 2022-01-11 | Common Equipment/Other Equipment: Does this structure have equipment? | No | Yes, structure appears to have equipment, specifically a line fuse cutout. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101384617 | EL DORADO J3811 POLES | Sierra(N) | 2021-04-01 | 2021-05-27 | 2022-01-11 | Anchor and Guys: Guy wire broken, damaged, clearance issues, corroded, covered by vegetation, overgrown, strain or abrasion | [Answer left blank] | Vegetation around down guy wire appears to be overgrown and in contact with the down guy wire above the insulator. | Agree | N/A | N¦A | 120724080 | Update a EC | Yes | No | Yes | No
101384622 | EL DORADO J3811 POLES | Sierra(N) | 2021-04-01 | 2021-05-27 | 2022-01-11 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are significant cracks in the top third of the pole, where the transformer and both crossarms are attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Single phase dead end corner pole with steel crossarms & hardware installed. | N\A | N\A | N\A | N\A | N\A
100022576 | NEVADA R0825 POLES | Sierra(N) | 2021-04-02 | 2021-05-18 | 2022-01-11 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | The pole appears to be cracked near the top of the pole and shows signs of decay. | Agree | N/A | N¦A | 117095373 | Update a EC | Yes | No | Yes | No
100022576 | NEVADA R0825 POLES | Sierra(N) | 2021-04-02 | 2021-05-18 | 2022-01-11 | Other Required Data: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100022576 | NEVADA R0825 POLES | Sierra(N) | 2021-04-02 | 2021-05-18 | 2022-01-11 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | Part of the high voltage sign is missing from the north side of the pole. | Disagree | Condition is not compelling | 1. High Voltage Sign Not Installed as Required - TD-2305M-JA02, Rev. 8 - Pg. 61 | The one high sign in good condition on the opposite side of the pole satisfies the standard found in OH: Marking, Rev. #18: 11/01/18 022168 Page 3 of 35. Marking, Numbering, and Identification of Line Structures 3. Routine Inspection A. The requirement in 1, “Poles That Support Line Conductors,” must be satisfied with the following exceptions: 1. Sign the Pole: It is acceptable to have only one sign, or stacked pairs of signs, below the lowest line conductor energized above 750 V, except as noted in 4 “Special Locations.” B. The requirements in 2, Poles That Do Not Support Line Conductors,” must be satisfied with the following exceptions: 1. Risers: It is acceptable to have only one sign, or stacked pairs of signs, below risers energized above 750 V. 4. Special Locations: If the pole is signed, high-voltage signs are required on both sides of the pole in the following locations: Near water areas suitable for sailboats. Near established boat ramps and associated rigging areas. Adjacent to swimming pools. In agricultural areas with movable irrigation piping. Locations, where in the judgement of the employee, high-voltage signs should be visible from all sides of the poles. | N\A | N\A | N\A | N\A | N\A
100022577 | NEVADA R0825 POLES | Sierra(N) | 2021-04-02 | 2021-05-18 | 2022-01-11 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | The pole number appears to be missing. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101413984 | EL DORADO J3824 POLES | Sierra(N) | 2021-04-02 | 2021-05-26 | 2022-01-11 | Vegetation: Tree causing strain or abrasion to secondary or service (only 1 service) | [Answer left blank] | Vegetation appears to be causing strain on service conductor heading east from pole. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101413984 | EL DORADO J3824 POLES | Sierra(N) | 2021-04-02 | 2021-05-26 | 2022-01-11 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole does not appear to be wrapped at the ground-line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100022585 | NEVADA R0825 POLES | Sierra(N) | 2021-04-03 | 2021-05-18 | 2022-01-11 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are cracks near the top the pole and signs of decay near the hardware. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100022585 | NEVADA R0825 POLES | Sierra(N) | 2021-04-03 | 2021-05-18 | 2022-01-11 | Non-Time-Dependent Issues: Pole steps are less than 8' 6" above the ground or any other accessible surface | [Answer left blank] | Pole step is at 7’ 3” (87 inches). | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100022585 | NEVADA R0825 POLES | Sierra(N) | 2021-04-03 | 2021-05-18 | 2022-01-11 | Other Required Data: Is there non-exempt equipment at the inspection location (Solid Blade or In-line disconnect) | [Answer left blank] | There appear to be non-exempt in-line disconnects on the structure. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100022585 | NEVADA R0825 POLES | Sierra(N) | 2021-04-03 | 2021-05-18 | 2022-01-11 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | High voltage sign is missing from the north side of the pole. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100022586 | NEVADA R0825 POLES | Sierra(N) | 2021-04-03 | 2021-05-18 | 2022-01-11 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There appear to be multiple woodpecker holes near the middle of the pole. Two holes appear to be greater than 4". | Agree | N/A | N¦A | Pole currently has existing Notification (117095898) for damage to pole. Inspector did not update existing EC Notification. Inspector created new EC Notification (120740023) for additional conditions found during inspection. | Update a EC | N\A | N\A | N\A | N\A
100022586 | NEVADA R0825 POLES | Sierra(N) | 2021-04-03 | 2021-05-18 | 2022-01-11 | Non-Time-Dependent Issues: Pole steps are less than 8' 6" above the ground or any other accessible surface | [Answer left blank] | Pole step is at 8’ 4” (100 inches). | Agree | N/A | N¦A | Pole currently has existing Notification (117095898) for damage to pole. Inspector did not update existing EC | Update a EC | N\A | N\A | N\A | N\A
100022586 | NEVADA R0825 POLES | Sierra(N) | 2021-04-03 | 2021-05-18 | 2022-01-11 | Other Required Data: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101382731 | EL DORADO J3824 POLES | Sierra(N) | 2021-04-03 | 2021-05-26 | 2022-01-11 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | showing signs of cracking, rotten or decay [Answer left blank] | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Three phase tangent pole with king pin, wood crossarm & hardware installed. | N\A | N\A | N\A | N\A | N\A
101382731 | EL DORADO J3824 POLES | Sierra(N) | 2021-04-03 | 2021-05-26 | 2022-01-11 | Conductor: Conductor has splices tied in proximity to insulator preventing free movement of splice with conductorConductor: Conductor has splices tied in proximity to insulator preventing free movement of splice with conductor | [Answer left blank] | On the south span, one splice appears to be within two feet of the insulator on the east phase and one splice appears to be within two feet of the insulator on the west phase. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101382731 | EL DORADO J3824 POLES | Sierra(N) | 2021-04-03 | 2021-05-26 | 2022-01-11 | Vegetation: Tree causing strain or abrasion to secondary or service (2 or more services) | [Answer left blank] | Vegetation appears to be causing strain on a service conductor heading east and on a service conductor heading west from the pole. | Agree | N/A | N¦A |  | Create "Other tag" | Yes | No | Yes | No
101383966 | EL DORADO I3910 POLES | Sierra(N) | 2021-04-03 | 2021-05-25 | 2022-01-11 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | showing signs of cracking, rotten or decay [Answer left blank] | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Single phase tangent pole with 9" brackets, anti-split bolt and steel crossarm & hardware installed. | N\A | N\A | N\A | N\A | N\A
100085430 | PLACER T0923 POLES | Sierra(N) | 2021-04-06 | 2021-05-17 | 2022-01-11 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | The pole appears to have a deep crack near the top of the pole. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Guy stub pole with down guy hardware installed. | N\A | N\A | N\A | N\A | N\A
100085467 | PLACER T0923 POLES | Sierra(N) | 2021-04-07 | 2021-05-17 | 2022-01-11 | Vegetation: Tree causing strain or abrasion to secondary or service (only 1 service) | [Answer left blank] | Tree limbs appear to be causing strain on the service line. | Agree | N/A | N¦A | 113027156 | Update a EC | Yes | No | Yes | No
100085467 | PLACER T0923 POLES | Sierra(N) | 2021-04-07 | 2021-05-17 | 2022-01-11 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | There appears to be an open wire secondary. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100085467 | PLACER T0923 POLES | Sierra(N) | 2021-04-07 | 2021-05-17 | 2022-01-11 | Other Required Data: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101384818 | EL DORADO I3915 POLES | Sierra(N) | 2021-04-07 | 2021-05-25 | 2022-01-11 | Anchor and Guys: Guy wire broken, damaged, clearance issues, corroded, covered by vegetation, overgrown, strain or abrasion | [Answer left blank] | Down guy appears to be in contact with vegetation above the insulator. | Agree | N/A | N¦A | 119210782 | Update a EC | Yes | No | Yes | No
100085424 | PLACER T0923 POLES | Sierra(N) | 2021-04-08 | 2021-05-17 | 2022-01-11 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | There appears to be an open wire secondary. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100085424 | PLACER T0923 POLES | Sierra(N) | 2021-04-08 | 2021-05-17 | 2022-01-11 | Other Required Data: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100263425 | PENINSULA B0617 POLES | Peninsula(C) | 2021-04-08 | 2021-05-12 | 2022-01-11 | Hardware and Framing: Tap clamps installed incorrectly | [Answer left blank] | Tap clamps are installed on the conductor armor rod instead of a tap guard. | Agree | N/A | N¦A | 120763291 | Update a EC | Yes | No | Yes | No
100263425 | PENINSULA B0617 POLES | Peninsula(C) | 2021-04-08 | 2021-05-12 | 2022-01-11 | Hardware and Framing: Crossarm integrity compromised by any of the following; damaged, broken, burnt, decayed, rotten, loose, missing hardware or showing severe signs of bent bolts or brackets, damaged bracing, gun shots, insect damage or woodpecker damage, splitting, or fails to meet clearance requirements | [Answer left blank] | Crossarm appears to be decaying. | Agree | N/A | N¦A | 120763291 | Update a EC | Yes | No | Yes | No
100263425 | PENINSULA B0617 POLES | Peninsula(C) | 2021-04-08 | 2021-05-12 | 2022-01-11 | Hardware and Framing: Molding missing, broken, damaged, or loose | [Answer left blank] | Ground wire molding has a 1-inch gap at 8’ 1” from ground level. | Agree | N/A | N¦A | 120763291 | Update a EC | Yes | No | Yes | No
100263425 | PENINSULA B0617 POLES | Peninsula(C) | 2021-04-08 | 2021-05-12 | 2022-01-11 | Hardware and Framing: Grounds exposed, broken, damaged, disconnected, unsecured, or missing (if required) | [Answer left blank] | Ground wire molding has a 1-inch gap at 8’ 1” from ground level. | Agree | N/A | N¦A | 120763291 | Update a EC | Yes | No | Yes | No
100263425 | PENINSULA B0617 POLES | Peninsula(C) | 2021-04-08 | 2021-05-12 | 2022-01-11 | Non-Time-Dependent Issues: Pole steps are less than 8' 6" above the ground or any other accessible surface | [Answer left blank] | Pole step is less than 8'0" from ground level. | Agree | N/A | N¦A | 120763291 | Update a EC | Yes | No | Yes | No
100263427 | PENINSULA B0617 POLES | Peninsula(C) | 2021-04-08 | 2021-05-12 | 2022-01-11 | Hardware and Framing: Molding missing, broken, damaged, or loose | [Answer left blank] | Section of molding appears damaged 15-20 feet from the ground. | Agree | N/A | N¦A | 117085003 | Update a EC | Yes | No | Yes | No
100263427 | PENINSULA B0617 POLES | Peninsula(C) | 2021-04-08 | 2021-05-12 | 2022-01-11 | Hardware and Framing: Grounds exposed, broken, damaged, disconnected, unsecured, or missing (if required) | [Answer left blank] | Section of ground wire appears exposed at 15-20 feet from the ground. | Agree | N/A | N¦A | 117085003 | Update a EC | Yes | No | Yes | No
100263427 | PENINSULA B0617 POLES | Peninsula(C) | 2021-04-08 | 2021-05-12 | 2022-01-11 | Non-Time-Dependent Issues: Climbing space obstructed | [Answer left blank] | Climbing space is obstructed by tree. | Agree | N/A | N¦A | 117085003 | Update a EC | Yes | No | Yes | No
100263427 | PENINSULA B0617 POLES | Peninsula(C) | 2021-04-08 | 2021-05-12 | 2022-01-11 | Other Required Data: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A | N\A | N\A | N\A | N\A | N\A | N\A
100313763 | PENINSULA B0617 POLES | Peninsula(C) | 2021-04-08 | 2021-05-12 | 2022-01-11 | Non-Time-Dependent Issues: Pole steps are less than 8' 6" above the ground or any other accessible surface | [Answer left blank] | Pole step is at 5’ 7” (67 inches). | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101383836 | EL DORADO I3909 POLES | Sierra(N) | 2021-04-08 | 2021-05-25 | 2022-01-11 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | The top of the pole shows signs of deterioration and has a large crack underneath hardware supporting pole-top insulator. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Three phase tangent pole with king pin, 9" brackets, anti-split bolt and hardware installed. | N\A | N\A | N\A | N\A | N\A
101383836 | EL DORADO I3909 POLES | Sierra(N) | 2021-04-08 | 2021-05-25 | 2022-01-11 | Anchor and Guys: Guy wire broken, damaged, clearance issues, corroded, covered by vegetation, overgrown, strain or abrasion | [Answer left blank] | Vegetation appears to be causing strain to the down guy wire above the insulator. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100324289 | PENINSULA C0615 POLES | Peninsula(C) | 2021-04-09 | 2021-05-10 | 2022-01-11 | Anchor and Guys: Guy wire broken, damaged, clearance issues, corroded, covered by vegetation, overgrown, strain or abrasion | [Answer left blank] | Bottom 4 feet of down guy is overgrown. | Disagree | Condition is not compelling | ELEC-1000 Training | Bushes can be pushed aside to view condition of anchor & preform | N\A | N\A | N\A | N\A | N\A
100324289 | PENINSULA C0615 POLES | Peninsula(C) | 2021-04-09 | 2021-05-10 | 2022-01-11 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | High voltage sign on one side of pole is faded. | Disagree | Condition is not compelling | 1. High Voltage Sign Not Installed as Required - TD-2305M-JA02, Rev. 8 - Pg. 61 | The one high sign in good condition on the opposite side of the pole satisfies the standard found in OH: Marking, Rev. #18: 11/01/18 022168 Page 3 of 35. Marking, Numbering, and Identification of Line Structures 3. Routine Inspection A. The requirement in 1, “Poles That Support Line Conductors,” must be satisfied with the following exceptions: 1. Sign the Pole: It is acceptable to have only one sign, or stacked pairs of signs, below the lowest line conductor energized above 750 V, except as noted in 4 “Special Locations.” B. The requirements in 2, Poles That Do Not Support Line Conductors,” must be satisfied with the following exceptions: 1. Risers: It is acceptable to have only one sign, or stacked pairs of signs, below risers energized above 750 V. 4. Special Locations: If the pole is signed, high-voltage signs are required on both sides of the pole in the following locations: Near water areas suitable for sailboats. Near established boat ramps and associated rigging areas. Adjacent to swimming pools. In agricultural areas with movable irrigation piping. Locations, where in the judgement of the employee, high-voltage signs should be visible from all sides of the poles. | N\A | N\A | N\A | N\A | N\A
100309534 | PENINSULA E0709 POLES | Peninsula(C) | 2021-04-13 | 2021-05-13 | 2022-01-12 | Anchor and Guys: Anchor rod broken, damaged, corroded, covered by vegetation/overgrown, soil-eroded, graded, or buried | [Answer left blank] | Anchor rod is buried. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101378943 | EL DORADO I3807 POLES | Sierra(N) | 2021-04-14 | 2021-05-24 | 2022-01-12 | Common Equipment/Other Equipment: Radial/EOL (End-Of-Line) configuration riser/pothead broken, damaged, loose, or flashed | [Answer left blank] | The riser/pothead on the pole appears to be damaged and the insulations appear to be broken, exposing the conductor. | Agree | N/A | N¦A | 119531346 | Update a EC | Yes | No | Yes | No
101378943 | EL DORADO I3807 POLES | Sierra(N) | 2021-04-14 | 2021-05-24 | 2022-01-12 | Hardware and Framing: Animal mitigation broken, damaged, or missing (if required) | [Answer left blank] | It appears that animal mitigation is missing on the line protection cutout and lightning arrestor. | Agree | N/A | N¦A | 119531346 | Update a EC | Yes | No | Yes | No
101378943 | EL DORADO I3807 POLES | Sierra(N) | 2021-04-14 | 2021-05-24 | 2022-01-12 | Hardware and Framing: Molding missing, broken, damaged, or loose | [Answer left blank] | It appears that molding is loose at about 9' from the bottom of the pole, exposing insulated ground wire. | Agree | N/A | N¦A | 119531346 | Update a EC | Yes | No | Yes | No
100022509 | NEVADA R0820 POLES | Sierra(N) | 2021-04-15 | 2021-05-18 | 2022-01-12 | Other Required Data: Is there non-exempt equipment at the inspection location (Solid Blade or In-line disconnect) | [Answer left blank] | There appear to be solid-blade disconnects on the structure. | Agree | N/A | N¦A | N\A | N\A | N\A | N\A | N\A | N\A
100022509 | NEVADA R0820 POLES | Sierra(N) | 2021-04-15 | 2021-05-18 | 2022-01-12 | Other Required Data: Is there non-exempt equipment at the inspection location (Lightning or Surge Arrester | [Answer left blank] | There appear to be non-exempt arresters on the structure. | Agree | N/A | N¦A | N\A | N\A | N\A | N\A | N\A | N\A
100022509 | NEVADA R0820 POLES | Sierra(N) | 2021-04-15 | 2021-05-18 | 2022-01-12 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | High voltage sign is missing from the north side of the pole. | Disagree | Condition is not compelling | 1. High Voltage Sign Not Installed as Required - TD-2305M-JA02, Rev. 8 - Pg. 61 | The one high sign in good condition on the opposite side of the pole satisfies the standard found in OH: Marking, Rev. #18: 11/01/18 022168 Page 3 of 35. Marking, Numbering, and Identification of Line Structures 3. Routine Inspection A. The requirement in 1, “Poles That Support Line Conductors,” must be satisfied with the following exceptions: 1. Sign the Pole: It is acceptable to have only one sign, or stacked pairs of signs, below the lowest line conductor energized above 750 V, except as noted in 4 “Special Locations.” B. The requirements in 2, Poles That Do Not Support Line Conductors,” must be satisfied with the following exceptions: 1. Risers: It is acceptable to have only one sign, or stacked pairs of signs, below risers energized above 750 V. 4. Special Locations: If the pole is signed, high-voltage signs are required on both sides of the pole in the following locations: Near water areas suitable for sailboats. Near established boat ramps and associated rigging areas. Adjacent to swimming pools. In agricultural areas with movable irrigation piping. Locations, where in the judgement of the employee, high-voltage signs should be visible from all sides of the poles. | N\A | N\A | N\A | N\A | N\A
100022569 | NEVADA R0820 POLES | Sierra(N) | 2021-04-15 | 2021-05-18 | 2022-01-12 | Anchor and Guys: Guy wire broken, damaged, clearance issues, corroded, covered by vegetation, overgrown, strain or abrasion | [Answer left blank] | There appears to be vegetation in contact with the guy wire above the guy insulator. | Agree | N/A | N¦A | 116818740 | Update a EC | Yes | No | Yes | No
100022574 | NEVADA R0820 POLES | Sierra(N) | 2021-04-15 | 2021-05-18 | 2022-01-12 | Vegetation: Tree causing strain or abrasion to secondary or service (only 1 service) | [Answer left blank] | The trunk of a tree appears to be putting strain on the secondary conductor. | Agree | N/A | N¦A | 116820178 | Update a EC | Yes | No | Yes | No
100022574 | NEVADA R0820 POLES | Sierra(N) | 2021-04-15 | 2021-05-18 | 2022-01-12 | Other Required Data: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A | N\A | N\A | N\A | N\A | N\A | N\A
100022574 | NEVADA R0820 POLES | Sierra(N) | 2021-04-15 | 2021-05-18 | 2022-01-12 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | High voltage sign is missing from the south side of the pole. | Disagree | Condition is not compelling | 1. High Voltage Sign Not Installed as Required - TD-2305M-JA02, Rev. 8 - Pg. 61 | The one high sign in good condition on the opposite side of the pole satisfies the standard found in OH: Marking, Rev. #18: 11/01/18 022168 Page 3 of 35. Marking, Numbering, and Identification of Line Structures 3. Routine Inspection A. The requirement in 1, “Poles That Support Line Conductors,” must be satisfied with the following exceptions: 1. Sign the Pole: It is acceptable to have only one sign, or stacked pairs of signs, below the lowest line conductor energized above 750 V, except as noted in 4 “Special Locations.” B. The requirements in 2, Poles That Do Not Support Line Conductors,” must be satisfied with the following exceptions: 1. Risers: It is acceptable to have only one sign, or stacked pairs of signs, below risers energized above 750 V. 4. Special Locations: If the pole is signed, high-voltage signs are required on both sides of the pole in the following locations: Near water areas suitable for sailboats. Near established boat ramps and associated rigging areas. Adjacent to swimming pools. In agricultural areas with movable irrigation piping. Locations, where in the judgement of the employee, high-voltage signs should be visible from all sides of the poles. | N\A | N\A | N\A | N\A | N\A
100022574 | NEVADA R0820 POLES | Sierra(N) | 2021-04-15 | 2021-05-18 | 2022-01-12 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground-line. | Agree | N/A | N¦A | N\A | N\A | N\A | N\A | N\A | N\A
100022678 | NEVADA R0820 POLES | Sierra(N) | 2021-04-15 | 2021-05-18 | 2022-01-12 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There appears to be a large crack at the top of the pole. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Three phase tangent pole with king pin, wood crossarm, down guy and hardware installed. | N\A | N\A | N\A | N\A | N\A
103916852 | NEVADA R0820 POLES | Sierra(N) | 2021-04-15 | 2021-05-18 | 2022-01-12 | Conductor: Conductor has splices tied in proximity to insulator preventing free movement of splice with conductor | [Answer left blank] | Splice on the west (road side) phase on the north span is within 2' of the insulator. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
103916852 | NEVADA R0820 POLES | Sierra(N) | 2021-04-15 | 2021-05-18 | 2022-01-12 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | Pole number is visible. | Agree | N/A | N¦A | N\A | N\A | N\A | N\A | N\A | N\A
101383875 | EL DORADO I3910 POLES | Sierra(N) | 2021-04-16 | 2021-05-25 | 2022-01-12 | Hardware and Framing: Crossarm integrity compromised by any of the following; damaged, broken, burnt, decayed, rotten, loose, missing hardware or showing severe signs of bent bolts or brackets, damaged bracing, gun shots, insect damage or woodpecker damage, splitting, or fails to meet clearance requirements | [Answer left blank] | Crossarm is split near where the wood pin and insulator are attached. | Agree | N/A | N¦A | 119621048 | Update a EC | Yes | No | Yes | No
103840528 | NEVADA R0820 POLES | Sierra(N) | 2021-04-16 | 2021-05-18 | 2022-01-12 | Conductor: Primary, secondary, and/or service conductors broken, damaged, burnt, corroded, loose, frayed or bird caging | [Answer left blank] | There appears to be bird-caging on the west span of the south (road side) phase of the conductor. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100030376 | PLACER S1023 POLES | Sierra(N) | 2021-04-17 | 2021-05-19 | 2022-01-12 | Anchor and Guys: Guy wire broken, damaged, clearance issues, corroded, covered by vegetation, overgrown, strain or abrasion | [Answer left blank] | The guy wire appears to be in contact with vegetation above the insulator. | Agree | N/A | N¦A | 120834599 | Update a EC | Yes | No | Yes | No
100263303 | PENINSULA B0611 POLES | Peninsula(C) | 2021-04-17 | 2021-05-12 | 2022-01-12 | Anchor and Guys: Does or should this location have a Guy? | No | Pole has down guy and overhead guy. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100263303 | PENINSULA B0611 POLES | Peninsula(C) | 2021-04-17 | 2021-05-12 | 2022-01-12 | Anchor and Guys: Anchor rod broken, damaged, corroded, covered by vegetation/overgrown, soil-eroded, graded, or buried | [Answer left blank] | Anchor rod is buried. | Agree | N/A | N¦A | 116979672 | Update a EC | Yes | No | Yes | No
100263303 | PENINSULA B0611 POLES | Peninsula(C) | 2021-04-17 | 2021-05-12 | 2022-01-12 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | Open wire secondary is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100263303 | PENINSULA B0611 POLES | Peninsula(C) | 2021-04-17 | 2021-05-12 | 2022-01-12 | Other Required Data: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100263303 | PENINSULA B0611 POLES | Peninsula(C) | 2021-04-17 | 2021-05-12 | 2022-01-12 | Non-Time-Dependent Issues: High sign missing, broken, or illegible (backwards / upside down) | [Answer left blank] | High voltage sign is missing from one side of pole. | Disagree | Condition is not compelling | 1. High Voltage Sign Not Installed as Required - TD-2305M-JA02, Rev. 8 - Pg. 61 | The one high sign in good condition on the opposite side of the pole satisfies the standard found in OH: Marking, Rev. #18: 11/01/18 022168 Page 3 of 35. Marking, Numbering, and Identification of Line Structures 3. Routine Inspection A. The requirement in 1, “Poles That Support Line Conductors,” must be satisfied with the following exceptions: 1. Sign the Pole: It is acceptable to have only one sign, or stacked pairs of signs, below the lowest line conductor energized above 750 V, except as noted in 4 “Special Locations.” B. The requirements in 2, Poles That Do Not Support Line Conductors,” must be satisfied with the following exceptions: 1. Risers: It is acceptable to have only one sign, or stacked pairs of signs, below risers energized above 750 V. 4. Special Locations: If the pole is signed, high-voltage signs are required on both sides of the pole in the following locations: Near water areas suitable for sailboats. Near established boat ramps and associated rigging areas. Adjacent to swimming pools. In agricultural areas with movable irrigation piping. Locations, where in the judgement of the employee, high-voltage signs should be visible from all sides of the poles. | N\A | N\A | N\A | N\A | N\A
100263304 | PENINSULA B0611 POLES | Peninsula(C) | 2021-04-17 | 2021-05-12 | 2022-01-12 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | Top section of pole appears to have deep cracks near secondary brackets. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Secondary pole with 3 rack and spool brackets and hardware installed. | N\A | N\A | N\A | N\A | N\A
100263304 | PENINSULA B0611 POLES | Peninsula(C) | 2021-04-17 | 2021-05-12 | 2022-01-12 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | Open wire secondary is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100263304 | PENINSULA B0611 POLES | Peninsula(C) | 2021-04-17 | 2021-05-12 | 2022-01-12 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | Pole number is visible. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103946979 | PENINSULA B0611 POLES | Peninsula(C) | 2021-04-17 | 2021-05-12 | 2022-01-12 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | Open wire secondary is present. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100035561 | PLACER T0612 POLES | Sierra(N) | 2021-04-19 | 2021-05-20 | 2022-01-12 | Hardware and Framing: Tap clamps installed incorrectly | [Answer left blank] | The tap clamp on the road-side conductor is installed directly on the conductor instead of on a tap guard. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100035561 | PLACER T0612 POLES | Sierra(N) | 2021-04-19 | 2021-05-20 | 2022-01-12 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100035553 | PLACER T0612 POLES | Sierra(N) | 2021-04-19 | 2021-05-20 | 2022-01-12 | Non-Time-Dependent Issues: Pole steps are less than 8' 6" above the ground or any other accessible surface | [Answer left blank] | Pole step is at 8’ 0” (96 inches). | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100035553 | PLACER T0612 POLES | Sierra(N) | 2021-04-19 | 2021-05-20 | 2022-01-12 | Other Required Data: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100035553 | PLACER T0612 POLES | Sierra(N) | 2021-04-19 | 2021-05-20 | 2022-01-12 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100035560 | PLACER T0612 POLES | Sierra(N) | 2021-04-19 | 2021-05-20 | 2022-01-12 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | Cracked at the top of the pole, including near where hardware is attached, and shows signs of decay. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100035560 | PLACER T0612 POLES | Sierra(N) | 2021-04-19 | 2021-05-20 | 2022-01-12 | Anchor and Guys: Guy wire broken, damaged, clearance issues, corroded, covered by vegetation, overgrown, strain or abrasion | [Answer left blank] | There appears to be vegetation in contact with the guy wire above the guy insulator. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100035560 | PLACER T0612 POLES | Sierra(N) | 2021-04-19 | 2021-05-20 | 2022-01-12 | Hardware and Framing: Secondary connectors (mini wedge and Insulink) installed on primary conductor | [Answer left blank] | There appear to be insulink connectors on the primary conductor jumpers. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100035560 | PLACER T0612 POLES | Sierra(N) | 2021-04-19 | 2021-05-20 | 2022-01-12 | Other Required Data: Is there non-exempt equipment at the inspection location (Hot tap clamp or Split Bolt connector) | [Answer left blank] | The asset has non-exempt Split-Bolt connectors on the primary conductor. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100035560 | PLACER T0612 POLES | Sierra(N) | 2021-04-19 | 2021-05-20 | 2022-01-12 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Dried vegetation is present within 10 feet of pole with non-exempt split bolt connectors on the primary conductor. | Disagree | N/A | ELEC-1000 Training | PG&E Inspection was completed Prior to the start of the 2021 fire season. Questions in the Inspect app related to vegetation in proximity to pole with Non-Exempt Equipment would not have been available for the inspector to answer until May 1st. | N\A | N\A | N\A | N\A | N\A
100074915 | PLACER T0612 POLES | Sierra(N) | 2021-04-20 | 2021-05-20 | 2022-01-13 | Other Required Data: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103669759 | PLACER S0911 POLES | Sierra(N) | 2021-04-20 | 2021-05-19 | 2022-01-13 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | Pole number is visible. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100029048 | PLACER S1023 POLES | Sierra(N) | 2021-04-21 | 2021-05-19 | 2022-01-13 | Other Required Data: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100029217 | PLACER S1023 POLES | Sierra(N) | 2021-04-21 | 2021-05-19 | 2022-01-13 | Anchor and Guys: Anchor rod broken, damaged, corroded, covered by vegetation/overgrown, soil-eroded, graded, or buried | [Answer left blank] | The anchor rod appears to be buried. | Agree | N/A | N¦A | 121804346 | Update a EC | Yes | No | Yes | No
100029217 | PLACER S1023 POLES | Sierra(N) | 2021-04-21 | 2021-05-19 | 2022-01-13 | Other Required Data: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100023473 | NEVADA MAP R0824 POLES | Sierra(N) | 2021-04-22 | 2021-05-18 | 2022-01-13 | Other Required Data: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100023476 | NEVADA MAP R0824 POLES | Sierra(N) | 2021-04-22 | 2021-05-18 | 2022-01-13 | Hardware and Framing: Tap clamps installed incorrectly | [Answer left blank] | Tap clamps do not appear to be installed on tap guards. One appears to be installed on the armor rod; the other appears to be installed directly on the conductor. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100023476 | NEVADA MAP R0824 POLES | Sierra(N) | 2021-04-22 | 2021-05-18 | 2022-01-13 | Other Required Data: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100023491 | NEVADA MAP R0824 POLES | Sierra(N) | 2021-04-22 | 2021-05-18 | 2022-01-13 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | Top section of pole appears to have deep cracks near secondary brackets. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Single phase double dead end angle pole pole with steel crossarm, down guy and hardware installed. | N\A | N\A | N\A | N\A | N\A
100023491 | NEVADA MAP R0824 POLES | Sierra(N) | 2021-04-22 | 2021-05-18 | 2022-01-13 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100023492 | NEVADA MAP R0824 POLES | Sierra(N) | 2021-04-22 | 2021-05-18 | 2022-01-13 | Other Required Data: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100023492 | NEVADA MAP R0824 POLES | Sierra(N) | 2021-04-22 | 2021-05-18 | 2022-01-13 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100023494 | NEVADA MAP R0824 POLES | Sierra(N) | 2021-04-22 | 2021-05-18 | 2022-01-13 | Anchor and Guys: Guy wire broken, damaged, clearance issues, corroded, covered by vegetation, overgrown, strain or abrasion | [Answer left blank] | There appears to be vegetation in contact with the guy wire above the guy insulator. | Agree | N/A | N¦A | 121804346 | Update a EC | Yes | No | Yes | No
100023494 | NEVADA MAP R0824 POLES | Sierra(N) | 2021-04-22 | 2021-05-18 | 2022-01-13 | Other Required Data: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100023495 | NEVADA MAP R0824 POLES | Sierra(N) | 2021-04-22 | 2021-05-18 | 2022-01-13 | Other Required Data: Pole number (yellow tag with "barcode") visible on pole | [Answer left blank] | Pole number is visible. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100072210 | PLACER T0612 POLES | Sierra(N) | 2021-04-22 | 2021-05-20 | 2022-01-14 | Anchor and Guys: Anchor rod broken, damaged, corroded, covered by vegetation/overgrown, soil-eroded, graded, or buried | [Answer left blank] | The guy anchor appears to be buried. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100072210 | PLACER T0612 POLES | Sierra(N) | 2021-04-22 | 2021-05-20 | 2022-01-14 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103824250 | PENINSULA F0806 POLES | Peninsula(C) | 2021-04-22 | 2021-05-11 | 2022-01-14 | Other Required Data: Tree anchor installed in tree by design | [Answer left blank] | Tree anchor is installed by design. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103824250 | PENINSULA F0806 POLES | Peninsula(C) | 2021-04-22 | 2021-05-11 | 2022-01-14 | Other Required Data: Is there non-exempt equipment at the inspection location (Universal or Open Link Fuse) | [Answer left blank] | Structure has non-exempt universal fuses. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103824250 | PENINSULA F0806 POLES | Peninsula(C) | 2021-04-22 | 2021-05-11 | 2022-01-14 | Other Required Data: 3 or more splices present in one phase of the span | [Answer left blank] | There are 6 splices on the east span, with 3 splices on the south phase and 3 splices on the north phase. Span does not cross over a major roadway. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100029192 | PLACER S0911 POLES | Sierra(N) | 2021-04-23 | 2021-05-19 | 2022-01-14 | Other Required Data: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100029194 | PLACER S0911 POLES | Sierra(N) | 2021-04-23 | 2021-05-19 | 2022-01-14 | Other Required Data: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100029194 | PLACER S0911 POLES | Sierra(N) | 2021-04-23 | 2021-05-19 | 2022-01-14 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100029197 | PLACER S0911 POLES | Sierra(N) | 2021-04-23 | 2021-05-19 | 2022-01-14 | Non-Time-Dependent Issues: Pole steps are less than 8' 6" above the ground or any other accessible surface | [Answer left blank] | Pole step is at 8’ 3” (99 inches). | Agree | N/A | N¦A | 116764670 | Update a EC | Yes | No | Yes | No
100029197 | PLACER S0911 POLES | Sierra(N) | 2021-04-23 | 2021-05-19 | 2022-01-14 | Other Required Data: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100029201 | PLACER S0911 POLES | Sierra(N) | 2021-04-23 | 2021-05-19 | 2022-01-14 | Other Required Data: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100033304 | PLACER S1023 POLES | Sierra(N) | 2021-04-14 | 2021-05-19 | 2022-01-14 | Anchor and Guys: Anchor rod broken, damaged, corroded, covered by vegetation/overgrown, soil-eroded, graded, or buried | [Answer left blank] | The guy anchor appears to be buried. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100036590 | PLACER MAP T0622 POLES | Sierra(N) | 2021-04-26 | 2021-05-20 | 2022-01-14 | Anchor and Guys: Anchor rod broken, damaged, corroded, covered by vegetation/overgrown, soil-eroded, graded, or buried | [Answer left blank] | The anchor rod appears to be buried. | Agree | N/A | N¦A | 121945054 | Update a EC | Yes | No | Yes | No
100036590 | PLACER MAP T0622 POLES | Sierra(N) | 2021-04-26 | 2021-05-20 | 2022-01-14 | Other Required Data: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | Transformer may contain PCB as there is no blue sticker. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100273954 | PENINSULA E0710 POLES | Peninsula(C) | 2021-04-27 | 2021-05-13 | 2022-01-14 | Non-Time-Dependent Issues: Visibility strips missing, broken, mismatched, or no longer reflective | [Answer left blank] | Visibility strips are missing. | Agree | N/A | N¦A | 116956191 | Update a EC | Yes | No | Yes | No
100273954 | PENINSULA E0710 POLES | Peninsula(C) | 2021-04-27 | 2021-05-13 | 2022-01-14 | Other Required Data: 3 or more splices present in one phase of the span | [Answer left blank] | There are 7 splices on the east span, with 3 splices on the north phase, 2 splices on the center phase, and 2 splices on the south phase. Span does not cross over a major roadway. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100273961 | PENINSULA E0710 POLES | Peninsula(C) | 2021-04-27 | 2021-05-13 | 2022-01-14 | Other Required Data: Is there non-exempt equipment at the inspection location (Universal or Open Link Fuse) | [Answer left blank] | Structure has non-exempt universal fuses. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100273961 | PENINSULA E0710 POLES | Peninsula(C) | 2021-04-27 | 2021-05-13 | 2022-01-14 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Structure has non-exempt universal fuses and dried leaves at the base. | Disagree | N/A | ELEC-1000 Training | PG&E Inspection was completed Prior to the start of the 2021 fire season. Questions in the Inspect app related to vegetation in proximity to pole with Non-Exempt Equipment would not have been available for the inspector to answer until May 1st. | N\A | N\A | N\A | N\A | N\A
100273962 | PENINSULA E0710 POLES | Peninsula(C) | 2021-04-27 | 2021-05-13 | 2022-01-14 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | Top third of pole appears to have a significant crack. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Three phase tangent pole with king pin, 9" brackets & hardware installed. | N\A | N\A | N\A | N\A | N\A
100273963 | PENINSULA E0710 POLES | Peninsula(C) | 2021-04-27 | 2021-05-13 | 2022-01-14 | Non-Time-Dependent Issues: Visibility strips missing, broken, mismatched, or no longer reflective | [Answer left blank] | Visibility strips are missing. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100273964 | PENINSULA E0710 POLES | Peninsula(C) | 2021-04-27 | 2021-05-13 | 2022-01-14 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | Pole is deformed (i.e., bowed). | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to be bowed due to down guy being pulled too tight. Three phase pole with king pin, wood crossarm and hardware installed. | N\A | N\A | N\A | N\A | N\A
100273964 | PENINSULA E0710 POLES | Peninsula(C) | 2021-04-27 | 2021-05-13 | 2022-01-14 | Vegetation: Support Structure with non-exempt equipment, has dried ground vegetation within 10' radius of Support Structure base | [Answer left blank] | Structure has non-exempt line fuses and dried leaves at the base. | Disagree | N/A | ELEC-1000 Training | PG&E Inspection was completed Prior to the start of the 2021 fire season. Questions in the Inspect app related to vegetation in proximity to pole with Non-Exempt Equipment would not have been available for the inspector to answer until May 1st. | N\A | N\A | N\A | N\A | N\A
100273964 | PENINSULA E0710 POLES | Peninsula(C) | 2021-04-27 | 2021-05-13 | 2022-01-14 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100040953 | PLACER T0924 POLES | Sierra(N) | 2021-04-28 | 2021-05-17 | 2022-01-14 | Hardware and Framing: Tap clamps installed incorrectly | [Answer left blank] | The tap clamps are incorrectly installed on the conductor armor rod instead of a tap guard. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
101410403 | EL DORADO J3812 POLES | Sierra(N) | 2021-04-29 | 2021-05-27 | 2022-01-14 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are large cracks at the top of the pole where the insulator hardware is installed. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
6.4 REPORT
103845541 | DIABLO D0911 POLES | Diablo(C) | 2020-02-19 | 2021-03-19 | 2022-02-07 | Conductor: Conductor has splices tied in within 2' of insulator preventing free movement of splice with conductor | [Answer left blank] | Conductor has splices which appear to be tied within two feet of insulator. | Agree | N/A | N¦A | Condition is attached to an open Notification (120747335) | N\A | N\A | N\A | N\A | N\A
100476357 | JUNK YARD FL TO HOLD DELETED DATA | Diablo(C) | 2020-02-21 | 2021-03-19 | 2022-02-07 | Conductor: Conductor has splices tied in within 2' of insulator preventing free movement of splice with conductor | [Answer left blank] | Conductor has splices which appear to be tied within two feet of insulator. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100476357 | JUNK YARD FL TO HOLD DELETED DATA | Diablo(C) | 2020-02-21 | 2021-03-19 | 2022-02-07 | Record Keeping: Location has a "buddy pole" (i.e. cut & kick pole with untransfered communications) | [Answer left blank] | Location has a buddy pole with untransferred communications. | Disagree | Condition does not exist | ELEC-1000 Training | Old pole is abandoned to telecom anid is not physically attached to PG&E power pole. Job Aid Overhead Inspection TD-2305M Pg.176-178 | N\A | N\A | N\A | N\A | N\A
100476360 | DIABLO D0911 POLES | Diablo(C) | 2020-02-21 | 2021-03-19 | 2022-02-07 | Vegetation: Distribution Facility / Pole located in State Responsibility Area (SRA) / Federal Responsibility Area (FRA) / High Fire Threat District (HFTD) with vegetation within 4’ of primary conductor | [Answer left blank] | Tree branches appear to be within four feet of primary. | Agree | N/A | N¦A | Condition is attached to an open Notification (120747335) | N\A | N\A | N\A | N\A | N\A
100476362 | DIABLO D0911 POLES | Diablo(C) | 2020-02-21 | 2021-03-19 | 2022-02-07 | Vegetation: Tree causing strain or abrasion to secondary or service | [Answer left blank] | Tree branch is in contact with service and appears to be causing strain. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100476362 | DIABLO D0911 POLES | Diablo(C) | 2020-02-21 | 2021-03-19 | 2022-02-07 | Record Keeping: What is the highest number of splices in a single phase of conductor within 1 span of this pole? | [Answer left blank] | There appears to be at least one splice on a phase of a conductor within one span of this pole, as shown in the photograph(s). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100495735 | DIABLO E15 POLES | Diablo(C) | 2020-06-17 | 2021-03-18 | 2022-02-07 | Hardware and Framing: Secondary connectors (mini wedge and Insulink) installed on primary conductor | [Answer left blank] | There appear to beInsulink secondary connectors on primary jumpers. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100495740 | DIABLO E15 POLES | Diablo(C) | 2020-06-17 | 2021-03-18 | 2022-02-07 | Conductor: Conductor has splices tied in within 2' of insulator preventing free movement of splice with conductor | [Answer left blank] | Conductor has a splice which appears to be tied within two feet of insulator. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100495740 | DIABLO E15 POLES | Diablo(C) | 2020-06-17 | 2021-03-18 | 2022-02-07 | Record Keeping: What is the highest number of splices in a single phase of conductor within 1 span of this pole? | [Answer left blank] | There appears to be at least one splice on a phase of a conductor within one span of this pole, as shown in the photograph(s). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100483833 | DIABLO D1521 POLES | Diablo(C) | 2020-06-23 | 2021-03-18 | 2022-02-07 | Conductor: Conductor has splices tied in within 2' of insulator preventing free movement of splice with conductor | [Answer left blank] | Conductor has a splice which appears to be tied within two feet of insulator. | Agree | N/A | N¦A | 110811058 | Update a EC | Yes | No | Yes | No
100483833 | DIABLO D1521 POLES | Diablo(C) | 2020-06-23 | 2021-03-18 | 2022-02-07 | Conductor has a splice which appears to be tied within two feet of insulator. | [Answer left blank] | Molding appears to be missing. | Agree | N/A | N¦A | 110811058 | Update a EC | Yes | No | Yes | Yes
100483833 | DIABLO D1521 POLES | Diablo(C) | 2020-06-23 | 2021-03-18 | 2022-02-07 | Hardware and Framing: Grounds exposed, broken, damaged, disconnected, unsecured, or missing | [Answer left blank] | Ground appears to be exposed. | Agree | N/A | N¦A | 110811058 | Update a EC | Yes | No | Yes | Yes
100483833 | DIABLO D1521 POLES | Diablo(C) | 2020-06-23 | 2021-03-18 | 2022-02-07 | Record Keeping: What is the highest number of splices in a single phase of conductor within 1 span of this pole? | [Answer left blank] | There appears to be at least one splice on a phase of a conductor within one span of this pole, as shown in the photograph(s). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100483839 | DIABLO D1521 POLES | Diablo(C) | 2020-06-24 | 2021-03-17 | 2022-02-07 | Anchor and Guys: Does or should this location have a Guy? | No | Asset has a secondary overhead guy. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100483843 | DIABLO D1521 POLES | Diablo(C) | 2020-06-24 | 2021-03-17 | 2022-02-07 | Conductor: Conductor has splices tied in within 2' of insulator preventing free movement of splice with conductor | [Answer left blank] | Conductor has splices which appear to be tied within two feet of insulator. | Agree | N/A | N¦A | Condition is attached to an open Notification (121607137) | N\A | N\A | N\A | N\A | N\A
102231968 | NORTH BAY MAP TT3221 POLES | North Bay(C) | 2020-06-24 | 2021-02-26 | 2022-02-07 | Record Keeping: What is the highest number of splices in a single phase of conductor within 1 span of this pole? | [Answer left blank] | There appears to be at least one splice on a phase of a conductor within one span of this pole, as shown in the photograph(s). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102231972 | NORTH BAY MAP TT3221 POLES | North Bay(C) | 2020-06-24 | 2021-02-26 | 2022-02-07 | Hardware and Framing: Is Hardware Framing present on this structure? | [Answer left blank] | Yes, hardware framing appears to be present on structure. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102231972 | NORTH BAY MAP TT3221 POLES | North Bay(C) | 2020-06-24 | 2021-02-26 | 2022-02-07 | Record Keeping: What is the highest number of splices in a single phase of conductor within 1 span of this pole? | [Answer left blank] | There appears to be at least one splice on a phase of a conductor within one span of this pole, as shown in the photograph(s). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102231982 | NORTH BAY MAP TT3221 POLES | North Bay(C) | 2020-06-24 | 2021-02-26 | 2022-02-07 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | The pole has large woodpecker holes underneath the crossarm, including one that appears to be greater than 4 inches indiameter. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
102231982 | NORTH BAY MAP TT3221 POLES | North Bay(C) | 2020-06-24 | 2021-02-26 | 2022-02-07 | Hardware and Framing: Crossarm damaged, broken, burnt, decayed, rotten, loose, missing hardware or showing signs of bent bolts or brackets, gun shots, insect damage or woodpecker damage, or splitting that compromises the integrity of the crossarm | [Answer left blank] | Crossarm bracket hardware appears to be loose. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
102231982 | NORTH BAY MAP TT3221 POLES | North Bay(C) | 2020-06-24 | 2021-02-26 | 2022-02-07 | Hardware and Framing: Select if there are risks, hazards or other maintenance conditions not previously captured in the checklist for Hardware Framing at this location | [Answer left blank] | Transformer brackethardware appears to be loose. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
102231982 | NORTH BAY MAP TT3221 POLES | North Bay(C) | 2020-06-24 | 2021-02-26 | 2022-02-07 | Record Keeping: What is the highest number of splices in a single phase of conductor within 1 span of this pole? | [Answer left blank] | There appears to be at least one splice on a phase of a conductor within one span of this pole, as shown in the photograph(s). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102231982 | NORTH BAY MAP TT3221 POLES | North Bay(C) | 2020-06-24 | 2021-02-26 | 2022-02-07 | Record Keeping: Transformer is Self-Protected (SP) | [Answer left blank] | Yes, the transformer is self-protected. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102231987 | NORTH BAY MAP TT3221 POLES | North Bay(C) | 2020-06-24 | 2021-02-26 | 2022-02-07 | Record Keeping: What is the highest number of splices in a single phase of conductor within 1 span of this pole? | [Answer left blank] | There appears to be at least one splice on a phase of a conductor within one span of this pole, as shown in the photograph(s). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102231997 | NORTH BAY MAP TT3221 POLES | North Bay(C) | 2020-06-24 | 2021-02-26 | 2022-02-07 | Conductor: Conductor has splices tied in within 2' of insulator preventing free movement of splice with conductor | [Answer left blank] | Conductor has a splice which appears to be tied within two feet of insulator. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
102231997 | NORTH BAY MAP TT3221 POLES | North Bay(C) | 2020-06-24 | 2021-02-26 | 2022-02-07 | Record Keeping: What is the highest number of splices in a single phase of conductor within 1 span of this pole? | [Answer left blank] | There appears to be at least one splice on a phase of a conductor within one span of this pole, as shown in the photograph(s). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102232134 | NORTH BAY MAP TT3221 POLES | North Bay(C) | 2020-06-25 | 2021-02-26 | 2022-02-07 | Conductor: Does this structure have a conductor? | No | Yes, this structure has a conductor. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102232134 | NORTH BAY MAP TT3221 POLES | North Bay(C) | 2020-06-25 | 2021-02-26 | 2022-02-07 | Record Keeping: What is the highest number of splices in a single phase of conductor within 1 span of this pole? | [Answer left blank] | There appears to be at least one splice on a phase of a conductor within one span of this pole, as shown in the photograph(s). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102232147 | NORTH BAY MAP TT3221 POLES | North Bay(C) | 2020-06-25 | 2021-02-26 | 2022-02-07 | Conductor: Conductor has splices tied in within 2' of insulator preventing free movement of splice with conductor | [Answer left blank] | Conductor has a splice which appears to be tied within two feet of insulator. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
102232147 | NORTH BAY MAP TT3221 POLES | North Bay(C) | 2020-06-25 | 2021-02-26 | 2022-02-07 | Record Keeping: What is the highest number of splices in a single phase of conductor within 1 span of this pole? | [Answer left blank] | There appears to be at least one splice on a phase of a conductor within one span of this pole, as shown in the photograph(s). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102232147 | NORTH BAY MAP TT3221 POLES | North Bay(C) | 2020-06-25 | 2021-02-26 | 2022-02-07 | Record Keeping: Transformer is suspect of having PCB" (guidance: look for blue sticker or indicator for no PCB). | [Answer left blank] | Transformer may have PCB, as there is no blue sticker indicating the absence of PCB. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102232147 | NORTH BAY MAP TT3221 POLES | North Bay(C) | 2020-06-25 | 2021-02-26 | 2022-02-07 | Record Keeping: Transformer is Self-Protected (SP) | [Answer left blank] | Yes, the transformer appears self-protected. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102232153 | NORTH BAY MAP TT3221 POLES | North Bay(C) | 2020-06-25 | 2021-02-26 | 2022-02-07 | Common Equipment/Other Equipment: Does this structure have equipment? | No | Yes, this structure has equipment. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102232153 | NORTH BAY MAP TT3221 POLES | North Bay(C) | 2020-06-25 | 2021-02-26 | 2022-02-07 | Record Keeping: What is the highest number of splices in a single phase of conductor within 1 span of this pole? | [Answer left blank] | There appears to be at least one splice on a phase of a conductor within one span of this pole, as shown in the photograph(s). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102232159 | NORTH BAY MAP TT3221 POLES | North Bay(C) | 2020-06-25 | 2021-02-26 | 2022-02-07 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There is evidence of splitting near the top of the pole, including where the crossarm is attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. Anti-split bolt is installed. | N\A | N\A | N\A | N\A | N\A
102232032 | NORTH BAY MAP TT3221 POLES | North Bay(C) | 2020-06-26 | 2021-02-26 | 2022-02-07 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There is evidence of cracking near the top of the pole, including where various bolts are attached at the equipment level. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. | N\A | N\A | N\A | N\A | N\A
102232032 | NORTH BAY MAP TT3221 POLES | North Bay(C) | 2020-06-26 | 2021-02-26 | 2022-02-07 | Conductor: Conductor has splices tied in within 2' of insulator preventing free movement of splice with conductor | [Answer left blank] | Conductor has a splice which appears to be tied within two feet of insulator. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
102232032 | NORTH BAY MAP TT3221 POLES | North Bay(C) | 2020-06-26 | 2021-02-26 | 2022-02-07 | Common Equipment/Other Equipment: Does this structure have equipment? | No | Yes, this structure has equipment. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102232032 | NORTH BAY MAP TT3221 POLES | North Bay(C) | 2020-06-26 | 2021-02-26 | 2022-02-07 | Hardware and Framing: Select if there are risks, hazards or other maintenance conditions not previously captured in the checklist for Hardware Framing at this location | [Answer left blank] | Secondary insulator hardware appears loose. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
102232032 | NORTH BAY MAP TT3221 POLES | North Bay(C) | 2020-06-26 | 2021-02-26 | 2022-02-07 | Record Keeping: What is the highest number of splices in a single phase of conductor within 1 span of this pole? | [Answer left blank] | There appears to be at least one splice on a phase of a conductor within one span of this pole, as shown in the photograph(s). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100483850 | DIABLO D1521 POLES | Diablo(C) | 2020-06-29 | 2021-03-17 | 2022-02-07 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There is evidence of cracking throughout the pole, including where various bolts are attached at the equipment level. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. | N\A | N\A | N\A | N\A | N\A
100483850 | DIABLO D1521 POLES | Diablo(C) | 2020-06-29 | 2021-03-17 | 2022-02-07 | Hardware and Framing: Hardware Framing molding missing, broken, damaged, or loose | [Answer left blank] | Gap appears in molding for ground wire. | Agree | N/A | N¦A | 121606363 | Update a EC | Yes | No | Yes | Yes
100483850 | DIABLO D1521 POLES | Diablo(C) | 2020-06-29 | 2021-03-17 | 2022-02-07 | Hardware and Framing: Grounds exposed, broken, damaged, disconnected, unsecured, or missing | [Answer left blank] | Ground appears to be exposed via gap in molding. | Agree | N/A | N¦A | 121606363 | Update a EC | Yes | No | Yes | Yes
100483850 | DIABLO D1521 POLES | Diablo(C) | 2020-06-29 | 2021-03-17 | 2022-02-07 | Non-Time-Dependent Issues: Visibility strips missing, broken, or no longer reflective | [Answer left blank] | Visibility strips appear to be broken. | Agree | N/A | N¦A | 121606363 | Update a EC | Yes | No | Yes | No
100483850 | DIABLO D1521 POLES | Diablo(C) | 2020-06-29 | 2021-03-17 | 2022-02-07 | Record Keeping: What is the highest number of splices in a single phase of conductor within 1 span of this pole? | [Answer left blank] | There appears to be at least one splice on a phase of a conductor within one span of this pole, as shown in the photograph(s). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100483852 | DIABLO D1521 POLES | Diablo(C) | 2020-06-29 | 2021-03-17 | 2022-02-07 | Record Keeping: What is the highest number of splices in a single phase of conductor within 1 span of this pole? | [Answer left blank] | There appears to be at least one splice on a phase of a conductor within one span of this pole, as shown in the photograph(s). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100483856 | DIABLO D1521 POLES | Diablo(C) | 2020-06-29 | 2021-03-17 | 2022-02-07 | Anchor and Guys: Does or should this location have a Guy? | No | Yes, a guy is present at this location. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100483856 | DIABLO D1521 POLES | Diablo(C) | 2020-06-29 | 2021-03-17 | 2022-02-07 | Hardware and Framing: Hardware Framing molding missing, broken, damaged, or loose | [Answer left blank] | Molding for underground service is not fully secured to pole. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | Yes
100483856 | DIABLO D1521 POLES | Diablo(C) | 2020-06-29 | 2021-03-17 | 2022-02-07 | Hardware and Framing: Grounds exposed, broken, damaged, disconnected, unsecured, or missing | [Answer left blank] | Ground wire appears to be exposed about 3 to 4 feet from bottom of pole. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | Yes
100483856 | DIABLO D1521 POLES | Diablo(C) | 2020-06-29 | 2021-03-17 | 2022-02-07 | Record Keeping: What is the highest number of splices in a single phase of conductor within 1 span of this pole? | [Answer left blank] | There appears to be at least one splice on a phase of a conductor within one span of this pole, as shown in the photograph(s). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102257608 | NORTH BAY MAP SS2906 POLES | North Bay(C) | 2020-07-03 | 2021-02-25 | 2022-02-07 | Record Keeping: What is the highest number of splices in a single phase of conductor within 1 span of this pole? | [Answer left blank] | There appears to be at least one splice on a phase of a conductor within one span of this pole, as shown in the photograph(s). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102257613 | NORTH BAY MAP SS2906 POLES | North Bay(C) | 2020-07-03 | 2021-02-25 | 2022-02-07 | Vegetation: Tree causing strain or abrasion to secondary or service | [Answer left blank] | Tree is in contact with serviceconductor, and branches appear to be causing strain. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
102257742 | NORTH BAY MAP SS2906 POLES | North Bay(C) | 2020-07-06 | 2021-02-25 | 2022-02-07 | Record Keeping: What is the highest number of splices in a single phase of conductor within 1 span of this pole? | [Answer left blank] | There appears to be at least one splice on a phase of a conductor within one span of this pole, as shown in the photograph(s). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102257743 | NORTH BAY MAP SS2906 POLES | North Bay(C) | 2020-07-06 | 2021-02-25 | 2022-02-07 | Record Keeping: What is the highest number of splices in a single phase of conductor within 1 span of this pole? | [Answer left blank] | There appears to be at least one splice on a phase of a conductor within one span of this pole, as shown in the photograph(s). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102257772 | NORTH BAY MAP SS2906 POLES | North Bay(C) | 2020-07-06 | 2021-02-25 | 2022-02-07 | Hardware and Framing: Tap clamps installed incorrectly | [Answer left blank] | Hot-line clamps do not have tap guards. | Agree | N/A | N¦A | Condition is attached to an open Notification (121496047) | N\A | N\A | N\A | N\A | N\A
102257772 | NORTH BAY MAP SS2906 POLES | North Bay(C) | 2020-07-06 | 2021-02-25 | 2022-02-07 | Record Keeping: Whatis the highest number of splices in a single phase of conductor within 1 span of this pole? | [Answer left blank] | There appears to be at least one splice on a phase of a conductor within one span of this pole, as shown in the photograph(s). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100539217 | DE ANZA J1404 POLES | De Anza(S) | 2020-07-09 | 2021-03-24 | 2022-02-07 | Non-Time-Dependent Issues: Visibility strips missing, broken, or no longer reflective | [Answer left blank] | There are no visibility strips on this structure. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100540036 | DE ANZA J1404 POLES | De Anza(S) | 2020-07-10 | 2021-03-24 | 2022-02-07 | Conductor: Conductor has splices tied in within 2' of insulator preventing free movement of splice with conductor | [Answer left blank] | Conductor has a splice which appears to be tied within two feet of insulator. | Agree | N/A | N¦A | 111884600 | Update a EC | Yes | No | Yes | No
100540036 | DE ANZA J1404 POLES | De Anza(S) | 2020-07-10 | 2021-03-24 | 2022-02-07 | Anchor and Guys: Guy wire broken, damaged, clearance issues, corroded, covered by vegetation, overgrown, strain or abrasion | [Answer left blank] | A tree is in contact with the guy wire and appears to be causing strain. | Agree | N/A | N¦A | Condition is attached to an open Notification (111884600) | N\A | N\A | N\A | N\A | N\A
100540036 | DE ANZA J1404 POLES | De Anza(S) | 2020-07-10 | 2021-03-24 | 2022-02-07 | Vegetation: Tree causing strain or abrasion to secondary or service | [Answer left blank] | A tree is in contact with theservice and appears to be causing strain. | Agree | N/A | N¦A | 111884600 | Update a EC | Yes | No | Yes | No
100540036 | DE ANZA J1404 POLES | De Anza(S) | 2020-07-10 | 2021-03-24 | 2022-02-07 | Non-Time-Dependent Issues: High sign missing or broken | [Answer left blank] | High voltage signis damaged. | Agree | N/A | N¦A | 111884600 | Update a EC | Yes | No | Yes | No
100540036 | DE ANZA J1404 POLES | De Anza(S) | 2020-07-10 | 2021-03-24 | 2022-02-07 | Record Keeping: What is the highest number of splices in a single phase of conductor within 1 span of this pole? | [Answer left blank] | There appears to be at least one splice on a phase of a conductor within one span of this pole, as shown in the photograph(s). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100540038 | DE ANZA J1404 POLES | De Anza(S) | 2020-07-10 | 2021-03-24 | 2022-02-07 | Anchor and Guys: Pole has unbalanced or unsupported strain at primary or communication level | [Answer left blank] | Pole appears to have unbalanced strain at communications level. | Agree | N/A | N¦A |  | Create "Other tag" | Yes | No | Yes | No
100540038 | DE ANZA J1404 POLES | De Anza(S) | 2020-07-10 | 2021-03-24 | 2022-02-07 | Anchor and Guys: Necessary guys missing or loose | [Answer left blank] | Communication guy disconnected from anchor support. | Agree | N/A | N¦A |  | Create "Other tag" | Yes | No | Yes | No
100540038 | DE ANZA J1404 POLES | De Anza(S) | 2020-07-10 | 2021-03-24 | 2022-02-07 | Hardware and Framing: Secondary connectors (mini wedge and Insulink) installed on primary conductor | [Answer left blank] | There appear to be mini wedge secondary connectors on primary conductor. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100540038 | DE ANZA J1404 POLES | De Anza(S) | 2020-07-10 | 2021-03-24 | 2022-02-07 | Record Keeping: What is the highest number of splices in a single phase of conductor within 1 span of this pole? | [Answer left blank] | There appears to be at least one splice on a phase of a conductor within one span of this pole, as shown in the photograph(s). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100557256 | DE ANZA J1404 POLES | De Anza(S) | 2020-07-10 | 2021-03-24 | 2022-02-07 | Conductor: Conductor has splices tied in within 2' of insulator preventing free movement of splice with conductor | [Answer left blank] | Conductor has splices which appear to be tied within two feet of insulator. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100557256 | DE ANZA J1404 POLES | De Anza(S) | 2020-07-10 | 2021-03-24 | 2022-02-07 | Anchor and Guys: Guy wire broken, damaged, clearance issues, corroded, covered by vegetation, overgrown, strain or abrasion | [Answer left blank] | Guy wire at communications level appears to be loose. | Agree | N/A | N¦A |  | Create "Other tag" | Yes | No | Yes | No
100557256 | DE ANZA J1404 POLES | De Anza(S) | 2020-07-10 | 2021-03-24 | 2022-02-07 | Hardware and Framing: Hardware Framing molding missing, broken, damaged, or loose | [Answer left blank] | Two gaps appear in molding for ground wire. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100557256 | DE ANZA J1404 POLES | De Anza(S) | 2020-07-10 | 2021-03-24 | 2022-02-07 | Hardware and Framing: Tap clamps installed incorrectly | [Answer left blank] | Hot-line clamps do not have tap guards. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100557256 | DE ANZA J1404 POLES | De Anza(S) | 2020-07-10 | 2021-03-24 | 2022-02-07 | Record Keeping: What is the highest number of splices in a single phase of conductor within 1 span of this pole? | [Answer left blank] | There appears to be at least one splice on a phase of a conductor within one span of this pole, as shown in the photograph(s). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103346185 | DE ANZA J1404 POLES | De Anza(S) | 2020-07-10 | 2021-03-24 | 2022-02-07 | Conductor: Conductor has splices tied in within 2' of insulator preventing free movement of splice with conductor | [Answer left blank] | Conductor has a splice which appears to be tied within two feet of insulator. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
103346185 | DE ANZA J1404 POLES | De Anza(S) | 2020-07-10 | 2021-03-24 | 2022-02-07 | Record Keeping: What is the highest number of splices in a single phase of conductor within 1 span of this pole? | [Answer left blank] | There appears to be at least one splice on a phase of a conductor within one span of this pole, as shown in the photograph(s). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102227804 | NORTH BAY MAP SS3116 POLES | North Bay(C) | 2020-07-20 | 2021-02-24 | 2022-02-07 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There are deep cracks throughout the pole, including where guys are attached. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. | N\A | N\A | N\A | N\A | N\A
102227811 | NORTH BAY MAP SS3116 POLES | North Bay(C) | 2020-07-20 | 2021-02-24 | 2022-02-07 | Record Keeping: Transformer is Self-Protected (SP) | [Answer left blank] | Yes, the transformer appearsself-protected. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102227827 | NORTH BAY MAP SS3116 POLES | North Bay(C) | 2020-07-20 | 2021-02-24 | 2022-02-07 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There is a large hole on the pole above the communications that appears to be greater than 4 inches in diameter. | Agree | N/A | N¦A | Condition is attached to an open Notification (119476659) | N\A | N\A | N\A | N\A | N\A
102227827 | NORTH BAY MAP SS3116 POLES | North Bay(C) | 2020-07-20 | 2021-02-24 | 2022-02-07 | Conductor: Conductor has splices tied in within 2' of insulator preventing free movement of splice with conductor | [Answer left blank] | Conductor has splices which appear to be tied within two feet of insulator. | Agree | N/A | N¦A | 119476659 | Update a EC | Yes | No | Yes | No
102227827 | NORTH BAY MAP SS3116 POLES | North Bay(C) | 2020-07-20 | 2021-02-24 | 2022-02-07 | Record Keeping: What is the highest number of splices in a single phase of conductor within 1 span of this pole? | [Answer left blank] | There appears to be at least one splice on a phase of a conductor within one span of this pole, as shown in the photograph(s). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102227828 | NORTH BAY MAP SS3116 POLES | North Bay(C) | 2020-07-20 | 2021-02-24 | 2022-02-07 | Record Keeping: What is the highest number of splices in a single phase of conductor within 1 span of this pole? | [Answer left blank] | There appears to be at least one splice on a phase of a conductor within one span of this pole, as shown in the photograph(s). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102295528 | NORTH BAY MAP SS3116 POLES | North Bay(C) | 2020-07-20 | 2021-02-24 | 2022-02-07 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There is a large hole at the top of the pole, where the crossarm bolt is attached.” | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
102227847 | NORTH BAY MAP SS3116 POLES | North Bay(C) | 2020-07-21 | 2021-02-24 | 2022-02-07 | Record Keeping: What is the highest number of splices in a single phase of conductor within 1 span of this pole? | [Answer left blank] | There appears to be at least one splice on a phase of a conductor within one span of this pole, as shown in the photograph(s). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102227873 | NORTH BAY MAP SS3116 POLES | North Bay(C) | 2020-07-21 | 2021-02-24 | 2022-02-07 | Anchor and Guys: Pole has unbalanced or unsupported strain at primary or communication level | [Answer left blank] | Communication-level guys are not attached to pole, and thus pole appears to have unsupported strain. | Agree | N/A | N¦A |  | Create "Other tag" | Yes | No | Yes | No
102227873 | NORTH BAY MAP SS3116 POLES | North Bay(C) | 2020-07-21 | 2021-02-24 | 2022-02-07 | Anchor and Guys: Necessary guys missing or loose | [Answer left blank] | Communication-level guys are not attached to pole, thus are missing in the proper location on the vertical standing pole. | Agree | N/A | N¦A |  | Create "Other tag" | Yes | No | Yes | No
102227873 | NORTH BAY MAP SS3116 POLES | North Bay(C) | 2020-07-21 | 2021-02-24 | 2022-02-07 | Record Keeping: Transformer is Self-Protected (SP) | [Answer left blank] | The transformer does not appear to be self-protected. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100513732 | DE ANZA I1314 POLES | De Anza(S) | 2020-08-08 | 3/23/2021 | 2022-02-07 | Record Keeping: What is the highest number of splices in a single phase of conductor within 1 span of this pole? | [Answer left blank] | There appears to be at least one splice on a phase of a conductor within one span of this pole, as shown in the photograph(s). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100513733 | DE ANZA I1314 POLES | De Anza(S) | 2020-08-08 | 3/23/2021 | 2022-02-07 | Conductor: Primary, secondary, and/or service conductors broken, damaged, burnt, corroded, loose, frayed or bird caging | [Answer left blank] | The lashing appears to be coming loose. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100513733 | DE ANZA I1314 POLES | De Anza(S) | 2020-08-08 | 3/23/2021 | 2022-02-07 | Anchor and Guys: Guy wire broken, damaged, clearance issues, corroded, covered by vegetation, overgrown, strain or abrasion | [Answer left blank] | A tree branch is in contact with the guy wire and appears to be causing strain. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100513741 | DE ANZA I1314 POLES | De Anza(S) | 2020-08-08 | 3/23/2021 | 2022-02-07 | Anchor and Guys: Guy wire broken, damaged, clearance issues, corroded, covered by vegetation, overgrown, strain or abrasion | [Answer left blank] | A tree branch is in contact with the guy wire and appears to be causing strain. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100513743 | DE ANZA I1314 POLES | De Anza(S) | 2020-08-08 | 3/23/2021 | 2022-02-07 | Hardware and Framing: Insulators chipped, cracked, corroded, contaminated, flashed, have signs of tracking, broken, damaged or squatting | [Answer left blank] | There appears to be debris in contact with the insulator. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100513743 | DE ANZA I1314 POLES | De Anza(S) | 2020-08-08 | 3/23/2021 | 2022-02-07 | Record Keeping: What is the highest number of splices in a single phase of conductor within 1 span of this pole? | [Answer left blank] | There appears to be at least one splice on a phase of a conductor within one span of this pole, as shown in the photograph(s). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100513744 | DE ANZA I1314 POLES | De Anza(S) | 2020-08-08 | 3/23/2021 | 2022-02-07 | Record Keeping: What is the highest number of splices in a single phase of conductor within 1 span of this pole? | [Answer left blank] | There appears to be at least one splice on a phase of a conductor within one span of this pole, as shown in the photograph(s). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100513745 | DE ANZA I1314 POLES | De Anza(S) | 2020-08-08 | 3/23/2021 | 2022-02-07 | Conductor: Conductor has splices tied in within 2' of insulator preventing free movement of splice with conductor | [Answer left blank] | Conductor has a splice which appears to be tied within two feet of insulator. | Disagree | Condition is not compelling | ELEC-1000 Training | Splice is within 2' of dead end shoe therefore does not need room to allow free monement of splice with conductor. | N\A | N\A | N\A | N\A | N\A
100513745 | DE ANZA I1314 POLES | De Anza(S) | 2020-08-08 | 3/23/2021 | 2022-02-07 | Anchor and Guys: Necessary guys missing or loose | [Answer left blank] | Guys appear to be loose. | Agree | N/A | N¦A | Condition is attached to an open Notification (120890740) | N\A | N\A | N\A | N\A | N\A
100513745 | DE ANZA I1314 POLES | De Anza(S) | 2020-08-08 | 3/23/2021 | 2022-02-07 | Non-Time-Dependent Issues: Guy marker missing, damaged, or broken | [Answer left blank] | The guy marker is broken. | Agree | N/A | N¦A | 120890740 | Update a EC | Yes | No | Yes | No
100513752 | DE ANZA I1314 POLES | De Anza(S) | 2020-08-08 | 3/23/2021 | 2022-02-08 | Record Keeping: What is the highest number of splices in a single phase of conductor within 1 span of this pole? | [Answer left blank] | There appears to be at least one splice on a phase of a conductor within one span of this pole, as shown in the photograph(s). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100513749 | DE ANZA I1314 POLES | De Anza(S) | 2020-08-10 | 3/23/2021 | 2022-02-08 | Non-Time-Dependent Issues: High sign missing or broken | [Answer left blank] | One of thehigh voltage signsis damaged. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100513749 | DE ANZA I1314 POLES | De Anza(S) | 2020-08-10 | 3/23/2021 | 2022-02-08 | Record Keeping: What isthe highest number of splices in a single phase of conductor within 1 span of this pole? | [Answer left blank] | There appears to be at least one splice on a phase of a conductor within one span of this pole, as shown in the photograph(s). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100552149 | DE ANZA I1314 POLES | De Anza(S) | 2020-08-10 | 3/23/2021 | 2022-02-08 | Record Keeping: What is the highest number of splices in a single phase of conductor within 1 span of this pole? | [Answer left blank] | There appears to be at least one splice on a phase of a conductor within one span of this pole, as shown in the photograph(s). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103855604 | DE ANZA I1314 POLES | De Anza(S) | 2020-08-10 | 3/23/2021 | 2022-02-08 | Conductor: Conductor has splices tied in within 2' of insulator preventing free movement of splice with conductor | [Answer left blank] | Conductor has a splice which appears to be tied within two feet of insulator. | Disagree | Condition is not compelling | ELEC-1000 Training | Splice is within 2' of dead end shoe therefore does not need room to allow free monement of splice with conductor. | N\A | N\A | N\A | N\A | N\A
103855604 | DE ANZA I1314 POLES | De Anza(S) | 2020-08-10 | 3/23/2021 | 2022-02-08 | Record Keeping: What is the highest number of splices in a single phase of conductor within 1 span of this pole? | [Answer left blank] | There appears to be at least one splice on a phase of a conductor within one span of this pole, as shown in the photograph(s). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100526618 | DE ANZA I1215 POLES | De Anza(S) | 2020-09-22 | 3/22/2021 | 2022-02-08 | Record Keeping: What is the highest number of splices in a single phase of conductor within 1 span of this pole? | [Answer left blank] | There appears to be at least one splice on a phase of a conductor within one span of this pole, as shown in the photograph(s). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100526619 | DE ANZA I1215 POLES | De Anza(S) | 2020-09-22 | 3/22/2021 | 2022-02-08 | Anchor and Guys: Guy wire broken, damaged, clearance issues, corroded, covered by vegetation, overgrown, strain or abrasion | [Answer left blank] | A tree branch is in contact with the guy wire and appears to be causing strain. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100526620 | DE ANZA I1215 POLES | De Anza(S) | 2020-09-22 | 3/22/2021 | 2022-02-08 | Anchor and Guys: Guy wire broken, damaged, clearance issues, corroded, covered by vegetation, overgrown, strain or abrasion | [Answer left blank] | A tree branch is in contact with the guy wire and appears to be causing strain. The guy insulator also appears to be out of alignment. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100526620 | DE ANZA I1215 POLES | De Anza(S) | 2020-09-22 | 3/22/2021 | 2022-02-08 | Non-Time-Dependent Issues: High sign missing or broken | [Answer left blank] | High voltage sign is broken. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100526620 | DE ANZA I1215 POLES | De Anza(S) | 2020-09-22 | 3/22/2021 | 2022-02-08 | Record Keeping: What is the highest number of splices in a single phase of conductor within 1 span of this pole? | [Answer left blank] | There appears to be at least one splice on a phase of a conductor within one span of this pole, as shown in the photograph(s). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100526620 | DE ANZA I1215 POLES | De Anza(S) | 2020-09-22 | 3/22/2021 | 2022-02-08 | Record Keeping: Vibration Dampers present at this location | [Answer left blank] | Vibration dampers are attached to the conductor. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100526624 | DE ANZA I1215 POLES | De Anza(S) | 2020-09-22 | 3/22/2021 | 2022-02-08 | Record Keeping: What is the highest number of splices in a single phase of conductor within 1 span of this pole? | [Answer left blank] | There appears to be at least one splice on a phase of a conductor within one span of this pole, as shown in the photograph(s). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100526625 | DE ANZA I1215 POLES | De Anza(S) | 2020-09-22 | 3/22/2021 | 2022-02-08 | Hardware and Framing: Animal mitigation broken, damaged, or missing | [Answer left blank] | Animal mitigation is partially missing. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100526626 | DE ANZA I1215 POLES | De Anza(S) | 2020-09-22 | 3/22/2021 | 2022-02-08 | Conductor:Primary, secondary, and/or service conductors broken, damaged, burnt, corroded, loose, frayed or bird caging | [Answer left blank] | Primary conductor appears to be damaged. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100526626 | DE ANZA I1215 POLES | De Anza(S) | 2020-09-22 | 3/22/2021 | 2022-02-08 | Conductor: Select if there are risks, hazards or other maintenance conditions not previously captured in the checklist for this conductor. | [Answer left blank] | There are multiple connectors on different jumpers. | Disagree | Condition is not compelling | ELEC-1000 Training | Multiple connectors on a primary jimmper is not a compelling condition. | N\A | N\A | N\A | N\A | N\A
100526626 | DE ANZA I1215 POLES | De Anza(S) | 2020-09-22 | 3/22/2021 | 2022-02-08 | Record Keeping: What is the highest number of splices in a single phase of conductor within 1 span of this pole? | [Answer left blank] | There appears to be at least one splice on a phase of a conductor within one span of this pole, as shown in the photograph(s). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100526666 | DE ANZA I1215 POLES | De Anza(S) | 2020-09-22 | 3/22/2021 | 2022-02-08 | Conductor: Conductor has splices tied in within 2' of insulator preventing free movement of splice with conductor | [Answer left blank] | Conductor has splices which appear to be tied within two feet of insulator. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100526666 | DE ANZA I1215 POLES | De Anza(S) | 2020-09-22 | 3/22/2021 | 2022-02-08 | Anchor and Guys: Anchor rod broken, damaged, corroded, covered by vegetation/overgrown, soil-eroded, graded, or buried | [Answer left blank] | Anchor rod connected to a branch that appears to have broken off the tree. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100526666 | DE ANZA I1215 POLES | De Anza(S) | 2020-09-22 | 3/22/2021 | 2022-02-08 | Hardware and Framing: Select if there are risks, hazards or other maintenance conditions not previously captured in the checklist for Hardware Framing at this location | [Answer left blank] | The pole top extensionand hardware appear to be loose. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100526666 | DE ANZA I1215 POLES | De Anza(S) | 2020-09-22 | 3/22/2021 | 2022-02-08 | Record Keeping: What is the highest number of splices in a single phase of conductor within 1 span of this pole? | [Answer left blank] | There appears to be at least one splice on a phase of a conductor within one span of this pole, as shown in the photograph(s). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100526670 | DE ANZA I1215 POLES | De Anza(S) | 2020-09-22 | 3/22/2021 | 2022-02-08 | Conductor: Conductor has splices tied in within 2' of insulator preventing free movement of splice with conductor | [Answer left blank] | Conductor has a splice which appears to be tied within two feet of insulator. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100526670 | DE ANZA I1215 POLES | De Anza(S) | 2020-09-22 | 3/22/2021 | 2022-02-08 | Non-Time-Dependent Issues: Visibility strips missing, broken, or no longer reflective | [Answer left blank] | Visibility strips are no longer reflective. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100526670 | DE ANZA I1215 POLES | De Anza(S) | 2020-09-22 | 3/22/2021 | 2022-02-08 | Record Keeping: What is the highest number of splices in a single phase of conductor within 1 span of this pole? | [Answer left blank] | There appears to be at least one splice on a phase of a conductor within one span of this pole, as shown in the photograph(s). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100526672 | DE ANZA I1215 POLES | De Anza(S) | 2020-09-22 | 3/22/2021 | 2022-02-08 | Record Keeping: What is the highest number of splices in a single phase of conductor within 1 span of this pole? | [Answer left blank] | There appears to be at least one splice on a phase of a conductor within one span of this pole, as shown in the photograph(s). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100526673 | DE ANZA I1215 POLES | De Anza(S) | 2020-09-22 | 3/22/2021 | 2022-02-08 | Conductor: Hand orpreform tie wire broken, damaged, burnt, loose, showing signs of wearing, missing, or missing armor rod | [Answer left blank] | Tie wire appears to be broken. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | Yes
100526673 | DE ANZA I1215 POLES | De Anza(S) | 2020-09-22 | 3/22/2021 | 2022-02-08 | Record Keeping: What is the highest number of splices in a single phase of conductor within 1 span of this pole? | [Answer left blank] | There appears to be at least one splice on a phase of a conductor within one span of this pole, as shown in the photograph(s). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100548248 | DE ANZA I1215 POLES | De Anza(S) | 2020-09-22 | 3/22/2021 | 2022-02-08 | Record Keeping: What is the highest number of splices in a single phase of conductor within 1 span of this pole? | [Answer left blank] | There appears to be at least one splice on a phase of a conductor within one span of this pole, as shown in the photograph(s). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100548249 | DE ANZA I1215 POLES | De Anza(S) | 2020-09-22 | 3/22/2021 | 2022-02-08 | Conductor: Conductor has splices tied in within 2' of insulator preventing free movement of splice with conductor | [Answer left blank] | Conductor has splices which appear to be tied within two feet of insulator. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100548249 | DE ANZA I1215 POLES | De Anza(S) | 2020-09-22 | 3/22/2021 | 2022-02-08 | Record Keeping: What is the highest number of splices in a single phase of conductor within 1 span of this pole? | [Answer left blank] | There appears to be at least one splice on a phase of a conductor within one span of this pole, as shown in the photograph(s). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
100548265 | DE ANZA I1215 POLES | De Anza(S) | 2020-09-22 | 3/22/2021 | 2022-02-08 | Anchor and Guys: Guy wire broken, damaged, clearance issues, corroded, covered by vegetation, overgrown, strain or abrasion | [Answer left blank] | A tree branch is in contact with the guy wire and appears to be causing strain. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
100548266 | DE ANZA I1215 POLES | De Anza(S) | 2020-09-22 | 3/22/2021 | 2022-02-08 | Structure: Pole broken, damaged, burnt, deformed, corroded, gunshot, or showing signs of cracking, rotten or decay | [Answer left blank] | There appears to be damage at the top of the pole. | Disagree | Condition is not compelling | ELEC-1000 Training | Pole appears to have normal cracks and splits due to weather and ageing of pole. | N\A | N\A | N\A | N\A | N\A
100548266 | DE ANZA I1215 POLES | De Anza(S) | 2020-09-22 | 3/22/2021 | 2022-02-08 | Conductor: Conductor has splices tied in within 2' of insulator preventing free movement of splice with conductor | [Answer left blank] | Conductor has a splice which appears to be tied within two feet of insulator. | Agree | N/A | N¦A | 121795368 | Update a EC | Yes | No | Yes | No
100548266 | DE ANZA I1215 POLES | De Anza(S) | 2020-09-22 | 3/22/2021 | 2022-02-08 | Anchor and Guys: Necessary guys missing or loose | [Answer left blank] | Guy wire at communications level appears to be loose. | Agree | N/A | N¦A |  | Create "Other tag" | Yes | No | Yes | No
100548266 | DE ANZA I1215 POLES | De Anza(S) | 2020-09-22 | 3/22/2021 | 2022-02-08 | Anchor and Guys: Guy wire broken, damaged, clearance issues, corroded, covered by vegetation, overgrown, strain or abrasion | [Answer left blank] | Theguy wire is in contact with a tree branch that appears to be causing strain. | Agree | N/A | N¦A | 121795368 | Update a EC | Yes | No | Yes | No
100548266 | DE ANZA I1215 POLES | De Anza(S) | 2020-09-22 | 3/22/2021 | 2022-02-08 | Vegetation: Tree-Connect causing damage to our facilities, dead or dying, or causing conductor height issues | [Answer left blank] | The anchor rod associated with the primary guy terminates in a tree stump | Agree | N/A | N¦A | Condition is attached to an open Notification (121795368) | N\A | N\A | N\A | N\A | N\A
100548266 | DE ANZA I1215 POLES | De Anza(S) | 2020-09-22 | 3/22/2021 | 2022-02-08 | Non-Time-Dependent Issues: Visibility strips missing, broken, or no longer reflective | [Answer left blank] | Visibility strips are partially covered by a “Quiet Zone” sign. | Agree | N/A | N¦A | 121795368 | Update a EC | Yes | No | Yes | No
100548266 | DE ANZA I1215 POLES | De Anza(S) | 2020-09-22 | 3/22/2021 | 2022-02-08 | Record Keeping: What is the highest number of splices in a single phase of conductor within 1 span of this pole? | [Answer left blank] | There appears to be at least one splice on a phase of a conductor within one span of this pole, as shown in the photograph(s). | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103787045 | DE ANZA I1215 POLES | De Anza(S) | 2020-09-22 | 3/22/2021 | 2022-02-08 | Anchor and Guys: Does or should this location have a Guy? | No | This location has a guy. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
103787045 | DE ANZA I1215 POLES | De Anza(S) | 2020-09-22 | 3/22/2021 | 2022-02-08 | Record Keeping: What is the highest number of splices in a single phase of conductor within 1 span of this pole? | [Answer left blank] | There appears to be at least one splice associated with primary conductor within one span of this pole, as shown in the photographs. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
12.21 REPORT
103613468 | SANTA ROSA KK2619 POLES | Sonoma(N) | 2021-06-26 | 2021-11-08 | 2022-02-10 | Hardware and Framing: Insulators or King Pin chipped, cracked, corroded, contaminated, flashed, have signs of tracking, broken or damaged | [Answer left blank] | The field side insulator appears to be chipped. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
103613468 | SANTA ROSA KK2619 POLES | Sonoma(N) | 2021-06-26 | 2021-11-08 | 2022-02-10 | Other Required Data: Open Wire Service (to weatherhead) or Open Wire Secondary at this location | [Answer left blank] | There appears to be an open wire secondary present at this location. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102019303 | SANTA ROSA KK2619 POLES | Sonoma(N) | 2021-06-26 | 2021-11-08 | 2022-02-10 | Conductor: Conductor has splices tied in proximity to insulator preventing free movement of splice with conductor | [Answer left blank] | There appears to be a splice within two feet of insulator on the south span on the east or roadside phase. | Agree | N/A | N¦A |  | Create a EC | Yes | No | Yes | No
102019303 | SANTA ROSA KK2619 POLES | Sonoma(N) | 2021-06-26 | 2021-11-08 | 2022-02-10 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102019302 | SANTA ROSA KK2619 POLES | Sonoma(N) | 2021-06-26 | 2021-11-08 | 2022-02-10 | Anchor and Guys: Does or should this location have a Guy? | [Answer left blank] | There appears to be an overhead guy on the asset. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
102019302 | SANTA ROSA KK2619 POLES | Sonoma(N) | 2021-06-26 | 2021-11-08 | 2022-02-10 | Anchor and Guys: Guy wire broken, damaged, clearance issues, corroded, covered by vegetation, overgrown, strain or abrasion | [Answer left blank] | Vegetation appears to be causing strain on the pole-to-pole guy. | Agree | N/A | N¦A | 121620034 | Update a EC | Yes | No | Yes | No
102019302 | SANTA ROSA KK2619 POLES | Sonoma(N) | 2021-06-26 | 2021-11-08 | 2022-02-10 | Vegetation: Branches are broken and can strike facilities and/or Tree is dead and can strike facilities | [Answer left blank] | A tree proximate to the asset appears to be dead. | Agree | N/A | N¦A |  | Create "Other tag" | Yes | No | Yes | No
102019302 | SANTA ROSA KK2619 POLES | Sonoma(N) | 2021-06-26 | 2021-11-08 | 2022-02-10 | Other Required Data: Pole wrapped at ground-line at this location | [Answer left blank] | The pole appears to be wrapped at the ground line. | Agree | N/A | N¦A |  | N\A | N\A | N\A | N\A | N\A
101970799 | SANTA ROSA KK2619 POLES | Sonoma(N) | 2021-06-26 | 2021-11-08 | 2022-02-10 | Conductor: Conductor has splices tied in proximity to insulator preventing free movement of splice with conductor | [Answer left blank] | A splice appears to be on a primary conductor within two feet of an insulator on the west or field phase of the span heading south. | Agree | N/A | N¦A | 121606274 | Update a EC | Yes | No | Yes | No
101970799 | SANTA ROSA KK2619 POLES | Sonoma(N) | 2021-06-26 | 2021-11-08 | 2022-02-10 | Anchor and Guys: Select if there are risks, hazards, or other maintenance conditions not previously captured in the checklist for Anchor & Guys section | [Answer left blank] | Vegetation appears to be in contact with the guy wire above the guy insulator. | Agree | N/A | N¦A | Inspector did Create EC Notification (121606274) for this condition but did not indicate overgrown down guy in the Anchor & Guys section of the Inspection Record. | N\A | N\A | N\A | N\A | N\A
101970799 | SANTA ROSA KK2619 POLES | Sonoma(N) | 2021-06-26 | 2021-11-08 | 2022-02-10 | Hardware and Framing: Tap clamps installed incorrectly | [Answer left blank] | One tap clamp appears to be installed incorrectly because it is installed on armor rod. | Agree | N/A | N¦A | 121606274 | Update a EC | Yes | No | Yes | No
101970799 | SANTA ROSA KK2619 POLES | Sonoma(N) | 2021-06-26 | 2021-11-08 | 2022-02-10 | Non-Time-Dependent Issues: Visibility strips missing, broken, mismatched, or no longer reflective | [Answer left blank] | Visibility strips on the north side of the pole are damaged. The top-most strip is almost missing. | Agree | N/A | N¦A | 121606274 | Update a EC | Yes | No | Yes | No