## Transmission
SAP Equipment ID (Auto-Populated) | Structure Type | MWC (Auto-Populated) | Structure Number (Auto-Populated) | QC Review Date (Auto-Populated) | Monitor Review Date (Auto-Populated) | Inspection Review Date (Auto-Populated) | Wildfire Risk Driver Condition (Auto-Populated) | Inspection Form Response Condition | FM Team Comments | Agree/Disagree with monitor | QC Specilaist Finding | Reference | Additional Comments | QC Review Action(s) | Does Tag need to be created/updated? | Did Tag get Created/updated for this condition? | Refer to Compliance supervisor?
41196201 | Steel | Concord | 087/568 | 2021-12-06 | 2020-11-17 | 2020-08-29 | CommentsTower finish type: | I don't know | Galvanized: The tower appears to have a galvanized finish | Agree | Condition is not compelling | TD-1001M REV5 ET Preventative Maintenace Manual |  | N/A | No | N/A | No
41196201 | Steel | Concord | 087/568 | 2021-12-06 | 2020-11-17 | 2020-08-29 | Structure Issues: Insulator hanger (eye) plate in poor condition | FALSE | These photos are insufficient to assess the condition of the insulator hanger plate because photo quality is low and the components partially obscure each other. | Disagree | Condition is not compelling | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | Photos provided are sufficient to evaluate the hanger plate condition. More than 1/2" material remaining. Refer to table 4 in TD-1001M | N/A | No | N/A | No
41196201 | Steel | Concord | 087/568 | 2021-12-06 | 2020-11-17 | 2020-08-29 | Insulator Issues: Insulators are damaged, contaminated, or in poor condition | FALSE | TRUE: Insulator bells shows signs of corrosion, and the porcelain skirt glaze has signs of crazing to the finis | Disagree | Condition is not compelling | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | Contamination (Light) Rust/Worn less than 30 %. Refer to table 4 in TD-1001M | N/A | No | N/A | No
41196201 | Steel | Concord | 087/568 | 2021-12-06 | 2020-11-17 | 2020-08-29 | Insulator Issues: Insulators' hardware cold-end in poor condition (e.g. C-hoo | FALSE | These photos are insufficient to assess the condition of the cold-end hardware because the hanger plate and clamp partially obscure each other. | Disagree | Condition is not compelling | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | Photos provided are sufficient to evaluate cold end hardware condition. | N/A | No | N/A | No
41196201 | Steel | Concord | 087/568 | 2021-12-06 | 2020-11-17 | 2020-08-29 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road | Agree | Condition is not compelling | TD-1009S |  | N/A | No | N/A | No
44652045 | Steel | Lakeville | 015/006 | 2021-12-06 | 2020-11-17 | 2020-05-26 | Structure Issues: Insulator hanger (eye) plate in poor condition | FALSE | These photos are insufficient to assess the condition of the hanger plate because it is partially obscured by a c-hook. | Disagree | Condition is not compelling | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | Photos provided are sufficient to evaluate the hanger plate condition. More than 1/2" material remaining. Refer to table 4 in TD-1001M | N/A | No | N/A | No
44652045 | Steel | Lakeville | 015/006 | 2021-12-06 | 2020-11-17 | 2020-05-26 | Insulator Issues: Insulators' hardware cold-end in poor condition (e.g. C-hook) | FALSE | These photos are insufficient to assess the condition of the cold-end hardware because the eyelet connector and c-hook partially obscure each other | Disagree | Condition is not compelling | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | Rust/worn less than 30%, refer to table 4 TD-1001M. There are multiple images captured to evaluate condition | N/A | No | N/A | No
44652045 | Steel | Lakeville | 015/006 | 2021-12-06 | 2020-11-17 | 2020-05-26 | Is the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be within 600 feet of a dwelling. | Agree | Condition is not compelling | TD-1009S |  | N/A | No | N/A | No
40861940 | Wood | Moss Landing | 000/008 | 2021-12-15 | 2020-11-18 | 2020-08-18 | Vehicular and mechanical issues: Bird, animal or insect damage (e.g. woodpecker) | FALSE | TRUE: There appears to be damage from a woodpecker or insect activity on the pole between the top and distribution cross arms. | Agree | Condition is not compelling | TD-1001M-JA06 Wood Poles - Non Steel Framing | Other reference table 4 TD-1001M | N/A | No | N/A | No
40861940 | Wood | Moss Landing | 000/008 | 2021-12-15 | 2020-11-18 | 2020-08-18 | Vegetation Issues: Vegetation removal required. | FALSE | True appears to be vegetation around the guy anchor. | Disagree | Condition does not exist | TD-1001M-JA20 Vegetation Non-conformance Job Aid | vegetation is not contacting the guy wire above the 506 Bob. Vegetation is not impacting climbing or ability to inspect. TD-1001M, TD-2305M | N/A | No | N/A | No
40861940 | Wood | Moss Landing | 000/008 | 2021-12-15 | 2020-11-18 | 2020-08-18 | Is there a distribution issue on a transmission structure with a distribution underbuild? | Blank | True: There appears to be cracking and rotting on the top of the cross arms. Additinally the transformer has oil seeping from one of the bushings. | Agree | N/A | TD-1001M REV5 ET Preventative Maintenace Manual | EC 101751045 Created. Replaced Crossarms, TXFMR, C/O with fuses | N/A | Yes | Yes | No
40861940 | Wood | Moss Landing | 000/008 | 2021-12-15 | 2020-11-18 | 2020-08-18 | Is the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road | Agree | Condition is not compelling | TD-1009S |  | N/A | No | N/A | No
40906443 | Wood | Eureka | 028/006 | 2021-12-15 | 2020-11-18 | 2020-08-04 | Does or should this structure have a guy? | FALSE | Yes: There appears to be guy wires on structures | Agree | Condition is not compelling | TD-1001M-JA13 Guys and Anchors |  | N/A | No | N/A | No
40906443 | Wood | Eureka | 028/006 | 2021-12-15 | 2020-11-18 | 2020-08-04 | Guy Issues: Load bearing guys loose | FALSE | TRUE: The guy wire insulating rod hardware appears loose at the top of the pole. | Disagree | Condition does not exist | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | Bolts do not appear to be backed off, no Gap between nuts and bonding . | N/A | No | N/A | No
40906443 | Wood | Eureka | 028/006 | 2021-12-15 | 2020-11-18 | 2020-08-04 | Type of insulator? | Polymer | Porcelain/Ceramic: The insulators apper to be porcelain | Agree | Condition is not compelling | TD-1001M REV5 ET Preventative Maintenace Manual |  | N/A | No | N/A | No
40906443 | Wood | Eureka | 028/006 | 2021-12-15 | 2020-11-18 | 2020-08-04 | Type of splice | FALSE | TRUE: There appears to be three compression splices within 10 feet of the hot end insulator. | Disagree | Condition does not exist | TD-1001M-JA14 Splices Job Aid | Per LC 115680455 completed work 12/10/2019 splices are 10' out, dampers installed. | N/A | No | N/A | No
40906443 | Wood | Eureka | 028/006 | 2021-12-15 | 2020-11-18 | 2020-08-04 | Is a splice within 10' of hot end insulator? | Blank | TRUE: There appears to be three compression splices within 10 feet of the hot end insulator. | Disagree | Condition does not exist | TD-1001M-JA14 Splices Job Aid | Per LC 115680455 completed work 12/10/2019 splices are 10' out, dampers installed. | N/A | No | N/A | No
40906430 | Wood | Eureka | 027/003 | 2021-12-15 | 2020-11-19 | 2020-06-03 | Anchor Rod Issues: Guy Anchor head is burried | FALSE | TRUE: The anchor head appears to be burried below ground level. | Disagree | Condition does not exist | TD-1001M-JA13 Guys and Anchors | Zoomed in an other images (DJI_0006.JPG), able to confirm anchor is not burried | N/A | No | N/A | No
40906430 | Wood | Eureka | 027/003 | 2021-12-15 | 2020-11-19 | 2020-06-03 | Vehicular and mechanical Issue: Earth arounf structure eroded, soil movement, slide | FALSE | TRUE: The pole butt does not appear to be covered with compacted earth. | Agree | N/A | TD-1001M REV5 ET Preventative Maintenace Manual | DXI9 created S-5 122985919 on 2/15/22 | N/A | Yes | Yes | No
40906430 | Wood | Eureka | 027/003 | 2021-12-15 | 2020-11-19 | 2020-06-03 | Structure Issues: Insulator hanger (eye) plate in poor condition | FALSE | These photos are insufficient to assess the condition of the hanger plate because it is partially obscured by a c-hook. | Disagree | Condition does not exist | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | Photos provided are sufficient to evaluate cold end hardware condition. More than 1/2" material remaining. Refer to TD-1001M table 4 | N/A | No | N/A | No
40906430 | Wood | Eureka | 027/003 | 2021-12-15 | 2020-11-19 | 2020-06-03 | Insulator Issues: Insulators hardware cold-end in poor condition (e.g.C-Hook) | FALSE | These photos are insufficient to assess the condition of the cold-end hardware because the hanger plate and c-hook partially obscure each other. | Disagree | Condition does not exist | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | Rust/worn less than 30%, refer to table 4 TD-1001M. Other drone photos can be used to evaluate conditions. | N/A | No | N/A | No
40906430 | Wood | Eureka | 027/003 | 2021-12-15 | 2020-11-19 | 2020-06-03 | Conductor Issues: Conductor is in poor condition | FALSE | True: The conductor appears to be birdcaged on the outside phase, just past damper. | Disagree | Condition is not compelling | TD-1001M-JA10 Conductor Conditions | Minor birdcaging, no compelling conditions to report. | N/A | No | N/A | No
40906430 | Wood | Eureka | 027/003 | 2021-12-15 | 2020-11-19 | 2020-06-03 | Type of splice: Compression | FALSE | TRUE: there appears to be three compression splices. | Agree | Condition is not compelling | TD-1001M-JA14 Splices Job Aid |  | N/A | No | N/A | No
40906430 | Wood | Eureka | 027/003 | 2021-12-15 | 2020-11-19 | 2020-06-03 | Are 2 or more splices present in any one phase per span. | Blank | TRUE: There appear to be two splices present on one phase. | Agree | Condition is not compelling | TD-1001M-JA14 Splices Job Aid |  | N/A | No | N/A | No
40585669 | Steel | Pismo Beach | 054/301 | 2021-12-15 | 2020-12-09 | 2020-05-15 | Tower finish type | weathered | Painted: The structure appears to have a painted finish with pervasive rust. | Disagree | Condition does not exist | TD-1001M-JA04 Steel Structures Corrosion and Deteriation | Tower finish is galvinized. LC 116862640 was created on 3/29/19 to paint structure | N/A | No | N/A | No
40585669 | Steel | Pismo Beach | 054/301 | 2021-12-15 | 2020-12-09 | 2020-05-15 | Structure Issues: Insulator hanger (eye) plate in poor condition | FALSE | These photos are insufficient to assess the condition of the hanger plate because it is partially obscured by a c-hook. | Disagree | Condition does not exist | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | Photos provided are sufficient to evaluate cold end hardware condition. More than 1/2" material remaining. Refer to TD-1001M table 4 | N/A | No | N/A | No
40585669 | Steel | Pismo Beach | 054/301 | 2021-12-15 | 2020-12-09 | 2020-05-15 | Insulator Issues: Insulators' hardware cold-end in poor condition (e.g. C-hook) | FALSE | These photos are insufficient to assess the condition of the cold-end hardware because the hanger plate and clamp partially obscure each other. | Disagree | Condition does not exist | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | Rust/worn less than 30%, refer to table 4 TD-1001M. | N/A | No | N/A | No
44420231 | Steel | Fresno | 039/238 | 2021-12-15 | 2020-12-09 | 2020-06-04 | Is vegetation preesent? | FALSE | Yes: Vegetation appears to be present at the foundation | Agree | Condition is not compelling | TD-1001M REV5 ET Preventative Maintenace Manual |  | N/A | No | N/A | No
44420231 | Steel | Fresno | 039/238 | 2021-12-15 | 2020-12-09 | 2020-06-04 | Is the shield wire or fiber grounded? | Blank | TRUE: The overhead ground wire appears to be grounded via structure. | Agree | Condition is not compelling | TD-1001M-JA11 OPGW |  | N/A | No | N/A | No
44420231 | Steel | Fresno | 039/238 | 2021-12-15 | 2020-12-09 | 2020-06-04 | Is the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be within 600 feet of multiple dwellings. | Agree | Condition is not compelling | TD-1009S |  | N/A | No | N/A | No
44420231 | Steel | Fresno | 039/238 | 2021-12-15 | 2020-12-09 | 2020-06-04 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road | Agree | Condition is not compelling | TD-1009S |  | N/A | No | N/A | No
44699315 | Steel | Victor | 18/005A | 2021-12-15 | 2021-01-12 | 2020-04-27 | Structure Issues: Insulator hanger (eye) plate in poor condition | FALSE | These photos are insufficient to assess the condition of the hanger plate because it is partially obscured by a c-hook. | Disagree | Condition does not exist | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | Photos provided are sufficient to evaluate cold end hardware condition. More than 1/2" material remaining. Refer to TD-1001M table 4 | N/A | No | N/A | No
44699315 | Steel | Victor | 18/005A | 2021-12-15 | 2021-01-12 | 2020-04-27 | Type of insulator? | Porcelain/Ceramic | Polymer, Porcelain/Ceramic: The structue appears to have both percelain and polymer insulators. | Agree | Condition is not compelling | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 |  | N/A | No | N/A | No
44699315 | Steel | Victor | 18/005A | 2021-12-15 | 2021-01-12 | 2020-04-27 | Insulator Issues: Insulators' hardware cold-end in poor condition (e.g. C-hook) | FALSE | The photos are insufficient to assess the condition of the cold-end hardware because the hanger plate and c-hook partially obscure each other. | Disagree | Condition does not exist | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | Rust/worn less than 30%, refer to table 4 TD-1001M. | N/A | No | N/A | No
44699315 | Steel | Victor | 18/005A | 2021-12-15 | 2021-01-12 | 2020-04-27 | Is the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be within 600 feet of multiple dwellings. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40661806 | Wood | Eureka | 003/002 | 2021-12-21 | 2021-01-14 | 2020-07-24 | Does or should this structure have a guy? | FALSE | Yes: The structure appears to have guys. | Disagree | Condition does not exist | TD-1009S | Guys are at Distribution Level , Not recognized in 2020 Drone inspections | N/A | No | No | No
40661806 | Wood | Eureka | 003/002 | 2021-12-21 | 2021-01-14 | 2020-07-24 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be within 600 feet of a frequently traveled trail. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40594504 | Steel | Pismo Beach | 015/102 | 2021-12-21 | 2020-11-19 | 2020-07-08 | Insulator Issues: Insulators are damaged, contaminated, or in poor condition | FALSE | TRUE: There appear to be bird droppings contaminating the insulators. | Agree | Condition is not compelling | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | LC 119353997 was created on 7/10/21, on 3/8/21 CIRT Reviewed an additional FSR and Cancelled this Notification, Weather Cleaned insulators | N/A | No | No | No
40594504 | Steel | Pismo Beach | 015/102 | 2021-12-21 | 2020-11-19 | 2020-07-08 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40615921 | Wood | Table Mountain | 000/010 | 2021-12-21 | 2020-11-30 | 2020-06-01 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and immediately next to a frequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40616965 | Wood | Table Mountain | 053/1034 | 2021-12-21 | 2020-11-16 | 2020-07-16 | Insulator Issues: Insulators' hardware hot-end/shoe clamp assembly in poor condition | FALSE | TRUE: One of the conductors does not appear to be seated properly in the insulator. | Agree | N/A | TD-1001M-JA10 Conductor Conditions | SDRE created LC on 12/23/21, Notification Number 122514108 | Create a LC | No | Yes | Yes | Escalated to AIR + team on 12/21/21, Air Replied No Notification Needed | Air Replied No LC needed on 12/22/21, Sent To T line CIRT for conformation and Training on 12/22/21 | SDRE created LC on 12/23/21, Notification Number 122514108
40616965 | Wood | Table Mountain | 053/1034 | 2021-12-21 | 2020-11-16 | 2020-07-16 | s the shield wire or fiber in poor condition? | FALSE | The photos are insufficient to determine whether fiber is properly seated in the bracket. | Disagree | Condition does not exist | TD-1001M-JA11 OPGW | Sherlock Photo 200701_204035_Oeec6229.jpg clearly shows Fiber Messenger cable seated Properly | N/A | No | N/A | No
40656341 | Steel | Table Mountain | 009/083 | 2021-12-21 | 2020-11-05 | 2020-06-04 | Foundation Issues: Concrete damaged or in poor condition | FALSE | TRUE: The concrete foundation appears to be crumbling on one tower leg. | Agree | N/A | TD-1001M-JA12 Foundation Condition TLine Structures & Supports | LC 115784136 was created on 2/4/2019 for this FDA, CIRT is reviewing | N/A | No | N/A | No
40656341 | Steel | Table Mountain | 009/083 | 2021-12-21 | 2020-11-05 | 2020-06-04 | Insulator Issues: Clamps in poor condition | FALSE | TRUE: The shoes appear to show signs of rust and the hardware appears to be in poor condition. | Agree | N/A | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | LC 119466178 was created on 8/11/20. CIRT cancelled stating that this work will be completed undrer LC 115784751 | N/A | No | N/A | No
40656341 | Steel | Table Mountain | 009/083 | 2021-12-21 | 2020-11-05 | 2020-06-04 | Insulator Issues: Insulators' hardware cold-end in poor condition (e.g. C-hook) | FALSE | TRUE: The photos are insufficient to assess the condition of the cold-end hardware due to photo quality and because the hanger plate and shackle partially obscure each other. However, the cold-end hardware shows signs of corrosion and deterioration on three insulator strings. | Agree | N/A | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | LC 119466178 was created on 8/11/20. CIRT cancelled stating that this work will be completed undrer LC 115784751 | N/A | No | N/A | No
40662205 | Wood | Eureka | 025/012 | 2021-12-21 | 11/19/2020 | 2020-07-31 | Is the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40769170 | Wood | Lakeville | 033/004 | 2021-12-21 | 11/17/2020 | 2020-09-11 | Vehicular and Mechanical Issues: Breaks or cracks or split in pole | FALSE | TRUE: There appears to be a large crack on the pole between the crossarm support. | Disagree | Condition is not compelling | TD-1001M-JA06 Wood Poles - Non Steel Framing | N/A | N/A | No | No | No
40769170 | Wood | Lakeville | 033/004 | 2021-12-21 | 11/17/2020 | 2020-09-11 | Framing Issues: Loose or missing bolts and nuts | FALSE | TRUE: The top insulator support bolts appear to be loose. | Disagree | Condition does not exist | TD-1001M-JA06 Wood Poles - Non Steel Framing | Bolts Are Not Loose | N/A | No | No | No
40769170 | Wood | Lakeville | 033/004 | 2021-12-21 | 11/17/2020 | 2020-09-11 | Is vegetation present? | FALSE | TRUE: Vegetation appears to be in close proximity to the structure and possibly the conductor. The photos are insufficient to determine the vegetation’s precise proximity to the conductor. | Disagree | Condition does not exist | TD-1001M-JA20 Vegetation Non-conformance Job Aid | Escalated to Air Team 12/21/21, Air Replied 12/22/21 No LC Needed | N/A | No | No | Yes | Escalated to Air Team 12/21/21, Extensive search found no other inspections | Air Replied on 12/22/21 No LC Needed
40815734 | Wood | Table Mountain | 007/017 | 2021-12-21 | 11/30/2020 | 2020-06-03 | Does or should this structure have a guy? | FALSE | TRUE: The structure appears to have two guys. | Disagree | Condition does not exist | TD-1009S | Guys are at Distribution Level, Not recognized in 2020 inspections | N/A | No | No | No
40817119 | Wood | Table Mountain | 017/340 | 2021-12-21 | 11/19/2020 | 2020-10-05 | Is Overhead Ground Wire/Fiber section applicable? | FALSE | TRUE: There appears to be fiber on the messenger wire. | Agree | Condition is not compelling | TD-1001M REV5 ET Preventative Maintenace Manual | N/A | N/A | No | No | No
40817119 | Wood | Table Mountain | 017/340 | 2021-12-21 | 11/19/2020 | 2020-10-05 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road or trail. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40820035 | Steel | Victor | 007/055 | 2021-12-21 | 11/16/2020 | 2020-05-12 | Structure Issues: Insulator hanger (eye) plate in poor condition | FALSE | The photos are insufficient to assess the condition of the hanger plate. | Disagree | Condition is not compelling | TD-1001M REV5 ET Preventative Maintenace Manual | 2021 Inspection Photos show cold end attachments and Hanger Plates in Good repair | N/A | No | No | No
40820035 | Steel | Victor | 007/055 | 2021-12-21 | 11/16/2020 | 2020-05-12 | Insulator Issues: Insulators' hardware cold-end in poor condition (e.g. C-hook) | FALSE | The photos are insufficient to assess the condition of the cold-end hardware. | Disagree | Condition does not exist | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | 2021 Inspection Photos show cold end attachments and Hanger Plates in Good repair | N/A | No | No | No
40820035 | Steel | Victor | 007/055 | 2021-12-21 | 11/16/2020 | 2020-05-12 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40857794 | Steel | Concord | A001/009 | 2021-12-21 | 11/30/2020 | 2020-06-11 | Structure Issues: Insulator hanger (eye) plate in poor condition | FALSE | These photos are insufficient to assess the condition of the hanger plate. | Disagree | Condition does not exist | TD-1001M-JA23 Idle Line Investigation | Sherlock Photos show Hanger Plates in Good Repair | N/A | No | No | No
40857794 | Steel | Concord | A001/009 | 2021-12-21 | 11/30/2020 | 2020-06-11 | Insulator Issues: Insulators' hardware cold-end in poor condition (e.g. C-hook) | FALSE | These photos are insufficient to assess the condition of the cold-end hardware. | Disagree | Condition does not exist | TD-1001M REV5 ET Preventative Maintenace Manual | Sherlock Photos show all Hanger Plates and Cold end Hardware. PHOTO DJI_ 0502.JPG SHOWS EXTREME TRACKING ON INSULATOR CREATE LC | N/A | No | No | Yes | Escalated To air Team 12/21/21 | AIR found that fed monitor used incorrect spreadsheet
40859707 | Steel | Fresno | 015/078 | 2021-12-21 | 12/8/2020 | 2020-05-27 | Structure Issues: Damaged primary members | FALSE | TRUE: The primary members appear to be bent at each phase. | Agree | Condition is not compelling | TD-1001M-JA04 Steel Structures Corrosion and Deteriation | LC 119116817 was created for this FDA on 6/6/20, Cancelled by CIRT on 6/20/20 Damaged member does not affect the structure | N/A | No | No | No
40859707 | Steel | Fresno | 015/078 | 2021-12-21 | 12/8/2020 | 2020-05-27 | Structure Issues: Insulator hanger (eye) plate in poor condition | FALSE | These photos are insufficient to assess the condition of the hanger plate because the c-hook and hanger plate partially obscure each other. | Disagree | Condition does not exist | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | Sherlock shows all Hanger Plates and Cold end attachments clearly, No Issues | N/A | No | No | No
40859707 | Steel | Fresno | 015/078 | 2021-12-21 | 12/8/2020 | 2020-05-27 | Insulator Issues: Insulators are damaged, contaminated, or in poor condition | FALSE | TRUE: Polymer insulators at all three phases of tower appear to show discoloration at the hot end. | Agree | N/A | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | NInsulators showing Signs of Corona Damage , Missing Corona Rings | Create a LC | Yes | Yes | Yes | Escalated To air Team 12/21/21 | Air Replied on 12/22/21 LC only needed for missing Corona Rings, Fed Montor attached Incorrect Photos for This Location, Air to create LC 12/8/21
40862839 | Steel | ETL.5790 | 007/058 | 2021-12-21 | 11/19/2020 | 2020-04-27 | Structure Issues: Damaged secondary members | FALSE | TRUE: The structure appears to have a slightly bent secondary member. | Agree | N/A | TD-1001M-JA04 Steel Structures Corrosion and Deteriation | LC 116607815 For this FDA was completed on 7/24/2019 | N/A | No | No | No
40862839 | Steel | ETL.5790 | 007/058 | 2021-12-21 | 11/19/2020 | 2020-04-27 | Structure Issues: Steel Structure Hardware Loose or missing | FALSE | TRUE: There appear to be multiple missing bolts. | Disagree | Condition does not exist | TD-1001M-JA04 Steel Structures Corrosion and Deteriation | TYpe FA Tower, Drawing 402706 shows missing Hole 's are pulling eyes. No Issues40 | N/A | No | No | No
40862839 | Steel | ETL.5790 | 007/058 | 2021-12-21 | 11/19/2020 | 2020-04-27 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled trail. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40906591 | Wood | Eureka | 035/011 | 2021-12-21 | 10/26/2020 | 2020-10-09 | Anchor Rod Issues: Anchor damaged or in poor condition | FALSE | TRUE: The photos are not sufficient to determine the condition of the guy anchor. | Agree | Condition is not compelling | TD-1001M-JA20 Vegetation Non-conformance Job Aid | LC 119599240 Pole Replacement Veg Clearing Completed on 4/30/21 | N/A | No | No | No
40906591 | Wood | Eureka | 035/011 | 2021-12-21 | 10/26/2020 | 2020-10-09 | Guy Issues: Guy marker missing (GO 95 infraction) | FALSE | TRUE: There appear to be no guy markers. | Agree | Condition is not compelling | TD-1001M-JA20 Vegetation Non-conformance Job Aid | LC 119599240 Pole Replacement Veg Clearing Completed on 4/30/21 | N/A | No | No | No
40906591 | Wood | Eureka | 035/011 | 2021-12-21 | 10/26/2020 | 2020-10-09 | Insulator Issues: Insulators are damaged, contaminated, or in poor condition | FALSE | TRUE: The structure appears to have only four insulators (the Job Aid requires five insulators). | Agree | Condition is not compelling | TD-1001M-JA20 Vegetation Non-conformance Job Aid | LC 119599240 Pole Replacement Veg Clearing Completed on 4/30/21, Insulators added | N/A | No | No | No
40906591 | Wood | Eureka | 035/011 | 2021-12-21 | 10/26/2020 | 2020-10-09 | Are 2 or more splices present in any one phase per span? | BLANK | The photos are insufficient to view the entire span between the structures. | Agree | Condition is not compelling | TD-1001M REV5 ET Preventative Maintenace Manual | 2021 Inspection Photos show No Sleeves Or Flying Bells | N/A | No | No | No
40906591 | Wood | Eureka | 035/011 | 2021-12-21 | 10/26/2020 | 2020-10-09 | Are mid-span bells (aka flying bells) present? | FALSE | The photos are insufficient to view the entire span between structures. | Agree | Condition is not compelling | TD-1001M REV5 ET Preventative Maintenace Manual | 2021 Inspection Photos show No Sleeves Or Flying Bells | N/A | No | No | No
40906591 | Wood | Eureka | 035/011 | 2021-12-21 | 10/26/2020 | 2020-10-09 | Vegetation Issues: Significant vegetation around base | FALSE | TRUE: Vegetation appears around the base of the structure. | Agree | Condition is not compelling | TD-1001M-JA20 Vegetation Non-conformance Job Aid | LC 119599240 Pole Replacement Veg Clearing Completed on 4/30/21 | N/A | No | No | No
40906591 | Wood | Eureka | 035/011 | 2021-12-21 | 10/26/2020 | 2020-10-09 | Vegetation Issues: Vegetation removal required | FALSE | TRUE: While the photos are insufficient to assess the amount of vegetation around all of the guys and anchors, at least one guy appears to be covered in vegetation. | Agree | Condition is not compelling | TD-1001M-JA20 Vegetation Non-conformance Job Aid | LC 119599240 Pole Replacement Veg Clearing Completed on 4/30/21 | N/A | No | No | No
40906591 | Wood | Eureka | 035/011 | 2021-12-21 | 10/26/2020 | 2020-10-09 | Is there a distribution underbuild present? | FALSE | TRUE: A distribution underbuild appears to be present. | Agree | Condition is not compelling | TD-1001M-JA06 Wood Poles - Non Steel Framing | N/A | N/A | No | No | No
40906591 | Wood | Eureka | 035/011 | 2021-12-21 | 10/26/2020 | 2020-10-09 | Is the structure in a rural area and in an orchard? | TRUE | FALSE: The structure appears to be in a forested area, not an orchard. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
41176327 | Wood | Lakeville | :015/002 | 2021-12-21 | 11/17/2020 | 2020-07-30 | Is the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
41176327 | Wood | Lakeville | :015/002 | 2021-12-21 | 11/17/2020 | 2020-07-30 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
42551013 | Steel | Victor | 009/017 | 2021-12-21 | 10/30/2020 | 2020-09-12 | Birds Nest Issues: Bird nest within 5 feet of energized equipment | FALSE | TRUE: There appears to be a bird’s nest within 5 feet of energized equipment. | Agree | Condition is not compelling | TD-1001M-JA09 Bird Nests Job Aid | N/A | N/A | No | No | No
42551013 | Steel | Victor | 009/017 | 2021-12-21 | 10/30/2020 | 2020-09-12 | Vegetation Issues: Vegetation removal required | FALSE | TRUE: There appears to be vegetation surrounding the base of the structure. | Agree | Condition is not compelling | TD-1001M-JA20 Vegetation Non-conformance Job Aid | N/A | N/A | No | No | No
44145239 | Wood | Sacramento | 013/447 | 2021-12-21 | 11/17/2020 | 2020-10-19 | Anchor Rod Issues: Guy Anchor head buried | FALSE | The photos are insufficient to determine whether the anchor head is buried. | Agree | N/A | TD-1001M-JA13 Guys and Anchors | N/A | N/A | No | No | No
44145239 | Wood | Sacramento | 013/447 | 2021-12-21 | 11/17/2020 | 2020-10-19 | Guy Issues: Guy damaged or in poor condition | FALSE | TRUE: The guy guards appear to be damaged. | Agree | N/A | TD-1001M-JA13 Guys and Anchors | LC 119513457 For this FDA was cancelled by CIRT, Work completed under LC 120879264 on 4/26/21 | N/A | No | No | No
44191067 | Wood | Table Mountain | 005/107 | 2021-12-21 | 11/19/2020 | 2020-07-07 | Is vegetation present? | FALSE | TRUE: There appears to be vegetation present within 18 inches of the structure. | Agree | Condition is not compelling | TD-1001M REV5 ET Preventative Maintenace Manual | N/A | N/A | No | No | No
44191067 | Wood | Table Mountain | 005/107 | 2021-12-21 | 11/19/2020 | 2020-07-07 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled trail. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
44217582 | Wood | Table Mountain | 017/018 | 2021-12-21 | 11/5/2020 | 2020-11-04 | Vegetation Issues: Vegetation removal required | FALSE | TRUE: There appears to be vegetation at the base of the pole. | Disagree | Condition is not compelling | TD-1001M-JA20 Vegetation Non-conformance Job Aid | Vegetation is Present , No Issues | N/A | No | No | No
44629392 | Steel | Table Mountain | 008/180 | 2021-12-21 | 11/17/2020 | 2020-08-31 | Is vegetation present? | FALSE | TRUE: There appears to be vegetation around the structure. | Agree | Condition is not compelling | TD-1001M-JA20 Vegetation Non-conformance Job Aid | N/A | N/A | No | No | No
44649365 | Steel | Table Mountain | 006/080 | 2021-12-20 | 2020-11-18 | 2020-07-10 | Structure Issues: Insulator hanger (eye) plate in poor condition | FALSE | The photos are insufficient to assess the condition of the hanger plate. | Disagree | Condition does not exist | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | Sherlock photos 200624_173930_f6fcd23.jpg and 200624_183106_67dddc9c.jpg show Hanger Plates in good repair | N/A | No | No | No
44649365 | Steel | Table Mountain | 006/080 | 2021-12-20 | 2020-11-18 | 2020-07-10 | Insulator Issues: Insulators' hardware cold-end in poor condition (e.g. C-hook) | FALSE | The photos are insufficient to assess the condition of the cold-end hardware. | Disagree | Condition does not exist | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | Sherlock Photos 200624_173931_71fbc45e.jpg and 200624_183106_67dddc9c.jpg show al Cold end C hooks in good repair | N/A | No | No | No
44649365 | Steel | Table Mountain | 006/080 | 2021-12-20 | 2020-11-18 | 2020-07-10 | Is vegetation present? | FALSE | TRUE: There appears to be vegetation around the base of the pole. | Agree | Condition is not compelling | TD-1001M-JA20 Vegetation Non-conformance Job Aid | N/A | N/A | No | No | No
44843331 | Steel | Table Mountain | 000/014 | 2021-12-20 | 2020-11-17 | 2020-06-02 | s a splice within 10' of hot end of insulator? | FALSE | TRUE: There appears to be a compression splice on each phase within 10' of the hot end of the insulator. | Disagree | Condition does not exist | TD-1001M-JA14 Splices Job Aid | Sherlock Photo 44843331_015.JPG shows all Splices more than 10' from support | N/A | No | No | No
40588963 | Wood | Lakeville | 007/095 | 2021-12-20 | 2021-01-15 | 2020-08-07 | Is structure number missing? | FALSE | TRUE: The SAP number does not appear to be present. | Disagree | Condition does not exist | TD-1008P-03 Numbering & Marking OH Tline | Sap Number is not Required | N/A | No | No | No
40588963 | Wood | Lakeville | 007/095 | 2021-12-20 | 2021-01-15 | 2020-08-07 | Is the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40863343 | Steel | Victor | 003/028 | 2021-12-20 | 2021-01-15 | 2020-05-12 | Structure Issues: Insulator hanger (eye) plate in poor condition | FALSE | The photos are not suffic ie nt to determine the condition of the hanger plate. | Disagree | Condition does not exist | TD-1001M-JA04 Steel Structures Corrosion and Deteriation | Sherlock Photos DJI_0480.JPG , DJI_0503.JPG and DJI_0476.JPG show Hanger Plates and C Hooks. No Issues | N/A | No | No | No
40863343 | Steel | Victor | 003/028 | 2021-12-20 | 2021-01-15 | 2020-05-12 | Structure Issues: Steel Structure Hardware Loose or mis s in g | FALSE | TRUE: There appear to be s e ve ra l mis s in g b o lts . | Disagree | Condition does not exist | TD-1001M-JA04 Steel Structures Corrosion and Deteriation | TYpe FA Tower, Drawing 402706 shows missing Hole 's are pulling eyes. No Issues | N/A | No | No | No
40863343 | Steel | Victor | 003/028 | 2021-12-20 | 2021-01-15 | 2020-05-12 | Insulator Issues: Insulators' hardware cold-end in poor condition (e.g. C-hook) | FALSE | The photos are not suffic ie nt to determine the condition of the cold-end hardware. | Disagree | Condition does not exist | TD-1001M-JA04 Steel Structures Corrosion and Deteriation | Sherlock Photos DJI_0480.JPG , DJI_0503.JPG and DJI_0476.JPG show Hanger Plates and C Hooks. No Issues | N/A | No | No | No
40913098 | Steel | Sacramento | 005/061A | 2021-12-20 | 2021-01-15 | 2020-05-19 | Tower finis h type: | Painted | Galvanized: The structure appears to have a galvanized finis h. | Agree | Condition is not compelling | TD-1001M-JA04 Steel Structures Corrosion and Deteriation | N/A | N/A | No | No | No
40585924 | Steel | Table Mountain | 003/059 | 2021-12-20 | 2021-01-19 | 2020-05-28 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of afrequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
42564788 | Wood | Moss Landing | 016/317C | 2021-12-20 | 2021-01-19 | 2020-06-03 | Vehicular and Mechanical Issues: Bird , a nima l o r ins e c t damage (e.g., woodpecker) | FALSE | TRUE: There appears to be woodpecker damage at the top of the pole. | Agree | N/A | TD-1001M-JA06 Wood Poles - Non Steel Framing | LC 119775853 For This FDA was completed on 8/20/21 | N/A | No | No | No
42564788 | Wood | Moss Landing | 016/317C | 2021-12-20 | 2021-01-19 | 2020-06-03 | Vehicular and Mechanical Issues: Pole-top damage or s p lit-top | FALSE | TRUE: There appears to be splitting at the top of the pole. | Agree | Condition is not compelling | TD-1001M-JA06 Wood Poles - Non Steel Framing | N/A | N/A | No | No | No
40751140 | Wood | Lakeville | 018/005 | 2021-12-20 | 2021-01-20 | 2020-08-10 | Vehicular and Mechanical Is s ue s : Bird , a nima l o r ins e c t damage (e.g., woodpecker) | FALSE | TRUE: The pole appears to have woodpecker damage. | Agree | N/A | TD-1001M-JA06 Wood Poles - Non Steel Framing | LC 119378261 Indicates Pole was Replaced on 7/27/21 | N/A | No | No | No
40751140 | Wood | Lakeville | 018/005 | 2021-12-20 | 2021-01-20 | 2020-08-10 | Vehicular and Mechanical Issues: Breaks or cracks or s p lit in p o le | FALSE | TRUE: The pole appears to have several deep cracks. | Agree | N/A | TD-1001M-JA06 Wood Poles - Non Steel Framing | LC 119378261 Indicates Pole was Replaced on 7/27/21 | N/A | No | No | No
40751140 | Wood | Lakeville | 018/005 | 2021-12-20 | 2021-01-20 | 2020-08-10 | Vehicular and Mechanical Issues: Pole-top damage or s p lit-top | FALSE | TRUE: The top of the pole appears to have several cracks and appears to be splitting. | Agree | N/A | TD-1001M-JA06 Wood Poles - Non Steel Framing | LC 119378261 Indicates Pole was Replaced on 7/27/21 | N/A | No | No | No
40751140 | Wood | Lakeville | 018/005 | 2021-12-20 | 2021-01-20 | 2020-08-10 | Type of insula tor? | N/A | Porcelain/Ceramic: The insulators appear to be porcelain. | Agree | Condition is not compelling | TD-1001M REV5 ET Preventative Maintenace Manual | N/A | N/A | No | No | No
40751140 | Wood | Lakeville | 018/005 | 2021-12-20 | 2021-01-20 | 2020-08-10 | Is the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40751140 | Wood | Lakeville | 018/005 | 2021-12-20 | 2021-01-20 | 2020-08-10 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40808631 | Steel | Lakeville | :003/017 | 2021-12-20 | 2021-01-20 | 2020-05-05 | Is the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be in a rural area within600 feet ofa d we llin g. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
44695523 | Steel | Sacramento | 009/159 | 2021-12-20 | 2021-01-20 | 2020-10-06 | Guy Issues: Guy damaged or in poor condition | FALSE | TRUE: The guy wire does not appear to be under tension. | Agree | N/A | TD-1001M-JA13 Guys and Anchors | LC 117546955 for this FDA was completed on 11/16/20 | N/A | No | No | No
44695523 | Steel | Sacramento | 009/159 | 2021-12-20 | 2021-01-20 | 2020-10-06 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled trail. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
41176341 | Wood | Lakeville | 015/016 | 2021-12-20 | 2021-01-25 | 2020-07-30 | Guy Issues: Guy insulato r in poor condition | FALSE | TRUE: Guys appear to be too close to the underbuild(within the six-foot “Cylinder of Proximity” identified in the Job Aid) and fiberglass rods are missing. | Agree | N/A | TD-1001M-JA13 Guys and Anchors | LC 115642338 to replace pole was completed on 3/5/21 | N/A | No | No | No
41176341 | Wood | Lakeville | 015/016 | 2021-12-20 | 2021-01-25 | 2020-07-30 | Is there a distribut io n issue on a transmis s io n structure with a distribut io n underbuild? | FALSE | TRUE: The d is trib ut io n crossarm appears to be older and the insulato r is under s tre s s , in p o te ntia l fa ilu re mode. | Agree | N/A | TD-1001M REV5 ET Preventative Maintenace Manual | LC 115642338 to replace pole was completed on 3/5/21 | N/A | No | No | No
41176341 | Wood | Lakeville | 015/016 | 2021-12-20 | 2021-01-25 | 2020-07-30 | Is the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be in a rural area and within 600feet of a dwelling. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
41176341 | Wood | Lakeville | 015/016 | 2021-12-20 | 2021-01-25 | 2020-07-30 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40581881 | Wood | Moss Landing | 015/136 | 2021-12-20 | 2021-01-26 | 2020-08-10 | Vehicular and Mechanical Issues: P o le-top damage or s p lit-top | FALSE | TRUE: The top of the pole appears to have cracks. | Agree | Condition is not compelling | TD-1001M-JA06 Wood Poles - Non Steel Framing | N/A | N/A | No | No | No
40581881 | Wood | Moss Landing | 015/136 | 2021-12-20 | 2021-01-26 | 2020-08-10 | Type of insula tor? | P o lyme r | Porcelain/Ceramic: The insulators appear to be porcelain/ceramic, not p o lyme r. | Agree | Condition is not compelling | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | N/A | N/A | No | No | No
40587741 | Steel | Lakeville | 032/160 | 2021-12-20 | 2021-01-26 | 2020-04-14 | Foundation Issues: C oncrete damaged or in poor condition | FALSE | TRUE: One concrete footing appears to be damaged. | Agree | N/A | TD-1001M-JA12 Foundation Condition TLine Structures & Supports | LC 119794506 for this FDA was completed on 9/22/20 | N/A | No | No | No
40587741 | Steel | Lakeville | 032/160 | 2021-12-20 | 2021-01-26 | 2020-04-14 | Is the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40587741 | Steel | Lakeville | 032/160 | 2021-12-20 | 2021-01-26 | 2020-04-14 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40702880 | Wood | Lakeville | 021/012 | 2021-12-20 | 2021-01-26 | 2020-05-13 | Is a splice within 10' of hot end of insulator? | FALSE | TRUE: There appear to be three splices within 10' of the hot end of the insulator. | Disagree | Condition does not exist | TD-1001M-JA14 Splices Job Aid | Sherlock Photo DJI-0165.JPG, DJI 0189.JPG& DJI_0174.JPG show no splices within 10' of support | N/A | No | No | No
40702880 | Wood | Lakeville | 021/012 | 2021-12-20 | 2021-01-26 | 2020-05-13 | Is the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40702880 | Wood | Lakeville | 021/012 | 2021-12-20 | 2021-01-26 | 2020-05-13 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40827899 | Wood | Table Mountain | 010/129 | 2021-12-20 | 2021-01-26 | 2020-07-23 | Vehicular and Mechanical Issues: P o le-top damage or s p lit-top | FALSE | TRUE: There appears to be a crack at the pole-top that goes to the center of the pole. | Agree | Condition is not compelling | TD-1001M-JA06 Wood Poles - Non Steel Framing | N/A | N/A | No | No | No
40588807 | Wood | Eureka | 053/000 | 2021-12-20 | 1/27/2021 | 2020-08-03 | Vehicular and Mechanical Issues: Pole-top damage or s p lit-top | FALSE | TRUE: There appears to be a crack at the pole-top that goes to the center of the pole. | Agree | Condition is not compelling | TD-1001M-JA06 Wood Poles - Non Steel Framing | N/A | N/A | No | No | No
40588807 | Wood | Eureka | 053/000 | 2021-12-20 | 1/27/2021 | 2020-08-03 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled trail. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40693125 | Wood | Table Mountain | 012/264 | 2021-12-20 | 1/27/2021 | 2020-05-29 | Is the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40693125 | Wood | Table Mountain | 012/264 | 2021-12-20 | 1/27/2021 | 2020-05-29 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequent ly traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40804940 | Steel | Concord | 002/016 | 2021-12-20 | 2021-01-27 | 2020-04-20 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequent ly traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
41144146 | Wood | Table Mountain | 006/113 | 2021-12-20 | 2021-01-27 | 2020-05-14 | Vehicular and Mechanical Issues: P o le-top damage or s p lit-top | FALSE | TRUE: The pole-top appears to b e s p littin g in line with the hardware bolts. | Disagree | Condition is not compelling | TD-1001M-JA06 Wood Poles - Non Steel Framing | N/A | N/A | No | No | No
41176369 | Wood | Lakeville | 017/005 | 2021-12-20 | 1/27/2021 | 2020-07-30 | Vehicular and Mechanical Issues: Breaks or cracks or s p lit in p o le | FALSE | TRUE: There appear to be vertical cracks from the top to the bottom of the pole. | Agree | Condition is not compelling | TD-1001M-JA06 Wood Poles - Non Steel Framing | LC 119330362 was craeted on 7/8/21 for this FDA, CIRT deternimed condition is acceptable. | N/A | No | No | No
41176369 | Wood | Lakeville | 017/005 | 2021-12-20 | 1/27/2021 | 2020-07-30 | Type of insula tor? | FALSE | Porcelain/Ceramic: The tra ns mis s io n ins ula to rs appear to be porcelain only. | Agree | Condition is not compelling | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | N/A | N/A | No | No | No
41176369 | Wood | Lakeville | 017/005 | 2021-12-20 | 1/27/2021 | 2020-07-30 | Birds Nest Issues: Bird nest within 5 feet of energized equipment | FALSE | TRUE: There appears to be evidence of a bird's nest inside the insulato r mounting bracket. | Agree | Condition is not compelling | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | N/A | N/A | No | No | No
44142064 | Steel | Table Mountain | 021/326 | 2021-12-20 | 1/27/2021 | 2020-07-06 | Vegetation Issues: Signific a nt vegetatio n around base | FALSE | TRUE: There appears to be a bush growing around the base of the pole. | Disagree | Condition does not exist | TD-1001M-JA20 Vegetation Non-conformance Job Aid | N/A | N/A | No | No | No
44142064 | Steel | Table Mountain | 021/326 | 2021-12-20 | 1/27/2021 | 2020-07-06 | Is the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
44811141 | Steel | Lakeville | 008/006 | 2021-12-20 | 2021-01-27 | 2020-08-25 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of afrequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40761337 | Wood | Lakeville | 008/096 | 2021-12-20 | 1/28/2021 | 2020-07-21 | Vehicular and Mechanical Issues: Pole-top damage or s p lit-top | FALSE | TRUE: The pole appears to have a split top. | Agree | Condition is not compelling | TD-1001M-JA06 Wood Poles - Non Steel Framing | N/A | N/A | No | No | No
44291269 | Wood | Sacramento | 007/209 | 2021-12-20 | 2021-01-28 | 2020-06-01 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
44291269 | Wood | Sacramento | 007/209 | 2021-12-20 | 2021-01-28 | 2020-06-01 | Is the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40823352 | Wood | Metcalf | ?009/007 | 2021-12-20 | 2/2/2021 | 2020-04-27 | Type of Splice: Compression | FALSE | TRUE: There appears to be a c o mp re s s io n s p lic e . | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40823352 | Wood | Metcalf | ?009/007 | 2021-12-20 | 2/2/2021 | 2020-04-27 | Is vegetation present? | FALSE | The photos are insuffic ie nt to determine the vegetation’s proximity to the pole. | Disagree | Condition does not exist | TD-1001M-JA20 Vegetation Non-conformance Job Aid | Sherlock Photo 40823352_036.JPG Clearly shows perimetor of Pole, No Vegetation issues | N/A | No | No | No
40823352 | Wood | Metcalf | ?009/007 | 2021-12-20 | 2/2/2021 | 2020-04-27 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40866251 | Steel | Concord | 011/048 | 2021-12-20 | 2021-02-02 | 2020-04-22 | Foundation Issues: C oncrete damaged or in poor condition | FALSE | TRUE: The concrete on the foundation appears to be crumbling/de teriora ting. | Agree | N/A | TD-1001M-JA12 Foundation Condition TLine Structures & Supports | LC 120932714 for this FDA was created on 5/4/21 | N/A | No | No | No
40866251 | Steel | Concord | 011/048 | 2021-12-20 | 2021-02-02 | 2020-04-22 | Insulator Issues: Insulators' hardware cold-end in poor condition (e.g. C-hook) | FALSE | The photos are not suffic ie nt to determine the condition of the cold-end hardware. | Agree | N/A | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | LC 122209234 was created 10/14/21 to eplace all insulators and hot cold end attachments | N/A | No | No | No
40866251 | Steel | Concord | 011/048 | 2021-12-20 | 2021-02-02 | 2020-04-22 | Is the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be in a rural area and within 6 0 0 fe e t o f mult ip le dwellings. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40866251 | Steel | Concord | 011/048 | 2021-12-20 | 2021-02-02 | 2020-04-22 | Is the structure in a rural area and within 600 ft o f a frequently traveled road/trail | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
41129361 | Steel | Lakeville | 013/059 | 2021-12-20 | 2021-02-02 | 2020-07-07 | Is the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
41129361 | Steel | Lakeville | 013/059 | 2021-12-20 | 2021-02-02 | 2020-07-07 | Is thestructure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40646058 | Steel | Concord | 001/012 | 2021-12-20 | 2021-01-28 | 2020-04-20 | Foundation Issues: Earth around structure eroded, soil movement, slide | FALSE | TRUE: The soil appears to be eroded around the uphill, right-hand foundation stub. | Disagree | Condition is not compelling | TD-1001M-JA12 Foundation Condition TLine Structures & Supports | N/A | N/A | No | No | No
40646058 | Steel | Concord | 001/012 | 2021-12-20 | 2021-01-28 | 2020-04-20 | nsulator Issues: Insulators’hardware hot-end/shoe clamp assembly in poor condition | FALSE | TRUE: A hot-end insulator bell appears to be rusting at the hot end of the conductor. The photos are insufficient to assess the level of rusting. | Agree | N/A | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | LC 117928038 FOR this FDA was completed on 6/4/2020 | N/A | No | No | No
40646058 | Steel | Concord | 001/012 | 2021-12-20 | 2021-01-28 | 2020-04-20 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40746006 | Steel | Concord | 008/054 | 2021-12-20 | 2021-01-28 | 2020-05-01 | Birds Nest Issues: Bird/Animal guards in poor condition | FALSE | TRUE: The bird guard in the lower middle phase appears to be rustedand bent. | Agree | DXI9 created S-5 122985874 on 2/15/22 | TD-1001M-JA09 Bird Nests Job Aid | N/A | Create a LC | Yes | Yes | No | DXI9 created S-5 122985874 on 2/15/22
40746006 | Steel | Concord | 008/054 | 2021-12-20 | 2021-01-28 | 2020-05-01 | Is the structure in a rural area and w ithin 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40746006 | Steel | Concord | 008/054 | 2021-12-20 | 2021-01-28 | 2020-05-01 | Is the structure in arural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40870401 | Steel | Sacramento | 008/068 | 2021-12-20 | 1/28/2021 | 2020-07-23 | Structure Issues: Damaged secondary members | FALSE | TRUE: The structure appears to have a bent secondary in the lower section at the base on the dow nhill leg. | Agree | N/A | TD-1001M-JA04 Steel Structures Corrosion and Deteriation | lc 121488518 WAS CREATED ON 6/8/21 FOR THIS FDA | N/A | No | No | No
40870401 | Steel | Sacramento | 008/068 | 2021-12-20 | 1/28/2021 | 2020-07-23 | Type of insulator? | Po l yme r | Porcelain/Ceramic: The insulators appear to be porcelain/ceramic. | Agree | Condition is not compelling | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | N/A | N/A | No | No | No
40870401 | Steel | Sacramento | 008/068 | 2021-12-20 | 1/28/2021 | 2020-07-23 | iS the shield wire or fiber grounded? | TRUE | FALSE: The overhead ground wire does not appear to be trimmed (left) and ground wire (right) appears out of thimble. | Agree | N/A | TD-1001M-JA10 Conductor Conditions | LC 119518203 For this FDA was completed on 11/16/21 | N/A | No | No | No
40870401 | Steel | Sacramento | 008/068 | 2021-12-20 | 1/28/2021 | 2020-07-23 | Is the shield wire or fiber bracket in poor condition? | FALSE | TRUE: The shield wire preform does not appear to be seated in the thimble and appears to be birdcaged. | Agree | N/A | TD-1001M-JA10 Conductor Conditions | LC 119518203 For this FDA was completed on 11/16/21 | N/A | No | No | No
40870401 | Steel | Sacramento | 008/068 | 2021-12-20 | 1/28/2021 | 2020-07-23 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and located within 600 feet of afrequently traveledtrail. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40771645 | Steel | Moss Landing | 014/128 | 2021-12-20 | 2021-01-29 | 2020-04-02 | Is the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40771645 | Steel | Moss Landing | 014/128 | 2021-12-20 | 2021-01-29 | 2020-04-02 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40822217 | Steel | Concord | 002/016 | 2021-12-20 | 1/29/2021 | 2020-05-05 | Is vegetation present? | FALSE | TRUE: There appears to be vegetation within 10 feet of the structure. | Agree | Condition is not compelling | TD-1001M-JA20 Vegetation Non-conformance Job Aid | N/A | N/A | No | No | No
40822217 | Steel | Concord | 002/016 | 2021-12-20 | 1/29/2021 | 2020-05-05 | Is the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40822217 | Steel | Concord | 002/016 | 2021-12-20 | 1/29/2021 | 2020-05-05 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40584955 | Wood | Lakeville | 001/021 | 2021-12-20 | 2/2/2021 | 2020-07-21 | Birds Nest Issues: Bird nest within 5 feet of energized equipment | FALSE | TRUE: There appears to be abird’s nest w ithin 5 feet of the conductor. | Agree | Condition is not compelling | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | N/A | N/A | No | No | No
40584955 | Wood | Lakeville | 001/021 | 2021-12-20 | 2/2/2021 | 2020-07-21 | Is the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40584955 | Wood | Lakeville | 001/021 | 2021-12-20 | 2/2/2021 | 2020-07-21 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of afrequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40600705 | Wood | Table Mountain | A005/114 | 2021-12-20 | 2/2/2021 | 2020-09-14 | Vehicular and Mechanical Issues: Pole-top damage or split-top | FALSE | TRUE: The top of the pole appears to have cracks, andbolts appear to go through cracks. | Agree | Condition is not compelling | TD-1001M-JA06 Wood Poles - Non Steel Framing | LC 115638219 was created on 1/3/2019 to repair Wood pecker Damage, Completed 2/28/21 | N/A | No | No | No
40600705 | Wood | Table Mountain | A005/114 | 2021-12-20 | 2/2/2021 | 2020-09-14 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of afrequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40812205 | Wood | Table Mountain | 005/104 | 2021-12-20 | 2/2/2021 | 2020-10-02 | Vehicular and Mechanical Issues: Pole-top damage or split-top | FALSE | TRUE: The bolts appear to go through the cracks on the pole-top. | Disagree | Condition is not compelling | TD-1001M-JA06 Wood Poles - Non Steel Framing | LC 115643105 was created on 1/4/19, On 2/21/19 CIRT reviewed and found No compelling issues | N/A | No | No | No
40870122 | Steel | Pismo Beach | 013/059 | 2021-12-20 | 2/2/2021 | 2020-05-18 | Insulator Issues: Insulators are out-of-plumb (>1 bell out-of-plumb) | FALSE | TRUE: The insulator strings appear to be out-of-plumb. | Agree | Condition is not compelling | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | Insulator Plumb Requires Minimum 2 Bells out of Plumbr For LC, Non FDA | N/A | No | No | No
40870122 | Steel | Pismo Beach | 013/059 | 2021-12-20 | 2/2/2021 | 2020-05-18 | Vegetation Issues: Significant vegetation around base | FALSE | TRUE: There appears to be significant vegetation grow th around the base of the tower. | Agree | N/A | TD-1001M-JA20 Vegetation Non-conformance Job Aid | LC 119294986 For this FDA was completed on 1/6/21 | N/A | No | No | No
40870122 | Steel | Pismo Beach | 013/059 | 2021-12-20 | 2/2/2021 | 2020-05-18 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of afrequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
44388082 | Steel | Table Mountain | 004/043A | 2021-12-20 | 2/2/2021 | 2020-06-05 | Tow er finish type: | I don't know | Weathered: The structure appears to have a weathered finish. | Agree | Condition is not compelling | TD-1001M-JA04 Steel Structures Corrosion and Deteriation | N/A | N/A | No | No | No
40661659 | Wood | Lakeville | 022/002 | 2021-12-17 | 2021-02-03 | 2020-05-15 | Vehicular and Mechanical Issues: Pole-top damage or split-top | FALSE | TRUE: There appearsto be cracking and damage to the pole-top. | Disagree | Condition is not compelling | TD-1001M-JA06 Wood Poles - Non Steel Framing | LC 115590189 was created on 12/22/18, on 2/13/19 CIRT Cancelled this Notification , Cracks and checks are Natural No issues | N/A | No | No | No
40744727 | Steel | Table Mountain | 028/235 | 2021-12-17 | 2/3/2021 | 2020-05-19 | Structure Issues: Damaged secondary members | FALSE | TRUE: A secondary member appears to be bent. | Agree | N/A | TD-1001M-JA04 Steel Structures Corrosion and Deteriation | LC 121492353 was created on 6/8/21 for this FDA | N/A | No | No | No
40744727 | Steel | Table Mountain | 028/235 | 2021-12-17 | 2/3/2021 | 2020-05-19 | Is the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be in a rural area and within approximately 600 feet of a dwelling. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40744727 | Steel | Table Mountain | 028/235 | 2021-12-17 | 2/3/2021 | 2020-05-19 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of afrequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40746169 | Steel | Concord | 002/014 | 2021-12-17 | 2/3/2021 | 2020-04-20 | Foundation Issues: Earth around structure eroded, soil movement, slide | FALSE | TRUE: The earth around and below the concrete foundation appears to be eroded. | Disagree | Condition is not compelling | TD-1001M-JA04 Steel Structures Corrosion and Deteriation | Escalated to Air+ on 12/21/21, Air replied on 12/22/21 Eroson less than 1', No LC needed | N/A | No | No | Yes | Escalated To air Team 12/21/21 | Air Replied on 12/22/21 Erosion less than 1 foot No LC needed
40746169 | Steel | Concord | 002/014 | 2021-12-17 | 2/3/2021 | 2020-04-20 | Tow er finish type: | Weathered | Galvanized: The finish type appears to be galvanized or painted, not weathered. | Agree | Condition is not compelling | TD-1001M-JA04 Steel Structures Corrosion and Deteriation | N/A | N/A | No | No | No
40746169 | Steel | Concord | 002/014 | 2021-12-17 | 2/3/2021 | 2020-04-20 | Structure Issues: Damaged secondary members | FALSE | TRUE: A secondary member appears to be bent. | Agree | Condition is not compelling | TD-1001M-JA04 Steel Structures Corrosion and Deteriation | N/A | N/A | No | No | No
44859707 | Steel | Table Mountain | 013/106 | 2021-12-17 | 2/3/2021 | 2020-08-17 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
44859707 | Steel | Table Mountain | 013/106 | 2021-12-17 | 2/3/2021 | 2020-08-17 | Type of splice: Compression | FALSE | TRUE: Onecompressionsplice appears to be present on one of the outside phases. | Disagree | Condition does not exist | TD-1001M-JA10 Conductor Conditions | Sherlock shows No Sleeves within 10' of support | N/A | No | No | No
40769596 | Wood | Table Mountain | 001/014 | 2021-12-17 | 2/4/2021 | 2020-07-16 | Framing Issues: Loose or missing bolts and nuts | FALSE | TRUE: There appears to be a loose U-bolt at the top of the pole. | Disagree | Condition does not exist | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | Sherlock Photo 200706_182455_08455_0816c71c.jpg shows no loose hardware , Normal shrinkage of Pole | N/A | No | No | No
40817237 | Steel | Pismo Beach | 014/100 | 2021-12-17 | 2/4/2021 | 2020-07-02 | nsulator Issues: Insulators are damaged, contaminated, or in poor condition | FALSE | TRUE: The insulators on all three phases appear to have contamination from bird waste. | Disagree | Condition does not exist | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | Escalated to Air+ on 12/21/21, Air replied on 12/22/21 Not enough Contamination to be an issue | N/A | No | No | Yes | Escalated To air Team 12/21/21 | Air Replied 12/22/21 Not enough Contamination to be an Issue
44159597 | Wood | Table Mountain | 001/026 | 2021-12-17 | 2021-02-04 | 2020-05-29 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of afrequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
44229485 | Wood | Table Mountain | A004/103 | 2021-12-17 | 2/4/2021 | 2020-06-24 | Conductor Issues: Jumpers in poor condition | FALSE | TRUE: All three phases of the structure appear to have w arping and bird caging on the road-side jumpers. | Agree | Condition is not compelling | TD-1001M-JA10 Conductor Conditions | N/A | N/A | No | No | No
44229485 | Wood | Table Mountain | A004/103 | 2021-12-17 | 2/4/2021 | 2020-06-24 | Is the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be in a rural area and located within 600 feet of a dwelling. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
44673317 | Steel | Table Mountain | 002/056 | 2021-12-17 | 2021-02-04 | 2020-05-28 | Type of insulator? | Porcelain/Ceramic | Polymer: The structure appears to have polymer insulators. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40589422 | Wood | Moss Landing | 004/108 | 2021-12-17 | 2/9/2021 | 2020-08-18 | Is the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40589422 | Wood | Moss Landing | 004/108 | 2021-12-17 | 2/9/2021 | 2020-08-18 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of afrequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40598938 | Wood | Sacramento | 001/020 | 2021-12-17 | 2/9/2021 | 2020-07-02 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of afrequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40599532 | Wood | Table Mountain | 011/000 | 2021-12-17 | 2021-02-09 | 2020-08-31 | Vehicular and Mechanical Issues: Breaks or cracks or split in pole | FALSE | TRUE: There appear to be cracks on the structure where the guy hardware attaches to the pole. | Disagree | Condition is not compelling | TD-1001M-JA06 Wood Poles - Non Steel Framing | N/A | N/A | No | No | No
40599532 | Wood | Table Mountain | 011/000 | 2021-12-17 | 2021-02-09 | 2020-08-31 | High voltage/danger sign(s) missing or installed incorrectly per E.D. 022168? | FALSE | TRUE: The high voltage sign appears to be missing the word “high.” | Disagree | Condition does not exist | 022168 HV Signs, Marking, Numbering | HV Signs are on Pole below Cross arm | N/A | No | No | No
40599532 | Wood | Table Mountain | 011/000 | 2021-12-17 | 2021-02-09 | 2020-08-31 | Framing Issues: Loose or missing bolts and nuts | FALSE | TRUE: There appears to be loose hardware and bolts on the structure. | Agree | N/A | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | LC 119371050 For arm replacement was completed on 9/21/21 | N/A | No | No | No
40648476 | Steel | Lakeville | 038/003 | 2021-12-17 | 2/9/2021 | 2020-10-07 | Type of insulator? | Po l yme r | Polymer, Porcelain/Ceramic: The structure appears to have both porcelain and polymer insulators. | Agree | Condition is not compelling | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | N/A | N/A | No | No | No
40651984 | Wood | Table Mountain | 005/101 | 2021-12-17 | 2/9/2021 | 2020-10-05 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of afrequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40818194 | Steel | Concord | 022/122 | 2021-12-17 | 2021-02-09 | 2020-05-12 | Conductor Issues: Jumpers in poor condition | FALSE | TRUE: There appears to be conductor bird caging on the j ump e r . | Agree | Condition is not compelling | TD-1001M-JA10 Conductor Conditions | N/A | N/A | No | No | No
40818194 | Steel | Concord | 022/122 | 2021-12-17 | 2021-02-09 | 2020-05-12 | Type of Splice: Compression | FALSE | TRUE: The structure appears to have a compression splice. | Agree | N/A | TD-1001M-JA14 Splices Job Aid | N/A | N/A | No | No | No
40818194 | Steel | Concord | 022/122 | 2021-12-17 | 2021-02-09 | 2020-05-12 | Is the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
44639187 | Steel | Table Mountain | 001/028 | 2021-12-17 | 2/9/2021 | 2020-06-02 | Foundation Issues: Earth around structure eroded, soil movement, slide | FALSE | TRUE: There appears to be earth erosion around the base of the structure. | Agree | N/A | TD-1001M-JA04 Steel Structures Corrosion and Deteriation | Escalated to Air + on 12/21/21, Air replied 12/22/21 No Issue with Small animal Burrow | N/A | No | No | Yes | Escalated To air Team 12/21/21 | Air Replied on 12/22/21 No Issue " small animal Burrow"
44646264 | Steel | Pismo Beach | 007/083 | 2021-12-17 | 2021-02-09 | 2020-07-16 | Is a splice within 10' of hot end of insulator? | FALSE | TRUE: There appears to be a splice within 10 feet of the hot end of the insulator on the outside phase. | Disagree | Condition does not exist | TD-1001M-JA14 Splices Job Aid | Sherlock Photo DJI_0785.JPG shows splice more than 10' from support | N/A | No | No | No
44646264 | Steel | Pismo Beach | 007/083 | 2021-12-17 | 2021-02-09 | 2020-07-16 | Is there a distribution underbuild present? | TRUE | FALSE: The distribution appears to be a parallel separate line, not an underbuild. | Agree | Condition is not compelling | TD-1001M REV5 ET Preventative Maintenace Manual | N/A | N/A | No | No | No
44696021 | Wood | Lakeville | A007/138 | 2021-12-17 | 2/9/2021 | 2020-08-10 | Does or should this structure have a guy? | FALSE | TRUE: This structure appears to have a guy w ire. | Disagree | Condition does not exist | TD-1001M-JA13 Guys and Anchors | Guy is at Distribution Level | N/A | No | No | No
44696021 | Wood | Lakeville | A007/138 | 2021-12-17 | 2/9/2021 | 2020-08-10 | Anchor Rod Issues: Anchor damaged or in poor condition | FALSE | The photos areinsufficient to evaluate the anchor condition. | Disagree | Condition does not exist | TD-1001M-JA13 Guys and Anchors | Distribution Guy appears to be a span guy, No anchor Present | N/A | No | No | No
44696021 | Wood | Lakeville | A007/138 | 2021-12-17 | 2/9/2021 | 2020-08-10 | Is the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
44696021 | Wood | Lakeville | A007/138 | 2021-12-17 | 2/9/2021 | 2020-08-10 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of afrequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40611232 | Wood | Sacramento | 010/234 | 2021-12-17 | 2021-02-10 | 2020-05-27 | Vehicular and Mechanical Issues: Pole-top damage or split-top | FALSE | TRUE: The pole-top appears to be splitting in line with the through-bolts. | Agree | N/A | TD-1001M-JA06 Wood Poles - Non Steel Framing | LC 117908102 to install split bolts was completed on 5/13/20 | N/A | No | No | No
40611232 | Wood | Sacramento | 010/234 | 2021-12-17 | 2021-02-10 | 2020-05-27 | High voltage/danger sign(s) missing or installed incorrectly per E.D. 022168? | FALSE | TRUE: Half of the high-voltage sign appears to be damaged. | Disagree | Condition does not exist | 022168 HV Signs, Marking, Numbering | HV Signs are Below Distribution arm | N/A | No | No | No
40611232 | Wood | Sacramento | 010/234 | 2021-12-17 | 2021-02-10 | 2020-05-27 | Insulator Issues: Insulators' hardware cold-end in poor condition (e.g. C-hook) | FALSE | The photos are not sufficient to determine the condition of the cold-end hardware. | Disagree | Condition does not exist | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | Insulator Hardware is clearly visible | N/A | No | No | No
40611232 | Wood | Sacramento | 010/234 | 2021-12-17 | 2021-02-10 | 2020-05-27 | Vegetation Issues: Vegetation removal required | FALSE | TRUE: There appears to be heavy vegetation around the anchor. | Disagree | Condition does not exist | TD-1001M-JA20 Vegetation Non-conformance Job Aid | Anchors are clearly visible No vegetation issues | N/A | No | No | No
40693428 | Wood | Sacramento | 000/003 | 2021-12-17 | 2021-02-10 | 2020-05-28 | Insulator Issues: Insulators' hardware cold-end in poor condition (e.g. C-hook) | FALSE | TRUE: Nuts on cold-end hardware appear to be loose. | Agree | Condition is not compelling | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | LC 119723206 for this FDA was cancelled by CIRT, Hardware is acceptably Tight | N/A | No | No | No
40693428 | Wood | Sacramento | 000/003 | 2021-12-17 | 2021-02-10 | 2020-05-28 | Vegetation Issues: Vegetation removal required | FALSE | TRUE: There appears to be vegetation around the anchorrequiring removal. | Agree | N/A | TD-1001M-JA20 Vegetation Non-conformance Job Aid | LC 115506063 indicates Vegetation removed 11/8/19 | N/A | No | No | No
40770715 | Wood | Table Mountain | 011/219 | 2021-12-17 | 2/10/2021 | 2020-09-12 | Does or should this structure have a guy? | FALSE | TRUE: This structure appears to have guys. | Disagree | Condition does not exist | TD-1001M-JA13 Guys and Anchors | Guys are at Communication Level | N/A | No | No | No
40770715 | Wood | Table Mountain | 011/219 | 2021-12-17 | 2/10/2021 | 2020-09-12 | Anchor Rod Issues: Obstructed View | FALSE | TRUE: Theview of the anchor rods is obstructed. | Agree | Condition is not compelling | TD-1001M-JA13 Guys and Anchors | Guys are at Communication Level | N/A | No | No | No
40770715 | Wood | Table Mountain | 011/219 | 2021-12-17 | 2/10/2021 | 2020-09-12 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of afrequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
41129338 | Steel | Lakeville | 008/036 | 2021-12-17 | 2/10/2021 | 2020-05-06 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of afrequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
44374623 | Steel | Table Mountain | 011/200 | 2021-12-17 | 2021-02-10 | 2020-05-11 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of afrequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
44761247 | Steel | Lakeville | A006/090 | 2021-12-17 | 2021-02-10 | 2020-08-07 | Is the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
42564791 | Wood | Moss Landing | 017/326B | 2021-12-17 | 2/12/2021 | 2020-06-03 | Is the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
42564791 | Wood | Moss Landing | 017/326B | 2021-12-17 | 2/12/2021 | 2020-06-03 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of afrequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40672167 | Steel | Table Mountain | 021/142 | 2021-12-17 | 2/16/2021 | 2020-08-29 | Insulator Issues: Insulators' hardware cold-end in poor condition (e.g. C-hook) | FALSE | TRUE: There appears to be cold-end hardware wear. Photos are insufficient to determine the level of wear. | Disagree | Condition does not exist | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | Sent to air team 12/17/21, Air replied 12/19/21 No Compelling issues | N/A | No | No | Yes | Sent to Air Team 12/17/21 | Air Replied on 12/19/21, No Compelliing Issues
40809632 | Wood | Sacramento | 002/052 | 2021-12-17 | 2/16/2021 | 2020-08-29 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of afrequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40826517 | Wood | Table Mountain | 013/263 | 2021-12-17 | 2021-02-16 | 2020-07-07 | Is the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40826517 | Wood | Table Mountain | 013/263 | 2021-12-17 | 2021-02-16 | 2020-07-07 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of afrequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
44191086 | Wood | Table Mountain | 004/092A | 2021-12-17 | 2021-02-16 | 2020-07-02 | Anchor Rod Issues: Anchor damaged or in poor condition | FALSE | The photos w ere insufficient to determine the condition of the anchors. | Agree | Condition is not compelling | TD-1001M-JA13 Guys and Anchors | Sherlock 2021 shows no anchor issues | N/A | No | No | No
44191086 | Wood | Table Mountain | 004/092A | 2021-12-17 | 2021-02-16 | 2020-07-02 | Insulator Issues: Insulators are damaged, contaminated, or in poor condition | FALSE | TRUE: There appears to be a piece of the insulator missing on the inside-phase insulator near the cold-end hardware. | Disagree | Condition does not exist | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | All Sherlock Photos show no insulator issues | N/A | No | No | No
44191086 | Wood | Table Mountain | 004/092A | 2021-12-17 | 2021-02-16 | 2020-07-02 | Vegetation Issues: Significant vegetation around base | FALSE | TRUE: There appears to be significant vegetation near the base of the structure and around the pole. | Disagree | Condition is not compelling | TD-1001M-JA20 Vegetation Non-conformance Job Aid | N/A | N/A | No | No | No
40589928 | Wood | Sacramento | 009/167 | 2021-12-17 | 2/17/2021 | 2020-10-28 | Anchor Rod Issues: Obstructed View | FALSE | TRUE: The anchor on one of the guys appears to be obstructed by vegetation. | Agree | N/A | TD-1001M-JA20 Vegetation Non-conformance Job Aid | Sherlock 2021 Photo 210420_172640_649_e3499add.jpg shows vegetation cleared around anchor | N/A | No | No | No
40589928 | Wood | Sacramento | 009/167 | 2021-12-17 | 2/17/2021 | 2020-10-28 | Vehicular and Mechanical Issues: Bird, animal or insect damage (e.g., woodpecker) | FALSE | TRUE: There appear to be woodpecker holes near the top of the pole. | Agree | N/A | TD-1001M-JA06 Wood Poles - Non Steel Framing | LC 120788101 created on 4/10/21 pole will be Replaced | N/A | No | No | No
40589928 | Wood | Sacramento | 009/167 | 2021-12-17 | 2/17/2021 | 2020-10-28 | Vehicular and Mechanical Issues: Pole-top damage or split-top | FALSE | TRUE: The pole-top appears to have a large crack. | Agree | N/A | TD-1001M-JA06 Wood Poles - Non Steel Framing | LC 120788101 created on 4/10/21 pole will be Replaced | N/A | No | No | No
40589928 | Wood | Sacramento | 009/167 | 2021-12-17 | 2/17/2021 | 2020-10-28 | Type of Splice: Compression | FALSE | TRUE: There appears to be a compression splice on the conductor. | Agree | N/A | TD-1001M-JA14 Splices Job Aid | N/A | N/A | No | No | No
40589928 | Wood | Sacramento | 009/167 | 2021-12-17 | 2/17/2021 | 2020-10-28 | Is a splice within 10' of hot end of insulator? | BLANK | TRUE: One compression splice appears to be located w ithin ten feet of the hot end of the insulator. | Agree | N/A | TD-1001M-JA14 Splices Job Aid | LC 121364753 work was completed on 5/28/21 | N/A | No | No | No
40589928 | Wood | Sacramento | 009/167 | 2021-12-17 | 2/17/2021 | 2020-10-28 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of afrequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40660117 | Wood | Sacramento | 004/140 | 2021-12-16 | 2021-02-17 | 2020-06-29 | Vehicular and Mechanical Issues: Pole-top damage or split-top | FALSE | TRUE: There appears to be a split in the pole. | Agree | N/A | TD-1001M-JA06 Wood Poles - Non Steel Framing | LC 119370846 shows pole replaced on 5/4/21 | N/A | No | No | No
40660117 | Wood | Sacramento | 004/140 | 2021-12-16 | 2021-02-17 | 2020-06-29 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of afrequently traveled road. | Agree | N/A | TD-1009S | N/A | N/A | No | No | No
40660193 | Steel | Sacramento | 004/053 | 2021-12-16 | 2021-02-17 | 2020-05-19 | Are dampers damaged, broken, or missing? | FALSE | TRUE: For the three-phase line, only one damper appears to be present. | Agree | Condition is not compelling | TD-1001M-JA14 Splices Job Aid | LC 115707928 shows Dampers installed on 1 Phase to mitigate splice within 10' of support | N/A | No | No | No
40682789 | Steel | Lakeville | 029/142 | 2021-12-16 | 2/17/2021 | 2020-05-27 | Type of insulator? | FALSE | Glass, Polymer: The structure appears to have both glass and polymer insulators. | Agree | Condition is not compelling | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | N/A | N/A | No | No | No
40682789 | Steel | Lakeville | 029/142 | 2021-12-16 | 2/17/2021 | 2020-05-27 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of afrequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40753089 | Steel | Pismo Beach | 032/144 | 2021-12-16 | 2/17/2021 | 2020-05-26 | Vegetation Issues: Significant vegetation around base | FALSE | TRUE: There appears to be significant vegetation around the footings and beneath the base of the structure. | Agree | N/A | TD-1001M-JA20 Vegetation Non-conformance Job Aid | 2021 Sherlock Photo's show Vegetation is not an issue | N/A | No | No | No
40753089 | Steel | Pismo Beach | 032/144 | 2021-12-16 | 2/17/2021 | 2020-05-26 | Vegetation Issues: Vegetation removal required | FALSE | TRUE: There appears to be significant vegetation around the footings and beneath the base of the structure, requiring removal. | Agree | Condition is not compelling | TD-1001M-JA20 Vegetation Non-conformance Job Aid | 2021 Sherlock Photo's show Vegetation is not an issue | N/A | No | No | No
40753089 | Steel | Pismo Beach | 032/144 | 2021-12-16 | 2/17/2021 | 2020-05-26 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of afrequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40763973 | Wood | Lakeville | 007/004 | 2021-12-16 | 2/17/2021 | 2020-06-24 | Vehicular and Mechanical Issues: Breaks or cracks or split in pole | FALSE | TRUE: The bottom of the pole appears to be damaged and is being supported by a truss. The pole appears to be bent. | Agree | N/A | TD-1001M-JA06 Wood Poles - Non Steel Framing | LC 115546051 shows pole was replaced on 6/17/21 | N/A | No | No | No
40763973 | Wood | Lakeville | 007/004 | 2021-12-16 | 2/17/2021 | 2020-06-24 | Vehicular and Mechanical Issues: Pole-top damage or split-top | FALSE | TRUE: The top of the pole appears to have multiple cracks. | Agree | N/A | TD-1001M-JA06 Wood Poles - Non Steel Framing | LC 115546051 shows pole was replaced on 6/17/21 | N/A | No | No | No
40664415 | Wood | Table Mountain | 008/168 | 2021-12-16 | 2/23/2021 | 2020-06-02 | Vehicular and Mechanical Issues: Bird, animal or insect damage (e.g., woodpecker) | FALSE | TRUE: The structure appears to have woodpecker damage | Agree | N/A | TD-1001M-JA06 Wood Poles - Non Steel Framing | LC 115077918 shows pole replaced on 8/25/20 | N/A | No | No | No
40668912 | Steel | Table Mountain | 018/145 | 2021-12-16 | 2021-02-23 | 2020-06-15 | Is the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40670122 | Steel | Sacramento | 003/032 | 2021-12-16 | 2/23/2021 | 2020-05-07 | Foundation Issues: Mastic sealant in poor condition | FALSE | TRUE: The mastic coverage on the concrete foundation appears to be peeled off. | Disagree | Condition is not compelling | TD-1001M-JA12 Foundation Condition TLine Structures & Supports | LC 121608651 for this FDA was cancelled on 6/28/21 By CIRT. Condition is acceptable | N/A | No | No | No
40670122 | Steel | Sacramento | 003/032 | 2021-12-16 | 2/23/2021 | 2020-05-07 | Type of insulator? | FALSE | Porcelain/Ceramic: The insulators appear to be porcelain, not polymer. | Agree | Condition is not compelling | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | N/A | N/A | No | No | No
40670122 | Steel | Sacramento | 003/032 | 2021-12-16 | 2/23/2021 | 2020-05-07 | Type of Splice: Compression | FALSE | TRUE: The structure appears to have a compression splice. | Agree | Condition is not compelling | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | N/A | N/A | No | No | No
40670122 | Steel | Sacramento | 003/032 | 2021-12-16 | 2/23/2021 | 2020-05-07 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of afrequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40679423 | Steel | Sacramento | 004/123 | 2021-12-16 | 2/23/2021 | 2020-06-01 | High voltage/danger sign(s) missing or installed incorrectly per E.D. 022168? | FALSE | TRUE: The structure appears to be missing high voltage signs on both sides of the structure. | Disagree | Condition does not exist | 022168 HV Signs, Marking, Numbering | HV Signs are Below Distribution arm | N/A | No | No | No
40679423 | Steel | Sacramento | 004/123 | 2021-12-16 | 2/23/2021 | 2020-06-01 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of afrequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40803754 | Wood | Victor | 004/056 | 2021-12-16 | 2021-02-23 | 2020-05-27 | Vehicular and Mechanical Issues: Bird, animal or insect damage (e.g., woodpecker) | FALSE | TRUE: The pole appears to have insect damage. | Agree | N/A | TD-1001M-JA06 Wood Poles - Non Steel Framing | LC 119112930 to replace pole , was completed on 4/2/21 | N/A | No | No | No
40803754 | Wood | Victor | 004/056 | 2021-12-16 | 2021-02-23 | 2020-05-27 | Vehicular and Mechanical Issues: Breaks or cracks or split in pole | FALSE | TRUE: The pole appears to have vertical cracking across the majority of the pole. | Agree | N/A | TD-1001M-JA06 Wood Poles - Non Steel Framing | LC 119112930 to replace pole , was completed on 4/2/21 | N/A | No | No | No
40803754 | Wood | Victor | 004/056 | 2021-12-16 | 2021-02-23 | 2020-05-27 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of afrequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40817357 | Wood | Sacramento | 017/464 | 2021-12-16 | 2021-02-23 | 2020-06-22 | High voltage/danger sign(s) missing or installed incorrectly per E.D. 022168? | FALSE | TRUE: The high voltage sign appears to be broken. | Agree | N/A | TD-1001M-JA06 Wood Poles - Non Steel Framing | LC 119196158 was created on 10/13/2020 To repair wood pecker damage and install HV signs. LC shows structure replaced on 7/15/21 | N/A | No | No | No
40818289 | Wood | Sacramento | 003/061 | 2021-12-16 | 2021-02-23 | 2020-07-06 | Vehicular and Mechanical Issues: Breaks or cracks or split in pole | FALSE | TRUE: The structure appears to have large vertical cracks in the off-trail side of the pole. | Disagree | Condition is not compelling | TD-1001M-JA06 Wood Poles - Non Steel Framing | N/A | N/A | No | No | No
40910996 | Steel | Table Mountain | 008/055 | 2021-12-16 | 2/23/2021 | 2020-08-20 | Are dampers present? | FALSE | TRUE: The structure appears to have dampers. | Agree | Condition is not compelling | TD-1001M REV5 ET Preventative Maintenace Manual | N/A | N/A | No | No | No
40910996 | Steel | Table Mountain | 008/055 | 2021-12-16 | 2/23/2021 | 2020-08-20 | Is the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
44637596 | Wood | Lakeville | 007/006 | 2021-12-16 | 2021-02-23 | 2020-09-02 | High voltage/danger sign(s) missing or installed incorrectly per E.D. 022168? | FALSE | TRUE: The high voltage signs appear to be missing. | Disagree | Condition does not exist | 022168 HV Signs, Marking, Numbering | HV Signs are below Distribution Level | N/A | No | No | No
44836545 | Steel | Eureka | 008/006 | 2021-12-16 | 2021-02-23 | 2020-07-27 | Anchor Rod Issues: Anchor damaged or in poor condition |  | The photos w ere insufficient to determine the condition of the anchor. | Disagree | Condition does not exist | TD-1001M-JA13 Guys and Anchors | Sherlock Photo 200714_170524_00258070.jpg shows both anchors in Good Condition | N/A | No | No | No
44836545 | Steel | Eureka | 008/006 | 2021-12-16 | 2021-02-23 | 2020-07-27 | Tow er finish type: | Painted | Weathered: The finish of the structure appears to be weathered, not painted. | Agree | Condition is not compelling | TD-1001M-JA04 Steel Structures Corrosion and Deteriation | N/A | N/A | No | No | No
44836545 | Steel | Eureka | 008/006 | 2021-12-16 | 2021-02-23 | 2020-07-27 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of afrequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40863340 | Wood | Victor | 001/008 | 2021-12-16 | 2021-03-09 | 2020-04-27 | Type of insulator? | Polymer, Porcelain/Ceramic | Porcelain/Ceramic: The insulators appear to be porcelain/ceramic. | Agree | Condition is not compelling | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | N/A | N/A | No | No | No
40586776 | Wood | Lakeville | 020/091 | 2021-12-16 | 3/10/2021 | 2020-06-17 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of afrequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40698755 | Wood | Table Mountain | ;001/002 | 2021-12-16 | 3/10/2021 | 2020-07-09 | Type of insulator? | Po l yme r | Porcelain/Ceramic: The insulators appear to beporcelain/ceramic. | Agree | Condition is not compelling | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | N/A | N/A | No | No | No
40698755 | Wood | Table Mountain | ;001/002 | 2021-12-16 | 3/10/2021 | 2020-07-09 | Is the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40761876 | Steel | Concord | 000/004 | 2021-12-16 | 2021-03-10 | 2020-04-06 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of afrequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40768514 | Wood | Lakeville | 033/005 | 2021-12-16 | 3/10/2021 | 2020-08-27 | Is the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40770520 | Wood | Eureka | 018/005 | 2021-12-16 | 3/10/2021 | 2020-07-10 | Vehicular and Mechanical Issues: Breaks or cracks or split in pole | FALSE | TRUE: There appear to be several cracks/splits along the length of the pole. | Agree | N/A | TD-1001M-JA06 Wood Poles - Non Steel Framing | LC 116471974 indicates pole was replaced during Storm work | N/A | No | No | No
40770520 | Wood | Eureka | 018/005 | 2021-12-16 | 3/10/2021 | 2020-07-10 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of afrequently traveled road. | Agree | N/A | TD-1009S | N/A | N/A | No | No | No
40822374 | Wood | Fresno | 003/006 | 2021-12-16 | 2021-03-10 | 2020-10-01 | Vehicular and Mechanical Issues: Bird, animal or insect damage (e.g., woodpecker) | FALSE | TRUE: There appears to be a woodpecker hole present approximately 2/3 of the wayup the pole. | Agree | Condition is not compelling | TD-1001M-JA06 Wood Poles - Non Steel Framing | LC 120834487 was created on 4/18/21 for this FDA, CIRT Cancelled Cracks are not significant | N/A | No | No | No
40822374 | Wood | Fresno | 003/006 | 2021-12-16 | 2021-03-10 | 2020-10-01 | Vehicular and Mechanical Issues: Breaks or cracks or split in pole | FALSE | TRUE: There appear to be several cracks/splits along the length of the pole. | Agree | Condition is not compelling | TD-1001M-JA06 Wood Poles - Non Steel Framing | LC 120834487 was created on 4/18/21 for this FDA, CIRT Cancelled Cracks are not significant | N/A | No | No | No
40822374 | Wood | Fresno | 003/006 | 2021-12-16 | 2021-03-10 | 2020-10-01 | High voltage/danger sign(s) missing or installed incorrectly per E.D. 022168? | FALSE | RUE: One side ofthehigh voltage sign appears to be detached. | Agree | N/A | 022168 HV Signs, Marking, Numbering | Work was completed on 5/5/21 | N/A | No | No | No
40822374 | Wood | Fresno | 003/006 | 2021-12-16 | 2021-03-10 | 2020-10-01 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of afrequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40911000 | Steel | Table Mountain | 008/059 | 2021-12-16 | 3/10/2021 | 2020-08-20 | Is the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40911000 | Steel | Table Mountain | 008/059 | 2021-12-16 | 3/10/2021 | 2020-08-20 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of afrequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40663139 | Steel | Pismo Beach | 007/032 | 2021-12-16 | 2021-03-12 | 2020-05-05 | Is vegetation present? | FALSE | TRUE: Vegetation appears to be within 10 feet of the asset. | Agree | Condition is not compelling | TD-1001M-JA20 Vegetation Non-conformance Job Aid | N/A | N/A | No | No | No
40663139 | Steel | Pismo Beach | 007/032 | 2021-12-16 | 2021-03-12 | 2020-05-05 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of afrequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40768372 | Wood | Sacramento | 008/210 | 2021-12-16 | 3/12/2021 | 2020-06-03 | s the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40907085 | Steel | Victor | A001/028 | 2021-12-16 | 3/12/2021 | 2020-04-10 | High voltage/danger sign(s) missing or installed incorrectly per E.D. 022168? | FALSE | TRUE: High voltage signs on both sides of the LDS pole appear to be damaged and appear to be in need of replacement. | Agree | Condition is not compelling | 022168 HV Signs, Marking, Numbering | HV Signs are visible below Distribution arm | N/A | No | No | No
40907085 | Steel | Victor | A001/028 | 2021-12-16 | 3/12/2021 | 2020-04-10 | Is there a distribution issue on a transmission structure w ith a distribution underbuild? | FALSE | TRUE: High voltage sign on the underbuild crossarm appears to be damaged; crossarm damaged. | Agree | Condition is not compelling | 022168 HV Signs, Marking, Numbering | HV Signs are visible below Distribution arm | N/A | No | No | No
40910127 | Steel | Table Mountain | 012/101 | 2021-12-16 | 3/12/2021 | 2020-06-04 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of afrequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
44141997 | Wood | Table Mountain | A024/514 | 2021-12-16 | 3/12/2021 | 2020-06-04 | Is structure number missing? | FALSE | TRUE: The SAP Number appears to be incorrect. Number on asset: T40771355 | Agree | Condition is not compelling | 022168 HV Signs, Marking, Numbering | N/A | N/A | No | No | No
44141997 | Wood | Table Mountain | A024/514 | 2021-12-16 | 3/12/2021 | 2020-06-04 | Conductor Issues: Conductor is in poor condition | FALSE | TRUE: Conductor appears to be twisted and bunched up by splice connection; irregular (not smooth). | Agree | Condition is not compelling | TD-1001M-JA10 Conductor Conditions | N/A | N/A | No | No | No
44141997 | Wood | Table Mountain | A024/514 | 2021-12-16 | 3/12/2021 | 2020-06-04 | Is the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
44141997 | Wood | Table Mountain | A024/514 | 2021-12-16 | 3/12/2021 | 2020-06-04 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of afrequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40605180 | Steel | Lakeville | 011/050 | 2021-12-16 | 2021-03-16 | 2020-04-09 | Type of Splice: Compression | FALSE | TRUE: There appears to be a compression splice on the top phase of the structure. | Agree | Condition is not compelling | TD-1001M-JA14 Splices Job Aid | N/A | N/A | No | No | No
40605180 | Steel | Lakeville | 011/050 | 2021-12-16 | 2021-03-16 | 2020-04-09 | Is a splice within 10' of hot end of insulator? | BLANK | TRUE: There appears to be a compression splice on the top phase within 10 feet of the hot end of the insulator. | Disagree | Condition does not exist | TD-1001M-JA14 Splices Job Aid | Sherlock Photo DJI_0136.JPG shows Splice more than 10' from Support | N/A | No | No | No
40605180 | Steel | Lakeville | 011/050 | 2021-12-16 | 2021-03-16 | 2020-04-09 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of afrequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40650231 | Steel | Fresno | 019/103 | 2021-12-16 | 2021-03-16 | 2020-08-07 | FAA lighting present? | FALSE | FALSE: There does not appear to be any FAA lighting present. | Agree | Condition is not compelling | TD-1001M REV5 ET Preventative Maintenace Manual | N/A | N/A | No | No | No
40650231 | Steel | Fresno | 019/103 | 2021-12-16 | 2021-03-16 | 2020-08-07 | Is the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40650231 | Steel | Fresno | 019/103 | 2021-12-16 | 2021-03-16 | 2020-08-07 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of afrequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40702063 | Wood | Sacramento | 017/558 | 2021-12-16 | 3/16/2021 | 2020-06-29 | Is structure number missing? | FALSE | TRUE: The structure number appears to be damaged. | Agree | N/A | 022168 HV Signs, Marking, Numbering | LC 120930828 was created on 5/4/21 for this FDA | N/A | No | No | No
40702063 | Wood | Sacramento | 017/558 | 2021-12-16 | 3/16/2021 | 2020-06-29 | High voltage/danger sign(s) missing or installed incorrectly per E.D. 022168? | FALSE | TRUE: The visibility markers do not appear to be yellow. | Agree | N/A | 022168 HV Signs, Marking, Numbering | LC 120930828 was created on 5/4/21 for this FDA | N/A | No | No | No
40702063 | Wood | Sacramento | 017/558 | 2021-12-16 | 3/16/2021 | 2020-06-29 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of afrequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40750305 | Wood | Lakeville | 039/005 | 2021-12-16 | 3/16/2021 | 2020-05-15 | Guy Issues: Guy bonded and not sectionalized | FALSE | TRUE: The fiberglass guy wire hardware appears not to be bonded. | Agree | N/A | TD-1001M-JA13 Guys and Anchors | LC 117295434 for this FDA was completed on 10/114/20 | N/A | No | No | No
40910965 | Steel | Table Mountain | 002/021 | 2021-12-16 | 2021-03-16 | 2020-06-24 | Type of insulator? | Po l yme r | Porcelain/Ceramic: All insulators appear to beporcelain/ceramic. | Agree | Condition is not compelling | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | N/A | N/A | No | No | No
44190970 | Wood | Table Mountain | 000/003 | 2021-12-16 | 3/16/2021 | 2020-05-28 | Vehicular and Mechanical Issues: Bird, animal or insect damage (e.g., woodpecker) | FALSE | TRUE: There appears to be woodpecker damage toward the top of the pole. | Agree | N/A | TD-1001M-JA06 Wood Poles - Non Steel Framing | LC 121541395 was created on 6/15/21 to replace pole | N/A | No | No | No
44190970 | Wood | Table Mountain | 000/003 | 2021-12-16 | 3/16/2021 | 2020-05-28 | Vehicular and Mechanical Issues: Breaks or cracks or split in pole | FALSE | TRUE: There appear to be multiple cracks in the pole. | Agree | N/A | TD-1001M-JA06 Wood Poles - Non Steel Framing | LC 121541395 was created on 6/15/21 to replace pole | N/A | No | No | No
44836558 | Wood | Table Mountain | A026/544 | 2021-12-16 | 3/16/2021 | 2020-06-04 | Vehicular and Mechanical Issues: Bird, animal or insect damage (e.g., woodpecker) | FALSE | TRUE: There appears to be woodpecker damage at the top of the pole. | Disagree | Condition is not compelling | TD-1001M-JA06 Wood Poles - Non Steel Framing | CIRT Cancelled LC 119144541 for this FDA Issue is to small to repair at this Time | N/A | No | No | No
44836558 | Wood | Table Mountain | A026/544 | 2021-12-16 | 3/16/2021 | 2020-06-04 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of afrequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40587771 | Wood | Lakeville | 009/010 | 2021-12-16 | 2021-03-17 | 2020-06-23 | Guy Issues: Guy marker missing (GO 95 infraction) | FALSE | TRUE: Tw o guy markers appear to be missing, and there appears to be minor damage to others. | Agree | N/A | TD-1001M-JA13 Guys and Anchors | LC 121336717 was created on 5/14/21 to replace anchor and Markers | N/A | No | No | No
40874793 | Wood | Sacramento | B022/493 | 2021-12-16 | 2021-03-17 | 2020-09-08 | Is structure number missing? | FALSE | TRUE: The structure number appears to be missing. | Agree | N/A | 022168 HV Signs, Marking, Numbering | LC 11786783 was completed on 10/22/2019 | N/A | No | No | No
41129323 | Steel | Lakeville | 005/020 | 2021-12-16 | 2021-03-17 | 2020-04-07 | Foundation Issues: Stub in concrete not sealed or water proofed | FALSE | TRUE: No mastic sealant appears to be present on any of the four footings. | Agree | N/A | TD-1001M-JA12 Foundation Condition TLine Structures & Supports | LC 119780826 For This FDA was completed on 3/11/21 | N/A | No | No | No
41129323 | Steel | Lakeville | 005/020 | 2021-12-16 | 2021-03-17 | 2020-04-07 | Is structure number missing? | FALSE | TRUE: The structure number appears to be missing. | Agree | N/A | 022168 HV Signs, Marking, Numbering | Structure Number installed as per LC 119780826 | N/A | No | No | No
41129323 | Steel | Lakeville | 005/020 | 2021-12-16 | 2021-03-17 | 2020-04-07 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of afrequently traveled road. | Agree | N/A | TD-1009S | N/A | N/A | No | No | No
41129368 | Steel | Lakeville | 015/066 | 2021-12-16 | 2021-03-17 | 2020-04-08 | Are dampers present? | FALSE | TRUE: Dampers appear to be present on all phases. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
41129368 | Steel | Lakeville | 015/066 | 2021-12-16 | 2021-03-17 | 2020-04-08 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of afrequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
44168167 | Steel | Table Mountain | 009/015 | 2021-12-16 | 2021-03-17 | 2020-07-03 | Is the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
44168167 | Steel | Table Mountain | 009/015 | 2021-12-16 | 2021-03-17 | 2020-07-03 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of afrequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40581957 | Wood | Table Mountain | 019/382 | 2021-12-16 | 3/19/2021 | 2020-07-07 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of afrequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40602015 | Wood | Table Mountain | 011/240 | 2021-12-16 | 3/19/2021 | 2020-06-16 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of afrequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40769394 | Wood | Eureka | 004/004 | 2021-12-16 | 2021-03-19 | 2020-07-29 | Vehicular and Mechanical Issues: Breaks or cracks or split in pole | FALSE | TRUE: The top of the pole appears to have splits up to 50% of the pole's diameter. | Agree | N/A | TD-1001M-JA06 Wood Poles - Non Steel Framing | LC 121338259 was created on 5/15/21 to Replace pole to steel | N/A | No | No | No
40810572 | Steel | Concord | 015/097 | 2021-12-16 | 2021-03-19 | 2020-04-10 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of afrequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40810919 | Wood | Eureka | 009/006 | 2021-12-16 | 2021-03-19 | 2020-07-31 | Is structure number missing? | FALSE | FALSE: The structure number appears to be missing. | Disagree | Condition does not exist | 022168 HV Signs, Marking, Numbering | Sherlock photo 200714_234453_0a07a212.jpg shows Structure number in place | N/A | No | No | No
40810919 | Wood | Eureka | 009/006 | 2021-12-16 | 2021-03-19 | 2020-07-31 | s there a distribution issue on a transmission structure w ith a distribution underbuild? | FALSE | TRUE: The high voltage sign on the underbuild crossarm appears to be hanging from the crossarm. | Agree | Condition is not compelling | 022168 HV Signs, Marking, Numbering | Condition Not compelling HV Signs below distribution arm | N/A | No | No | No
40810919 | Wood | Eureka | 009/006 | 2021-12-16 | 2021-03-19 | 2020-07-31 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40814634 | Steel | Lakeville | 21/086 | 2021-12-16 | 2021-03-19 | 2020-04-09 | Foundation Issues: Mastic sealant in poor condition | FALSE | TRUE: Mastic sealant appears to be missing on all four footings. | Agree | N/A | TD-1001M-JA12 Foundation Condition TLine Structures & Supports | LC 121487843 was created on 6/8/21 for this FDA | N/A | No | No | No
40814634 | Steel | Lakeville | 21/086 | 2021-12-16 | 2021-03-19 | 2020-04-09 | Structure Issues: Steel Structure Hardware Loose or missing | FALSE | TRUE: Bolts appear to be missing on tertiary members where they attach to primary me mb e r s . | Disagree | Condition does not exist | TD-1001M-JA04 Steel Structures Corrosion and Deteriation | Drawing Number 309424 Shows No Bolts Missing | N/A | No | No | No
40672183 | Steel | Sacramento | 002/022 | 2021-12-15 | 2021-04-14 | 2020-05-06 | Foundation Issues: Mastic sealant in poor condition | FALSE | TRUE: The mastic sealant appears to be in poor condition | Agree | N/A | TD-1001M-JA12 Foundation Condition TLine Structures & Supports | LC 121391467, was created on 5/24/21 | N/A | No | No | No
40672183 | Steel | Sacramento | 002/022 | 2021-12-15 | 2021-04-14 | 2020-05-06 | Vegetation Issues: Significant vegetation around base | FALSE | TRUE: Vegetation around footings appears to be significant. | Disagree | Condition is not compelling | TD-1001M-JA20 Vegetation Non-conformance Job Aid | N/A | N/A | No | No | No
40672183 | Steel | Sacramento | 002/022 | 2021-12-15 | 2021-04-14 | 2020-05-06 | Vegetation Issues: Vegetation removal required | FALSE | TRUE: Non-immediate vegetation removal appears to be required. | Disagree | Condition is not compelling | TD-1001M-JA20 Vegetation Non-conformance Job Aid | N/A | N/A | No | No | No
40672183 | Steel | Sacramento | 002/022 | 2021-12-15 | 2021-04-14 | 2020-05-06 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled trail. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40822812 | Wood | Sacramento | 008/086 | 2021-12-15 | 2021-04-14 | 2020-05-19 | Structure Issues: Steel Structure Hardware Loose or missing | FALSE | TRUE: Several bolts appear to be missing from the structure. | Disagree | Condition does not exist | TD-1001M-JA04 Steel Structures Corrosion and Deteriation | Drawing 402706, No Bolts Missing | N/A | No | No | No
40822812 | Wood | Sacramento | 008/086 | 2021-12-15 | 2021-04-14 | 2020-05-19 | Are 2 or more splices present in any one phase per span? | FALSE | TRUE: There appear to be three splices total on the center phase. | Agree | Condition is not compelling | TD-1001M-JA14 Splices Job Aid | N/A | N/A | No | No | No
40822812 | Wood | Sacramento | 008/086 | 2021-12-15 | 2021-04-14 | 2020-05-19 | Vegetation Issues: Significant vegetation around base | FALSE | TRUE: There appears to be significant vegetation around the footingsof the structure. | Disagree | Condition is not compelling | TD-1001M-JA20 Vegetation Non-conformance Job Aid | N/A | N/A | No | No | No
40822812 | Wood | Sacramento | 008/086 | 2021-12-15 | 2021-04-14 | 2020-05-19 | Vegetation Issues: Vegetation removal required | FALSE | TRUE: Vegetation removal appears to be required. | Disagree | Condition is not compelling | TD-1001M-JA20 Vegetation Non-conformance Job Aid | N/A | N/A | No | No | No
40822812 | Wood | Sacramento | 008/086 | 2021-12-15 | 2021-04-14 | 2020-05-19 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40908540 | Wood | Table Mountain | 028/483 | 2021-12-15 | 2021-04-14 | 2020-07-06 | Vehicular and Mechanical Issues: Breaks or cracks or split in pole | FALSE | TRUE: There appear to be cracks in the bottom and the middle sections of the pole. | Disagree | Condition is not compelling | TD-1001M-JA06 Wood Poles - Non Steel Framing | Issues are Not Compelling | N/A | No | No | No
40908540 | Wood | Table Mountain | 028/483 | 2021-12-15 | 2021-04-14 | 2020-07-06 | Is the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40659622 | Steel | Lakeville | 040/193 | 2021-12-15 | 2021-04-15 | 2020-04-23 | Structure Issues: Steel Structure Hardware Loose or missing | FALSE | TRUE: The structure appears to have missing bolts. | Disagree | Condition does not exist | TD-1001M-JA04 Steel Structures Corrosion and Deteriation | Type G tower drawing 309424 shows No Bolts missing | N/A | No | No | No
40659622 | Steel | Lakeville | 040/193 | 2021-12-15 | 2021-04-15 | 2020-04-23 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40679317 | Wood | Sacramento | 009/224 | 2021-12-15 | 2021-04-15 | 2020-06-03 | Is the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40698884 | Wood | Table Mountain | 003/060 | 2021-12-15 | 2021-04-15 | 2020-07-07 | Anchor Rod Issues: Obstructed View | FALSE | TRUE: Vegetation appears to obstruct the view of the anchor. | Agree | N/A | TD-1009S | N/A | N/A | No | No | No
40698884 | Wood | Table Mountain | 003/060 | 2021-12-15 | 2021-04-15 | 2020-07-07 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40746285 | Steel | Concord | 004/020 | 2021-12-15 | 2021-04-15 | 2020-05-06 | Structure Issues: Steel Structure Hardware Loose or missing | FALSE | TRUE: The structure appears to have missing bolts. | Disagree | Condition does not exist | TD-1001M-JA04 Steel Structures Corrosion and Deteriation | Type G tower drawing 309424 shows No Bolts missing | N/A | No | No | No
40746285 | Steel | Concord | 004/020 | 2021-12-15 | 2021-04-15 | 2020-05-06 | Insulator Issues: Insulators' hardware cold-end in poor condition (e.g. C-hook) | FALSE | TRUE: The jumper support insulator C-hook appears to be in poor condition. | Disagree | Condition does not exist | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | sent to air team 12/17/21, Air replied 12/19/21 No Compelling issues | N/A | No | No | No | Sent to Air Team 12/17/21 | Air Replied on 12/19/21, No Compelliing Issues
40746285 | Steel | Concord | 004/020 | 2021-12-15 | 2021-04-15 | 2020-05-06 | Type of Splice: Compression | FALSE | TRUE: The structure appears to have a compression splice. | Agree | Condition is not compelling | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | N/A | N/A | No | No | No
40760857 | Steel | Metcalf | 015/064 | 2021-12-15 | 2021-04-15 | 2020-05-20 | Structure Issues: Steel Structure Hardware Loose or missing | FALSE | TRUE: There appear to be multiple missing bolts. The horizontal members appear to each be missing a bolt. | Disagree | Condition does not exist | TD-1001M-JA04 Steel Structures Corrosion and Deteriation | Drawing 39324 shows bolts not missing | N/A | No | No | No
40865385 | Wood | Sacramento | 006/155 | 2021-12-15 | 2021-04-15 | 2020-05-28 | Is the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40865385 | Wood | Sacramento | 006/155 | 2021-12-15 | 2021-04-15 | 2020-05-28 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40911297 | Steel | Table Mountain | 019/153 | 2021-12-15 | 2021-04-15 | 2020-05-28 | Vegetation Issues: Significant vegetation around base | FALSE | TRUE: There appears to be significant vegetation around the base of the structure. | Disagree | Condition is not compelling | TD-1001M-JA20 Vegetation Non-conformance Job Aid | Sherlock Photo K_00873.JPG shows no Compelling Issues | N/A | No | No
41135445 | Wood | Concord | 000/004 | 2021-12-15 | 2021-04-15 | 2020-07-20 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road/trail. | Agree | N/A | TD-1009S | N/A | N/A | No | No | No
40592235 | Steel | Table Mountain | 052/391 | 2021-12-15 | 2021-04-16 | 2020-08-05 | Foundation Type: | Earth | Concrete: The foundation appears to be concrete. | Agree | Condition is not compelling | TD-1001M-JA12 Foundation Condition TLine Structures & Supports | N/A | N/A | No | No | No
40592235 | Steel | Table Mountain | 052/391 | 2021-12-15 | 2021-04-16 | 2020-08-05 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled trail. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40594185 | Wood | Moss Landing | A015/326 | 2021-12-15 | 2021-04-16 | 2020-10-13 | Vehicular and Mechanical Issues: Pole-top damage or split-top | FALSE | TRUE: The pole appears to have a split top. | Disagree | Condition is not compelling | TD-1001M-JA06 Wood Poles - Non Steel Framing | Sherlock Photo 201003_223159_979e6df4.jpg Shows No Compelling Issues | N/A | No | No | No
40594185 | Wood | Moss Landing | A015/326 | 2021-12-15 | 2021-04-16 | 2020-10-13 | High voltage/danger sign(s) missing or installed incorrectly perE.D. 022168? | FALSE | TRUE: One of the high voltage signs appears to be missing. | Disagree | Condition does not exist | 022168 HV Signs, Marking, Numbering | Sherlock Photo 201003_223112_4a0b.jpg shows HV Signs below Distribution Level | N/A | No | No | No
40594185 | Wood | Moss Landing | A015/326 | 2021-12-15 | 2021-04-16 | 2020-10-13 | Is vegetation present? | FALSE | TRUE: There appears to be vegetation around both the base of the pole and the guy anchor. | Agree | Condition is not compelling | TD-1001M REV5 ET Preventative Maintenace Manual | N/A | N/A | No | No | No
40761367 | Wood | Sacramento | 002/084 | 2021-12-15 | 2021-04-16 | 2020-07-02 | Is structure number missing? | FALSE | TRUE: The tag appears to be bent and the structure number is not visible. | Agree | N/A | 022168 HV Signs, Marking, Numbering | LC 119314249 For this FDA was cancelled no work needed | N/A | No | No | No
40871538 | Steel | Table Mountain | 014/098 | 2021-12-15 | 2021-04-16 | 2020-07-23 | Foundation Issues: Mastic sealant in poor condition | FALSE | TRUE: There does not appear to be any mastic sealant present. | Agree | N/A | TD-1001M-JA12 Foundation Condition TLine Structures & Supports | Existing LC 120652889 For this FDA was updated 5/14/21 | N/A | No | No | No
40871538 | Steel | Table Mountain | 014/098 | 2021-12-15 | 2021-04-16 | 2020-07-23 | Structure Issues: Steel Structure Hardware Loose or missing | FALSE | TRUE: Bolts for some secondary members appear to be missing. | Disagree | Condition does not exist | TD-1001M-JA04 Steel Structures Corrosion and Deteriation | Drawing 402706 FA Type Tower No bolts missing | N/A | No | No | No
40871538 | Steel | Table Mountain | 014/098 | 2021-12-15 | 2021-04-16 | 2020-07-23 | High voltage/danger sign(s) missing or installed incorrectly per E.D. 022168? | FALSE | TRUE: One danger sign appears to be missing. | Agree | N/A | 022168 HV Signs, Marking, Numbering | LC 119781002 indicates HV Signs were installed on 3/19/21 | N/A | No | No | No
44733399 | Steel | Table Mountain | 012/219 | 2021-12-15 | 2021-04-16 | 2020-05-14 | Is birds nest present? | FALSE | TRUE: There appear to be multiple nests on the structure. | Agree | Condition is not compelling | TD-1001M REV5 ET Preventative Maintenace Manual | N/A | N/A | No | No | No
44733399 | Steel | Table Mountain | 012/219 | 2021-12-15 | 2021-04-16 | 2020-05-14 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40585967 | Steel | Table Mountain | 007/001 | 2021-12-15 | 2021-04-20 | 2020-11-05 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40650234 | Wood | Table Mountain | A008/166 | 2021-12-15 | 2021-04-20 | 2020-06-17 | Is the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40650234 | Wood | Table Mountain | A008/166 | 2021-12-15 | 2021-04-20 | 2020-06-17 | Is thestructure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40701215 | Wood | Table Mountain | 012/242 | 2021-12-15 | 2021-04-20 | 2020-09-12 | Does or should this structure have a guy? | FALSE | TRUE: The structure appears to have a guy. | Disagree | Condition does not exist | TD-1001M-JA13 Guys and Anchors | Photos show Guy at Communication Level | N/A | No | No | No
40701215 | Wood | Table Mountain | 012/242 | 2021-12-15 | 2021-04-20 | 2020-09-12 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40762067 | Steel | Lakeville | 058/284 | 2021-12-15 | 2021-04-20 | 2020-04-24 | Foundation Issues: Earth around structure eroded, soil movement, slide | FALSE | TRUE: The earth around the structure appears to be eroded. | Agree | N/A | TD-1001M-JA12 Foundation Condition TLine Structures & Supports | LC 119637560 For this FDA was completed on 3/15/21 | N/A | No | No | No
40762067 | Steel | Lakeville | 058/284 | 2021-12-15 | 2021-04-20 | 2020-04-24 | Foundation Issues: Mastic sealant in poor condition | FALSE | TRUE: At least one footing appears to be missing mastic sealant. | Agree | N/A | TD-1001M-JA12 Foundation Condition TLine Structures & Supports | LC 119637560 For this FDA was completed on 3/15/21 | N/A | No | No | No
40762067 | Steel | Lakeville | 058/284 | 2021-12-15 | 2021-04-20 | 2020-04-24 | Structure Issues: Damaged secondary members | FALSE | TRUE: One of the secondary members appears to be bent. | Agree | N/A | TD-1001M-JA04 Steel Structures Corrosion and Deteriation | LC 119720848 was completed on 3/15/21 for this FDA | N/A | No | No | No
40762067 | Steel | Lakeville | 058/284 | 2021-12-15 | 2021-04-20 | 2020-04-24 | Vegetation Issues: Significant vegetation around base | FALSE | TRUE: There appears to be significant vegetation around the base of the structure. | Agree | N/A | TD-1001M-JA20 Vegetation Non-conformance Job Aid | LC 115761258 for this FDA was closed on 5/4/20, All work complete | N/A | No | No | No
40762067 | Steel | Lakeville | 058/284 | 2021-12-15 | 2021-04-20 | 2020-04-24 | Is the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40762067 | Steel | Lakeville | 058/284 | 2021-12-15 | 2021-04-20 | 2020-04-24 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40762100 | Steel | Lakeville | 006/035 | 2021-12-14 | 2021-04-20 | 2020-04-14 | Is the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40762100 | Steel | Lakeville | 006/035 | 2021-12-14 | 2021-04-20 | 2020-04-14 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40813445 | Wood | Sacramento | 010/241 | 2021-12-14 | 2021-04-20 | 2020-10-06 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40913043 | Steel | Sacramento | 017/147 | 2021-12-14 | 2021-04-20 | 2020-07-23 | Type of Splice: Compression | FALSE | TRUE: There appears to be a compression splice. | Agree | Condition is not compelling | TD-1001M-JA14 Splices Job Aid | N/A | N/A | No | No | No
40913043 | Steel | Sacramento | 017/147 | 2021-12-14 | 2021-04-20 | 2020-07-23 | Is a splice within 10' of hot end of insulator? | BLANK | TRUE: There appears to be a splice within 10 feet of the hot end of insulator. | Disagree | Condition does not exist | TD-1001M-JA14 Splices Job Aid | Sherlock Photo 017_147_40913043_009.JPG shows splice more than 10' to DE Shoe | N/A | No | No | No
40586043 | Wood | Sacramento | 010/196 | 2021-12-14 | 2021-04-21 | 2020-08-17 | Framing Issues: Ground w ire in poor condition | FALSE | FALSE: The photos are notsufficient to determine the condition of the bonding of the outside phases. | Agree | Condition is not compelling | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | Sherlock 2021 Photo 210420_172844_380_1abe9b81.jpg shows Bond wire stapled securly to pole | N/A | No | No | No
40586043 | Wood | Sacramento | 010/196 | 2021-12-14 | 2021-04-21 | 2020-08-17 | Is the structure ina rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40660512 | Steel | Moss Landing | 014/073 | 2021-12-14 | 2021-04-21 | 2020-04-01 | Foundation Issues: Earth around structure eroded, soil movement, slide | FALSE | TRUE: There appears to be erosion around one of the footing foundations. | Disagree | Condition is not compelling | TD-1001M-JA12 Foundation Condition TLine Structures & Supports | N/A | N/A | No | No | No
40660512 | Steel | Moss Landing | 014/073 | 2021-12-14 | 2021-04-21 | 2020-04-01 | Structure Issues: Loose or mi s s i ng me mb e r s | FALSE | TRUE: A member appears to be connected on one end and not connected on the other. | Agree | N/A | TD-1001M-JA04 Steel Structures Corrosion and Deteriation | LC 118771371 shows this FDA was corrected on 6/30/21 | N/A | No | No | No
40660512 | Steel | Moss Landing | 014/073 | 2021-12-14 | 2021-04-21 | 2020-04-01 | Type of insulator? | Type of insulator? | Polymer, Porcelain/Ceramic: Porcelain/ceramic and polymer insulators appear to be present. | Agree | Condition is not compelling | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | N/A | N/A | No | No | No
40660512 | Steel | Moss Landing | 014/073 | 2021-12-14 | 2021-04-21 | 2020-04-01 | Is vegetation present? | FALSE | TRUE: Vegetation appears to be present on one of the footings. | Agree | Condition is not compelling | TD-1001M REV5 ET Preventative Maintenace Manual | N/A | N/A | No | No | No
40660512 | Steel | Moss Landing | 014/073 | 2021-12-14 | 2021-04-21 | 2020-04-01 | Is Overhead Ground Wire/Fiber section applicable? | FALSE | TRUE: Fiber shield wires appear to be present. | Agree | Condition is not compelling | TD-1001M-JA11 OPGW | N/A | N/A | No | No | No
40660512 | Steel | Moss Landing | 014/073 | 2021-12-14 | 2021-04-21 | 2020-04-01 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40771234 | Wood | Table Mountain | 021/448 | 2021-12-14 | 2021-04-21 | 2020-06-04 | Does or should this structure have a guy? | FALSE | TRUE: A guy appears to be present. | Disagree | Condition does not exist | TD-1009S | ! 2020 Photo does not show Guy, 2021 inspection Sherlock Photo 2020_05_09_22_29_00066.jpg shows Guy is at distribution Level | N/A | No | No | No
40771234 | Wood | Table Mountain | 021/448 | 2021-12-14 | 2021-04-21 | 2020-06-04 | Is vegetation present? | FALSE | TRUE: Tall grass appears to be present around the base of the pole. | Agree | Condition is not compelling | TD-1001M REV5 ET Preventative Maintenace Manual | N/A | N/A | No | No | No
40771234 | Wood | Table Mountain | 021/448 | 2021-12-14 | 2021-04-21 | 2020-06-04 | Is the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40771234 | Wood | Table Mountain | 021/448 | 2021-12-14 | 2021-04-21 | 2020-06-04 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40815438 | Steel | Lakeville | 014/066 | 2021-12-14 | 2021-04-21 | 2020-05-14 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40822969 | Steel | Pismo Beach | 008/036 | 2021-12-14 | 2021-04-21 | 2020-05-26 | Type of Splice: Compression | FALSE | TRUE: One compression splice appears to be present. | Agree | Condition is not compelling | TD-1001M-JA14 Splices Job Aid | N/A | N/A | No | No | No
40822969 | Steel | Pismo Beach | 008/036 | 2021-12-14 | 2021-04-21 | 2020-05-26 | Is the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling. | Disagree | Condition does not exist | TD-1009S | ET GIS Shows over 600" to the Nearest structure | N/A | No | No | No
40594983 | Steel | Sacramento | 003/031 | 2021-12-14 | 2021-04-23 | 2020-05-06 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of afrequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40600664 | Wood | Table Mountain | 005/001 | 2021-12-14 | 2021-04-23 | 2020-07-16 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of afrequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40608391 | Steel | Sacramento | 006/070 | 2021-12-14 | 2021-04-23 | 2020-05-19 | Type of Splice: Compression | FALSE | TRUE: There appears to be a compression splice on the center-phase conductor. | Agree | Condition is not compelling | TD-1001M-JA14 Splices Job Aid | N/A | N/A | No | No | No
40608391 | Steel | Sacramento | 006/070 | 2021-12-14 | 2021-04-23 | 2020-05-19 | Is a splice within 10' of hot end of insulator? | BLANK | TRUE: There appears to be a compression splice on the center-phase conductor w ithin 10 feet of the hot endofaninsulator. | Disagree | Condition does not exist | TD-1001M-JA14 Splices Job Aid | Sherlock Photo 40608391.JPG shows a splice on either side of insulator 10' From Support | N/A | No | No | No
40608391 | Steel | Sacramento | 006/070 | 2021-12-14 | 2021-04-23 | 2020-05-19 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road. | Agree | Condition is not compelling | TD-1009S | Sherlock Photo 40608391_001.JPG shows ROW Road | N/A | No | No | No
40750222 | Steel | Victor | 002/004 | 2021-12-14 | 2021-04-23 | 2020-05-05 | Foundation Issues: Mastic sealant in poor condition | FALSE | TRUE: The mastic sealant on at least one footing appears to be in poor condition. | Agree | N/A | TD-1001M-JA12 Foundation Condition TLine Structures & Supports | LC 120947465 was created on 5/7/2021 for this FDA | N/A | No | No | No
40750222 | Steel | Victor | 002/004 | 2021-12-14 | 2021-04-23 | 2020-05-05 | Type of Splice: Compression | FALSE | TRUE: There appears to be a compression splice on each phase. | Agree | Condition is not compelling | TD-1001M-JA14 Splices Job Aid | N/A | N/A | No | No | No
40750222 | Steel | Victor | 002/004 | 2021-12-14 | 2021-04-23 | 2020-05-05 | Type of Splice: Other | FALSE | RUE: There appears to be a splice on one of the outside phases. | Agree | Condition is not compelling | TD-1001M-JA14 Splices Job Aid | N/A | N/A | No | No | No
40750318 | Wood | Lakeville | 016/004 | 2021-12-14 | 2021-04-23 | 2020-10-06 | Type of Splice: Compression | FALSE | TRUE: There appears to be a compression splice on the conductor. | Agree | Condition is not compelling | TD-1001M-JA14 Splices Job Aid | N/A | N/A | No | No | No
40750318 | Wood | Lakeville | 016/004 | 2021-12-14 | 2021-04-23 | 2020-10-06 | Is vegetation present? | FALSE | TRUE: There appears to be vegetation around the base of the structure. | Agree | Condition is not compelling | TD-1001M-JA20 Vegetation Non-conformance Job Aid | N/A | N/A | No | No | No
40805040 | Steel | Concord | 005/022 | 2021-12-13 | 2021-04-23 | 2020-04-20 | Structure Issues: Steel Structure Hardware Loose or missing | FALSE | TRUE: Several bolts appear to be missing from multiple horizontal tertiary members. | Disagree | Condition does not exist | TD-1001M-JA04 Steel Structures Corrosion and Deteriation | Drawing Number 206891 Type FA Tower | N/A | No | No | No
40805040 | Steel | Concord | 005/022 | 2021-12-13 | 2021-04-23 | 2020-04-20 | Insulator Issues:Insulators' hardware cold-end in poor condition (e.g. C-hook) | FALSE | TRUE: The c-hook appears to be in poor condition. | Agree | N/A | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | LC 118946429 was created on 4/24/20 to replace insulator, Updated on 4/24/21 to replace all and hot and cold ends, Completed on 7/29/21 | N/A | No | No | No
40805040 | Steel | Concord | 005/022 | 2021-12-13 | 2021-04-23 | 2020-04-20 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40597214 | Wood | Sacramento | B023/517 | 2021-12-13 | 2021-04-27 | 2020-09-08 | Is the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40698471 | Wood | Eureka | 003/012 | 2021-12-13 | 2021-04-27 | 2020-09-14 | Insulator Issues: Insulators are damaged, contaminated, or in poor condition | FALSE | TRUE: The insulators appear to be contaminated from bird droppings and moss. | Agree | N/A | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | LC 121537451 To wash insulators was created to wash insulators on 6/14/21. Updated on 10/11/21 to replace all insulators | N/A | No | No | No
40824596 | Steel | Table Mountain | 004/017 | 2021-12-13 | 2021-04-27 | 2020-11-04 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40867465 | Wood | Table Mountain | 008/019 | 2021-12-13 | 2021-04-27 | 2020-07-16 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40906799 | Wood | Victor | 007/144 | 2021-12-13 | 2021-04-27 | 2020-04-06 | Vehicular and Mechanical Issues: Breaks or cracks or split in pole | FALSE | TRUE: The structure appears to have cracks near the bottom of the pole. There also appears to be a crack near the center of the pole. | Disagree | Condition is not compelling | TD-1001M-JA06 Wood Poles - Non Steel Framing | Sherlock photo 2020_03_06_09_57_30_00402.jpg shows No Compelling Issues | N/A | No | No | No
40906799 | Wood | Victor | 007/144 | 2021-12-13 | 2021-04-27 | 2020-04-06 | Vehicular and Mechanical Issues: Pole-top damage or split-top | FALSE | TRUE: The structure appears to have a crack near the top of the pole. | Disagree | Condition is not compelling | TD-1001M-JA06 Wood Poles - Non Steel Framing | Sherlock Photo 2020_03_05_13_49_53_00788.jpg shows No compelling Issues | N/A | No | No | No
41129308 | Steel | Lakeville | 001/005 | 2021-12-13 | 2021-04-27 | 2020-05-11 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
44396925 | Steel | Sacramento | 006/151 | 2021-12-13 | 2021-04-27 | 2020-05-29 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road/trail. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40653348 | Steel | Table Mountain | 031/263 | 2021-12-13 | 2021-04-28 | 2020-05-28 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40700974 | Wood | Lakeville | 047/002 | 2021-12-13 | 2021-04-28 | 2020-08-06 | Is the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40700974 | Wood | Lakeville | 047/002 | 2021-12-13 | 2021-04-28 | 2020-08-06 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40747177 | Wood | Moss Landing | 005/050 | 2021-12-13 | 2021-04-28 | 2020-04-17 | High voltage/danger sign(s) missing or installed incorrectly per E.D. 022168? | FALSE | TRUE: A high voltage sign appears to be present below the distribution underbuild, but no high voltage signs are present below the transmission conductors. | Disagree | Condition does not exist | 022168 HV Signs, Marking, Numbering | HV Signs are Present Below Distribution Level | N/A | No | No | No
40747177 | Wood | Moss Landing | 005/050 | 2021-12-13 | 2021-04-28 | 2020-04-17 | Type of Splice: Compression | FALSE | TRUE: There appear to be 5 compression splices on the transmission conductors. | Agree | Condition is not compelling | TD-1001M-JA14 Splices Job Aid | N/A | N/A | No | No | No
40747177 | Wood | Moss Landing | 005/050 | 2021-12-13 | 2021-04-28 | 2020-04-17 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40753541 | Steel | Lakeville | 016/084 | 2021-12-13 | 2021-04-28 | 2020-05-29 | Structure Issues: Steel Structure Hardware Loose or missing | FALSE | TRUE: Several bolts appear to be missing in the low er section of the structure. | Disagree | Condition does not exist | TD-1001M-JA04 Steel Structures Corrosion and Deteriation | Drawing Number 309646 shows No missing Bolts | N/A | No | No | No
40753541 | Steel | Lakeville | 016/084 | 2021-12-13 | 2021-04-28 | 2020-05-29 | Is the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40815702 | Wood | Table Mountain | 011/218 | 2021-12-13 | 2021-04-28 | 2020-07-07 | Does or should this structure have a guy? | FALSE | TRUE: This structure appears to have a guy. | Disagree | Condition does not exist | TD-1009S | Sherlock Photo 200626_212716_98bde094.jpg shows Guy is at distribution Level | N/A | No | No | No
40815702 | Wood | Table Mountain | 011/218 | 2021-12-13 | 2021-04-28 | 2020-07-07 | Is the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40818658 | Steel | Lakeville | 052/257 | 2021-12-13 | 2021-04-28 | 2020-04-13 | Foundation Issues: Mastic sealant in poor condition | FALSE | TRUE: The mastic sealant appears to be in poor conditionon all four footings. | Agree | N/A | TD-1001M-JA12 Foundation Condition TLine Structures & Supports | Work Completed under LC 115761186 on 6/10/20 | N/A | No | No | No
40818658 | Steel | Lakeville | 052/257 | 2021-12-13 | 2021-04-28 | 2020-04-13 | Structure Issues: Steel Structure Hardware Loose or missing | FALSE | TRUE: Bolts appear to be missing in the low er section of the structure. | Disagree | Condition does not exist | TD-1001M-JA04 Steel Structures Corrosion and Deteriation | Drawing Number 309646 | N/A | No | No | No
40818658 | Steel | Lakeville | 052/257 | 2021-12-13 | 2021-04-28 | 2020-04-13 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | RUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40609125 | Steel | Pismo Beach | 020/090 | 2021-12-13 | 2021-05-04 | 2020-05-06 | Structure Issues: Steel Structure Hardware Loose or missing | FALSE | TRUE: The structure appears to have missing bolts on the secondary member. | Disagree | Condition does not exist | TD-1001M-JA04 Steel Structures Corrosion and Deteriation | Drawing Number 309646 | N/A | No | No | No
40609125 | Steel | Pismo Beach | 020/090 | 2021-12-13 | 2021-05-04 | 2020-05-06 | Type of insulator? | N/A | Porcelain/Ceramic: There appear to be porcelain/ceramic insulators present. | Agree | Condition is not compelling | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | N/A | N/A | No | No | No
40609125 | Steel | Pismo Beach | 020/090 | 2021-12-13 | 2021-05-04 | 2020-05-06 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40745905 | Steel | Concord | 002/015 | 2021-12-13 | 2021-05-04 | 2020-04-20 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road/trail. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40750569 | Steel | Lakeville | 015/075 | 2021-12-13 | 2021-05-04 | 2020-04-23 | Climbing steps installed incorrectly? | FALSE | TRUE: The steps appear to be missing in the top section. | Disagree | Condition does not exist | TD-1001M-JA04 Steel Structures Corrosion and Deteriation | Drawing Number 309646 | N/A | No | No | No
40809247 | Wood | Lakeville | 006/006 | 2021-12-13 | 2021-05-04 | 2020-07-27 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of afrequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40809408 | Wood | Moss Landing | 015/311 | 2021-12-13 | 2021-05-04 | 2020-09-11 | Are dampers present | FALSE | TRUE: There appear to be dampers present. | Agree | Condition is not compelling | TD-1001M REV5 ET Preventative Maintenace Manual | N/A | N/A | No | No | No
40809408 | Wood | Moss Landing | 015/311 | 2021-12-13 | 2021-05-04 | 2020-09-11 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road/trail. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40816207 | Wood | Table Mountain | 000/016 | 2021-12-13 | 2021-05-04 | 2020-06-03 | High voltage/danger sign(s) missing or installed incorrectly per E.D. 022168? | FALSE | TRUE: The high voltage sign appears to damaged. | Disagree | Condition does not exist | 022168 HV Signs, Marking, Numbering | Sherlock Photo 2020_05_09_08_54_23_00158.JPG shows HV Signs Below Distribution on Pole | N/A | No | No | No
40816207 | Wood | Table Mountain | 000/016 | 2021-12-13 | 2021-05-04 | 2020-06-03 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road/trail. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40819431 | Steel | Metcalf | 014/057 | 2021-12-13 | 2021-05-04 | 2020-10-02 | Structure Issues: Steel Structure Hardware Loose or missing | FALSE | TRUE: The structure appears to have missing bolts. | Disagree | Condition does not exist | TD-1001M-JA04 Steel Structures Corrosion and Deteriation | Drawing Number 309646 | N/A | No | No | No
40861163 | Steel | Lakeville | 046/228 | 2021-12-13 | 2021-05-04 | 2020-04-24 | Foundation Issues: Mastic sealant in poor condition | FALSE | RUE: The mastic sealant appears to be in poor condition. | Agree | N/A | TD-1001M-JA12 Foundation Condition TLine Structures & Supports | LC 115742366 shows mastic repair completed 1/16/20 | N/A | No | No | No
41129322 | Steel | Lakeville | 005/019 | 2021-12-13 | 2021-05-04 | 2020-04-07 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road/trail. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
44202752 | Wood | Sacramento | 010/095B | 2021-12-13 | 2021-05-04 | 2020-06-04 | Anchor Rod Issues: Obstructed View | FALSE | TRUE: The foundation of some anchors appears to be obstructed. | Disagree | Condition does not exist | TD-1001M-JA13 Guys and Anchors | All anchors appear to be visible in Sherlock | N/A | No | No | No
44667807 | Steel | Lakeville | 020/004 | 2021-12-13 | 2021-05-04 | 2020-07-31 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road/trail. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40667681 | Steel | Lakeville | 009/003 | 2021-12-13 | 2021-05-07 | 2020-04-16 | Foundation Issues: Mastic Sealant in Poor Condition | FALSE | TRUE: There appears to be no mastic sealant on the concrete foundation. | Agree | Condition is not compelling | TD-1001M-JA12 Foundation Condition TLine Structures & Supports | Mastic sealant in good repair in 2021 Photos | N/A | No | No | No
40667681 | Steel | Lakeville | 009/003 | 2021-12-13 | 2021-05-07 | 2020-04-16 | Is structure number missing? | FALSE | TRUE: The structure number appears to be missing. | Agree | N/A | 022168 HV Signs, Marking, Numbering | Structure Number in Good repair 2021 Photos | N/A | No | No | No
40667681 | Steel | Lakeville | 009/003 | 2021-12-13 | 2021-05-07 | 2020-04-16 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40752839 | Wood | Lakeville | 009/004 | 2021-12-13 | 2021-05-07 | 2020-07-21 | Vehicular and Mechanical Issues: Bird, animal or insect damage (e.g., woodpecker) | FALSE | TRUE: There appears to be woodpecker damage at the top of the pole. | Disagree | Condition does not exist | TD-1001M-JA06 Wood Poles - Non Steel Framing | Esaclated to Air Team on 12-15-21, Air replied No Notificationj needed | N/A | No | No | No | No existing LC'S for this FDA | Escalated to Air 12-15-21, Air replied NO Notification needed
40752839 | Wood | Lakeville | 009/004 | 2021-12-13 | 2021-05-07 | 2020-07-21 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road. | Agree | Condition is not compelling | TD-1009S | Inspection Form Response is No Not False | N/A | No | No | No
40766539 | Wood | Sacramento | 005/104 | 2021-12-13 | 2021-05-07 | 2020-06-15 | Are dampers present? | FALSE | RUE: The structure appears to have preform dampers. | Agree | Condition is not compelling | TD-1001M REV5 ET Preventative Maintenace Manual | Inspection Form Response is No Not False | N/A | No | No | No
40766539 | Wood | Sacramento | 005/104 | 2021-12-13 | 2021-05-07 | 2020-06-15 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | RUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road. | Agree | Condition is not compelling | TD-1009S | Inspection Form Response is No Not False | N/A | No | No | No
40870282 | Steel | Pismo Beach | 025/109 | 2021-12-13 | 2021-05-07 | 2020-05-18 | ntsTow er finish type: | Painted | Galvanized: The structure appears to have a galvanized finish. | Agree | Condition is not compelling | TD-1001M-JA04 Steel Structures Corrosion and Deteriation | N/A | N/A | No | No | No
40870282 | Steel | Pismo Beach | 025/109 | 2021-12-08 | 2021-05-07 | 2020-05-18 | Structure Issues: Steel Structure Hardware Loose or missing | FALSE | TRUE: Several bolts appear to be missing from secondary me mb e r s . | Disagree | Condition does not exist | TD-1001M-JA04 Steel Structures Corrosion and Deteriation | Drawing Number 309646 | N/A | No | No | No
40870282 | Steel | Pismo Beach | 025/109 | 2021-12-08 | 2021-05-07 | 2020-05-18 | Is structure number missing? | FALSE | TRUE: The structure number appears to be missing. | Disagree | Condition does not exist | 022168 HV Signs, Marking, Numbering | DJI_0634.jpg shows structure number | N/A | No | No | No
40870282 | Steel | Pismo Beach | 025/109 | 2021-12-08 | 2021-05-07 | 2020-05-18 | Is the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40870282 | Steel | Pismo Beach | 025/109 | 2021-12-08 | 2021-05-07 | 2020-05-18 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40587144 | Steel | Moss Landing | C007/031 | 2021-12-13 | 2021-07-08 | 2021-04-22 | Is there OPGW or Shield Wire Present? | Blank | No: The structure does not appear to have OPGW or shield wire. | Agree | Condition is not compelling | TD-1001M-JA11 OPGW | N/A | N/A | No | No | No
40590798 | Steel | Table Mountain | 032/211 | 2021-12-13 | 2021-06-29 | 2021-04-16 | Is there OPGW or Shield Wire Present? | Blank | No: The structure does not appear to have OPGW or shield wire. | Agree | Condition is not compelling | TD-1001M-JA11 OPGW | N/A | N/A | No | No | No
40590833 | Steel | Table Mountain | 012/091 | 2021-12-13 | 2021-07-23 | 2021-06-01 | Splices present? | No | Yes: There appear to be splices present. | Agree | Condition is not compelling | TD-1001M-JA14 Splices Job Aid | Condition is not compelling | N/A | No | No | No
40591238 | Wood | Table Mountain | 003/039 | 2021-12-13 | 2021-06-23 | 2021-05-25 | Cold end hardware type: C-hook | Cold end hardware type: C-hook | FALSE: The structure does not appear to have ac-hook. | Agree | Condition is not compelling | N/A | N/A | N/A | No | No | No
40592497 | Steel | Table Mountain | 006/051 | 2021-12-13 | 2021-07-20 | 2021-06-02 | Splices present? | No | Yes: There appear to be splices present. | Agree | Condition is not compelling | TD-1001M-JA14 Splices Job Aid | Condition is not compelling | N/A | No | No | No
40592503 | Steel | Table Mountain | 026/211 | 2021-12-13 | 2021-07-23 | 2021-06-10 | Rural area and structure within 600 ft of a frequently traveled road/trail | Blank | FALSE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road/trail. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40599155 | Wood | Metcalf | 006/010 | 2021-12-13 | 2021-07-19 | 2021-06-04 | Porcelain/Ceramic | Blank | TRUE: The structure appears to have porcelain/ceramic insulators. | Agree | Condition is not compelling | N/A | Sherlock search shows 7 Poly and 2 Porcelin Insulators. | N/A | No | No | No
40599267 | Wood | Metcalf | 006/064 | 2021-12-13 | 2021-07-09 | 2021-05-27 | Pole-top has damage or split-top | Blank | TRUE: The top of the pole appears to be hollowed out. | Agree | N/A | TD-1001M-JA06 Wood Poles - Non Steel Framing | LC 119570408 Shows Srtucture is Scheduled For Replacement in 2021 | N/A | No | No | No | Existing LC
40599267 | Wood | Metcalf | 006/064 | 2021-12-13 | 2021-07-09 | 2021-05-27 | Splices present? | No | Yes: There appear to be splices on the conductors. | Agree | Condition is not compelling | TD-1001M-JA14 Splices Job Aid | Sherlock Search shows Splices present | N/A | No | No | No
40599828 | Wood | Table Mountain | 000/032 | 2021-12-13 | 2021-07-13 | 2021-06-22 | Distribution underbuilt present | Blank | TRUE: The structure appears to have a distribution underbuild. | Agree | Condition is not compelling | N/A | N/A | N/A | No | No | No
40601405 | Steel | Table Mountain | 070/610 | 2021-12-13 | 2021-07-13 | 2021-06-12 | Anti-climbing damged or needed per E.D. 022168 | Blank | TRUE: The structure appears to need anti-climbing guards. | Disagree | Condition does not exist | 022168 HV Signs, Marking, Numbering | Sherlock Photo N_000003.JPG shows a Fence between structure and Road, No evidence of a Camp, Graffiti or unauthorized Climbing | N/A | No | No | No
40602109 | Wood | Eureka | 095/011 | 2021-12-13 | 2021-07-13 | 2021-06-10 | Structure has breaks / cracks / splits | Blank | RUE: The structure appears to have cracks on both poles. | Disagree | Condition is not compelling | N/A | Sherlock Search shows minor Crack, Structure Has Split Bolts, Inspection Form Does Not state Blank, It Reads No Non-Steel Structures issues or compelling abnormal conditions to report | N/A | No | No | No
40604327 | Steel | Fresno | 019/130 | 2021-12-13 | 2021-06-23 | 2021-04-27 | Structure Location Type | Agriculture | None: The structure appears to be located in a mountainous area with no signs of agriculture nearby. | Agree | Condition is not compelling | N/A | N/A | N/A | No | No | No
40604327 | Steel | Fresno | 019/130 | 2021-12-13 | 2021-06-23 | 2021-04-27 | Cold end hardware type: C-hook | Cold end hardware type: C-hook | FALSE: The structure does not appear to have c-hooks. | Disagree | Condition does not exist | N/A | Inspection Record States, Cold end hardware type: c-hook, shackles, clevis, other | N/A | No | No | No
40608668 | Steel | Pismo Beach | 052/210 | 2021-12-13 | 2021-06-23 | 2021-05-21 | Is there OPGW or Shield WirePresent? | No | Yes: The structure appears to have shield wire. | Agree | Condition is not compelling | TD-1001M-JA11 OPGW | Sherlock search shows no compelling issues | N/A | No | No | No
40608668 | Steel | Pismo Beach | 052/210 | 2021-12-13 | 2021-06-23 | 2021-05-21 | Rural area and structure within 600 ft of a frequently traveled road/trail | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road/trail. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40608668 | Steel | Pismo Beach | 052/210 | 2021-12-13 | 2021-06-23 | 2021-05-21 | Cold end hardware type:C-hook | Cold end hardware type:C-hook | FALSE: The structure does not appear to have a c-hook. | Disagree | Condition does not exist | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | Inspection Record States, Cold end hardware type: c-hook, shackles, clevis, other | N/A | No | No | No
40614256 | Wood | Lakeville | 021/000 | 2021-12-13 | 2021-07-23 | 2021-06-17 | Insulators are damaged, contaminated, arcing/tracking or in poor condition | Blank | ALSE: There appears to be contamination on the insulators. | Disagree | Condition is not compelling | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | Sherlock search Shows , Slight Contamination. Notes light Damage | N/A | No | No | No
40616411 | Wood | Lakeville | 033/000 | 2021-12-13 | 2021-07-20 | 2021-06-02 | Does this structure have a guy? | No | Yes: The structure appears to have a guy. | Disagree | Condition does not exist | TD-1001M REV5 ET Preventative Maintenace Manual | Sherlock search shows Guy is at Distribution Level | N/A | No | No | No
40643013 | Steel | Victor | 000/003 | 2021-12-13 | 2021-07-12 | 2021-04-20 | Steel Structure hardware loose or missing (e.g vibrating members) | Blank | TRUE: The structure appears to have missing bolts. | Disagree | Condition does not exist | TD-1001M-JA04 Steel Structures Corrosion and Deteriation | Drawing Number 402706 Type FA Tower | N/A | No | No | No
40643013 | Steel | Victor | 000/003 | 2021-12-13 | 2021-07-12 | 2021-04-20 | Tower finish in poor condition | Blank | TRUE: The tower finish appears to be in poor condition. Sap Search Shows No Existing LC"S | Agree | N/A | TD-1001M-JA04 Steel Structures Corrosion and Deteriation | Escalated to air 12-15-21 Air+ Replied No Notification needed | Create a LC | No | No | No | Escalated To Air 12-15-21 | Air Replied No LC Needed
40643013 | Steel | Victor | 000/003 | 2021-12-13 | 2021-07-12 | 2021-04-20 | Is there OPGW or Shield Wire Present? | Blank | Yes: The structure appears to have OPGW. | Disagree | Condition does not exist | TD-1001M-JA11 OPGW | N/A | N/A | No | No | No
40643013 | Steel | Victor | 000/003 | 2021-12-13 | 2021-07-12 | 2021-04-20 | Rural area and structure within 600 ft of a frequently traveled road/trail | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road/trail. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40643023 | Steel | Victor | 009/073 | 2021-12-13 | 2021-07-09 | 2021-04-20 | Is there OPGW or Shield Wire Present? | Blank | No: The structure does not appear to have OPGW or shield wire. | Agree | Condition is not compelling | TD-1001M-JA11 OPGW | N/A | N/A | No | No | No
40643410 | Steel | Victor | 011/092 | 2021-12-13 | 2021-06-25 | 2021-04-20 | Is there OPGW or Shield Wire Present? | Blank | No: The structure does not appear to have OPGW or shield wire. | Agree | Condition is not compelling | TD-1001M-JA11 OPGW | N/A | N/A | No | No | No
40652657 | Wood | Victor | 022/305 | 2021-12-10 | 2021-07-08 | 2021-05-10 | Rural area and structure within 600 ft of a frequently traveled road/trail | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road/trail. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40652657 | Wood | Victor | 022/305 | 2021-12-10 | 2021-07-08 | 2021-05-10 | High voltage signs missing, damaged, or installed incorrectly (see E.D. 022168 further details see GO 95) | Blank | TRUE: The structure appears to be missing a high voltage sign. | Agree | N/A | 022168 HV Signs, Marking, Numbering | Sherlock search shows missing HV Signs Scheduled on LC 120805688 | N/A | No | No | No | Existing LC
40655143 | Wood | Sacramento | 008/140 | 2021-12-10 | 2021-07-08 | 2021-05-14 | Distribution underbuilt present | Blank | TRUE: The structure appears to have a distribution underbuild. | Agree | Condition is not compelling | N/A | N/A | N/A | No | No | No
40662098 | Wood | Lakeville | 001/002 | 2021-12-10 | 2021-07-02 | 2021-05-17 | Switch Control Mechanism present? | No | es: The switch appears to have a manual operating handle. | Agree | Condition is not compelling | N/A | N/A | N/A | No | No | No
40662098 | Wood | Lakeville | 001/002 | 2021-12-10 | 2021-07-02 | 2021-05-17 | Grading / Corona rings present | Blank | TRUE: The insulators appear to have corona rings. | Agree | Condition is not compelling | N/A | N/A | N/A | No | No | No
40662577 | Steel | Moss Landing | 013/062 | 2021-12-10 | 2021-06-29 | 2021-04-16 | Steel Structure hardware loose or missing (e.g vibrating members) | Blank | TRUE: The structure appears to have missing hardware. | Disagree | Condition does not exist | N/A | Drawing Number 309646 | N/A | No | No | No
40662577 | Steel | Moss Landing | 013/062 | 2021-12-10 | 2021-06-29 | 2021-04-16 | Isthere OPGW or Shield Wire Present? | Blank | Yes: The structure appears to have OPGW. | Agree | N/A | TD-1001M-JA11 OPGW | N/A | N/A | No | No | No
40662577 | Steel | Moss Landing | 013/062 | 2021-12-10 | 2021-06-29 | 2021-04-16 | Vegetation present? | No | Yes: There appearsto be vegetation present around the foundation. | Agree | Condition is not compelling | N/A | N/A | N/A | No | No | No
40664044 | Steel | Victor | 006/051 | 2021-12-10 | 2021-06-24 | 2021-03-30 | Is there OPGW or Shield Wire Present? | Blank | No: The structure does not appear to have OPGW or shield wire. | Agree | Condition is not compelling | TD-1001M-JA11 OPGW | N/A | N/A | No | No | No
40664044 | Steel | Victor | 006/051 | 2021-12-10 | 2021-06-24 | 2021-03-30 | Anti-climbing damged or needed per E.D.022168 | Blank | TRUE: The structure appears to need anti-climbing guards. | Disagree | Condition does not exist | 022168 HV Signs, Marking, Numbering | Sherlock Photo DJI_0593.JPG shows structure Near what appears to be a Driveway. No Evidence of Graffiti, Camps, Or unauthorized Climbing | N/A | No | No | No
40664073 | Steel | Lakeville | 013/052 | 2021-12-10 | 2021-07-13 | 2021-06-17 | Tower Finish Type | Painted | Galvanized: The tower finish appears to be galvanized. | Agree | Condition is not compelling | N/A | N/A | N/A | No | No | No
40664073 | Steel | Lakeville | 013/052 | 2021-12-10 | 2021-07-13 | 2021-06-17 | Tower finish in poor condition | Blank | TRUE: The tower finish appears to be in poor condition. | Disagree | Condition does not exist | TD-1001M-JA04 Steel Structures Corrosion and Deteriation | Sherlock search shows NO Photos of Tower finish in poor condition | N/A | No | No | No
40664295 | Steel | Victor | 012/072 | 2021-12-10 | 2021-06-28 | 2021-04-15 | Secondary members are damaged or in poor condition | Blank | TRUE: Mult iple secondary members appear to be bent. | Agree | N/A | TD-1001M-JA04 Steel Structures Corrosion and Deteriation | Escalated to air 12-15-21 Air+ Replied No Notification needed | Create a LC | No | No | No | Escalated to air 12-15-21 | Air Replied No Notification Needed
40664295 | Steel | Victor | 012/072 | 2021-12-10 | 2021-06-28 | 2021-04-15 | Steel Structure hardware damaged (i.e. nuts and bolts) | Blank | TRUE: A bolt appears to be loose. | Agree | N/A | TD-1001M-JA04 Steel Structures Corrosion and Deteriation | Escalated to air 12-15-21 Air+ Replied No Notification needed | Create a LC | No | No | No | Escalated to air 12-15-21 | Air Replied No Notification Needed
40664295 | Steel | Victor | 012/072 | 2021-12-10 | 2021-06-28 | 2021-04-15 | Splices present? | No | Yes: The structure appears to have a splice. | Agree | Condition is not compelling | TD-1001M-JA14 Splices Job Aid | N/A | N/A | No | No | No
40664295 | Steel | Victor | 012/072 | 2021-12-10 | 2021-06-28 | 2021-04-15 | Is there OPGW or Shield Wire Present? | Blank | No: The structure does not appear to have OPGW or shield wire. | Agree | Condition is not compelling | TD-1001M-JA11 OPGW | N/A | N/A | No | No | No
40666961 | Wood | Lakeville | 000/013 | 2021-12-10 | 2021-06-25 | 2021-05-15 | Guy is loose / slack | Blank | TRUE: The bottom guy appears to be slack. | Agree | N/A | TD-1001M-JA13 Guys and Anchors | Escalated to air 12-15-21 Air+ Replied No Notification needed | Create a LC | No | No | No | Escalated to air 12-15-21 | Air Replied No Notification Needed
40666961 | Wood | Lakeville | 000/013 | 2021-12-10 | 2021-06-25 | 2021-05-15 | Jumpers present? | No | Yes: There appear to be jumpers on the structure. | Agree | N/A | N/A | N/A | N/A | No | No | No
40666961 | Wood | Lakeville | 000/013 | 2021-12-10 | 2021-06-25 | 2021-05-15 | Cold end hardware type: C-hook | Blank | TRUE: C-hooks appear to be present on dead-end insulator connections. | Agree | Condition is not compelling | N/A | N/A | N/A | No | No | No
40666961 | Wood | Lakeville | 000/013 | 2021-12-10 | 2021-06-25 | 2021-05-15 | Grading / Corona rings present | Blank | TRUE: Grading rings appear to be present on the dead-end insulators on the hot-end connection. | Agree | Condition is not compelling | N/A | N/A | N/A | No | N/A | No
40666961 | Wood | Lakeville | 000/013 | 2021-12-10 | 2021-06-25 | 2021-05-15 | High voltage signs missing, damaged, or installed incorrectly (see E.D. 022168 further details see GO 95) | Blank | TRUE: The structure appears to be missing a high voltage sign. | Agree | N/A | 022168 HV Signs, Marking, Numbering | LC 119781275 shows structure to be replaced in 2021 | N/A | No | No | No
40681934 | Steel | Concord | 027/107 | 2021-12-10 | 2021-06-24 | 2021-04-29 | Steel Structure hardware loose or missing (e.g vibrating members) | Blank | TRUE: The structure appears to have missing bolts on the secondary members where they attach to the primary leg members in several areas. | Disagree | Condition does not exist | N/A | Drawing Number 309646 | N/A | No | No | No
40685007 | Wood | Lakeville | 013/140 | 2021-12-10 | 2021-07-20 | 2021-06-18 | Polymer | Blank | TRUE: The insulators appear to be polymer. | Agree | Condition is not compelling | N/A | N/A | N/A | No | No | No
40689432 | Steel | Pismo Beach | 026/112 | 2021-12-10 | 2021-06-22 | 2021-04-08 | Steel Structure hardware loose or missing (e.g vibrating members) | Blank | TRUE: The structure appears to have missing bolts. | Disagree | Condition does not exist | N/A | Drawing Number 211223 | N/A | No | No | No
40689432 | Steel | Pismo Beach | 026/112 | 2021-12-10 | 2021-06-22 | 2021-04-08 | Rural area and structure within 600 ft of a frequently traveled road/trail | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road/trail. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40738304 | Wood | Table Mountain | 005/107 | 2021-12-10 | 2021-06-28 | 2021-05-17 | Does this structure have a guy? | No | Yes: The structure appears to have a guy. | Disagree | Condition does not exist | N/A | Sherlock Photo 210419_184257_125_1295620e.jpg shows guy at Distribution Level | N/A | No | No | No
40738304 | Wood | Table Mountain | 005/107 | 2021-12-10 | 2021-06-28 | 2021-05-17 | Rural area and within 600 feet of a dwelling or camp | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling or camp. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40750555 | Wood | Lakeville | 016/004 | 2021-12-10 | 2021-06-28 | 2021-05-12 | Structure has Bird, animal or insect damage (e.g., woodpecker) | Blank | TRUE: The structure appears to have woodpecker damage | Agree | N/A | TD-1001M-JA06 Wood Poles - Non Steel Framing | Sherlock Photo N_000258.JPG shows woodpecker Damage | Create a LC | Yes | Yes | No | No existing LC"S | Escalated To Air 12/15/21, Air replied yes LC Needed , Created 12/10/21 By Air
40751889 | Wood | Sacramento | 000/014 | 2021-12-10 | 2021-07-02 | 2021-05-17 | Does this structure have a guy? | No | Yes: The structure appears to have a guy. | Disagree | Condition does not exist | N/A | Sherlock Photo 210419_201814_285_935e6e00.jpg shows Guys are at Distribution evel | N/A | No | No | No
40751889 | Wood | Sacramento | 000/014 | 2021-12-10 | 2021-07-02 | 2021-05-17 | Rural area and structure within 600 ft of a frequently traveled road/trail | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road/trail | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40751889 | Wood | Sacramento | 000/014 | 2021-12-10 | 2021-07-02 | 2021-05-17 | Cold end hardware type: C-hook | Cold end hardware type: c-hook | ALSE: Thestructure does not appear to have a c-hook. | Agree | Condition is not compelling | N/A | N/A | N/A | No | No | No
40753091 | Steel | Pismo Beach | 034/154 | 2021-12-10 | 2021-07-08 | 2021-03-11 | Is there OPGW or Shield Wire Present? | Blank | o: The structure does not appear to have OPGW or shield wire. | Agree | Condition is not compelling | TD-1001M-JA11 OPGW | N/A | N/A | No | No | No
40760579 | Wood | Pismo Beach | 006/055 | 2021-12-10 | 2021-06-24 | 2021-04-23 | ural area and structure within 600 ft of a frequently traveled road/trail | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road/trail. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40761885 | Steel | Concord | 001/009 | 2021-12-10 | 2021-07-02 | 2021-04-29 | Shield Wire or OPGW grounded | Blank | TRUE: The OPGW appears to be grounded. | Agree | N/A | TD-1001M-JA11 OPGW | N/A | N/A | No | No | No
40762414 | Steel | Pismo Beach | 011/044 | 2021-12-10 | 2021-07-02 | 2021-04-28 | Is there OPGW or Shield Wire Present? | No | Yes: The structure appears to have an overhead ground wire. | Agree | Condition is not compelling | TD-1001M-JA11 OPGW | N/A | N/A | No | No | No
40762689 | Steel | Table Mountain | 032/214 | 2021-12-10 | 2021-07-09 | 2021-04-12 | Splices present? | No | Yes: There appear to be splices on the conductors. | Agree | Condition is not compelling | N/A | N/A | N/A | No | No | No
40762689 | Steel | Table Mountain | 032/214 | 2021-12-10 | 2021-07-09 | 2021-04-12 | Is there OPGW or Shield Wire Present? | Blank | No: The structure does not appear to have OPGW or shield wire. | Agree | Condition is not compelling | TD-1001M-JA11 OPGW | N/A | N/A | No | No | No
40762689 | Steel | Table Mountain | 032/214 | 2021-12-10 | 2021-07-09 | 2021-04-12 | Anti-climbing damged or needed per E.D. 022168 | Blank | TRUE: The structure appears to need anti-climbing guards. | Disagree | Condition does not exist | 022168 HV Signs, Marking, Numbering | Sherlock Photo J-000004.JPG shows no evidence of Graffiti, Camps or unauthorixed Climbing | N/A | No | No | No
40763150 | Steel | Pismo Beach | 009/147 | 2021-12-10 | 2021-07-08 | 2021-03-30 | Is there OPGW or Shield Wire Present? | Blank | No: The structure does not appear to have OPGW or shield wire. | Agree | Condition is not compelling | N/A | N/A | N/A | No | No | No
40763150 | Steel | Pismo Beach | 009/147 | 2021-12-10 | 2021-07-08 | 2021-03-30 | Rural area and structure within 600 ft of a frequently traveled road/trail | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road/trail. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40763380 | Wood | Fresno | 000/004 | 2021-12-10 | 2021-07-06 | 2021-05-12 | Operating assembly in poor condition or inoperable | Blank | TRUE: There appears to be loose hardware and bolts on the operating rod. | Agree | Condition does not exist | TD-1001M-JA15 Switches Job Aid | LC 120612704 Shows that Switch and T Line was Removed | N/A | No | No | No
40763380 | Wood | Fresno | 000/004 | 2021-12-10 | 2021-07-06 | 2021-05-12 | Rural area and within 600 feet of a dwelling or camp | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling or camp. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40764774 | Steel | Sacramento | 009/084 | 2021-12-10 | 2021-06-28 | 2021-04-14 | Is there OPGW or Shield Wire Present? | Blank | Yes: The structure appears to have a shield wire. | Agree | Condition is not compelling | TD-1001M-JA11 OPGW | N/A | N/A | No | No | No
40764774 | Steel | Sacramento | 009/084 | 2021-12-10 | 2021-06-28 | 2021-04-14 | Rural area and structure within 600 ft of a frequently traveled road/trail | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road/trail. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40767454 | Wood | Sacramento | 003/073 | 2021-12-10 | 2021-06-29 | 2021-05-19 | Polymer | Blank | TRUE: The structure appears to have polymer insulators. | Agree | Condition is not compelling | N/A | N/A | N/A | No | No | No
40767990 | Wood | Metcalf | 010/004 | 2021-12-10 | 2021-07-12 | 2021-04-23 | Cotter key missing / out of place / improperly positioned | Blank | TRUE: The cotter key on the top phase shoe appears to be damaged. | Agree | Condition is not compelling | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | N/A | N/A | No | No | No
40767990 | Wood | Metcalf | 010/004 | 2021-12-10 | 2021-07-12 | 2021-04-23 | Vegetation present? | No | Yes: There appears to be vegetation present at the base of the pole. | Agree | Condition is not compelling | N/A | N/A | N/A | No | No | No
40770580 | Wood | Lakeville | 019/004 | 2021-12-10 | 2021-07-13 | 2021-06-01 | 2 or more splices present one phase/span | Blank | TRUE: There appear to be 2 or more splices present in the top and bottom phases/spans. | Agree | Condition is not compelling | TD-1001M-JA14 Splices Job Aid | N/A | N/A | No | No | No
40770580 | Wood | Lakeville | 019/004 | 2021-12-10 | 2021-07-13 | 2021-06-01 | Splices within 10" of structure | Blank | TRUE: There appears to be a splice within 10 feet of the structure. | Disagree | Condition does not exist | TD-1001M-JA14 Splices Job Aid | Existing LC 115589333 was updated 6/30/20, Field inspection shows sleeves Greater than 10' from support, Dampers installed on conductors with sleeves No Issues | N/A | No | No | No
40770580 | Wood | Lakeville | 019/004 | 2021-12-10 | 2021-07-13 | 2021-06-01 | Polymer | Blank | TRUE: The insulators appear to be polymer. | Agree | Condition is not compelling | N/A | N/A | N/A | No | No | No
40770580 | Wood | Lakeville | 019/004 | 2021-12-10 | 2021-07-13 | 2021-06-01 | Rural area and structure within 600 ft of a frequently traveled road/trail | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road/trail. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40770580 | Wood | Lakeville | 019/004 | 2021-12-10 | 2021-07-13 | 2021-06-01 | Vegetation present? | No | Yes: There appears to be vegetation at the base of the pole. | Agree | Condition is not compelling | N/A | N/A | N/A | No | No | No
40770580 | Wood | Lakeville | 019/004 | 2021-12-10 | 2021-07-13 | 2021-06-01 | Bird Guard Present? | No | Yes: There appear to be bird guards present. | Agree | Condition is not compelling | N/A | N/A | N/A | No | No | No
40770580 | Wood | Lakeville | 019/004 | 2021-12-10 | 2021-07-13 | 2021-06-01 | Are Bird/Animal guards in poor condition? | Blank | Yes: One of the bird guards appears to be missing. | Agree | N/A | N/A | N/A | N/A | No | No | No
40770692 | Wood | Sacramento | 000/005 | 2021-12-10 | 2021-07-22 | 2021-06-08 | Cold end hardware type: C-ho | Blank | TRUE: The structure appears to have c-hooks. | Agree | Condition is not compelling | N/A | N/A | N/A | No | No | No
40770692 | Wood | Sacramento | 000/005 | 2021-12-10 | 2021-07-22 | 2021-06-08 | Distribution underbuilt present | Blank | TRUE: The structure appears to have a distribution underbuild. | Agree | Condition is not compelling | N/A | N/A | N/A | No | No | No
40772323 | Wood | Pismo Beach | 007/118 | 2021-12-10 | 2021-07-09 | 2021-04-27 | Rural area and structure within 600 ft of a frequently traveled road/trail | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road/trail. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40772323 | Wood | Pismo Beach | 007/118 | 2021-12-10 | 2021-07-09 | 2021-04-27 | Distribution underbuilt present | Blank | TRUE: The structure appears to have a distribution underbuild. | Agree | Condition is not compelling | N/A | N/A | N/A | No | No | No
40805297 | Steel | Sacramento | 021/166 | 2021-12-10 | 2021-06-25 | 2021-04-28 | Rural area and within 600 feet of a dwelling or camp | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling or camp. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40810014 | Steel | Table Mountain | 090/457 | 2021-12-10 | 2021-07-19 | 2021-06-02 | Shield Wire or OPGW grounded | Blank | The OPGW does not appear to be grounded. | Agree | Condition is not compelling | N/A | N/A | N/A | No | No | No
40811229 | Steel | Moss Landing | C013/056 | 2021-12-10 | 2021-07-06 | 2021-04-22 | Is there OPGW or Shield Wire Present? | Blank | No: The structure does not appear to have OPGW or shield wire. | Agree | Condition is not compelling | TD-1001M-JA11 OPGW | N/A | N/A | No | No | No
40812936 | Steel | Lakeville | 010/076 | 2021-12-10 | 2021-07-08 | 2021-04-13 | Tower Finish Type | Galvanized | Painted: The structure appears to have a painted finish. | Agree | Condition is not compelling | N/A | N/A | N/A | No | No | No
40812936 | Steel | Lakeville | 010/076 | 2021-12-10 | 2021-07-08 | 2021-04-13 | Is there OPGW or Shield Wire Present? | Blank | No: The structure does not appear to have OPGW or shield wire. | Agree | Condition is not compelling | TD-1001M-JA11 OPGW | N/A | N/A | No | No | No
40816214 | Wood | Table Mountain | 006/098 | 2021-12-10 | 2021-06-23 | 2021-05-22 | Does this structurehave a guy? | NO | Yes: The structure appears to have a guy wire. | Disagree | Condition does not exist | N/A | Sherlock Photo 210422_163832_997_14b1480.jpg shows guy is at communication Level | N/A | No | No | No
40816214 | Wood | Table Mountain | 006/098 | 2021-12-10 | 2021-06-23 | 2021-05-22 | Automatic guy splice present? | Blank | Yes: The guy wire appears to have an automatic splice. | Disagree | Condition does not exist | N/A | Sherlock Photo 210422_163832_997_14b1480.jpg shows guy is at communication Level | N/A | No | No | No
40816214 | Wood | Table Mountain | 006/098 | 2021-12-10 | 2021-06-23 | 2021-05-22 | Vegetation present? | NO | Yes: There appears to be vegetation present around the base of the pole. | Agree | Condition is not compelling | N/A | N/A | N/A | No | No | No
40816214 | Wood | Table Mountain | 006/098 | 2021-12-10 | 2021-06-23 | 2021-05-22 | Significant vegetation around concrete foundation / base of pole | Blank | TRUE: Significant vegetation appears to be present within 10 feet of the base of the pole. | Disagree | Condition does not exist | N/A | Sherlock Photo 210421_223356_623_d21818d7.jpg shows No significant vegetation around Base of Pole | N/A | No | No | No
40816214 | Wood | Table Mountain | 006/098 | 2021-12-10 | 2021-06-23 | 2021-05-22 | Anchor / Guying covered by vegetation | Blank | TRUE: The anchor and guy marker appear to be covered by vegetation. | Disagree | Condition does not exist | N/A | Sherlock Photo 210422_163832_997_14b1480.jpg shows guy is at communication Level | N/A | No | No | No
40822812 | Steel | Sacramento | 008/086 | 2021-12-10 | 2021-06-23 | 2021-05-12 | Rural area and structure within 600 ft of a frequently traveled road/trail | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road/trail. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40824242 | Wood | Sacramento | 005/145 | 2021-12-10 | 2021-07-06 | 2021-05-07 | Does this structure have aguy? | NO | es: The structure appears to have a guy. | Disagree | Condition does not exist | N/A | Sherlock Photo 2020_05_08_12_28_40_00266.jpg shows Guy is at Distribution Level | N/A | No | No | No
40863068 | Steel | Pismo Beach | 006/028 | 2021-12-10 | 2021-07-09 | 2021-04-29 | Mastic sealant in poor condition | Blank | TRUE: The mastic sealant appears to be deteriorating. | Disagree | Condition is not compelling | TD-1001M-JA12 Foundation Condition TLine Structures & Supports | Inspector mentioned Minor wear in Report, Sherlock search shows no compelling issues | N/A | No | No | No
40863068 | Steel | Pismo Beach | 006/028 | 2021-12-10 | 2021-07-09 | 2021-04-29 | Rural area and structure within 600 ft of a frequently traveled road/trail | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road/trail. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40863068 | Steel | Pismo Beach | 006/028 | 2021-12-10 | 2021-07-09 | 2021-04-29 | Cold end hardware type: C-hook | Blank | TRUE: There structure appears to have c-hooks. | Agree | Condition is not compelling | N/A | Inspector mentioned C Hooks in Notes | N/A | No | No | No
40869640 | Wood | Sacramento | 002/071 | 2021-12-09 | 2021-06-22 | 2021-05-11 | Splices present? | NO | Yes: Thestructure appears to have multiple splices. | Agree | Condition is not compelling | TD-1001M-JA14 Splices Job Aid | Sherlock Photo 21417_165424_755_50643a1d.jpg shows Multiple splices | N/A | No | No | No
40869640 | Wood | Sacramento | 002/071 | 2021-12-09 | 2021-06-22 | 2021-05-11 | 2 or more splices present one phase/span | Blank | FALSE: There were insufficient photos to determine if 2 or more splices were present on one phase/span. | Agree | Condition does not exist | TD-1001M-JA14 Splices Job Aid | Sherlock Search does not show 2 or more splices in a span. I did not see this discrepancy in inspection Report | N/A | No | No | No
40869640 | Wood | Sacramento | 002/071 | 2021-12-09 | 2021-06-22 | 2021-05-11 | Automatic splices greater 10' to clamp | Blank | FALSE: There were insufficient photos to determine whether there are automatic splices greater than 10 feet from the clamp. | Disagree | Condition does not exist | TD-1001M-JA14 Splices Job Aid | Sherlock search shows no automatic splices, I did not see this discrepancy in inspection report | N/A | No | No | No
40869640 | Wood | Sacramento | 002/071 | 2021-12-09 | 2021-06-22 | 2021-05-11 | Rural area and within 600 feet of a dwelling or camp | Blank | RUE: The structure appears to be in a rural area and within 600 feet of a dwelling or camp. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40869640 | Wood | Sacramento | 002/071 | 2021-12-09 | 2021-06-22 | 2021-05-11 | Rural area and structure within 600 ft of a frequently traveled road/trail | Blank | RUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road/trail. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40872989 | Steel | Concord | 001/008 | 2021-12-09 | 2021-07-02 | 2021-04-23 | Splices present? | NO | Yes: There appear to be multiple splices on the conductors. | Agree | Condition is not compelling | N/A | N/A | N/A | No | No | No
40872989 | Steel | Concord | 001/008 | 2021-12-09 | 2021-07-02 | 2021-04-23 | Splices within 10' of structure | Blank | TRUE: There appear to be multiple splices on the conductors within 10 feet of the structure. | Disagree | Condition does not exist | TD-1001M-JA14 Splices Job Aid | Sherlock Search shows no splices within 10 ft of Support | N/A | No | No | No
40874631 | Wood | Sacramento | 003/047 | 2021-12-09 | 2021-07-12 | 2021-06-10 | Rural area and structure within 600 ft of a frequently traveled road/trail | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road/trail. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40874631 | Wood | Sacramento | 003/047 | 2021-12-09 | 2021-07-12 | 2021-06-10 | Distribution underbuilt present | Blank | TRUE: The structure appears to have a distribution underbuild. | Agree | Condition is not compelling | N/A | N/A | N/A | No | No | No
40874826 | Wood | Sacramento | 012/330 | 2021-12-09 | 2021-06-22 | 2021-05-27 | Rural area and structure within 600 ft of a frequently traveled road/trail | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road/trail. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40874826 | Wood | Sacramento | 012/330 | 2021-12-09 | 2021-06-22 | 2021-05-27 | High voltage signs missing, damaged, or installed incorrectly (see E.D. 022168 further details see GO 95) | Blank | TRUE: The structure appears to be missing a high voltage sign. | Disagree | Condition does not exist | 022168 HV Signs, Marking, Numbering | Sherlock Photos 210416_215600_269_5ef9ced1.jpg & 210417_171049_33_77e56183.jpg shows HV Signs Below Distribution level | N/A | No | No | No
40904166 | Wood | Victor | 028/422 | 2021-12-09 | 2021-06-24 | 2021-05-10 | Rural area and structure within 600 ft of a frequently traveled road/trail | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road/trail | Agree | Condition is not compelling | TD-1009S |  | N/A | No | No | No
40904175 | Wood | Victor | 028/413 | 2021-12-09 | 2021-06-25 | 2021-05-11 | Does this structure have a guy? | NO | Yes: The structure appears to have guys. | Disagree | Condition does not exist | N/A | Sherlock Photo DJI_0637.JPG shows Gys are communication and Distribution Guy's | N/A | No | No | No
40913153 | Wood | Sacramento | 007/102 | 2021-12-09 | 2021-06-24 | 2021-05-20 | Rural area and within 600 feet of a dwelling or camp | Blank | RUE: The structure appears to be in a rural area and within 600 feet of a dwelling or camp. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
42549851 | Wood | Sacramento | 004/111 | 2021-12-09 | 2021-06-24 | 2021-05-13 | Does this structure have a guy? | NO | Yes: The structure appears to have a guy wire. | Disagree | Condition does not exist | N/A | Sherlock Photo 210416_183232_802_ade086c2.jpg sshows guy is at communication Level | N/A | No | No | No
42549851 | Wood | Sacramento | 004/111 | 2021-12-09 | 2021-06-24 | 2021-05-13 | Rural area and within 600 feet of a dwelling or camp | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling or camp. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
42549851 | Wood | Sacramento | 004/111 | 2021-12-09 | 2021-06-24 | 2021-05-13 | Rural area and structure within 600 ft of a frequently traveled road/trail | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road/trail. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
42549851 | Wood | Sacramento | 004/111 | 2021-12-09 | 2021-06-24 | 2021-05-13 | Guy marker missing (GO 95 infraction) | Blank | TRUE: The guy marker appears to be missing. | Disagree | Condition does not exist | N/A | Sherlock Photo 210416_183232_802_ade086c2.jpg sshows guy is at communication Level | N/A | No | No | No
42572614 | Wood | Sacramento | 000/003C | 2021-12-09 | 2021-07-23 | 2021-06-12 | What kind of structure is this? | Wood | Steel: The structure appears to be light duty steel. | Agree | Condition is not compelling | N/A | N/A | N/A | No | No | No
42572614 | Wood | Sacramento | 000/003C | 2021-12-09 | 2021-07-23 | 2021-06-12 | Tower Finish Type | Blank | Weathered: The tower finish appears to be weathered. | Agree | Condition is not compelling | N/A | N/A | N/A | No | No | No
42572614 | Wood | Sacramento | 000/003C | 2021-12-09 | 2021-07-23 | 2021-06-12 | Foundation Type | Blank | Blank | Agree | Condition is not compelling | N/A | N/A | N/A | No | No | No
44164585 | Wood | Table Mountain | 003/083 | 2021-12-09 | 2021-06-25 | 2021-05-20 | Crossarm present? | YES | No: Thestructure does not appear to have a crossarm. | Agree | Condition is not compelling | N/A | N/A | N/A | No | No | No
44203628 | Steel | Sacramento | 002/060 | 2021-12-09 | 2021-07-12 | 2021-06-18 | Polymer | Blank | TRUE: The structure appears to have polymer insulators. | Agree | Condition is not compelling | N/A | N/A | N/A | No | No | No
44420029 | Steel | Eureka | 026/007 | 2021-12-09 | 2021-07-22 | 2021-06-18 | Cold end hardware type: C-hook | Blank | TRUE: The structure appears to have c-hooks. | Agree | Condition is not compelling | N/A | N/A | N/A | No | No | No
44420029 | Steel | Eureka | 026/007 | 2021-12-09 | 2021-07-22 | 2021-06-18 | Distribution underbuilt present | Blank | TRUE: The structure appears to have a distribution underbuild. | Agree | Condition is not compelling | N/A | N/A | N/A | No | No | No
44877346 | Steel | Lakeville | Z003/006 | 2021-12-09 | 2021-07-20 | 2021-06-25 | Structure Location Type | None | Agriculture: The structure appears to be located in an agricultural area. | Agree | Condition is not compelling | N/A | N/A | N/A | No | No | No
44877346 | Steel | Lakeville | Z003/006 | 2021-12-09 | 2021-07-20 | 2021-06-25 | Rural area and within 600 feet of a dwelling or camp | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
45015281 | Steel | Victor | 008/104 | 2021-12-09 | 2021-07-13 | 2021-06-10 | Splices within 10' of structure | Blank | TRUE: There appears to be a splice within 10 feet of the structure. | Disagree | Condition is not compelling | TD-1001M-JA14 Splices Job Aid | Sherlock Photo 210410_171601_757_a516f827.jpg shows spliceb more than 10 ft from support | N/A | No | No | No
40580984 | Steel | Concord | 007/045 | 2021-12-09 | 2021-08-05 | 2021-04-24 | Mastic sealant in poor condition | Blank | TRUE: The mastic sealant appears to be in poor condition. | Agree | N/A | TD-1001M-JA12 Foundation Condition TLine Structures & Supports | LC 119108875 shows Foundations will be resealed, Numerous LC'S for mastic cancelled | N/A | No | No | No | Existing LC
40594162 | Steel | Lakeville | 018/091 | 2021-12-09 | 2021-07-27 | 2021-06-01 | Insulators are damaged, contaminated, arcing/tracking or in poor condition | Blank | TRUE: The insulators on each phase appear to have contamination. | Disagree | Condition is not compelling | N/A | Circuit appears to be Grounded and Idle in Sherlock Photos, No signs of Tracking | N/A | No | No | No
40602490 | Wood | Sacramento | 001/050 | 2021-12-09 | 2021-08-06 | 2021-05-11 | Polymer | Blank | TRUE: The insulators appear to be polymer. | Agree | Condition is not compelling | N/A | Monitor incorrectly entered Blank on Inspection Form Response, Correct answer ids Porcelin/Ceramic | N/A | No | No | No
40650157 | Steel | Sacramento | 012/142A | 2021-12-09 | 2021-08-03 | 2021-06-12 | Distribution underbuilt present | Blank | FALSE: The structure appears to have distribution underbuild. | Agree | Condition is not compelling | N/A | N/A | N/A | No | No | No
40650157 | Steel | Sacramento | 012/142A | 2021-12-09 | 2021-08-03 | 2021-06-12 | High voltage signs missing, damaged, or installed incorrectly (see E.D. 022168 further details see GO 95) | Blank | TRUE: There appears to be a high voltage sign missing on the upper portion of 12/142B. | Agree | N/A | 022168 HV Signs, Marking, Numbering | SAP Shows HV Sign will be replaced under LC 117374643 | N/A | No | No | No | Existing LC
40654863 | Wood | Sacramento | 015/228 | 2021-12-09 | 2021-08-09 | 2021-05-01 | Rural area and structure within 600 ft of a frequently traveled road/trail | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road/trail. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40654863 | Wood | Sacramento | 015/228 | 2021-12-09 | 2021-08-09 | 2021-05-01 | Distribution underbuilt present | Blank | TRUE: The structure appears to have distribution underbuild. | Agree | Condition is not compelling | N/A | N/A | N/A | No | No | No
40664579 | Steel | Moss Landing | 037/162 | 2021-12-09 | 2021-08-03 | 2021-05-21 | Is there OPGW or Shield Wire Present? | NO | es: The structure appears to have shield wire. | Agree | Condition is not compelling | TD-1001M-JA11 OPGW | N/A | N/A | No | No | No
40677135 | Wood | Table Mountain | 000/022 | 2021-12-09 | 2021-08-06 | 2021-06-09 | Cold end hardware type: C-hook | Cold end hardware type: c-hook | The structure does not appear to have a c-hook. | Agree | Condition is not compelling | N/A | N/A | N/A | No | No | No
40701722 | Wood | Table Mountain | 001/044 | 2021-12-09 | 2021-08-05 | 2021-05-20 | Structure has breaks / cracks / splits | Blank | TRUE: The structure appears to have cracks. | Agree | Condition is not compelling | TD-1001M-JA06 Wood Poles - Non Steel Framing | Sherlock Photo 210422_172052_417_42f3dc16.jpg Shows no indication of rot | N/A | No | No | No
40701722 | Wood | Table Mountain | 001/044 | 2021-12-09 | 2021-08-05 | 2021-05-20 | Pole-top has damage or split-top | Blank | TRUE: The structure appears to have pole-top damage. | Agree | Condition is not compelling | TD-1001M-JA06 Wood Poles - Non Steel Framing | Sherlock Photo 210422_172052_417_42f3dc16.jpg Shows no indication of rot | N/A | No | No | No
40701722 | Wood | Table Mountain | 001/044 | 2021-12-09 | 2021-08-05 | 2021-05-20 | High voltage signs missing, damaged, or installed incorrectly (see E.D. 022168 further details see GO 95) | Blank | TRUE: A high voltage sign appears to be damaged. | Disagree | Condition does not exist | 022168 HV Signs, Marking, Numbering | Sherlock Photos 210422_172052_417_42f3dc16.jpg & 210422_201119_936_ddd7a39a.jpg shows HV Signs on Both sides of Crossarm | N/A | No | No | No
40751812 | Wood | Sacramento | 003/063 | 2021-12-09 | 2021-08-05 | 2021-05-19 | What kind of structure is this? | Wood | Steel: The structure appears to be steel. | Agree | Condition is not compelling | N/A | N/A | N/A | No | No | No
40756559 | Steel | Concord | 012/054 | 2021-12-09 | 2021-08-05 | 2021-05-04 | Splices present? | NO | Yes: Splices appear to be present. | Agree | Condition is not compelling | TD-1001M-JA14 Splices Job Aid | N/A | N/A | No | No | No
40756559 | Steel | Concord | 012/054 | 2021-12-09 | 2021-08-05 | 2021-05-04 | Glass | Blank | TRUE: The structure appears to have glass insulators. | Agree | Condition is not compelling | N/A | N/A | N/A | No | No | No
40756559 | Steel | Concord | 012/054 | 2021-12-09 | 2021-08-05 | 2021-05-04 | Cold-end hardware is in poor condition (e.g. c-hook or clevis) | Blank | RUE: The finish on the c-hook appears to be diminished. The pictures are insufficient to gauge the amount of wear. | Disagree | Condition is not compelling | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | Sherlock Photo DJI_0825.JPG shows surface Rust, Less Than 30% material Loss | N/A | No | No | No
40758138 | Steel | Moss Landing | 016/124 | 2021-12-09 | 2021-07-27 | 2021-06-03 | Vegetation present? | NO | Yes: Vegetation appears to be present near the base of the structure. | Agree | Condition is not compelling | N/A | N/A | N/A | No | No | No
40768175 | Steel | Victor | 000/004 | 2021-12-09 | 2021-08-09 | 2021-05-21 | Vegetation present? | NO | Yes: Vegetation appears to be present. | Agree | Condition is not compelling | N/A | N/A | N/A | No | No | No
40809992 | Wood | Table Mountain | 000/016 | 2021-12-09 | 2021-08-02 | 2021-05-19 | Rural area and structure within 600 ft of a frequently traveled road/trail | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road/trail. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40814632 | Steel | Concord | 005/026 | 2021-12-09 | 2021-07-30 | 2021-06-27 | Vegetation present? | Yes | es: There appears to be vegetation present near the base of the structure. | Agree | Condition is not compelling | N/A | Monitor incorrectly entered YES on inspection form Response. Inspection Form states NO vegetation Present | N/A | No | No | No
40815455 | Steel | Table Mountain | 009/067 | 2021-12-09 | 2021-07-27 | 2021-06-11 | Tower finish in poor condition | Blank | TRUE: The tower finish appears to be in poor condition. The rust appears mostly in the upper section of the tower. | Disagree | Condition does not exist | TD-1001M-JA04 Steel Structures Corrosion and Deteriation | LC 116744896 for this FDA was cancelled on 3/18/19, surface Rust acceptable | N/A | Yes | No | No
40815455 | Steel | Table Mountain | 009/067 | 2021-12-09 | 2021-07-27 | 2021-06-11 | Conductor damage (e.g gunshot, broken strands, arcing, twisted bundle) or in poor condition | Blank | TRUE: The conductor appears to show bird caging at the dead end. | Agree | Condition is not compelling | N/A | N/A | N/A | No | No | No
40816295 | Steel | Table Mountain | 022/206 | 2021-12-09 | 2021-08-10 | 2021-06-11 | Is there OPGW or Shield Wire Present? | NO | Yes: The structure appears to have OPGW. | Agree | Condition is not compelling | TD-1001M-JA11 OPGW | N/A | N/A | No | No | No
40861421 | Wood | Lakeville | 016/008 | 2021-12-09 | 2021-08-02 | 2021-05-21 | High voltage signs missing, damaged, or installed incorrectly (see E.D. 022168 further details see GO 95) | Blank | TRUE: A high voltage sign appears to be missing. | Disagree | Condition does not exist | 022168 HV Signs, Marking, Numbering | Sherlock Photo 3(624).jpg shows HV Signs below Distribution Level | N/A | No | No | No
40861966 | Wood | Sacramento | 000/019 | 2021-12-09 | 2021-08-10 | 2021-05-18 | High voltage signs missing, damaged, or installed incorrectly (see E.D. 022168 further details see GO 95) | Blank | TRUE: One of the high voltage signs appears to be damaged. | Agree | N/A | 022168 HV Signs, Marking, Numbering | Existing LC 117461693 shows to complete by 5/8/21 Update LC | Update a LC | No | No | No | Existing LC
40863584 | Steel | Pismo Beach | 010/039 | 2021-12-09 | 2021-07-30 | 2021-06-04 | Is there OPGW or Shield Wire Present? | NO | Yes: The structure appears to have a shield wire. | Agree | Condition is not compelling | TD-1001M-JA11 OPGW | N/A | N/A | No | No | No
40868727 | Wood | Table Mountain | 002/054 | 2021-12-09 | 2021-07-27 | 2021-05-20 | Rural area and within 600 feet of a dwelling or camp | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling or camp. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40868727 | Wood | Table Mountain | 002/054 | 2021-12-09 | 2021-07-27 | 2021-05-20 | High voltage signs missing, damaged, or installed incorrectly (see E.D. 022168 further details see GO 95) | Blank | TRUE: The structure appears to be missing high voltage signs. | Disagree | Condition does not exist | 022168 HV Signs, Marking, Numbering | Sherlock Photo 210422_201043_506_e9f29bc9.jpg shows HVSighns below Distribution Level | N/A | No | No | No
40870163 | Wood | Eureka | 013/009 | 2021-12-09 | 2021-08-06 | 2021-06-23 | Conductor damage (e.g gunshot, broken strands, arcing, twisted bundle) or in poor condition | Blank | TRUE: There appears to be bird caging on the conductor. | Agree | Condition is not compelling | TD-1001M-JA10 Conductor Conditions | N/A | N/A | No | No | No
40906272 | Wood | Eureka | 002/010 | 2021-12-09 | 2021-07-27 | 2021-06-02 | Guy marker missing (GO 95 infraction) | Blank | TRUE: A guy marker appears to be missing. | Disagree | Condition is not compelling | N/A | Sherlock Photo N_000132.jpg shows guy marker missing is a Distribution level guy not indentified in transmission Inspections | N/A | No | No | No
40909000 | Wood | Sacramento | 006/115 | 2021-12-09 | 2021-08-10 | 2021-06-09 | Polymer | Blank | TRUE: The structure appears to have polymer insulators. | Agree | Condition is not compelling | N/A | N/A | N/A | No | No | No
40912483 | Wood | Lakeville | 007/001 | 2021-12-09 | 2021-08-02 | 2021-06-09 | Does this structure have a guy? | NO | Yes: There structure appears to have a guy. | Agree | Condition is not compelling | N/A | Sherlock E 00924 shows Guys | N/A | No | No | No
40912483 | Wood | Lakeville | 007/001 | 2021-12-09 | 2021-08-02 | 2021-06-09 | Structure has breaks / cracks / splits | Blank | TRUE: The structure appears to have cracks. | Agree | Condition is not compelling | TD-1001M-JA06 Wood Poles - Non Steel Framing | N/A | N/A | No | No | No
40912483 | Wood | Lakeville | 007/001 | 2021-12-09 | 2021-08-02 | 2021-06-09 | Rural area and structure within 600 ft of a frequently traveled road/trail | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road/trail. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40912483 | Wood | Lakeville | 007/001 | 2021-12-09 | 2021-08-02 | 2021-06-09 | Guy marker missing (GO 95 infraction) | Blank | TRUE: A guy marker appears to be missing. | Agree | Condition is not compelling | N/A | Sherlock Photo E_000917.jpg showsThis is a secondary Guy, Not recognized in Transmission inspections, | N/A | No | No | No
42574171 | Wood | Pismo Beach | 021/295B | 2021-12-09 | 2021-07-26 | 2021-06-24 | Structure has Bird, animal or insect damage (e.g., woodpecker) | Blank | TRUE: The structure appears to have animal damage. | Agree | N/A | TD-1001M-JA06 Wood Poles - Non Steel Framing | Existing LC 121549011 in Place to Replace Structure Created 6/29/21 | N/A | No | No | No | Existing LC
42574171 | Wood | Pismo Beach | 021/295B | 2021-12-09 | 2021-07-26 | 2021-06-24 | Structure has breaks / cracks / splits | Blank | TRUE: The structure appears to have cracks and holes throughout the pole. | Agree | N/A | TD-1001M-JA06 Wood Poles - Non Steel Framing | Existing LC 121549011 in Place to Replace Structure Created 6/29/21 | N/A | No | No | No | Existing LC
42624181 | Wood | Table Mountain | 001/033B | 2021-12-09 | 2021-07-27 | 2021-06-27 | Polymer | Blank | TRUE: The structure appears to have polymer insulators. | Agree | Condition is not compelling | N/A | N/A | N/A | No | No | No
43249454 | Steel | Victor | 022/131A | 2021-12-09 | 2021-08-06 | 2021-03-31 | Mastic sealant in poor condition | Blank | TRUE: The mastic sealant appears to be deteriorating. | Disagree | Condition does not exist | TD-1001M-JA12 Foundation Condition TLine Structures & Supports | Direct Buried, Stubs do not Require Mastic | N/A | No | No | No
43249454 | Steel | Victor | 022/131A | 2021-12-09 | 2021-08-06 | 2021-03-31 | Rural area and structure within 600 ft of a frequently traveled road/trail | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road/trai | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
43249454 | Steel | Victor | 022/131A | 2021-12-09 | 2021-08-06 | 2021-03-31 | Bird Nest Present? | NO | Yes: There appears to be a bird nest. | Agree | Condition is not compelling | N/A | N/A | N/A | No | No
44254473 | Steel | Sacramento | 000/009A | 2021-12-09 | 2021-07-27 | 2021-06-12 | Rural area and structure within 600 ft of a frequently traveled road/trail | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road/trail. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
44815074 | Steel | Lakeville | 008/005 | 2021-12-09 | 2021-07-27 | 2021-06-07 | Rural area and structure within 600 ft of a frequently traveled road/trail | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road/trail | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
44865988 | Steel | Lakeville | 001/002 | 2021-12-09 | 2021-08-10 | 2021-05-12 | Polymer | Blank | TRUE: The structure appears to have polymer insulators. | Agree | Condition is not compelling | N/A | N/A | N/A | No | No | No
44976266 | Steel | Moss Landing | 012/098 | 2021-12-09 | 2021-08-03 | 2021-04-22 | Does this structure have a guy? | NO | Yes: There structure appears to have two guys. | Disagree | Condition does not exist | N/A | Sherlock Photo J_000458.jpg shows Guys are at distribution Level | N/A | No | No | No
44976266 | Steel | Moss Landing | 012/098 | 2021-12-09 | 2021-08-03 | 2021-04-22 | Automatic guy splice present? | Blank | No: There does not appear to be a guy splice present. | Disagree | Condition does not exist | N/A | Nothing in Inspection Record about Guy splices | N/A | No | No | No
44976266 | Steel | Moss Landing | 012/098 | 2021-12-09 | 2021-08-03 | 2021-04-22 | Is there OPGW or Shield Wire Present? | Blank | No: The structure does not appear to have OPGW or shield wire present. | Agree | Condition is not compelling | TD-1001M-JA11 OPGW | N/A | N/A | No | No | No
44976266 | Steel | Moss Landing | 012/098 | 2021-12-09 | 2021-08-03 | 2021-04-22 | High voltage signs missing, damaged, or installed incorrectly (see E.D. 022168 further details see GO 95) | Blank | TRUE: A high voltage sign appears to be missing. | Disagree | Condition does not exist | 022168 HV Signs, Marking, Numbering | Sherlock Photo J_000458.jpg shows HV Signs are Below distribution Level | N/A | No | No | No
40577350 | Wood | Table Mountain | 000/020 | 2021-12-09 | 2021-09-02 | 2021-05-20 | Does this structure have a guy? | NO | Yes: The structure appears to have a guy. | Agree | Condition is not compelling | N/A | N/A | N/A | No | No | No
40577350 | Wood | Table Mountain | 000/020 | 2021-12-09 | 2021-09-02 | 2021-05-20 | Rural area and within 600 feet of a dwelling or camp | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling or camp. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40577350 | Wood | Table Mountain | 000/020 | 2021-12-09 | 2021-09-02 | 2021-05-20 | Rural area and structure within 600 ft of a frequently traveled road/trail | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road/trail | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40577350 | Wood | Table Mountain | 000/020 | 2021-12-09 | 2021-09-02 | 2021-05-20 | High voltage signs missing, damaged, or installed incorrectly (see E.D. 022168 further details see GO 95) | Blank | TRUE: The high voltage signs appear to be damaged. | Disagree | Condition does not exist | 022168 HV Signs, Marking, Numbering | Sherlock Photo 210422_192900_448_4a6a4bo03.jpg shows HV Signs under distribution arm on Pole | N/A | No | No | No
40587310 | Steel | Table Mountain | 055/271 | 2021-12-09 | 2021-08-31 | 2021-06-15 | Rural area and structure within 600 ft of a frequently traveled road/trail | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road/trail. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40594795 | Steel | Pismo Beach | 006/031 | 2021-12-09 | 2021-08-31 | 2021-06-22 | Rural area and structure within 600 ft of a frequently traveled road/trail | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road/trail. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40616031 | Wood | Table Mountain | 014/344 | 2021-12-09 | 2021-09-07 | 2021-06-10 | Splices present? | NO | Yes: Splices appear to be present. | Agree | Condition is not compelling | TD-1001M-JA14 Splices Job Aid | N/A | N/A | No | No | No
40654200 | Steel | Sacramento | 026/193 | 2021-12-08 | 2021-09-07 | 2021-04-28 | Secondary members are damaged or in poor condition | Blank | TRUE: A secondary member located at the top of the structure above the glass insulators appears to be damaged. | Agree | N/A | TD-1001M-JA04 Steel Structures Corrosion and Deteriation | Existing LC 115787331, Notes that on 5/1/21 work was completed. Condition still exists | Update a LC | Yes | Yes | No | Escalated for LC on 12--21 | Air agreed to update LC Created on 12/8/21
40692809 | Wood | Sacramento | 013/262 | 2021-12-08 | 2021-09-07 | 2021-05-10 | Splices present? | NO | Yes: Splices appear to be present. | Agree | Condition is not compelling | TD-1001M-JA14 Splices Job Aid | N/A | N/A | No | No | No
40744757 | Steel | Pismo Beach | 044/254 | 2021-12-08 | 2021-09-02 | 2021-04-08 | Dampers in poor condition, out of position or missing (Fatigued, i.e. drooping or missing weight) | Blank | TRUE: Two out of three phases appear to have dampers missing. | Disagree | Condition does not exist | 022178 Construction Requirements for Pole Line Guys | Damper on 1 Phase to mitigate Sleeve, No Evidence of Dampers being on additional 2 Phases | N/A | No | No | No | Escalated for LC on 12--21 | NO ISSUES FOUND
40744757 | Steel | Pismo Beach | 044/254 | 2021-12-08 | 2021-09-02 | 2021-04-08 | Bird Guard Present? | NO | Yes: Bird guards appear to be present. | Agree | Condition is not compelling | N/A | L_002475.JPG clearly shows Bird Guard | N/A | No | No | No
40758793 | Wood | Table Mountain | 008/185 | 2021-12-08 | 2021-08-31 | 2021-06-08 | Rural area and structure within 600 ft of a frequently traveled road/trail | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road/trail | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40759857 | Steel | Table Mountain | 057/284 | 2021-12-08 | 2021-09-07 | 2021-06-02 | Glass | Blank | TRUE: There structure appears to have glass insulators. | Agree | Condition is not compelling | N/A | N/A | N/A | No | No | No
40762738 | Steel | Moss Landing | 016/075 | 2021-12-08 | 2021-08-31 | 2021-06-22 | Rural area and structure within 600 ft of a frequently traveled road/trail | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road/trai | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40766444 | Wood | Sacramento | 013/265 | 2021-12-08 | 2021-08-31 | 2021-05-10 | Rural area and within 600 feet of a dwelling or camp | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling or camp. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40803759 | Wood | Victor | 009/111 | 2021-12-08 | 2021-09-02 | 2021-05-07 | Rural area and structure within 600 ft of a frequently traveled road/trail | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road/trail. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40808835 | Wood | Lakeville | 031/007 | 2021-12-08 | 2021-08-31 | 2021-07-01 | Rural area and structure within 600 ft of a frequently traveled road/trail | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road/trail. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40808835 | Wood | Lakeville | 031/007 | 2021-12-08 | 2021-08-31 | 2021-07-01 | Guy marker missing (GO 95 infraction) | Blank | The guy marker appears to be damaged. | Disagree | Condition does not exist | TD-1001M-JA13 Guys and Anchors | _01fd45a7.jpg shows Guy is Not for T Line, Distribution gu marker is not an A Tag Not Identified in Transmission inspection | N/A | No | No | No
40824455 | Wood | Lakeville | 001/007 | 2021-12-08 | 2021-09-07 | 2021-07-30 | Structure has Bird, animal or insect damage (e.g., woodpecker) | Blank | TRUE: The structure appears to have woodpecker damage. | Agree | N/A | N/A | LC 121824217 was created on 7/31/21 for this FDA | N/A | No | No | No
40824455 | Wood | Lakeville | 001/007 | 2021-12-08 | 2021-09-07 | 2021-07-30 | Structure has breaks / cracks / splits | Blank | TRUE: The structure appears to have cracks. | Agree | N/A | TD-1001M-JA06 Wood Poles - Non Steel Framing | Existing LC 121824217 was Created on 7/31/21 to replace pole | N/A | Yes | No | No
40824455 | Wood | Lakeville | 001/007 | 2021-12-08 | 2021-09-07 | 2021-07-30 | ural area and structure within 600 ft of a frequently traveled road/trail | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road/trail. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40858016 | Steel | Concord | 007/033 | 2021-12-08 | 2021-09-07 | 2021-07-15 | Dampers present? | NO | es: Dampers appear to be present. | Agree | Condition is not compelling | N/A | N/A | N/A | No | No | No
40868975 | Wood | Sacramento | 024/661 | 2021-12-08 | 2021-09-02 | 2021-05-27 | Rural area and structure within 600 ft of a frequently traveled road/trail | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road/trail. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40868975 | Wood | Sacramento | 024/661 | 2021-12-08 | 2021-09-02 | 2021-05-27 | High voltage signs missing, damaged, or installed incorrectly (see E.D. 022168 further details see GO 95) | Blank | TRUE: The high voltage sign appears to be damaged. | Disagree | Condition does not exist | 022168 HV Signs, Marking, Numbering | a_16b89f6.jpg shows HV Signs on pole Below Distribution arm | N/A | No | No | No
40873585 | Wood | Sacramento | 011/217 | 2021-12-08 | 2021-09-07 | 2021-05-10 | Rural area and within 600 feet of a dwelling or camp | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling or camp. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40874204 | Wood | Sacramento | 016/438 | 2021-12-08 | 2021-09-02 | 2021-05-07 | Rural area and structure within 600 ft of a frequently traveled road/trail | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road/trail. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40913093 | Steel | Sacramento | 003/033A | 2021-12-08 | 2021-09-02 | 2021-05-15 | Rural area and structure within 600 ft of a frequently traveled road/trail | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road/trail. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40913132 | Wood | Sacramento | 008/128 | 2021-12-08 | 2021-09-01 | 2021-05-20 | Rural area and structure within 600 ft of a frequently traveled road/trail | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road/trail. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
42572844 | Wood | Sacramento | 023/283C | 2021-12-08 | 2021-09-07 | 2021-06-12 | Splices present? | NO | es: Splices appear to be present. | Agree | Condition is not compelling | TD-1001M-JA14 Splices Job Aid | N/A | N/A | No | No | No
42572844 | Wood | Sacramento | 023/283C | 2021-12-08 | 2021-09-07 | 2021-06-12 | Polymer | Blank | TRUE: The structure appears to have polymer insulators. | Agree | Condition is not compelling | N/A | N/A | N/A | No | No | No
42572847 | Wood | Sacramento | 024/296B | 2021-12-08 | 2021-09-01 | 2021-06-12 | Rural area and structure within 600 ft of a frequently traveled road/trail | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road/trai | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
44328884 | Steel | Pismo Beach | 000/004 | 2021-12-08 | 2021-09-01 | 2021-05-03 | Jumpers present? | NO | Yes: Jumpers appear to be present. | Agree | Condition is not compelling | N/A | N/A | N/A | No | No | No
44359637 | Steel | Victor | 006/071 | 2021-12-08 | 2021-09-02 | 2021-05-07 | High voltage signs missing, damaged, or installed incorrectly (see E.D. 022168 further details see GO 95) | Blank | TRUE: The high voltage signs appear to be missing. | Agree | N/A | N/A | LC 121381184 was created on 5/22/21 for this FDA | N/A | No | No | No
44761241 | Steel | Table Mountain | 001/036 | 2021-12-08 | 2021-09-01 | 2021-05-22 | Polymer | Blank | TRUE: The structure appears to have polymer insulators. | Agree | N/A | N/A | Escalated for LC on 12--21 LC Created on 12/8/21 | Create a LC | Yes | Yes | No | Escalated for LC on 12--21 | Air Agreed to create LC creation Date 12/8/21
44761241 | Steel | Table Mountain | 001/036 | 2021-12-08 | 2021-09-01 | 2021-05-22 | Rural area and structure within 600 ft of a frequently traveled road/trail | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road/trail. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
44761241 | Steel | Table Mountain | 001/036 | 2021-12-08 | 2021-09-01 | 2021-05-22 | Climbing steps installed incorrectly | Blank | TRUE: One climbing step appears to be in contact with a polymer insulator. | Agree | N/A | TD-1001M-JA04 Steel Structures Corrosion and Deteriation | Escalated for LC on 12--21 LC Created on 12/8/21 | Create a LC | Yes | Yes | No | Escalated for LC on 12--21 | Air Agreed to create LC creation Date 12/8/21
44886655 | Steel | Sacramento | 016/442 | 2021-12-08 | 2021-09-07 | 2021-06-18 | Rural area and structure within 600 ft of a frequently traveled road/trail | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road/trail | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40585958 | Wood | Midway | 007/135 | 2021-12-08 | 2021-08-17 | 2021-07-05 | Bolts and nuts loose or missing | Blank | TRUE: The structure appears to have loose bolts. | Disagree | Condition does not exist | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | Escalated for LC on 12--21 Air Team Determined No Damage Present | N/A | No | No | No | Escalated for LC on 12--21 | Arial Team Determined No Damage Present
40586590 | Steel | Concord | 008/041 | 2021-12-08 | 2021-08-13 | 2021-06-28 | Steel Structure hardware loose or missing (e.g vibrating members) | Blank | RUE: The structure appears to be missing bolts. | Disagree | Condition does not exist | TD-1001M REV5 ET Preventative Maintenace Manual | Drawing Number 309646 | N/A | No | No | No
40586590 | Steel | Concord | 008/041 | 2021-12-08 | 2021-08-13 | 2021-06-28 | Insulators are damaged, contaminated, arcing/tracking or in poor condition | Blank | Blank | Disagree | Condition does not exist | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | Insulator not damaged, clearly visible in Sherlock image 131 of 298 (N_000074.JPG) that the “damage” is contamination sitting on top of the shed. Also, the missing bolt at the base of the tower is a single hole catch as per design. | N/A | No | No | No | Escalated for LC on 12--21 | Arial Team Determined No Damage Present
40586590 | Steel | Concord | 008/041 | 2021-12-08 | 2021-08-13 | 2021-06-28 | Grading / Corona rings present | Blank | TRUE: The structure appears to have corona rings. | Agree | Condition is not compelling | TD-1001M REV5 ET Preventative Maintenace Manual | N/A | N/A | No | No | No
40590407 | Wood | Fresno | 004/001 | 2021-12-08 | 2021-08-12 | 2021-04-22 | What kind of structure is this? | Wood | Steel: The structure appears to be a steel pole. | Agree | Condition is not compelling | TD-1001M REV5 ET Preventative Maintenace Manual | Inspect a pp Shows LDS P | N/A | No | No | No
40590407 | Wood | Fresno | 004/001 | 2021-12-08 | 2021-08-12 | 2021-04-22 | Is there OPGW or Shield Wire Present? | Blank | No: The structure does not appear to have OPGW or shield wire. | Agree | N/A | N/A | N/A | N/A | No | No | No
40598519 | Wood | Sacramento | 010/183 | 2021-12-08 | 2021-08-30 | 2021-05-14 | Do Asset Traits differ? | NO | es: The structure appears to be steel. | Agree | Condition is not compelling | TD-1001M REV5 ET Preventative Maintenace Manual | Inspect a pp Shows LDS P | N/A | No | No | No
40598519 | Wood | Sacramento | 010/183 | 2021-12-08 | 2021-08-30 | 2021-05-14 | What kind of structure is this? | Wood | Steel: The structure appears to be steel. | Agree | Condition is not compelling | TD-1001M REV5 ET Preventative Maintenace Manual | Inspect a pp Shows LDS P | N/A | No | No | No
40603359 | Wood | Sacramento | 011/204 | 2021-12-08 | 2021-08-30 | 2021-05-19 | Tower number missing | Blank | TRUE: The tower number appears to be missing. | Disagree | Condition does not exist | TD-1008P-03 Numbering & Marking OH Tline | Tower Number Missing: Structure ID and SAP is present in Sherlock image 1 of 38 (210420_172926_025_3ef04fcc.jpg) | N/A | No | No | No | Escalated for LC on 12--21 | Arial Team Found Str ID
40614549 | Wood | Lakeville | 000/010 | 2021-12-08 | 2021-08-17 | 2021-07-28 | Rural area and structure within 600 ft of a frequently traveled road/trail | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road/trail. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40616427 | Wood | Lakeville | 026/010 | 2021-12-08 | 2021-08-27 | 2021-06-01 | Rural area and within 600 feet of a dwelling or camp | Blank | to be in a rural area and within 600 feet of a dwelling or camp. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40616427 | Wood | Lakeville | 026/010 | 2021-12-08 | 2021-08-27 | 2021-06-01 | Tower number missing | Blank | TRUE: The tower number appears to be missing. | Disagree | Condition does not exist | 022168 HV Signs, Marking, Numbering | Tower Number Missing: Structure ID is present in Sherlock image 8 of 57 (210426_194016_237_fa2ba8c1.jpg) | N/A | No | No | No | Escalated for LC on 12--21 | Arial Team Found Str ID
40646731 | Steel | Lakeville | 044/212 | 2021-12-08 | 2021-08-31 | 2021-06-16 | Rural area and the structure in an orchard | Rural & In an Orchard | FALSE: The structure does not appear to be in an orchard. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40648786 | Steel | Concord | 000/003 | 2021-12-08 | 2021-08-13 | 2021-04-19 | Rural area and within 600 feet of a dwelling or camp | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling or camp. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40648786 | Steel | Concord | 000/003 | 2021-12-08 | 2021-08-13 | 2021-04-19 | Tower finish in poor condition | Blank | TRUE: The tower finish appears to be in poor condition. | Disagree | Condition is not compelling | TD-1001M REV5 ET Preventative Maintenace Manual | A_001271.jpg shows slight surface rust | N/A | No | No | No
40648786 | Steel | Concord | 000/003 | 2021-12-08 | 2021-08-13 | 2021-04-19 | Tower Finish Type | Galvanized | Painted: The structure appears to be painted. | Disagree | Condition is not compelling | TD-1001M REV5 ET Preventative Maintenace Manual | A_001266.jpg shows galvanized finish | N/A | No | No | No
40658320 | Wood | Sacramento | 023/632 | 2021-12-08 | 2021-08-16 | 2021-05-27 | Rural area and structure within 600 ft of a frequently traveled road/trail | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road/trail. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40660222 | Steel | Table Mountain | 024/163 | 2021-12-07 | 2021-08-30 | 2021-04-15 | Steel Structure hardware loose or missing (e.g vibrating members) | Blank | TRUE: The structure appears to be missing bolts. | Disagree | Condition does not exist | TD-1001M REV5 ET Preventative Maintenace Manual | LC 120690663 was Cancelled 3/30/21 Bolts not needed as per CIRT CCLL | N/A | No | No | No | Drawing Number 402706
40660222 | Steel | Table Mountain | 024/163 | 2021-12-07 | 2021-08-30 | 2021-04-15 | Tower finish in poor condition | Blank | TRUE: The tower finish appears to be in poor condition. | Disagree | Condition does not exist | TD-1001M REV5 ET Preventative Maintenace Manual | Escalated To air 12-15-19, Air Replied No Notification Needed | N/A | No | No | No |  | Escalated To air 12-15-19, Air Replied No Notification Needed
40660222 | Steel | Table Mountain | 024/163 | 2021-12-07 | 2021-08-30 | 2021-04-15 | Rural area and structure within 600 ft of a frequently traveled road/trail | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road/trail. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40663209 | Wood | Victor | 008/003 | 2021-12-07 | 2021-08-27 | 2021-07-28 | Rural area and structure within 600 ft of a frequently traveled road/trail | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road/trail. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40664750 | Wood | Sacramento | 007/181 | 2021-12-07 | 2021-08-27 | 2021-07-30 | Rural area and structure within 600 ft of a frequently traveled road/trail | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road/trail. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40664750 | Wood | Sacramento | 007/181 | 2021-12-07 | 2021-08-27 | 2021-07-30 | High voltage signs missing, damaged, or installed incorrectly (see E.D. 022168 further details see GO 95) | Blank | TRUE: One high voltage sign appears to be damaged and the other sign appears to be missing. | Agree | Condition is not compelling | 022168 HV Signs, Marking, Numbering | HV Signs are visible below Distribution Cross arm | N/A | No | No | No
40674738 | Wood | Metcalf | 007/002 | 2021-12-07 | 2021-08-12 | 2021-05-27 | Rural area and structure within 600 ft of a frequently traveled road/trail | Cold end hardware type: c-hoo | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road/trail. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40684094 | Steel | Table Mountain | 079/402 | 2021-12-07 | 2021-08-17 | 2021-07-24 | Grading/Corona rings in poor condition | Blank | TRUE: The bolts securing the grading rings appear to be loose on both sides. | Agree | N/A | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | No Existing LC found | Create a LC | Yes | Yes | Yes | Escalated for LC on 12--21 | Air Agreed to create LC, Creation Date 12/7/21
40689356 | Steel | Victor | 000/003 | 2021-12-07 | 2021-08-30 | 2021-04-19 | Steel Structure hardware loose or missing (e.g vibrating members) | Blank | TRUE: The structure appears to be missing bolts. | Disagree | Condition does not exist | TD-1001M-JA04 Steel Structures Corrosion and Deteriation | N/A | N/A | No | No | No
40689356 | Steel | Victor | 000/003 | 2021-12-07 | 2021-08-30 | 2021-04-19 | Insulators are damaged, contaminated, arcing/tracking or in poor condition | Blank | TRUE: The insulators appear to be in poor condition. | Disagree | Condition is not compelling | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | There is no signs of Rust or tracking on insulators | N/A | No | No | No
40701745 | Wood | Table Mountain | 008/192 | 2021-12-07 | 2021-08-30 | 2021-05-20 | Rural area and structure within 600 ft of a frequently traveled road/trail | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road/trail. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40767171 | Steel | Sacramento | 012/213 | 2021-12-07 | 2021-08-17 | 2021-07-28 | Cold end hardware type: C-hook | Cold end hardware type: c-hoo | FALSE: The structure does not appear to have c-hooks. | Agree | Condition is not compelling | N/A | N/A | N/A | No | No | No
40767171 | Steel | Sacramento | 012/213 | 2021-12-07 | 2021-08-17 | 2021-07-28 | High voltage signs missing, damaged, or installed incorrectly (see E.D. 022168 further details see GO 95) | Blank | TRUE: The structure appears to be missing a high voltage sign. | Disagree | Condition does not exist | 022168 HV Signs, Marking, Numbering | Sherlock Photo B_1787748336BB Shows HV Signs below Distributin Crossarm on Pole | N/A | No | No | No
40815725 | Steel | Table Mountain | 028/186 | 2021-12-07 | 2021-08-17 | 2021-07-05 | Steel Structure hardware loose or missing (e.g vibrating members) | Blank | TRUE: The structure appears to have missing bolts on a secondary member. | Disagree | Condition does not exist | TD-1001M-JA04 Steel Structures Corrosion and Deteriation | Drawing Number 402706 FA Tower | N/A | No | No | No
40815725 | Steel | Table Mountain | 028/186 | 2021-12-07 | 2021-08-17 | 2021-07-05 | Mastic sealant in poor condition | Blank | TRUE: The mastic sealant appears to be in poor condition. | Agree | N/A | TD-1001M-JA12 Foundation Condition TLine Structures & Supports | No Existing LC found | Create a LC | Yes | Yes | Yes | Escalated for LC on 12--21 | Air Agreed to create LC, Creation Date 12/7/21
40815725 | Steel | Table Mountain | 028/186 | 2021-12-07 | 2021-08-17 | 2021-07-05 | Rural area and structure within 600 ft of a frequently traveled road/trail | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road/trail. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40818223 | Steel | Lakeville | 034/149 | 2021-12-07 | 2021-08-27 | 2021-07-09 | Vegetation present? | NO | Yes: Vegetation appears to be present at the base of the structure. | Agree | Condition is not compelling | TD-1001M REV5 ET Preventative Maintenace Manual | N/A | N/A | No | No | No
40818829 | Steel | Lakeville | 021/097 | 2021-12-07 | 2021-08-13 | 2021-06-05 | Structure Location Type | NONE | Agriculture: The structure appears to be located in an agricultural area. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40824348 | Wood | Sacramento | 005/128 | 2021-12-07 | 2021-08-12 | 2021-05-13 | Does this structure have a guy? | NO | Yes: The structure appears to have a guy. | Disagree | Condition does not exist | TD-1001M-JA13 Guys and Anchors | Guy is at Distribution Level | N/A | No | No | No
40826169 | Wood | Lakeville | 030/006 | 2021-12-07 | 2021-08-31 | 2021-07-05 | Structure is Burnt | Blank | TRUE: The structure appears to be burnt. | Agree | N/A | TD-1001M-JA06 Wood Poles - Non Steel Framing | N/A | Create a LC | Yes | N/A | Yes | Escalated to distro supervisor A. Clouse 12/7/21
40826169 | Wood | Lakeville | 030/006 | 2021-12-07 | 2021-08-31 | 2021-07-05 | Insulators are damaged, contaminated, arcing/tracking or in poor condition | Blank | TRUE: The insulators appear to be contaminated. | Disagree | Condition does not exist | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | Sherlock Photo OC3F5D2922D2_orig.jpeg shows slight bird dropping | N/A | No | No | No
40861006 | Wood | Eureka | 016/008 | 2021-12-07 | 2021-08-12 | 2021-06-29 | Rural area and within 600 feet of a dwelling or camp | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling or camp. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40861006 | Wood | Eureka | 016/008 | 2021-12-07 | 2021-08-12 | 2021-06-29 | Vegetation present? | NO | Yes: Vegetation appears to be present. | Agree | Condition is not compelling | TD-1001M REV5 ET Preventative Maintenace Manual | N/A | N/A | No | No | No
40861006 | Wood | Eureka | 016/008 | 2021-12-07 | 2021-08-12 | 2021-06-29 | Anchor / Guying covered by vegetation | Blank | TRUE: The anchor appears to be covered by vegetation. | Agree | N/A | TD-1001M-JA20 Vegetation Non-conformance Job Aid | N/A | N/A | No | No | No
40861006 | Wood | Eureka | 016/008 | 2021-12-07 | 2021-08-12 | 2021-06-29 | Third-Party Non-Utility Infraction | Blank | TRUE: There appears to be barbed wire and signage attached to the pole. | Agree | Condition is not compelling | N/A | N/A | N/A | No | No | No
40869531 | Steel | Lakeville | 039/188 | 2021-12-07 | 2021-08-30 | 2021-05-06 | Rural area and structure within 600 ft of a frequently traveled road/trail | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road/trail. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40908960 | Wood | Martin | 003/067 | 2021-12-07 | 2021-08-30 | 2021-06-09 | Rural area and structure within 600 ft of a frequently traveled road/trail | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road/trail. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
44223084 | Steel | Moss Landing | 011/078B | 2021-12-07 | 2021-08-17 | 2021-07-14 | Polymer | Blank | TRUE: The structure appears to have polymer insulators. | Agree | Condition is not compelling | TD-1001M REV5 ET Preventative Maintenace Manual | N/A | N/A | No | No | No
44223736 | Steel | Sacramento | 020/413 | 2021-12-07 | 2021-08-31 | 2021-05-10 | Structure Location Type | NONE | Agriculture: The structure appears to be located in an agricultural area. | Agree | Condition is not compelling | TD-1001M REV5 ET Preventative Maintenace Manual | N/A | N/A | No | No | No
44223736 | Steel | Sacramento | 020/413 | 2021-12-07 | 2021-08-31 | 2021-05-10 | Rural area and within 600 feet of a dwelling or camp | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling or camp. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
44223736 | Steel | Sacramento | 020/413 | 2021-12-07 | 2021-08-31 | 2021-05-10 | Rural area and the structure in an orchard | Blank | TRUE: The structure appears to be located in a rural area and in an orchard. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
44223736 | Steel | Sacramento | 020/413 | 2021-12-07 | 2021-08-31 | 2021-05-10 | Rural area and structure within 600 ft of a frequently traveled road/trail | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road/trail. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
44926579 | Steel | Sacramento | 011/167 | 2021-12-07 | 2021-08-27 | 2021-05-06 | Foundation Type | Direct Buried | Unable to Identify: The photos are insufficient to identify the foundation type or condition. | Agree | Condition is not compelling | TD-1001M REV5 ET Preventative Maintenace Manual | N/A | N/A | No | No | No
44926579 | Steel | Sacramento | 011/167 | 2021-12-07 | 2021-08-27 | 2021-05-06 | Vegetation present? | NO | Yes: The photos are insufficient to determine whether vegetation is present. | Agree | Condition is not compelling | TD-1001M REV5 ET Preventative Maintenace Manual | Photos clearly show vegetation is Present with no Compelling issues | N/A | No | No | No
44929949 | Steel | Sacramento | 006/177 | 2021-12-07 | 2021-08-12 | 2021-05-11 | High voltage signs missing, damaged, or installed incorrectly (see E.D. 022168 further details see GO 95) | Blank | TRUE: The high voltage sign appears to be damaged. | Disagree | Condition does not exist | 022168 HV Signs, Marking, Numbering | _c6938126.jpg shows HV Signs Below Distribution arm on Pole | N/A | No | No | No
44989197 | Steel | Lakeville | 003/004 | 2021-12-07 | 2021-08-16 | 2021-06-04 | Polymer | Blank | TRUE: The structure appears to have polymer insulators. | Agree | Condition is not compelling | TD-1001M REV5 ET Preventative Maintenace Manual | N/A | N/A | No | No | No
44989197 | Steel | Lakeville | 003/004 | 2021-12-07 | 2021-08-16 | 2021-06-04 | Cold end hardware type: C-hook | Blank | RUE: The structure appears to have c-hooks. | Agree | Condition is not compelling | TD-1001M REV5 ET Preventative Maintenace Manual | N/A | N/A | No | No | No
44989197 | Steel | Lakeville | 003/004 | 2021-12-07 | 2021-08-16 | 2021-06-04 | High voltage signs missing, damaged, or installed incorrectly (see E.D. 022168 further details see GO 95) | Blank | TRUE: The high voltage signs appear to be missing. | Disagree | Condition does not exist | 022168 HV Signs, Marking, Numbering | E_000134.jpg Shows HV Signs under Distribution on Pole | N/A | No | No | No
45023559 | Steel | Eureka | 059/003B | 2021-12-07 | 2021-08-16 | 2021-07-15 | Guy broken / damaged, corroded or in poor condition | Blank | TRUE: The cotter key appears to be missing from the guy hardware at the pin hole. | Disagree | Condition does not exist | TD-1001M REV5 ET Preventative Maintenace Manual | M-00449jpg, shows cotter key in Place | N/A | No | No | No
45023559 | Steel | Eureka | 059/003B | 2021-12-07 | 2021-08-16 | 2021-07-15 | Polymer | Blank | Blank | Agree | Condition is not compelling | TD-1001M REV5 ET Preventative Maintenace Manual | N/A | N/A | No | No | No
45070080 | Steel | Eureka | 112/002C | 2021-12-07 | 2021-08-16 | 2021-07-12 | Conductor damage (e.g gunshot, broken strands, arcing, twisted bundle) or in poor condition | Blank | TRUE: There appear to be several conductor locations that show damage from bird caging. | Disagree | Condition is not compelling | TD-1001M-JA10 Conductor Conditions | No Broken Strands, Slight Bircaging Present | N/A | No | No | No
45070080 | Steel | Eureka | 112/002C | 2021-12-07 | 2021-08-16 | 2021-07-12 | Rural area and within 600 feet of a dwelling or cam | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling or camp. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
45070080 | Steel | Eureka | 112/002C | 2021-12-07 | 2021-08-16 | 2021-07-12 | Rural area and structure within 600 ft of a frequently traveled road/trail | Blank | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road/trail. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
45070080 | Steel | Eureka | 112/002C | 2021-12-07 | 2021-08-16 | 2021-07-12 | Anchor / Guying covered by vegetation | Blank | TRUE: The anchor/guy appears to be covered by vegetation. | Agree | N/A | N/A | N/A | N/A | No | No | No
45105736 | Wood | Eureka | 064/005A | 2021-12-07 | 2021-08-17 | 2021-07-15 | What kind of structure is this? | Wood | Steel: The structure appears to be steel. | Agree | Condition is not compelling | TD-1001M REV5 ET Preventative Maintenace Manual | N/A | N/A | No | No | No
45105736 | Wood | Eureka | 064/005A | 2021-12-07 | 2021-08-17 | 2021-07-15 | Tower Finish Type | Answer Blank | Weathered: The structure appears to have a weathered finish. | Agree | Condition is not compelling | TD-1001M REV5 ET Preventative Maintenace Manual | N/A | N/A | No | No | No
45105736 | Wood | Eureka | 064/005A | 2021-12-07 | 2021-08-17 | 2021-07-15 | Foundation Type | Answer Blank | Direct buried: The structure appears to be direct buried. | Agree | Condition is not compelling | TD-1001M REV5 ET Preventative Maintenace Manual | N/A | N/A | No | No | No
40604969 | Steel | Victor | 006/049 | 2022-01-18 | 2020-11-18 | 2020-04-15 | Tower finis h type: | Weathered | Galvanized: The tower finish appears to be galvanized. | Agree | Condition is not compelling | TD-1001M REV5 ET Preventative Maintenace Manual | N/A | N/A | No | No | No | Report Indicates 3 conditions, 1 In Report
40676665 | Steel | Table Mountain | 050/380 | 2022-01-18 | 2020-11-18 | 2020-08-05 | Foundation Type: | Direct Embedded (Tower) | C oncrete: The foundatio n appears to be concrete. | Agree | Condition is not compelling | TD-1001M REV5 ET Preventative Maintenace Manual | N/A | N/A | No | No | No
40676665 | Steel | Table Mountain | 050/380 | 2022-01-18 | 2020-11-18 | 2020-08-05 | Tower finis h type: | I don't know | Galvanized: The tower finish appears to be galvanized. | Agree | Condition is not compelling | TD-1001M REV5 ET Preventative Maintenace Manual | N/A | N/A | No | No | No
40676665 | Steel | Table Mountain | 050/380 | 2022-01-18 | 2020-11-18 | 2020-08-05 | Structure Issues: Steel Structure Hardware Loose or mis s in g | F a ls e | TRUE: There appear to be three bolts missing on secondary members of the lower and middle sections of the tower. | Disagree | Condition does not exist | TD-1001M-JA04 Steel Structures Corrosion and Deteriation | Type FA Tower, Drawing # 402706, Holes are pulling eyes. No Missing Bolts | N/A | No | No | No
40676665 | Steel | Table Mountain | 050/380 | 2022-01-18 | 2020-11-18 | 2020-08-05 | Type of Splice: Compression | FALSE | TRUE: There appear to be splices on all three phase | Agree | Condition is not compelling | TD-1001M-JA14 Splices Job Aid | N/A | N/A | No | No | No
40676665 | Steel | Table Mountain | 050/380 | 2022-01-18 | 2020-11-18 | 2020-08-05 | Are dampers present? | FALSE | TRUE: There appear to be dampers present on the lines. | Agree | Condition is not compelling | TD-1001M REV5 ET Preventative Maintenace Manual | N/A | N/A | No | No | No
40676665 | Steel | Table Mountain | 050/380 | 2022-01-18 | 2020-11-18 | 2020-08-05 | Is the sheild wire or fiber grounded? | [Answer left blank] | TRUE: The fiber appears to be grounded to the tower. | Agree | Condition is not compelling | TD-1001M REV5 ET Preventative Maintenace Manual | N/A | N/A | No | No | No
40676665 | Steel | Table Mountain | 050/380 | 2022-01-18 | 2020-11-18 | 2020-08-05 | Is the structure in a rural area and in an orchard? | TRUE | False: The structure does not appear to be in an Orchard | Agree | Condition is not compelling | TD-1001M REV5 ET Preventative Maintenace Manual | N/A | N/A | No | No | No
40805323 | Steel | Sacramento | 000/007 | 2022-01-18 | 2020-11-18 | 2020-05-19 | Conductor Issues: Armor rod damaged, in poor condition, o r mis s in g | F a ls e | TRUE: The a rmo r ro d in the middle phase appears to be missing. An outside armor rod appears to be incorrectly positioned in the connector. | Agree | Condition does not exist | TD-1001M-JA10 Conductor Conditions | LC 119478089 was created for No armor rod on Center Phase, Cancelled By CIRT as Per Cirt No armor Rod Required on Copper Conductor | N/A | No | No | No
40877587 | Wood | Table Mountain | 021/411 | 2022-01-18 | 2020-11-18 | 2020-07-15 | Guy Issues: Guy marker mis s in g (GO 95 infract io n) | F a ls e | TRUE: Guy markers appear to be missing on both guys. | Agree | N/A | TD-1001M REV5 ET Preventative Maintenace Manual | LC 119341484 shows all work completed on 6/2/21 | N/A | No | No | No | S 5 # 122774268 Created 1/19/22 @ 10:41, Before finding Existing LC showing all work Complete
40877587 | Wood | Table Mountain | 021/411 | 2022-01-18 | 2020-11-18 | 2020-07-15 | Guy Issues: Load-bearing Guys loose | F a ls e | TRUE: The guy wire insula t ing rod hardware appears to be loose at the top of the pole. | Agree | Condition is not compelling | TD-1001M REV5 ET Preventative Maintenace Manual | LC 119341484 shows all work completed on 6/2/21 | N/A | No | No | No
40654450 | Steel | Concord | 005/031 | 2022-01-18 | 2020-11-19 | 2020-04-02 | Foundation Issues: Earth covered or buried | F a ls e | TRUE: O ne foundatio n appears to be covered with earth. | Agree | N/A | TD-1001M-JA12 Foundation Condition TLine Structures & Supports | LC 116623526 for this FDA shows all All work completed on 6/24/21 | N/A | No | No | No
40654450 | Steel | Concord | 005/031 | 2022-01-18 | 2020-11-19 | 2020-04-02 | Structure Issues: Insulator hanger (eye) plate in poor condition | F a ls e | The photos are not suffic ie nt to determine the condition of the hanger plate. | Agree | N/A | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | LC 121642183 was created on 6/30/21 for this FDA | N/A | Yes | Yes | No
40654450 | Steel | Concord | 005/031 | 2022-01-18 | 2020-11-19 | 2020-04-02 | Insulator Issues: Insulators' hardware cold-end in poor condition (e.g. C-hook) | F a ls e | The photos are not suffic ie nt to determine the condition of the cold-end hardware. | Agree | N/A | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | LC 121642183 was created on 6/30/21 for this FDA | N/A | Yes | Yes | No
40654450 | Steel | Concord | 005/031 | 2022-01-18 | 2020-11-19 | 2020-04-02 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | F a ls e | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40751682 | Steel | Table Mountain | 041/305 | 2022-01-18 | 2020-11-19 | 2020-08-20 | Insulator Issues: Insulator s' hardware cold-end in poor condition (e.g. C-hook) | F a ls e | The photos are not suffic ie nt to determine the condition of the cold-end hardware. | Disagree | Condition does not exist | TD-1001M REV5 ET Preventative Maintenace Manual | Pronto photos clearly show all cold end attachments and Hanbger plates in good condition | N/A | No | No | No
40751682 | Steel | Table Mountain | 041/305 | 2022-01-18 | 2020-11-19 | 2020-08-20 | Structure Issues: Insulator hanger (eye) plate in poor condition | F a ls e | The photos are not suffic ie nt to determine the condition of the hanger plate. | Disagree | Condition does not exist | TD-1001M REV5 ET Preventative Maintenace Manual | Pronto photos clearly show all cold end attachments and Hanbger plates in good condition | N/A | No | No | No
40751819 | Wood | Sacramento | 012/224 | 2022-01-18 | 2020-11-19 | 2020-06-01 | Vehicular and Mechanical Issues: Breaks or cracks or s p lit in p o le | F a ls e | TRUE: There appears to be vertical cracking on the entire pole surface from the top to the bottom. | Disagree | Condition is not compelling | TD-1001M REV5 ET Preventative Maintenace Manual | LC 121381118 shows that Pole was reframed on 6/8/21 Pole shows no damage | N/A | No | No | No
40751819 | Wood | Sacramento | 012/224 | 2022-01-18 | 2020-11-19 | 2020-06-01 | Vehicular and Mechanical Issues: Pole-top damage or s p lit-top | F a ls e | TRUE: The pole appears to have a split top to the center of the pole. | Disagree | Condition is not compelling | TD-1001M REV5 ET Preventative Maintenace Manual | LC 121381118 shows that Pole was reframed on 6/8/21 Pole shows no damage | N/A | No | No | No | Fed Report indicates 3 infractions , 2 in Report
40596226 | Steel | Concord | 009/040 | 2022-01-18 | 2020-12-02 | 2020-04-20 | Foundation Issues: Mastic sealant in poor condition | FALSE | TRUE: The mastic sealant appears to be deteriorating and exposing the concrete and metal at each base. | Agree | N/A | TD-1001M-JA12 Foundation Condition TLine Structures & Supports | LC 118947779 shows work completed on 1/20/21 | N/A | No | No | No
40596226 | Steel | Concord | 009/040 | 2022-01-18 | 2020-12-02 | 2020-04-20 | Foundation Issues: Stub in concrete not sealed or water proofed | FALSE | TRUE: The mastic sealant appears to be deteriorating and exposing the concrete and metal at each base. | Agree | N/A | TD-1001M-JA12 Foundation Condition TLine Structures & Supports | LC 118947779 shows work completed on 1/20/21 | N/A | No | No | No
40596226 | Steel | Concord | 009/040 | 2022-01-18 | 2020-12-02 | 2020-04-20 | Foundation Issues: TSP Anchor bolts in poor conditions | TRUE | FALSE: This structure appears to be a lattice structure, not a tubular steel pole. | Agree | N/A | TD-1001M-JA04 Steel Structures Corrosion and Deteriation | N/A | N/A | No | No | No
40596226 | Steel | Concord | 009/040 | 2022-01-18 | 2020-12-02 | 2020-04-20 | Structure Issues: Insulator hanger (eye) plate in poor condition | F a ls e | The photos are not suffic ie nt to determine the condition of the hanger plate. | Disagree | Condition does not exist | TD-1001M REV5 ET Preventative Maintenace Manual | Sherlock photos show hanger plates in Good repair | N/A | No | No | No
40596226 | Steel | Concord | 009/040 | 2022-01-18 | 2020-12-02 | 2020-04-20 | Insulator Issues: Insulators' hardware cold-end in poor condition (e.g. C-hook) | F a ls e | The photos are not suffic ie nt to determine the condition of the cold-end hardware. | Disagree | Condition does not exist | TD-1001M REV5 ET Preventative Maintenace Manual | Sherlock Photos show C hooks in god repair | N/A | No | No | No
40596226 | Steel | Concord | 009/040 | 2022-01-18 | 2020-12-02 | 2020-04-20 | Is vegetation present? | F a ls e | TRUE: There appears to be vegetatio n present around one base of the structure. | Agree | Condition is not compelling | TD-1001M REV5 ET Preventative Maintenace Manual | N/A | N/A | No | No | No
40596226 | Steel | Concord | 009/040 | 2022-01-18 | 2020-12-02 | 2020-04-20 | Is the s hie ld wire o r fib e r grounded? | [Answer left blank] | TRUE: The structure's overhead ground wire appears to be grounded. | Agree | Condition is not compelling | TD-1001M-JA11 OPGW | N/A | N/A | No | No | No | Fed Report indicates 8 Infractions, 7 in report
40644180 | Steel | Concord | 000/003 | 2022-01-18 | 2020-12-08 | 2020-08-29 | Structure Issues: Damaged p rima ry me mb e rs | F a ls e | TRUE: There appears to be rusting and corrosion where p rima ry a nd secondary me mb e rs jo in in the b o tto m phase. | Disagree | Condition is not compelling | TD-1001M-JA04 Steel Structures Corrosion and Deteriation | N/A | N/A | No | No | No
40644180 | Steel | Concord | 000/003 | 2022-01-18 | 2020-12-08 | 2020-08-29 | Vegetation Issues: Signific a nt vegetatio n around base | F a ls e | TRUE: One corner of the foundation appears to be covered in woody vegetation. | Agree | N/A | TD-1001M REV5 ET Preventative Maintenace Manual | LC 119618877 was completed on 11/2/20 for this FDA | N/A | No | No | No
40644180 | Steel | Concord | 000/003 | 2022-01-18 | 2020-12-08 | 2020-08-29 | Vegetation Issues: Vegetation removal required | F a ls e | TRUE: One corner of the foundation appears to be covered in woody vegetation. | Agree | N/A | TD-1001M REV5 ET Preventative Maintenace Manual | LC 119618877 was completed on 11/2/20 for this FDA | N/A | No | No | No | Duplicate in Report
40644180 | Steel | Concord | 000/003 | 2022-01-18 | 2020-12-08 | 2020-08-29 | Is the structure in a rural area and within 600 ft of a d we llin gor camp? | F a ls e | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40644180 | Steel | Concord | 000/003 | 2022-01-18 | 2020-12-08 | 2020-08-29 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | F a ls e | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40866108 | Wood | Sacramento | B024/542 | 2022-01-18 | 2020-12-09 | 2020-10-06 | Insulator Issues: Insulators are damaged, contaminated, or in poor condition | F a ls e | The photos are insuffic ie nt to assess the condition of the sides or bottom of the ins ula to rs . | Agree | N/A | N/A | 6/17/21 sherlock Photos show sides and bottom of insulators with No Issues | N/A | Yes | Yes | No | Create LC for Missing Bridging No EC or LC found in SAP | S 5 # 122774252 Created 1/19/22 @ 11:09
40657103 | Steel | Lakeville | 059/292 | 2022-01-18 | 2020-12-17 | 2020-04-23 | Is the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40657103 | Steel | Lakeville | 059/292 | 2022-01-18 | 2020-12-17 | 2020-04-23 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40664742 | Wood | Sacramento | 023/651 | 2022-01-18 | 2020-12-17 | 2020-06-22 | Insulator Issues: Insulators' hardware hot-end/shoe clamp assembly in poor condition | FALSE | TRUE: Twist on pole adds strain to center-phase conductor. | Agree | N/A | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | LC 119194764 was completed on 8/10/21, Reframed pole | N/A | No | No | No
40664742 | Wood | Sacramento | 023/651 | 2022-01-18 | 2020-12-17 | 2020-06-22 | Are marker balls in poor condition? | No | N/A: No marker balls appear to be present. | Agree | Condition does not exist | TD-1001M REV5 ET Preventative Maintenace Manual | Inspector was refering to visibility strips, Not needed as per CIRT LC 119194761 | N/A | No | No | No
40771653 | Wood | Moss Landing | 010/098 | 2022-01-18 | 2020-12-17 | 2020-04-02 | Does or should this structure have a guy? | FALSE | TRUE: The structure appears to have a guy. | Disagree | Condition does not exist | TD-1001M REV5 ET Preventative Maintenace Manual | Guy is at Distribution Level | N/A | No | No | No
40771653 | Wood | Moss Landing | 010/098 | 2022-01-18 | 2020-12-17 | 2020-04-02 | Is the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40771653 | Wood | Moss Landing | 010/098 | 2022-01-18 | 2020-12-17 | 2020-04-02 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40650055 | Wood | Sacramento | 010/360 | 2022-01-18 | 2020-12-18 | 2020-08-28 | Framing Issues: Insulator hanger (eye) plate in poor condition | FALSE | TRUE: The photos are not sufficient to determine the condition of the D-Bolt. | Agree | N/A | TD-1001M REV5 ET Preventative Maintenace Manual | Sherlock 6/2/21 Photos show cold end hardware in Good repair, LC 120897601 is in place to replace pole | N/A | No | No | No
40650055 | Wood | Sacramento | 010/360 | 2022-01-18 | 2020-12-18 | 2020-08-28 | Insulator Issues: Insulators' hardware cold-end in poor condition (e.g. C-hook) | FALSE | The photos are not sufficient to determine the condition of the cold-end hardware. | Agree | N/A | TD-1001M REV5 ET Preventative Maintenace Manual | Sherlock 6/2/21 Photos show cold end hardware in Good repair, LC 120897601 is in place to replace pole | N/A | No | No | No
40803641 | Steel | Pismo Beach | 046/267 | 2022-01-18 | 2020-12-18 | 2020-05-18 | Anti-climbing needed per E.D. 022168 and TD-1009S? | FALSE | TRUE: The structure appears to be located near a dwelling and a road. | Disagree | Condition does not exist | TD-1001M REV5 ET Preventative Maintenace Manual | LC 117003919 was created on 4/10/2019 for this FDA, CIRT cancelled , No public road/ No Public access | N/A | No | No | No
40803641 | Steel | Pismo Beach | 046/267 | 2022-01-18 | 2020-12-18 | 2020-05-18 | Are marker balls in poor condition? | No | N/A: No marker balls appear to be present. | Agree | Condition is not compelling | TD-1001M REV5 ET Preventative Maintenace Manual | N/A | N/A | No | No | No
40803641 | Steel | Pismo Beach | 046/267 | 2022-01-18 | 2020-12-18 | 2020-05-18 | Is the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No | Report indicates 5 conditions, 3 Shown in Report
40648489 | Wood | Lakeville | 047/003 | 2022-01-18 | 2021-01-12 | 2020-04-30 | Anchor Rod Issues: Obstructed View | FALSE | The photos are not sufficient to assess the condition of the anchor. | Agree | N/A | TD-1001M-JA13 Guys and Anchors | Create LC for buried anchors | Create a LC | Yes |  |  | S 5 # 122774269 created on 1/19/22 @ 11:158
40648489 | Wood | Lakeville | 047/003 | 2022-01-18 | 2021-01-12 | 2020-04-30 | Vehicular and Mechanical Issues: Bird, animal or insect damage (e.g., woodpecker) | FALSE | TRUE: The top portion of the pole appears to show woodpecker damage. | Agree | N/A | TD-1001M-JA06 Wood Poles - Non Steel Framing | LC 118991435 For this FDA was completed on 6/17/21 | N/A | No | No | No
40648489 | Wood | Lakeville | 047/003 | 2022-01-18 | 2021-01-12 | 2020-04-30 | Vehicular and Mechanical Issues: Breaks or cracks or split in pole | FALSE | TRUE: The top portion of the pole appears to show cracking. | Disagree | Condition is not compelling | TD-1001M-JA06 Wood Poles - Non Steel Framing | N/A | N/A | No | No | No
40648489 | Wood | Lakeville | 047/003 | 2022-01-18 | 2021-01-12 | 2020-04-30 | Vehicular and Mechanical Issues: Pole-top damage or split-top | FALSE | TRUE: The pole-top appears to be starting to split. |  |  | TD-1001M-JA06 Wood Poles - Non Steel Framing | N/A | N/A | No | No | No
40648489 | Wood | Lakeville | 047/003 | 2022-01-18 | 2021-01-12 | 2020-04-30 | Conductor Issues: Jumpers in poor condition | FALSE | TRUE: A few inches of the jumper on the bottom phase appears to show bird caging. | Agree | Condition is not compelling | TD-1001M-JA10 Conductor Conditions | N/A | N/A | No | No | No
40649102 | Wood | Moss Landing | 015/137 | 2022-01-18 | 2021-01-12 | 2020-08-10 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled trail | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40813547 | Steel | Sacramento | 010/107 | 2022-01-18 | 2021-01-12 | 2020-05-19 | Foundation Issues: Concrete damaged or in poor condition | FALSE | TRUE: Each corner of the foundation appears to show varying levels of deterioration | Agree | N/A | TD-1001M-JA12 Foundation Condition TLine Structures & Supports | LC 119088768 was created on 6/1/20 for this FDA | N/A | No | No | No
40813547 | Steel | Sacramento | 010/107 | 2022-01-18 | 2021-01-12 | 2020-05-19 | Type of Splice: Compression | FALSE | TRUE: There appears to be a compression splice in the center phase. | Agree | N/A | TD-1001M-JA10 Conductor Conditions | N/A | N/A | No | No | No
40813547 | Steel | Sacramento | 010/107 | 2022-01-18 | 2021-01-12 | 2020-05-19 | Are splices in poor condition? | [Answer left blank] | The photos are insufficient to assess the condition of the splice. | Disagree | Condition does not exist | TD-1001M-JA10 Conductor Conditions | Sherlock Photo DRUM-RIO OSO #1_010-107- shows Good image of compression splice | N/A | No | No | No
40813547 | Steel | Sacramento | 010/107 | 2022-01-18 | 2021-01-12 | 2020-05-19 | Is vegetation present? | FALSE | TRUE: Vegetation appears to be present at the base of the structure. | Agree | Condition is not compelling | TD-1001M REV5 ET Preventative Maintenace Manual | N/A | N/A | No | No | No
40813547 | Steel | Sacramento | 010/107 | 2022-01-18 | 2021-01-12 | 2020-05-19 | Is the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40767143 | Wood | Sacramento | 024/355 | 2022-01-18 | 2021-01-13 | 2020-05-28 | Vehicular and Mechanical Issues: Breaks or cracks or split in pole | FALSE | TRUE: There appears to be light to moderate cracking at the pole top. | Agree | Condition is not compelling | TD-1001M-JA06 Wood Poles - Non Steel Framing | LC 119326557 for Wood pecker holes, Cracks not a compelling issue was Found completed on 6/3/21, CIRT Cancelled | N/A | No | No | No
40767143 | Wood | Sacramento | 024/355 | 2022-01-18 | 2021-01-13 | 2020-05-28 | Vehicular and Mechanical Issues: Pole-top damage or split-top | FALSE | TRUE: There appears to be light to moderate cracking in the midsection. | Agree | Condition is not compelling | TD-1001M-JA06 Wood Poles - Non Steel Framing | LC 119326557 for Wood pecker holes, Cracks not a compelling issue was Found completed on 6/3/21, CIRT Cancelled | N/A | No | No | No
40808554 | Wood | Victor | 001/006A | 2022-01-19 | 2021-01-13 | 2020-05-04 | Insulator Issues: Insulators' hardware hot-end/shoe clamp assembly in poor condition | FALSE | TRUE: A PG&E inspector identified an issue with the cotter key not fully seated for the outer phase, but appeared to fail to identify the same issue for the center phase. | Agree | Condition does not exist | TD-1001M-JA10 Conductor Conditions | A Sap and sherlock 2021 Photos # DJI_0179 & DJI _ 0213, Show's all Cotter Keys in Place. | N/A | No | No | No
44853798 | Steel | Table Mountain | 002/057B | 2022-01-19 | 2021-01-13 | 2020-07-09 | Tower finish type: | I don't know | Weathered: The structure finish appears to be weathered steel. | Agree | Condition is not compelling | TD-1001M REV5 ET Preventative Maintenace Manual | N/A | N/A | No | No | No
40592327 | Steel | Lakeville | 001/010 | 2022-01-19 | 2021-01-14 | 2020-05-07 | Foundation Issues: Obstructed View | FALSE | TRUE: At least one of the corners of the foundation is obscured by vegetation. | Agree | N/A | TD-1001M REV5 ET Preventative Maintenace Manual | LC 116582728, Showws that all Vegetation work was completed upon arrival, 6/29/20 | N/A | No | No | No
40592327 | Steel | Lakeville | 001/010 | 2022-01-19 | 2021-01-14 | 2020-05-07 | Vegetation Issues: Significant vegetation around base | FALSE | TRUE: There appears to be significant woody vegetation around the base of the structure. | Agree | N/A | TD-1001M REV5 ET Preventative Maintenace Manual | LC 116582728, Showws that all Vegetation work was completed upon arrival, 6/29/20 | N/A | No | No | No
40592327 | Steel | Lakeville | 001/010 | 2022-01-19 | 2021-01-14 | 2020-05-07 | Is the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No | Report indicates 4 conditions, 3 are in Report
40594149 | Wood | Moss Landing | 007/154 | 2022-01-19 | 2021-01-14 | 2020-06-03 | Vehicular and Mechanical Issues: Bird, animal or insect damage (e.g., woodpecker) | FALSE | TRUE: There appears to be woodpecker damage throughout the pole. | Agree | N/A | TD-1001M-JA06 Wood Poles - Non Steel Framing | LC 119120045 for this FDA shows all work completed on 6/29/21 | N/A | No | No | No
40594149 | Wood | Moss Landing | 007/154 | 2022-01-19 | 2021-01-14 | 2020-06-03 | Vehicular and Mechanical Issues: Breaks or cracks or split in pole | FALSE | TRUE: There appears to be significant cracking throughout the pole. | Disagree | Condition is not compelling | TD-1001M-JA06 Wood Poles - Non Steel Framing | LC 119354010 was created on 7/10/20 For cracks in Pole cancelled by CIRT on 8/6/20. Damage not significant | N/A | No | No | No
40594149 | Wood | Moss Landing | 007/154 | 2022-01-19 | 2021-01-14 | 2020-06-03 | Vehicular and Mechanical Issues: Pole-top damage or split-top | FALSE | TRUE: The pole-top appears to be cracked. | Disagree | Condition is not compelling | TD-1001M-JA06 Wood Poles - Non Steel Framing | LC 119354010 was created on 7/10/20 For cracks in Pole cancelled by CIRT on 8/6/20. Damage not significant | N/A | No | No | No
40594149 | Wood | Moss Landing | 007/154 | 2022-01-19 | 2021-01-14 | 2020-06-03 | Insulator Issues: Insulators' hardware cold-end in poor condition (e.g. C-hook) | FALSE | TRUE: There appears to be loose hardware on the post insulator pole bracket in the lowest phase. | Agree | N/A | TD-1001M-JA07 Hardware & Insulators corrosion Rev2 | Create LC | Create a LC |  |  |  | S 5 # 122774270 created on 1/19/22 @ 11:22
40594149 | Wood | Moss Landing | 007/154 | 2022-01-19 | 2021-01-14 | 2020-06-03 | Vegetation Issues: Significant vegetation around base | FALSE | TRUE: There appears to be heavy vegetation near the base of the pole. | Agree | N/A | TD-1001M-JA20 Vegetation Non-conformance Job Aid | LC 115672193 For Veg Removal shows Completed on 4/28/20. See sherlock Image DJI_0353(2).JPG | N/A | No | No | No
40594149 | Wood | Moss Landing | 007/154 | 2022-01-19 | 2021-01-14 | 2020-06-03 | Is there a distribution issue on a transmission structure with a distribution underbuild? | FALSE | TRUE: The crossarm on the distribution underbuild appears to be twisted. | Agree | Condition is not compelling | TD-1001M REV5 ET Preventative Maintenace Manual | N/A | N/A | No | No | No
40594149 | Wood | Moss Landing | 007/154 | 2022-01-19 | 2021-01-14 | 2020-06-03 | Is the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40594149 | Wood | Moss Landing | 007/154 | 2022-01-19 | 2021-01-14 | 2020-06-03 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
41184072 | Steel | Table Mountain | 005/039 | 2022-01-19 | 2021-01-14 | 2020-06-24 | Structure Issues: Insulator hanger (eye) plate in poor condition | FALSE | TRUE: The hanger plates on multiple phases appear to show rust and corrosion, including an elongation of the hanger plate eye | Disagree | Condition is not compelling | TD-1001M REV5 ET Preventative Maintenace Manual | Sherlock Files From 2019 and 2020 Inspections clearly Show Hanger Plates and Cold end Hardware in Good Repair | N/A | No | No | No
41184072 | Steel | Table Mountain | 005/039 | 2022-01-19 | 2021-01-14 | 2020-06-24 | Insulator Issues: Insulators' hardware cold-end in poor condition (e.g. C-hook) | FALSE | The photos are not sufficient to determine the condition of the cold-end hardware | Disagree | Condition is not compelling | TD-1001M REV5 ET Preventative Maintenace Manual | Sherlock Files From 2019 and 2020 Inspections clearly Show Hanger Plates and Cold end Hardware in Good Repair | N/A | No | No | No
40826509 | Wood | Table Mountain | 009/183 | 2022-01-19 | 2021-01-15 | 2020-08-29 | Insulator Issues: Insulators' hardware cold-end in poor condition (e.g. C-hook) | FALSE | The photos are not sufficient to determine the condition of the cold-end hardware. | Disagree | Condition does not exist | TD-1001M REV5 ET Preventative Maintenace Manual | Sherlock Photos CARIBOU-WESTWOOD 009-183-40826509_026,_022 &_029 Clearly show cold end Hardware in Good Repair | N/A | No | No | No
40876409 | Wood | Moss Landing | 008/009 | 2022-01-19 | 2021-01-19 | 2020-05-29 | Vehicular and Mechanical Issues: Pole-top damage or split-top | FALSE | TRUE: The pole-top appears to be splitting where insulator bolts attach. | Disagree | Condition is not compelling | TD-1001M-JA06 Wood Poles - Non Steel Framing | Condition is not compelling, Split Bolt in place to prevent Cracking through pole | N/A | No | No | No
40876409 | Wood | Moss Landing | 008/009 | 2022-01-19 | 2021-01-19 | 2020-05-29 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road or trai | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
44779069 | Steel | Lakeville | 005/063 | 2022-01-19 | 2021-01-19 | 2020-08-06 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No | Report indicates 2 Conditions, 1 In Report
40739975 | Steel | Concord | 000/002B | 2022-01-20 | 2020-11-17 | 2020-08-17 | Guy Issues: Guy damaged or in poor conditio | FALSE | TRUE: The guy wire appears to have slipped part of the way. | Agree | N/A | TD-1001M-JA13 Guys and Anchors | Three Bolt Guy Connetors appear to have Slipped | Create a LC | Yes | Yes |  | LC 12278/5234 created 1/21/22 @ 07:55
40739975 | Steel | Concord | 000/002B | 2022-01-20 | 2020-11-17 | 2020-08-17 | Vegetation Issues: Vegetation removal required | FALSE | TRUE: There appears to be vegetation around the guy anchor. | Agree | N/A | TD-1001M-JA20 Vegetation Non-conformance Job Aid | Create Veg Tag | Create "Other tag" | Yes | Yes |  | Created Veg LC on 1/21/21 @ 07:02, 122782417
40739975 | Steel | Concord | 000/002B | 2022-01-20 | 2020-11-17 | 2020-08-17 | Is the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40760177 | Steel | Sacramento | 043/304 | 2022-01-20 | 2020-10-26 | 2020-10-06 | Structure Issues: Insulator hanger (eye) plate in poor condition | FALSE | The photos are insufficient to assess the condition of the hanger plate. | Agree | N/A | TD-1001M REV5 ET Preventative Maintenace Manual | Sherlock 2021 Photos G_004446, 00447,00448,00449,00451,00452,,00453,00454,00455,00456,00457 shows Hanger Plates and Clold end attachments " C Hooks in good Repair | N/A | No | No | No
40760177 | Steel | Sacramento | 043/304 | 2022-01-20 | 2020-10-26 | 2020-10-06 | Is structure number missing? | FALSE | TRUE: The structure appears to be missing a structure number. | Disagree | Condition does not exist | 022168 HV Signs, Marking, Numbering | 2021 Sherlock Photo DJI_0195.JPG clearly shows Structure Number | N/A | No | No | No
40760177 | Steel | Sacramento | 043/304 | 2022-01-20 | 2020-10-26 | 2020-10-06 | Anti-climbing needed per E.D. 022168 and TD-1009S? | FALSE | TRUE: The structure appears to be located near a farm, but does not have anti-climbing guards. | Disagree | Condition does not exist | 022168 HV Signs, Marking, Numbering | Structure is not near Public access, No signs of Graffiti or unauthorized Climbing | N/A | No | No | No
40760177 | Steel | Sacramento | 043/304 | 2022-01-20 | 2020-10-26 | 2020-10-06 | Insulator Issues: Insulators' hardware cold-end in poor condition (e.g. C-hook) | FALSE | The photos are insufficient to assess the condition of the cold-end hardware. However, there appears to be wear on the middle-phase and bottomphase c-hooks. | Agree | N/A | TD-1001M REV5 ET Preventative Maintenace Manual | Sherlock 2021 Photos G_004446, 00447,00448,00449,00451,00452,,00453,00454,00455,00456,00457 shows Hanger Plates and Clold end attachments " C Hooks in good Repair | N/A | No | No | No
40760177 | Steel | Sacramento | 043/304 | 2022-01-20 | 2020-10-26 | 2020-10-06 | Are marker balls in poor condition? | No | N/A: There do not appear to be any marker balls. | Agree | Condition is not compelling | TD-1001M REV5 ET Preventative Maintenace Manual | N/A | N/A | No | No | No
40760177 | Steel | Sacramento | 043/304 | 2022-01-20 | 2020-10-26 | 2020-10-06 | Is the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: A structure appears to be in a rural area and within 600 feet of a dwelling | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40668707 | Wood | Victor | 007/012 | 2022-01-20 | 2021-08-03 | 2021-04-08 | Structure has breaks / cracks / splits | [Answer left blank] | TRUE: The structure appears to have cracks. | Agree | N/A | TD-1001M-JA06 Wood Poles - Non Steel Framing | LC 120829396 indicates That Pole was replaced on 8/8/21 | N/A | No | No | No
40668707 | Wood | Victor | 007/012 | 2022-01-20 | 2021-08-03 | 2021-04-08 | Pole-top has damage or splittop | [Answer left blank] | TRUE: The structure appears to have pole-top damage. | Agree | N/A | TD-1001M-JA06 Wood Poles - Non Steel Framing | LC 120829396 indicates That Pole was replaced on 8/8/21 | N/A | No | No | No
40770092 | Wood | Lakeville | 011/122 | 2022-01-20 | 2021-07-19 | 2021-06-07 | Distribution underbuilt present | [Answer left blank] | TRUE: The structure appears to have a distribution underbuild. | Agree | Condition is not compelling | TD-1001M REV5 ET Preventative Maintenace Manual | N/A | N/A | No | No | No
40770092 | Wood | Lakeville | 011/122 | 2022-01-20 | 2021-07-19 | 2021-06-07 | Distribution issue on a Transmission structure with Distribution underbuild | [Answer left blank] | TRUE: The structure appears to have an incomplete high voltage sign on the distribution underbuild. | Agree | N/A | 022168 HV Signs, Marking, Numbering |  | Create "Other tag" | Yes | Yes | No | LC created for Damaged HV Signs on 1/21/22 @ 07:37, LC 122785422 | Identified Missing Bridging, LC Created on 1/21/22, LC 122785424
40753858 | Steel | Pismo Beach | 018/075 | 2022-01-20 | 2021-08-27 | 2021-06-24 | Vegetation present? | No | Yes: Vegetation appears to be present. | Agree | Condition is not compelling | TD-1001M REV5 ET Preventative Maintenace Manual | N/A | N/A | No | No | No
40666824 | Wood | Table Mountain | 010/013 | 2022-01-20 | 2021-04-14 | 2020-06-15 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40867804 | Wood | Table Mountain | 010/200 | 2022-01-20 | 2021-04-20 | 2020-10-02 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40913117 | Steel | Sacramento | 017/151 | 2022-01-20 | 2021-05-07 | 2020-04-29 | Structure Issues: Steel Structure Hardware Damaged (i.e. nuts and bolts) | FALSE | TRUE: There appears to be a missing bolt on a secondary membe | Disagree | Condition does not exist | TD-1001M-JA04 Steel Structures Corrosion and Deteriation | Tower is Type G Drawing 309424 show these Holes are Pulling eyes | N/A | No | No | No
40595890 | Wood | Lakeville | 000/011 | 2022-01-20 | 2021-05-18 | 2020-05-21 | Does or should this structure have a guy? | FALSE | TRUE: The structure appears to have 2 guys. | Disagree | Condition does not exist | TD-1001M-JA13 Guys and Anchors | Guys are at Distribution Level , Noot Identified during Transmission inspection | N/A | No | No | No
40595890 | Wood | Lakeville | 000/011 | 2022-01-20 | 2021-05-18 | 2020-05-21 | Anchor Rod Issues: Obstructed View | FALSE | TRUE: Vegetation appears to be obstructing the view of one of the anchors. | Disagree | Condition does not exist | TD-1001M-JA13 Guys and Anchors | Anchors are for Distribution Guys, Not Identified in Transmission inspections. Minor work | N/A | No | No | No
40595890 | Wood | Lakeville | 000/011 | 2022-01-20 | 2021-05-18 | 2020-05-21 | Is structure number missing? | FALSE | TRUE: The structure number appears to be missing. | Agree | N/A | 022168 HV Signs, Marking, Numbering | In 2021 inspection Str Number is shown in Photo O_00812.JPG | N/A | No | No | No
40702059 | Wood | Sacramento | 011/370 | 2022-01-20 | 2021-05-18 | 2020-08-28 | Vehicular and Mechanical Issues: Pole-top damage or split-top | FALSE | TRUE: Cracking appears to be present at the top of the pole. | Agree | N/A | TD-1001M-JA06 Wood Poles - Non Steel Framing | LC 117490001 was created on 6/25/19 to replace Pole, all Work completed on 9/16/21 | N/A | No | No | No
40702059 | Wood | Sacramento | 011/370 | 2022-01-20 | 2021-05-18 | 2020-08-28 | Is structure number missing? | FALSE | FALSE: A tag with the structure number appears to be present, but the tag is bent. | Agree | N/A | 022168 HV Signs, Marking, Numbering | LC 117490001 was created on 6/25/19 to replace Pole, all Work completed on 9/16/21 | N/A | No | No | No
40702059 | Wood | Sacramento | 011/370 | 2022-01-20 | 2021-05-18 | 2020-08-28 | High voltage/danger sign(s) missing or installed incorrectly per E.D. 022168? | FALSE | TRUE: The high voltage sign appears to be missing. | Agree | N/A | 022168 HV Signs, Marking, Numbering | LC 117490001 was created on 6/25/19 to replace Pole, all Work completed on 9/16/21 | N/A | No | No | No
40702059 | Wood | Sacramento | 011/370 | 2022-01-20 | 2021-05-18 | 2020-08-28 | Is the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40745898 | Steel | Concord | 002/015 | 2022-01-20 | 2021-05-18 | 2020-04-10 | Foundation Issues: Earth covered or buried | FALSE | TRUE: One footing appears to be partially covered by loose earth. | Agree | Condition is not compelling | TD-1001M-JA12 Foundation Condition TLine Structures & Supports | N/A | N/A | No | No | No
40745898 | Steel | Concord | 002/015 | 2022-01-20 | 2021-05-18 | 2020-04-10 | Structure Issues: Steel Structure Hardware Loose or missing | FALSE | TRUE: Bolts appear to be missing from a secondary member around the base. | Disagree | Condition does not exist | TD-1001M-JA04 Steel Structures Corrosion and Deteriation | Type GT tower, Drawing Number 309424 shows these Holes as Pulling Eyes | N/A | No | No | No
40745898 | Steel | Concord | 002/015 | 2022-01-20 | 2021-05-18 | 2020-04-10 | Type of Splice: Twist | FALSE | TRUE: One twist splice appears to be present. | Agree | Condition is not compelling | TD-1001M-JA14 Splices Job Aid | N/A | N/A | No | No | No
40745898 | Steel | Concord | 002/015 | 2022-01-20 | 2021-05-18 | 2020-04-10 | Is vegetation present? | FALSE | TRUE: Vegetation appears to be present around footings. | Agree | Condition is not compelling | TD-1001M REV5 ET Preventative Maintenace Manual | N/A | N/A | No | No | No
40745898 | Steel | Concord | 002/015 | 2022-01-20 | 2021-05-18 | 2020-04-10 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40752265 | Steel | Table Mountain | 054/405 | 2022-01-20 | 2021-05-18 | 2020-08-11 | Structure Issues: Damaged secondary members | FALSE | TRUE: A secondary member appears to be bent. | Agree | N/A | TD-1001M-JA04 Steel Structures Corrosion and Deteriation | LC 115772348 was created on 0/31/19 For this FDA, All work completed on 02/03/21 | N/A | No | No | No
40752265 | Steel | Table Mountain | 054/405 | 2022-01-20 | 2021-05-18 | 2020-08-11 | Structure Issues: Steel Structure Hardware Loose or missing | FALSE | TRUE: Several bolts appear to be missing from the structure. | Disagree | Condition does not exist | TD-1001M-JA04 Steel Structures Corrosion and Deteriation | Tyower type is FA, Drawing Number 206891 shows these as pulling eyes | N/A | No | No | No
40752265 | Steel | Table Mountain | 054/405 | 2022-01-20 | 2021-05-18 | 2020-08-11 | Is the shield wire or fiber in poor condition? | [Answer left blank | TRUE: Shield wire ground jumpers appear to be overlong and appear to be starting to birdcage | Agree | Condition is not compelling | TD-1001M-JA10 Conductor Conditions | LC 119935450 was created on 10/22/20 For This FDA , All work completed on 11/10/20 | N/A | No | No | No
40752265 | Steel | Table Mountain | 054/405 | 2022-01-20 | 2021-05-18 | 2020-08-11 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40808937 | Steel | Lakeville | 046/226 | 2022-01-20 | 2021-05-18 | 2020-04-24 | Foundation Issues: Mastic sealant in poor condition | FALSE | TRUE: Mastic sealant appears to be deteriorating. | Agree | N/A | TD-1001M-JA12 Foundation Condition TLine Structures & Supports | LC 115754664 was created on 1/26/21 for this FDA, All work completed on 7/16/20
40808937 | Steel | Lakeville | 046/226 | 2022-01-20 | 2021-05-18 | 2020-04-24 | Structure Issues: Steel Structure Hardware Loose or missing | FALSE | TRUE: Bolts appear to be missing near the base of the structure. | Disagree | Condition does not exist | TD-1001M-JA04 Steel Structures Corrosion and Deteriation | Type GT Tower, Drawing Number 309424 shows Holes as Pulling Eyes | N/A | No | No | No
40808937 | Steel | Lakeville | 046/226 | 2022-01-20 | 2021-05-18 | 2020-04-24 | Is Overhead Ground Wire/Fiber sec | FALSE | TRUE: Static wire appears to be present. | Agree | Condition is not compelling | TD-1001M REV5 ET Preventative Maintenace Manual | N/A | N/A | No | No | No
40808937 | Steel | Lakeville | 046/226 | 2022-01-20 | 2021-05-18 | 2020-04-24 | Is the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40825724 | Wood | Lakeville | 001/019 | 2022-01-20 | 2021-05-18 | 2020-08-07 | Vehicular and Mechanical Issues: Breaks or cracks or split in pole | FALSE | TRUE: Cracks appear to be present along the entire length of the pole. | Disagree | Condition is not compelling | TD-1001M-JA06 Wood Poles - Non Steel Framing | N/A | N/A | No | No | No
40825724 | Wood | Lakeville | 001/019 | 2022-01-20 | 2021-05-18 | 2020-08-07 | Is the structure in a rural area and within 600 ft of a dwelling or camp? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a dwelling. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40825724 | Wood | Lakeville | 001/019 | 2022-01-20 | 2021-05-18 | 2020-08-07 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No
40876080 | Wood | Lakeville | 052/009 | 2022-01-20 | 2021-05-18 | 2020-08-06 | Is the structure in a rural area and within 600 ft of a frequently traveled road/trail? | FALSE | TRUE: The structure appears to be in a rural area and within 600 feet of a frequently traveled road. | Agree | Condition is not compelling | TD-1009S | N/A | N/A | No | No | No