## EO Ignition Investigation Edits
Index | Create Date | Fire Latitude | Fire Longitude | Executive Summary | PG&E Facility Ignition | CPUC Reportable Ignition | HFTD | EPSS Circuit | Circuit | Circuit Level - Fire Potential Index | Incident Name | Suspected Initiating Event | Failure Driver | Failure Sub-Driver | County | Division | Asset Family Cause | Equipment Type Associated to Ignition | Nominal Voltage | Primary/Secondary | Type of Construction
20241201 | 2024-08-23 | 39.0327 | -121.3087 | On 08/23/2024 at 0614 hours, a PG&E Troubleshooter was dispatched to the LINCOLN 1104, a 12kV distribution Circuit on 4N/O 9711 MC COURTNEY RD, Placer County in response to a Fire report. Initial analysis indicates that the Utility work operation was the cause of the ignition. It has been determined that a balloon came into contact with distribution line on August 22 around 2338 hours, the control center received abnormal alarms from Line Recloser (LR) 997576 and LR 51756 which protect the Lincoln 1104 circuit. Distribution troubleshooter was dispatched to inspect the line. Due to the nighttime darkness and the similarity in color between the rose gold balloon and the steel pole, it was difficult to identify the cause. Following standard procedure, the control center manually reenergized the line, which ignited the grass below and caused the ignition. While no PG&E assets were damaged, a tag was created to inspect the conductor for any damage and determine if any repairs are required. The ensuing fire was between 10-20 acres and suppressed by California Fire Department. This incident caused a power outage affecting 113 customers. This incident location occurred within aTire2 HFTD, R3 FPI, and HFRA zone. Enhanced powerline safety settings-EPSS were enable for the LINCOLN 1104 at the time of the incident. A PG&E Crew created a tag to inspect for necessary repairs to the conductor on 08/23/2024 This information is preliminary. | Yes | Yes | Tier 2 | Yes | LINCOLN 1104 | R3 | FAR | Utility work / Operation | Utility work / Operation | Re-energized into fault after patrol | Placer | Sierra | Distribution | Conductor - Primary | 12000 | Primary | Overhead