## Slide 1: FIGURE PG&E-8.2.1-1
WDRM V4 1-N
Manually review list of CPZ’s in Foundry Work Planning Center (WPC)
Is CPZ less then 1 mile?
Proceed/combine if adjacent CPZ is within 2027-2030 outlook or the only HFTD CPZ.
Exclude if adjacent CPZ is not within 2027-2030 outlook
Begin High Level Feasibility Review
No
Yes
Does this segment already have work in the current workplan/or complete?
Does this segment have risk that extends beyond this segment’s borders?
Does this segment have HFRA adjustments or adjacent buffer zones?
Is this segment near an HFTD border? Consider Inclusion if < 2 miles for PSPS/EPSS benefit
Exclude these areas from scoping if completed or in 2025-26 workplan.
Consider for scope exclusion
Consider for scope inclusion
Include in Scope
Remove
Add
Yes
Yes
Yes
Document in Foundry including polygon(s), workplan, and comments as necessary
Begin Review for Removal, Remote Grid, or LEIP
Create preliminary .kmz in Google Earth to show proposed OH/UG route and Mainline/Tap line Designation.
Are there any idle lines or redundant circuit ties that can be removed?
Are there any locations that a Remote Grid/LEIP would be an economical solution?
Remote Grid & Customer LEIP Screening Process
Update scope .kmz in Google Earth
Yes
Yes
Cost Benefit Analysis
Decision
Step
Key
Create Specific Planning Orders, WBS elements, Notifications, and PM Orders.

## Slide 2: FIGURE PG&E-8.2.1-2
Begin UG Cost Benefit Analysis
Input OH/UG alternative scope mileage and unit cost assumptions into Foundry WPC Feedback Loop Tool
Is the UG CBR > 1 and within 50% of the OH + EPSS CBR and is the UG NB > OH NB
Begin Hybrid Analysis
No
Proceed to scoping meeting with UG alternative as preferred.
Are there areas identified with High tree strike potential within the circuit segment?
No/Low (0-5) High (6+)
Area of impact identified, relocate to underground preferred, update Hybrid .kmz
Yes
Yes
Are there Egress / Ingress concerns expressed by PSS team?
Does PSPS polygon affect only part of the CPZ?
Input OH/UG alternative scope mileage and unit cost assumptions into Foundry WPC Feedback Loop Tool
Begin Hybrid Cost Benefit Analysis
Is the Hybrid CBR > 1 and within 50% of the OH + EPSS CBR and is the Hybrid NB > OH NB
Remove the targeted underground for PSPS impacted areas.
Is the new Hybrid CBR > 1 and within 50% of the OH + EPSS CBR and is the Hybrid NB > OH NB
Remove the targeted underground for Ingress/Egress impacted areas.
Is the new Hybrid CBR > 1 and within 50% of the OH + EPSS CBR and is the Hybrid NB > OH NB
Yes
Yes
Proceed to scoping meeting with Hybrid alternative as preferred.
Proceed to scoping meeting with Overhead alternative as preferred.
Desktop Scoping Meeting
Decision
Step
Key
Yes
Yes
Yes
No
No
No

## Slide 3: FIGURE PG&E-8.2.1-3
Begin Preparation for Desktop Scoping Meeting
Create Business Case and Route in EDRS per DOA.
Request Project Manager via the Project Front Door
Save .kmz to shared drive and send to scoping team for review.
Analyze CPZ fire risk, vegetation, engineering requirements, collect land/bio/cultural/constructability limitations, and complete field visits as necessary.
Begin developing preliminary key-sketches based on preferred design.
Desktop Scoping Meeting
Review Virtually via Teams with Scoping Participants.
Are there any significant dependency or constructability limitations in the areas of impact?
Update .kmz routes based on discussion and document dependency requirements.
Estimating recommends segmentation into sub-projects for estimating and construction.
Begin Final Cost Analysis and DBM
Yes
No
Input updated all Alternative scope mileage and unit cost assumptions into Foundry WPC Feedback Loop Tool
Is the Preferred Alt. CBR > 1 and within 50% of the OH + EPSS CBR and is the Preferred Alt. NB > OH NB?
Update As-scoped to the preferred alternative that meets CBR/NB criteria.
Create Specific Planning Orders, WBS elements, Notifications, and PM Orders for sub-projects.
Review Segments, Scope, and Schedule and initiate Key Sketch update.
Update Key Sketch and Work Description including all protection, switching and voltage control
Was the Key sketch approved by Distribution Planning and Senior Grid Design Engineer?
No
Update Sharepoint with Key sketch and other scoping documents
Yes
Route DBM in EDRS for Approval and update Schedule
Project Manager Attaches Scope to each project Segment in SAP.
Grid Design Engineer completes IN03 task in SAP.
Scoping Complete
Decision
Step
Key
Yes
No