## Table 1
#VALUE!
Table 1: Customers Notified and De-energized1
| Total Customers Notified | Total Customers De-energized | Total Customers Cancelled | MBL Customers De-energized | Counties De-energized | Tribes De-energized | Circuits Transmission De-energized | Circuits Unique Distribution Circuits in Any Version of Scope | Circuits Distribution Circuits De-energized | Hazard Count | CFI De-energized
| 15,766 2 | 212 3 | 15555 | 9 | 3 | 0 | 3 | 27 | 4 | 1 | 25
1 The information, times, and figures referenced in this report are based on the best available information available at the time of this report’s submission. The information, times, and figures herein are subject to revision based on further analysis and validation.
2 Of the 15,766 customer notifications sent to customers, all customers received Cancel notifications if they were removed from scope. However, one transmission-level customer was not deenergized despite their inclusion in the final scope. See Section 5.6 for details.
3 Of the 212 customers de-energized, two customers did not receive any notifications before de-energization, due to no valid contact information. For further details, please refer to Section 5.5.

## Table 2
#VALUE!
Table 2: 2024 PSPS Risk-Benefit Consequence Modeling Considerations
| Consequence Type | Wildfire Consequence Considerations | PSPS Consequence Considerations
| Safety | Calculated based on maximum population impacts derived from Technosylva wildfire simulation models and a fatality ratio based on National Fire Protection Association (NFPA) data. | Calculated from an estimate of Equivalent Fatalities (EF) per Million Customer Minutes Interrupted (MMCI). The EF/MMCI ratio is estimated from previous PG&E PSPS outages and other large external outage events.1
| Reliability | N/A | Calculated directly from the potential number of customers impacted and outage duration based on customer minutes interrupted.
| Financial | Calculated based on maximum building impacts derived from Technosylva wildfire simulation models and a cost per structure burned previously evaluated in 2020 RAMP Report.2 | Calculated based on two financial estimates 1) distribution of a lump sum cost of execution across all relevant circuits and 2) an estimated proxy cost per customer in scope per PSPS.3
1 Previous PG&E PSPS include 2019-2021 events, and other large external outage events include the 2003 Northeast Blackout in New York City, 2011 Southwest Blackout in San Diego, 2012 Derecho Windstorms, 2012 Superstorm Sandy, 2017 Hurricane Irma, 2021 Blackout event.
2 See A.20-06-012.
3 The assumptions used in these calculations, including the proxy cost per customer per PSPS, are subject to be updated and are not intended to prejudge or create precedent with regard to the development of more precise values of resiliency or cost of PSPS metrics being considered in other ongoing proceedings at the California Public Utilities Commission, such as the Risk-Based Decision-Making Rulemaking [R.20.07.013] and the Microgrid and Resiliency Strategies.

## Table 3
#VALUE!
Table 3: Notification Descriptions
| Type of Notification | Recipients | Description
| PRIORITY NOTIFICATION: 48-72 hours in advance of anticipated de-energization1 | Public Safety Partners, CBOs,2 transmission level customers, and municipal utilities | On July 18, 2024, PG&E’s Meteorology Team noted a potential PSPS and updated the weather forecast on pge.com/weather to “elevated” in certain parts of the service area. At this time, local PG&E representatives called each County Office of Emergency Services (OES) in PG&E’s electrical service area and select Tribes and cities to inform them that PG&E is monitoring an increased potential of PSPS outages. Following PG&E’s activation of its EOC, the following was completed: • PG&E submitted a PSPS Notification Form to Cal OES (California Governor's Office of Emergency Services) and sent an e-mail to the CPUC notifying them that PG&E’s EOC has been activated and that PG&E is monitoring for potential PSPS. • PG&E sent notifications to other Public Safety Partners3 via call, text and e-mail; these notifications included the following information: o Estimated window of the de-energization time. o When weather is anticipated to pass. o Estimated Time of Restoration (ETOR). o Links to the PSPS Portal where event-specific maps and information are available. • Local PG&E representatives called potentially impacted County OES and select Tribes to inform them that PG&E is monitoring an increased potential of PSPS.
| WATCH NOTIFICATION: 24-48 hours in advance of anticipated de-energization | Public Safety Partners, CBOs, and All Customers (including MBL program customers and SIV customers), transmission level customers, and municipal utilities | During this time, the following was completed: • PG&E submitted a PSPS Notification Form to Cal OES. • PG&E sent notifications to other Public Safety Partners, transmission level customers, municipal utilities, and all customers via call, text message and e-mail; these notifications included the following information: o Estimated window of the de-energization time. o When the adverse weather is anticipated to pass. o ETOR. o For Public Safety Partners only: Links to the PSPS Portal. o For Customers only: Potentially impacted addresses, links to PSPS Updates webpage with CRC information, and resources for AFN customers, including but not limited to information on the MBL program, language support, and the Portable Battery Program. o For transmission-level customers only: Transmission Substation Name and Line name serving substation. • PG&E sent notifications to MBL program customers, including tenants of master metered accounts, and SIV customers every hour until the customer confirmed receipt of the notification. • PG&E also sent Cancellation Notifications to Public Safety Partners and customers within two hours of being removed from scope; this was to inform them that power would not be shut off. Customer notifications were provided in English, with information on how to get PSPS information in translated languages. Customers with their language preference selected in their PG&E accounts received in-language (translated) notifications. Public Safety Partner notifications were provided in English.
| WARNING NOTIFICATION: 1-4 hours in advance of anticipated de-energization, if possible | Public Safety Partners, CBOs, and All Customers (including MBL program customers, SIV customers), transmission level customers, and municipal utilities | During this time, the following was completed: • PG&E submitted a PSPS Notification Form to Cal OES and sent an e-mail to the CPUC notifying them that PG&E has made the decision to de-energize. • PG&E sent notifications to other Public Safety Partners, transmission-level customers, and customers; these notifications included the same key PSPS timing information and resource links as the “Watch Notification.” • PG&E sent notifications to MBL program customers, including tenants of master metered accounts, and SIV customers every hour until the customer confirmed receipt of the notification. • PG&E also sent Cancellation Notifications to Public Safety Partners and customers within two hours of being removed from scope; this was to inform them that power would be shut off. Customer notifications were provided in English, with information on how to get PSPS information in translated languages. Customers with their language preference selected in their PG&E accounts received in-language (translated) notifications. Public Safety Partner notifications were provided in English.
| POWER OFF NOTIFICATION: When de-energization is initiated | Public Safety Partners, CBOs, and All Customers (including MBL program customers and SIV customers), transmission level customers4, and municipal utilities | When shut off was initiated, the following was completed: • PG&E submitted a PSPS State Notification Form to Cal OES and sent an e-mail to the CPUC to notify them that de-energization has been initiated. • Agency Representatives of PG&E conducted a live call and/or sent an e-mail, as appropriate, to County OES that were within the potential PSPS scope area and select Tribes and cities to inform them that customers within their jurisdiction were beginning to be de-energized. • PG&E Grid Control Center (GCC) conducted live agent calls to impacted transmission-level customers. • PG&E sent notification to other Public Safety Partners, municipal utilities, transmission level customers and customers via call, text messages, and e-mail, which included: o Impacted addresses (for customers only). o De-energization time. o When the adverse weather is anticipated to pass. o For Customers Only: Links to the PSPS Updates webpage with CRC information, and resources for AFN customers, including but not limited to information on the MBL program, Meals on Wheels, language support, and the Portable Battery Program. Customer notifications were provided in English, with information on how to get PSPS information in translated languages. Customers with their language preference selected in their PG&E accounts received in-language (translated) notifications. Public Safety Partner notifications were provided in English.
| WEATHER “ALL-CLEAR”/ETOR UPDATE NOTIFICATION: Immediately before re-energization begins | Public Safety Partners, CBOs, and All Customers (including MBL program customers and SIV customers), transmission level customers, and municipal utilities | After the weather event had passed and the area is deemed safe to begin patrols and restoration, PG&E completed the following: • Submitted a PSPS State Notification Form to Cal OES and sent an e-mail to the CPUC notifying them that PG&E is initiating re-energization patrols. • Sent notifications to other Public Safety Partners, transmission level customers5, municipal utilities and customers via call, text message and e-mail; these notifications included the ETOR. • Sent “PSPS update” notifications to customers if their ETOR changed; two ways that an ETOR may change include: o New field or meteorology conditions. o Damage was found during patrols and repair is needed. Customer notifications were provided in English, with information on how to get PSPS information in translated languages. Customers with their language preference selected in their PG&E accounts received in-language (translated) notifications. Public Safety Partner notifications were provided in English.
| RESTORATION NOTIFICATION: When re-energization is complete | Public Safety Partners, CBOs, and All Customers (including MBL program customers and SIV customers), transmission level customers, and municipal utilities | GCC conducted live agent calls to notify impacted transmission-level customers of restoration. Once customers, including MBL program customers and SIV customers, were restored, they received notifications via call, text and e-mail. This was done using an automated process that issued customer notifications every 15 minutes upon restoration of service. Customer notifications were provided in English, with information on how to get PSPS information in translated languages. Customers with their language preference selected in their PG&E accounts received in-language (translated) notifications. Once all customers were restored, PG&E submitted the final PSPS State Notification Form to Cal OES, sent an e-mail to the CPUC confirming restoration of PSPS outages and reclassification of customers if applicable, and sent a notification to Public Safety Partners via call, text and e-mail. Public Safety Partner notifications were provided in English.
1 PG&E sent Priority Notifications to Public Safety Partners and transmission-level customers as soon as the EOC activated for the July 20-21, 2024 PSPS. See Section 5.2 and 5.5 for more information.
2 Phase 3 D.21-06-034, Appendix A, page A9, Section G. MBL and AFN Communities, No. 4, Each electric investor-owned utility must provide proactive notification and impacted zip code information to paratransit agencies that may serve all the known transit- or paratransit-dependent persons that may need access to a CRC during a PSPS.
3 Other Public Safety Partners refers to first/emergency responders at the local, state, and federal level, water, wastewater, and communication service providers, affected CCAs, publicly owned utilities/electrical cooperatives, the CPUC, the California Governor’s Office of Emergency Services, and the California Department of Forestry and Fire Protection.
4 Transmission-level customers receive a GCC live call before de-energization and prior to re-energization.
5 Transmission lines serving impacted Transmission-level Customers and Municipal Utilities may cut across multiple Fire Index Areas (FIAs) and will only be notified when all those FIAs that the line cuts across have been given the All-Clear.

## Table 4
#VALUE!
Table 4: Customer Notification Timeline Summary
| Event Order | Minimum Timeline1 | Notification Sent to: | Approximate Time Sent (PDT) | Message | Notes | Who made the Notification
| Pre-De-energization (Prior) | 72-48 hours | Public Safety Partners** | 07/18/2024 9:46 PM | Priority |  | PG&E
| Pre-De-energization (Prior) | 48-24 hours | Public Safety Partners** | 07/19/2024 9:23 AM | Watch |  | PG&E
| Pre-De-energization (Prior) | 48-24 hours | All Customers*** | 07/19/2024 9:22 AM | Watch |  | PG&E
| Pre-De-energization (Prior) | 24-12 hours | Public Safety Partners** | 07/19/2024 1:27 PM | Watch |  | PG&E
| Pre-De-energization (Prior) | 24-12 hours | All Customers*** | 07/19/2024 1:27 PM | Watch |  | PG&E
| Pre-De-energization (Prior) | 24-12 hours | Public Safety Partners** | 07/19/2024 10:05 PM | Watch |  | PG&E
| Pre-De-energization (Prior) | 24-12 hours | All Customers*** | 07/19/2024 10:06 PM | Watch |  | PG&E
| Pre-De-energization (Prior) | 4-1 hours | Public Safety Partners** | 07/20/2024 8:07 AM | Warning |  | PG&E
| Pre-De-energization (Prior) | 4-1 hours | All Customers*** | 07/20/2024 8:08 AM | Warning |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Public Safety Partners** | 07/20/2024 2:59 PM | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Public Safety Partners** | 07/20/2024 3:38 PM | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Public Safety Partners** | 07/20/2024 3:53 PM | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Public Safety Partners** | 07/20/2024 4:09 PM | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | Public Safety Partners** | 07/20/2024 9:45 PM | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | All Customers*** | 07/20/2024 2:59 PM | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | All Customers*** | 07/20/2024 3:38 PM | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | All Customers*** | 07/20/2024 3:53 PM | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | All Customers*** | 07/20/2024 4:09 PM | Power Off |  | PG&E
| Initiation (During) | When De-energization is initiated (Power Off) | All Customers*** | 07/20/2024 9:45 PM | Power Off |  | PG&E
| Initiation (During) | Immediately before re-energization | Public Safety Partners** | 07/20/2024 7:47 PM | Inspecting/Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization | All Customers*** | 07/20/2024 7:47 PM | Inspecting/Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization | Public Safety Partners** | 07/20/2024 9:18 PM | Inspecting/Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization | All Customers*** | 07/20/2024 9:18 PM | Inspecting/Weather All-Clear |  | PG&E
| Initiation (During) | Immediately before re-energization | Public Safety Partners** | 07/21/2024 8:00 AM | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization | All Customers*** | 07/21/2024 8:00AM | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization | Public Safety Partners** | 07/21/2024 9:20 AM | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization | All Customers*** | 07/21/2024 9:20 AM | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization | Public Safety Partners** | 07/21/2024 10:20 AM | ETOR Update |  | PG&E
| Initiation (During) | Immediately before re-energization | All Customers*** | 07/21/2024 10:20 AM | ETOR Update |  | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 07/20/2024 4:10 PM | Restore | First initial Restoration Notification sent. | PG&E
| Restoration (After) | After re-energization was completed | Public Safety Partners** | 07/20/2024 11:46 PM | Restore | Last Restoration Notification sent. | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 07/20/2024 4:10 PM | Restore | First initial Restoration Notification sent. | PG&E
| Restoration (After) | After re-energization was completed | All Customers*** | 07/20/2024 11:46 PM | Restore | Last Restoration Notification sent. | PG&E
| Cancellation | Cancellation within 2-hours of decision to cancel | Public Safety Partners** | 07/19/2024 9:15 PM | Cancel | Only Public Safety Partners removed from scope received the cancel notification. The decision to descope these customers was made at 8:49 PM PDT on 7/19/2024. | PG&E
| Cancellation | Cancellation within 2-hours of decision to cancel | All Customers*** | 07/19/2024 9:15 PM | Cancel | Only Customers removed from scope received the cancel notification. The decision to descope these customers was made at 8:49 PM PDT on 7/19/2024. | PG&E
| Cancellation | Cancellation within 2-hours of decision to cancel | Public Safety Partners** | 07/20/2024 9:58 PM | Cancel | Only Public Safety Partners removed from scope received the cancel notification. The decision to descope these customers was made at 9:27 PM PDT on 07/20/2024. | PG&E
| Cancellation | Cancellation within 2-hours of decision to cancel | All Customers*** | 07/20/2024 9:58 PM | Cancel | Only Customers removed from scope received the cancel notification. The decision to descope these customers was made at 9:27 PM PDT on 07/20/2024. | PG&E
| Cancellation | Cancellation within 2-hours of decision to cancel | All Customers*** | 07/20/2024 9:58 PM | Cancel | Only Customers removed from scope received the cancel notification. The decision to descope these customers was made at 9:27 PM PDT on 07/20/2024. | PG&E
*A subset of Public Safety Partners, including Tribes, cities, counties, and community choice aggregators
**A subset of Public Safety Partners, including water, wastewater, and communication service providers
***All Customers, including MBL program customers and SIV customers
1 D.19-05-042, Appendix A, Timing of Notification.

## Table 5
#VALUE!
Table 5: Notifications to Customers where Positive or Affirmative Notification was Attempted1
| Designation | Total Number of customers2 | Notification Attempts Made3 | Timing of Attempts4 (PDT) | Who made the Notification Attempt | Successful Positive Notification5
| MBL6 | 953 | 953 Watch Notifications | 07/19/2024 9:22 AM | PG&E | 889 Watch Notifications
| MBL7 | 953 | 395 Warning Notifications | 07/19/2024 1:45 PM | PG&E | 20 Warning Notifications
| MBL8 | 953 | 1,348 Overall Notifications | 07/19/2024 9:22 AM | PG&E | 909 Overall Notifications
| MBL behind a master meter7 | 16 | 16 Watch Notifications | 07/19/2024 9:23 AM | PG&E | 14 Watch Notifications
| MBL behind a master meter8 | 16 | 7 Warning Notifications | 07/20/2024 8:09 AM | PG&E | 3 Warning Notifications
| MBL behind a master meter9 | 16 | 23 Overall Notifications | 07/19/2024 9:23 AM | PG&E | 17 Overall Notifications
| SIV | 84 | 84 Watch Notifications | 07/19/2024 9:22 AM | PG&E | 84 Watch Notifications
| SIV | 84 | 39 Warning Notifications | 07/20/2024 8:08 AM | PG&E | 7 Warning Notifications
| SIV | 84 | 123 Overall Notifications | 07/19/2024 9:22 AM | PG&E | 91 Overall Notifications
1 Counts of Notification Attempts Made will not reflect the actual total of customers notified as both MBL and SIV customers can appear in both subset groups.
2 Total number of customers notified where notification was attempted. Count includes customers that may have been removed from scope or received Cancellation Notifications prior to de-energization, but still received Watch and/or Warning notifications.
3 Count of Warning Notifications includes doorbell rings and Live Agent phone calls.
4 Initial start time notification was sent.
5 PG&E considers successful positive notifications as those in which the notification was successfully delivered to the customer (i.e., no bounce back) and the customer acknowledges receipt of the notification.
6 Residential tenants of master-metered customers can also qualify for Medical Baseline quantities. The Medical Baseline category for the purposes of Table 5 does not include MBL program customers who are master meter tenants.
7 PG&E has additional processes in place to ensure MBL customers are notified. Master meter tenants are contacted directly to be considered a positive notification. Contacting the property or building manager does not count as a positive notification.

## Table 6
#VALUE!
Table 6: Outcomes of Notifications to De-energized Medical Baseline Program Customers
| Count | Type of Notifications to De-energized MBL Customers1 | Description
| 9 | Total De-energized MBL Program Customers | The number of customers de-energized who participate in PG&E’s MBL Program
| 9 | Total Notifications Attempted / Sent | The total sum of automated notifications attempted via call, text, and e-mail, in-person doorbell ring visit attempts and/or Live Agent phone calls.
| 0 | Total Notifications Not Attempted / Sent | Total MBL program customers de-energized that PG&E did not attempt to notify.
| 9 | Total Notifications Delivered | The total sum of automated notifications sent via call, text, and e-mail.
| 0 | Total Notifications Not Delivered | Total MBL program customers de-energized whose notification was not delivered.
| 4 | Total Notifications Initially Acknowledged | The total sum of automated notifications sent via call, text and email where notification was acknowledged.
| 16 | Total In-Person Visits/Doorbell Rings and Live Agent Phone Calls | Total attempted doorbell ring for impacted MBL program customers where PG&E made contact with the customer (either in person or via phone call in advance of visit) or left a door hanger.2 This includes call attempts made by Live Agent representatives to MBL program customers that had not yet confirmed receipt of their automated notification or answered the door during PG&E’s in-person visit. Refer to Table 7 for the detailed breakdown of this category.
| 9 | Total Notifications Received | Customers who acknowledged their notification by taking one of the following actions: answered an automated or Live Agent phone call, responded to a text message, opened an e-mail, or greeted an in-person doorbell ring (excludes voicemails left, text message delivered only and not confirmed, door hanger left).
| 0 | Total Notifications Not Received | Total MBL program customers who did not confirm receipt / acknowledge their automated notifications, Live Agent phone calls or in-person doorbell ring. Customers who did not answer a doorbell ring were left a door hanger.
1 Based on SPID.
2 Customers may have confirmed receipt of their notifications in multiple channels (e.g., automated notification and/or doorbell ring); therefore, the counts of total attempted and successful notifications are not mutually exclusive.

## Table 7
#VALUE!
Table 7: Count and Type of Additional Notifications to De-energized Medical Baseline Program Customers
| Count | Type of Additional Notifications to Impacted Medical Baseline Customers1 | Description
| 6 | Total In-Person Visits / Doorbell Rings | Doorbell ring attempts to impacted MBL program customers where PG&E made contact with the customer (either in person or via phone call in advance of visit) or left a door hanger.2
| 10 | Live Agent Phone Calls | Calls made by Live Agent representatives to MBL program customers that had not yet confirmed receipt of their automated notification or answered the door during PG&E’s in-person visit.
1 Based on SPID.
2 Customers may have confirmed receipt of their notifications in multiple channels (e.g., automated notification and/or doorbell ring); therefore, the counts of total attempted and successful notifications are not mutually exclusive.

## Table 8
#VALUE!
Table 8: Notification Failure Causes
| Notifications Sent to | Notification Failure Description | Number of Failures | Explanation of Failure
| Public Safety Partners excluding Critical Facilities and Infrastructure1 | Entities who did not receive 48-to 72-hour priority notification | 0 2 | No failures.
| Public Safety Partners excluding Critical Facilities and Infrastructure2 | Entities who did not receive 24-to 48-hour watch notification | 0 | No failures.
| Public Safety Partners excluding Critical Facilities and Infrastructure3 | Entities who did not receive 4-to 24-hour warn notification | 0 | No failures.
| Public Safety Partners excluding Critical Facilities and Infrastructure4 | Entities who did not receive 1–4-hour imminent notification | 0 | No failures.
| Public Safety Partners excluding Critical Facilities and Infrastructure5 | Entities who did not receive any notifications before de-energization | 0 | No failures.
| Public Safety Partners excluding Critical Facilities and Infrastructure6 | Entities who were not notified immediately before re-energization | 0 | No failures.
| Public Safety Partners excluding Critical Facilities and Infrastructure7 | Entities who did not receive cancellation notification within two hours of the decision to cancel | 0 | No failures.
| Critical Facilities and Infrastructure3 | Facilities who did not receive 48-to 72-hour priority notification | 0 4 | No failures.
| Critical Facilities and Infrastructure4 | Facilities who did not receive 1–4-hour imminent notification | 0 | No failures.
| Critical Facilities and Infrastructure5 | Facilities who did not receive any notifications before de-energization | 0 | No failures.
| Critical Facilities and Infrastructure6 | Facilities who were not notified at de-energization initiation | 1 | This transmission-level facility was not notified at de-energization initiation and when re-energization was complete, due to a human error on manual process.
| Critical Facilities and Infrastructure7 | Facilities who were not notified immediately before re-energization | 0 | No failures.
| Critical Facilities and Infrastructure8 | Facilities who were not notified when re-energization is complete | 1 | This transmission-level facility was not notified at de-energization initiation and when re-energization is complete, due to human error on a manual process.
| Critical Facilities and Infrastructure9 | Facilities who did not receive cancellation notification within two hours of the decision to cancel | 0 | No failures.
| All other affected customers | Customers who did not receive 24–48-hour priority notifications | 0 | No failures.
| All other affected customers | Customers who did not receive 1–4-hour imminent notifications | 0 | No failures.
| All other affected customers | Customers who did not receive any notifications before de-energization | 0 | No failures.
| All other affected customers | Customers who were not notified at de-energization initiation | 1 (no MBL) | This customer was impacted by a data error that caused them to miss all post-outage notifications. This issue was resolved with a mapping correction.
| All other affected customers | Customers who were not notified immediately before re-energization | 1 (no MBL) | This customer was impacted by a data error that caused them to miss all post-outage notifications. This issue was resolved with a mapping correction.
| All other affected customers | Customers who were not notified when re-energization is complete | 1 (no MBL) | This customer was impacted by a data error that caused them to miss all post-outage notifications. This issue was resolved with a mapping correction.
| All other affected customers | Customers who did not receive cancellation notification within two hours of the decision to cancel | 0 | No failures.
1 Only includes Tribes, cities, counties, and CCAs.
2 48-72-hour notifications were sent shortly after EOC activation. See Section 5.2 and 5.5 for additional detail.
3 Includes Public Safety Partners who are critical facilities and infrastructure customers.
4 48-72-hour notifications were sent shortly after EOC activation. See Section 5.2 and 5.5 for additional detail.

## Table 9
#VALUE!
Table 9: PSPS Portal Time & Date for Map Sharing
| Date | Time PDF and GIS Maps Shared
| 2024-07-18 | 21:27 PDT
| 2024-07-19 | 8:18 PDT
| 2024-07-19 | 12:48 PDT
| 2024-07-19 | 21:00 PDT
| 2024-07-19 | 4:55 PDT
| 2024-07-20 | 21:38 PDT

## Table 10
#VALUE!
Table 10: PSPS Notifications Submitted to Cal OES
| Date | Time PDF and GIS Maps Shared
| 2024-07-18 | 20:14 PDT
| 2024-07-19 | 07:20 PDT
| 2024-07-19 | 13:09 PDT
| 2024-07-19 | 15:24 PDT
| 2024-07-19 | 21:08 PDT
| 2024-07-20 | 06:53 PDT
| 2024-07-20 | 15:17 PDT
| 2024-07-20 | 15:54 PDT
| 2024-07-20 | 20:06 PDT
| 2024-07-20 | 21:29 PDT
| 2024-07-21 | 07:18 PDT
| 2024-07-21 | 10:37 PDT

## Table 11
#VALUE!
Table 11: PSPS Notifications Submitted to Cal CPUC
| Date | Time PDF and GIS Maps Shared
| 2024-07-18 | 18:49 PDT
| 2024-07-19 | 21:30 PDT
| 2024-07-20 | 08:30 PDT
| 2024-07-20 | 15:13 PDT
| 2024-07-20 | 16:03 PDT
| 2024-07-20 | 20:13 PDT
| 2024-07-20 | 22:06 PDT
| 2024-07-20 | 22:25 PDT
| 2024-07-20 | 22:29 PDT
| 2024-07-20 | 22:52 PDT
| 2024-07-21 | 10:54 PDT

## Table 12
#VALUE!
Table 12: Customer Notifications Based on Language Preference
| Language | Total Notifications1 | Percent
| English | 311741 | 97.34%
| Spanish | 8218 | 2.57%
| Chinese (Mandarin & Cantonese) | 168 | 0.05%
| Korean | 60 | 0.02%
| Vietnamese | 48 | 0.02%
| Hindi | 24 | 0.01%
| Portuguese | 18 | 0.01%
| Total | 320277 | 100%
1 Total notifications do not include doorbell rings and Live Agent phone calls.

## Table 13
#VALUE!
Table 13: Call Center Support Services1
| Total Calls Handled | PSPS Calls Handled | Average Response Time for PSPS-related Calls (seconds) | Number of calls handled by Call Center Translation Services | Number of languages Supported by Call Center Translation Services
| 28641 | 509 | 43 | 789 | 240
1 Metrics are provided from July 18, 2024, through July 21, 2024.

## Table 14
#VALUE!
Table 14: Generators Available for Critical Facilities and Infrastructure Customers
| Generator Type | Number of Units | Individual Size (MW) | Run Time (Hrs.)1 | Description
| Diesel Generator | 3 | 0.032 | 31 | 3 units on reserve in Sacremento
| Diesel Generator | 1 | 0.065 | 31 | 1 unit on reserve in San Leandro
| Diesel Generator | 1 | 0.07 | 31 | 1 unit on reserve in Sacramento
| Diesel Generator | 8 | 0.1 | 27 | 8 units on reserve in Sacramento
| Diesel Generator | 2 | 0.125 | 24 | 2 units on reserve in San Leandro
| Diesel Generator | 9 | 0.2 | 24 | 8 units on reserve in San Leandro. 1 unit on reserve in Sacramento.
| Diesel Generator | 3 | 0.275 | 22 | 3 units on reserve in Sacramento
| Diesel Generator | 2 | 0.57 | 24 | 2 units on reserve in San Leandro
| Diesel Generator | 2 | 1.5 | 10 | 2 units on reserve in Benecia
| Diesel Generator | 8 | 1 | 31 | 5 units on reserve at Sacramento. 3 units pre-stagged at ICU Hospital.
| Diesel Generator | 6 | 1.14 | 22 | 6 units on reserve in San Leandro
| Diesel Generator | 1 | 2 | 35 | 1 unit on reserve in Sacramento
1 Estimated based on a 75% load. Barring mechanical failure and refueling the temporary generators have the ability to operate continuously throughout a typical PSPS.

## Table 15
#VALUE!
Table 15: CFI Customers Energized with Backup Generation Customers Energized with Backup Generation
| County | Site Type | Generation Deployed (MW) | Duration of Operation | Reason Deployed
| Contra Costa | Byron Airport | 0.2 | 4 hours 50 minutes | Public Safety – airport cannot operate without their fire suppression system.
| Contra Costa | Byron Airport | 0.1 | 5 hours 5 minutes | Public Safety – airport cannot operate without their fire suppression system.

## Table 16
#VALUE!
Table 16: Number and Nature of Complaints due to the July 20 – 21, 2024, PSPS
| Nature of Complaints | Number of Complaints
| Communications/Notifications Including, but not limited to complaints regarding lack of notice, excessive notices, confusing notice, false alarm notice, problems with getting up-to-date information, inaccurate information provided, not being able to get information in the prevalent languages and/or information accessibility, complaints about website, Public Safety Partner Portal, Representational State Transfer (REST)/Digital Asset Manager (DAM) sites (as applicable). | 6
| PSPS Frequency/Duration Including, but not limited to complaints regarding the frequency and/or duration of PSPS, including delays in restoring power, scope of PSPS and dynamic of weather conditions. | 9
| Safety/Health Concern Including, but not limited to complaints regarding difficulties experienced by AFN/MBL populations, traffic accidents due to non-operating traffic lights, inability to get medical help, well water or access to clean water, inability to keep property cool/warm during outage raising health concern. | 13
| General PSPS Dissatisfaction/Other Including, but not limited to complaints about being without power during PSPS and related hardships such as food loss, income loss, inability to work/attend school, plus any PSPS-related complaints that do not fall into any other category. | 32
| Outreach/Assistance Including, but not limited to complaints regarding CRCs, community crew vehicles, backup power, hotel vouchers, other assistance provided by utility to mitigate impact of PSPS. | 2

## Table 17
#VALUE!
Table 17: Weather All-Clear Times
| All-Clear Zones | Weather All-Clear Date and Time
| TP-05 | 07/20/2024 19:30 PDT
| 530A (TP-04) | 07/20/2024 20:40 PDT

## Table 18
#VALUE!
Table 18: Lessons Learned from the PSPS
| Issue | Discussion | Resolution
| Customer Notification | A customer was impacted by a data issue that caused them to miss all post-outage notifications. | We have corrected the customer's mapping to prevent future missed notifications and continue to refine our process.
| Customer Notification | A transmission-level facility was not notified at de-energization initiation and when re-energization was complete, due to an error on a manual process. | We plan to review processes with responsible personnel and consider additional training.

## Table 19
#VALUE!
Table 19: Maximum Wind Gusts Recorded July 20 – 21, 2024, in Impacted Counties
| County | Maximum Wind Gust (mph) | Station ID | Station Name
| Alameda | 42 | AATC1 | Altamont
| Contra Costa | 58 | 234PG | Black Diamond Mines
| San Joaquin | 43 | CF123 | I-580 – West of SR-132

## Table A-1.1
#VALUE!
Table A-1.1: Factors Considered in the Decision to Shut Off Power for Each Distribution Circuit De-energized During the July 20 – 21, 2024 PSPS
| Circuit Name | Time Place | Forecast ws_ mph | Forecast ws_ mph_ 50m | Forecast wg_ ec_ mph | Forecast temp_2m_f | Forecast flame_ length_ ft_2hr | Forecast rate_ of_ spread_chhr_2hr | Forecast area_ acres_ 8hr | Forecast rh_ 2m | Forecast vpd2m_mb | Forecast prob_cat | Forecast dfm_ 10hr | Forecast dfm_ 100 hr | Forecast dfm_ 1000 hr | Forecast lfm_ herb | Forecast lfm_ woody | Forecast lfm_ chamise_new | Forecast sum_ tree ovr | Forecast prob_ ignition | Forecast cfpd | Agency HWW | Agency HWA | Agency RFW | Agency GACC_High Risk | Observed Observed ws_ mph | Observed Observed wg_ mph | Observed Observed temp_f | Observed Observed RH_% | Observed Observed ws_ mph_ AC | Observed Observed wg_ mph_ AC | Observed Observed temp_f_AC | Observed Observed RH_%_AC | Observed open_psps_tags | Observed Tx impacts_yes_no | Observed PSPS Potential Risk Consequence | Observed PSPS Potential Benefit
| BRENTWOOD 2105 | TP04 | 26 | 34 | 50 | 103 | 10.5 | 135.4 | 14035 | 12.2 | 63.2 | 0.939 | 0.033 | 0.065 | 0.058 | 30 | 82 | 71 | 56.7 | 0.00336 | 21.8 | No | No | No | No | 25 | 33 | 104 | 17 | 28 | 37 | 92 | 31 | Yes | No | 0.23968 | 370.3
| HERDLYN 1102 | TP04 | 31 | 38 | 49 | 102 | 11.7 | 171.4 | 18168 | 13.2 | 60.7 | 0.897 | 0.032 | 0.057 | 0.054 | 30 | 80 | 73 | -99 | 0.00254 | 16.4 | No | No | No | No | 32 | 37 | 101 | 17 | 30 | 37 | 91 | 22 | Yes | No | 0.16798 | 101.5
| VASCO 1102 | TP05 | 19 | 24 | 35 | 95 | 12.9 | 193.1 | 36589 | 16.8 | 46.9 | 0.936 | 0.041 | 0.078 | 0.072 | 30 | 77 | 74 | 994.3 | 0.0004 | 2.5 | No | No | No | No | 32 | 37 | 98 | 20 | 30 | 35 | 81 | 26 | Yes | No | 0.12158 | 1031.4
| VASCO 1103 | TP05 | 23 | 30 | 40 | 96 | 12.7 | 197.4 | 28324 | 16.4 | 49.1 | 0.901 | 0.043 | 0.087 | 0.076 | 30 | 81 | 73 | -99 | 0.00058 | 2.8 | No | No | No | No | 32 | 37 | 98 | 20 | 30 | 35 | 81 | 34 | Yes | No | 0.11736 | 1228.4

## Table A-1.2
#VALUE!
Table A-1.2: Description, Units, and Value provided for Factors Considered in the Decision to Shut Off Power for Each Distribution Circuit De-energized During the July 20 – 21
| Forecast / Agency / Observed | Value | Name | Unit | Value Provided | Description
| Agency | HWW | High Wind Warning | N/A | Yes/No during event | High Wind Warning from the Federal National Weather Service.
| Agency | HWA | High Wind Advisory | N/A | Yes/No during event | High Wind Advisory from the Federal National Weather Service.
| Agency | RFW | Red Flag Warning | N/A | Yes/No during event | Red Flag Warning from the Federal National Weather Service.
| Agency | GACC_HighRisk | GACC High Risk | N/A | Yes/No during event | High Risk issued by the Federal North or South Operations Predictive Services.
| Forecast | prob_cat | Fire Potential Index (FPI) | probability outputs | max | Fire Potential Index (FPI) Model Output - Probability of a catastrophic fire if an ignition were to occur. FPI component of the CFPD model.
| Forecast | dfm_10hr | Dead Fuel Moisture Content 10 hrs | fuel moisture fraction | min | Dead Fuel Moisture in 10-hour fuel moisture class. Can be scaled to percentage by multiplying by 100.
| Forecast | dfm_100hr | Dead Fuel Moisture Content 100 hrs | fuel moisture fraction | min | Dead Fuel Moisture in 100-hour moisture class. Can be scaled to percentage by multiplying by 100.
| Forecast | dfm_1000hr | Dead Fuel Moisture Content 1000 hrs | fuel moisture fraction | min | Dead Fuel Moisture in 1000-hour moisture class. Can be scaled to percentage by multiplying by 100.
| Forecast | lfm_herb | Live Fuel Moisture Content-herbacous | % | min | Live Fuel Moisture Percentage of herbaceous plant species. (% of species that is comprised of water)
| Forecast | lfm_woody | Live Fuel Moisture Content-woody | % | min | Live Fuel Moisture Percentage of woody plant species. (% of species that is comprised of water)
| Forecast | lfm_chamise_new | Live Fuel Moisture Content-shrub | % | min | Live Fuel Moisture Percentage of Chamise (shrub) plant species. (% of species that is comprised of water)
| Forecast | sum_tree_ovr | Tree Overstike | ft | max | Sum of tree overstrike in a 2 x 2 km grid cell area in ft.
| Forecast | prob_ignition | Ignition Probability Weather (IPW) Model Output | Probability | max | Ignition Probability Weather (IPW) Model Output - Probability of Ignition based on the probability of outages by cause. Ignition component of the CFPD model. Ignition Probability Weather Model - A model that provides estimates of the probability of an ignition given an outage on an hourly basis.
| Forecast | cfpd | Catastrophic Fire Probability (CFPD) | Scaled Probability | max | The product of probability of catastrophic fire (Prob_Cat) and IPW - probability of ignition (prob_ignition). This product is called the (CFPD) Catastrophic Fire Probability distribution model. Scaled by 1000 to covert to an integer value.
| Observed | Observed ws_mph | Observed Sustained Wind Speed during Event | mph | max | The maximum sustained wind speed recorded by weather stations mapped to each circuit from planned de-energization time to anticipated all-clear time.
| Observed | Observed wg_mph | Observed Peak Wind Gust during Event | mph | max | The maximum wind gust recorded by weather stations mapped to each circuit from planned de-energization time to anticipated all- clear time.
| Observed | Observed temp_f | Observed Temperature during Event | degrees F | max | The maximum temperature recorded by weather stations mapped to each circuit from planned de-energization time to anticipated all-clear time.
| Observed | Observed RH_% | Observed Relative Humidity During Event | % | min | Minimum relative humidity recorded by all weather stations mapped to each circuit from planned de-energization time to anticipated all-clear time.
| Observed | Observed ws_mph_AC | Observed Sustained Wind Speed at All Clear | mph | max | The maximum sustained wind speed recorded by weather stations mapped to each circuit at the all-clear time.
| Observed | Observed wg_mph_AC | Observed Peak Wind Gust at All Clear | mph | max | The maximum wind gust recorded by weather stations mapped to each circuit at the all-clear time.
| Observed | Observed temp_f_AC | Observed Temperature at All Clear | degrees F | max | The maximum temperature recorded by weather stations mapped to each circuit at the all-clear time.
| Observed | Observed RH_%_AC | Observed Relative Humidity at All Clear | % | min | Minimum relative humidity recorded by all weather stations mapped to each circuit at the all-clear time.
| Observed | open_psps_tags | Open PSPS Qualified Tags | N/A | Yes/No During Event | PSPS-Qualified Tags include P1 (tree represents an immediate risk) and P2 (tree is damaged or diseased and could fall into nearby power lines) tree tags and Electric Corrective tags (Priority A - emergency, B - urgent, and E/F - risk-based).
| Observed | Tx_impacts_yes_no | Impacted by Transmission | N/A | Yes/No During Event | Distribution lines that would have been de-energized due to de- energization of upstream transmission lines, regardless of whether those distribution lines would have also been de- energized due to direct distribution PSPS.
| Forecast | ws_mph | Sustained wind speeds | mph | max | Sustained windspeed in miles per hour at 10 meters above ground level.
| Forecast | ws_mph_50m | Sustained wind speeds at 50 m | mph | max | Sustained windspeed in miles per hour at 50 meters above ground level.
| Forecast | wg_ec_mph | Forecasted Peak Wind Gust | mph | max | Wind gust in miles per hour at 10 meters above ground level.
| Forecast | temp_2m_f | Temperature | degrees F | max | Temperature in Fahrenheit at 2 meters above ground level.
| Forecast | flame_length_ft_2hr | Flame length | ft | max | Flame length in feet on fire front for first 2 hours of fire spread simulation from Technosylva.
| Forecast | rate_of_spread_chhr_2hr | Rate of spread | chains/hr | max | Rate of fire spread in chains per hour for first 2 hours of fire spread simulation from Technosylva.
| Forecast | area_acres_8hr | Acres burned | acres | max | Acres burned in the 8-hour fire spread simulation from Technosylva.
| Forecast | rh_2m | Relative Humidity | % | min | Relative Humidity in percent at 2 meters above ground level.
| Forecast | vpd2m_mb | Vapor Pressure Deficit | mb | max | Vapor Pressure Deficit in millibar at 2m above surface.

## Table A-2.1
#VALUE!
Table A-2.1: Factors Considered in the Decision to Shut Off Power for Each Transmission Circuit De-energized During the July 20 – 21, 2024 PSPS
| Forecast Circuit Name | Forecast ws_mph | Forecast ws_mph_50m | Forecast wg_ec_mph | Forecast temp_2m_f | Forecast flame_length_ft_2hr | Forecast rate_of_spread_chhr_2hr | Forecast area_acres_8hr | Forecast rh_2m | Forecast vpd2m_mb | Agency HWW | Agency HWA | Agency RFW | Agency GACC_High Risk | Forecast prob_cat | Forecast dfm_10hr | Forecast dfm_100hr | Forecast dfm_1000hr | Forecast lfm_herb | Forecast lfm_woody | Forecast lfm_chamise_new | Forecast sum_tree_ovr | Forecast OA | Forecast cdft | Observed Observed ws_mph | Observed Observed wg_mph | Observed Observed temp_f | Observed Observed RH_% | Observed Observed ws_mph_AC | Observed Observed wg_mph_AC | Observed Observed temp_f_AC | Observed Observed RH_%_AC | Observed High Fire Risk Area (Y/N) | Observed High Risk Vegetation Present on Circuit (Y/N) | Observed Tx_impacts_yes_no | PSPS Risk vs. Benefit PSPS Potential Risk Consequence | PSPS Risk vs. Benefit PSPS Potential Benefit
| Vasco-Herdlyn 60kV | 29.1 | No | 50 | 103 | 12 | 173.3 | 25664 | 21 | 61 | No | No | No | No | 0.66 | 0.04 | 0.08 | 0.07 | 30 | No | 74 | No | 0.018 | 12 | No | No | No | No | No | No | No | No | No | No | Yes | 0.10486 | 765.6
| Tesla-Stockton CoGen Jct | 32.5 | No | 45 | 101 | 18 | 135.9 | 11560 | 17 | 58 | No | No | No | No | 0.68 | 0.03 | 0.05 | 0.05 | 30 | No | 74 | No | 0.027 | 36 | No | No | No | No | No | No | No | No | No | No | Yes | 0.1047 | 63.8
| US Windpower 60 kV tap | 23.5 | No | 40.8 | 90 | 12 | 173.3 | 21729 | 26 | 37 | No | No | No | No | 0.53 | 0.05 | 0.1 | 0.08 | 30 | No | 76 | No | No | No | No | No | No | No | No | No | No | No | No | No | Yes | 0.1047 | 338.2

## Table A-2.2
#VALUE!
Table A-2.2: Description, Units, and Value provided for Factors Considered in the Decision to Shut Off Power for Each Transmission Circuit De-energized During the July 20 – 21, 2024 PSPS
| Forecast / Agency / Observed | Value | Name | Unit | Value Provided | Description
| Agency | HWW | High Wind Warning | N/A | Yes/No during event | High Wind Warning from the Federal National Weather Service.
| Agency | HWA | High Wind Advisory | N/A | Yes/No during event | High Wind Advisory from the Federal National Weather Service.
| Agency | RFW | Red Flag Warning | N/A | Yes/No during event | Red Flag Warning from the Federal National Weather Service.
| Agency | GACC_HighRisk | GACC High Risk | N/A | Yes/No during event | High Risk issued by the Federal North or South Operations Predictive Services.
| Forecast | ws_mph | Sustained wind speeds | mph | max | Sustained windspeed in miles per hour at 10 meters above ground level.
| Forecast | ws_mph_50m | Sustained wind speeds at 50 m | mph | max | Sustained windspeed in miles per hour at 50 meters above ground level.
| Forecast | wg_ec_mph | Gust wind speeds | mph | max | Wind gust in miles per hour at 10 meters above ground level.
| Forecast | temp_2m_f | Temperature | degrees F | max | Temperature in Fahrenheit at 2 meters above ground level.
| Forecast | flame_length_ft_2hr | Flame length | ft | max | Flame length in feet on fire front for first 2 hours of fire spread simulation from Technoslyva.
| Forecast | rate_of_spread_chhr_2hr | Rate of spread | chains/hr | max | Rate of fire spread in chains per hour for first 2 hours of fire spread simulation from Technoslyva.
| Forecast | area_acres_8hr | Acres burned | acres | max | Acres burned in the 8-hour fire spread simulation from Technosylva.
| Forecast | rh_2m | Relative Humidity | % | min | Relative Humidity in percent at 2 meters above ground level.
| Forecast | vpd2m_mb | Vapor Pressure Deficit | mb | max | Vapor Pressure Deficit in millibar at 2m above surface
| Forecast | prob_cat | Fire Potential Index (FPI) | probability outputs | max | Fire Potential Index (FPI) Model Output - Probability of a catastrophic fire if an ignition were to occur. FPI component of the CFPD model.
| Forecast | dfm_10hr | Dead Fuel Moisture Content 10 hrs (%) | fuel moisture fraction | min | Dead Fuel Moisture in 10-hour fuel moisture class. Can be scaled to percentage by multiplying by 100.
| Forecast | dfm_100hr | Dead Fuel Moisture Content 100 hrs (%) | fuel moisture fraction | min | Dead Fuel Moisture in 100-hour moisture class. Can be scaled to percentage by multiplying by 100.
| Forecast | dfm_1000hr | Dead Fuel Moisture Content 1000 hrs (%) | fuel moisture fraction | min | Dead Fuel Moisture in 1000-hour moisture class. Can be scaled to percentage by multiplying by 100.
| Forecast | lfm_herb | Live Fuel Moisture Content-herbacous | % | min | Live Fuel Moisture Percentage of herbaceous plant species. (% of species that is comprised of water)
| Forecast | lfm_woody | Live Fuel Moisture Content-woody | % | min | Live Fuel Moisture Percentage of woody plant species. (% of species that is comprised of water)
| Forecast | lfm_chamise_new | Live Fuel Moisture Content-shrub | % | min | Live Fuel Moisture Percentage of Chamise (shrub) plant species. (% of species that is comprised of water)
| Forecast | sum_tree_ovr | Tree Overstike | ft | max | Sum of tree overstrike in a 2 x 2 km grid cell area in ft.
| Forecast | OA | Transmission Operability Assessment (OA) | Probability | max | Ignition Probability Weather (IPW) Model Output - Probability of Ignition based on the probability of outages by cause. Ignition component of the CFPD model. Ignition Probability Weather Model - A model that provides estimates of the probability of an ignition given an outage on an hourly basis
| Forecast | cfpt | Catastrophic Fire Potential (CFPT) | Scaled Probability | max | The product of probability of catastrophic fire (Prob_Cat) and IPW - probability of ignition (prob_ignition). This product is called the (CFPD) Catastrophic Fire Probability distribution model. Scaled by 1000 to covert to an integer value.
| Observed | Observed ws_mph | Observed Sustained Wind Speed during Event | mph | max | The maximum sustained wind speed recorded by weather stations mapped to each circuit from de-energization time to all-clear time.
| Observed | Observed wg_mph | Observed Wind gust during Event | mph | max | The maximum sustained wind gust recorded by weather stations mapped to each circuit from de-energization time to all-clear time.
| Observed | Observed temp_f | Observed Temperature during event | degrees F | max | The maximum temperature recorded by weather stations mapped to each circuit from de-energization time to all-clear time.
| Observed | Observed RH_% | Observed Relative Humidity During Event | % | min | Minimum relative humidity recorded by all weather stations mapped to each circuit from de-energization time to all-clear time.
| Observed | Observed ws_mph_AC | Observed Sustained Wind Speed at All Clear | mph | max | The maximum sustained wind speed recorded by weather stations mapped to each circuit at the all-clear time.
| Observed | Observed wg_mph_AC | Observed Sustained Wind gust at All Clear | mph | max | The maximum sustained wind gust recorded by weather stations mapped to each circuit at the all-clear time.
| Observed | Observed temp_f_AC | Observed Temperature at All Clear- | degrees F | max | The maximum temperature recorded by weather stations mapped to each circuit at the all-clear time.
| Observed | Observed RH_%_AC | Observed Relative Humidity at All Clear | % | min | Minimum relative humidity recorded by all weather stations mapped to each circuit at the all-clear time.
| Observed | High Fire Risk Area | High Fire Risk Area | N/A | Yes/No During Event | Labeled ‘Yes’ when Circuit goes through High Fire Risk Area.
| Observed | High Risk Vegetation Present on Circuit | High Risk Vegetation Present on Circuit | N/A | Yes/No During Event | High risk vegetation present on the circuit
| Observed | transmission_impacts_yes_no | Impacted by Transmission | N/A | Yes/No During Event | Distribution lines that would have been de-energized due to de-energization of upstream transmission lines, regardless of whether those distribution lines would have also been de-energized due to direct distribution PSPS.
| Observed | PSPS Potential Risk Consequence | PSPS Potential Risk Consequence | MAVF Score | Yes | Measure of the adverse impact to customers due to de-energization.
| Observed | PSPS Potential Benefit | PSPS Potential Benefit | MAVF Score | Yes | Measure of the adverse impact to customers due to a catastrophic fire.

## Table B-1
#VALUE!
Table B-1. Circuits De-Energized During the July 20 – 21, 2024 PSPS
| Distribution / Transmission | Circuit Name | De-Energization Date and Time | All-Clear Date and Time | Restoration Date and Time | Key Communities | HFTD Tier(s) | Total Customers | Residential Customers | Commercial / Industrial Customers | Medical Baseline Customers | AFN other than MBL Customers | Other Customers
| Distribution | BRENTWOOD 2105 | 07/20/2024 15:25 PDT | 07/20/2024 20:40 PDT | 07/20/2024 21:49 PDT | CONTRA COSTA | Partially Outside HFTD, Tier 2 | 60 | 21 | 35 | 3 | 2 | 4
| Distribution | HERDLYN 1102 | 07/20/2024 15:30 PDT | 07/20/2024 20:40 PDT | 07/20/2024 23:16 PDT | CONTRA COSTA, ALAMEDA, SAN JOAQUIN | Outside HFTD | 123 | 70 | 39 | 4 | 13 | 14
| Distribution | VASCO 1102 | 07/20/2024 14:43 PDT | 07/20/2024 19:30 PDT | 07/20/2024 20:58 PDT | ALAMEDA | Outside HFTD | 12 | 8 | 4 | 2 | 0 | 0
| Distribution | VASCO 1103 | 07/20/2024 14:37 PDT | 07/20/2024 19:30 PDT | 07/20/2024 21:00 PDT | ALAMEDA | Outside HFTD | 16 | 11 | 4 | 0 | 2 | 1
| Transmission | Vasco-Herdlyn 60kV | 07/20/2024 15:40 PDT | 07/20/2024 20:40 PDT | 07/21/2024 08:22 PDT | CONTRA COSTA, ALAMEDA | Outside HFTD | 1 | 0 | 0 | 0 | 0 | 0
| Transmission | Tesla-Stockton COGEN Jct 115kV | 07/20/2024 16:09 PDT | 07/20/2024 20:40 PDT | 07/21/2024 08:30 PDT | ALAMEDA, SAN JOAQUIN | Outside HFTD | 0 | 0 | 0 | 0 | 0 | 0
| Transmission | US Windpower Tap | 07/20/2024 15:40 PDT | 07/20/2024 20:40 PDT | 07/21/2024 08:22 PDT | ALAMEDA | Outside HFTD | 0 | 0 | 0 | 0 | 0 | 0
| Total | [6 empty] | 212 | 110 | 82 | 9 | 17 | 19

## Table C-1
#VALUE!
Table C-1. Damages & Hazards Found Within the De-Energized Areas
| Circuit Name | County | Structure Identifier | Tier 2/3 or Non-HFTD | Damage / Hazard | Type of Damage/Hazard | Description of Damage
| Vasco 1103 | Alameda | 103776869 | Non-HFTD | Hazard | Vegetation | Tree branch on line

## Table D-1
#VALUE!
Table D-1. Public Safety Partners Contacted
| Organization/Jurisdiction | Title | HFTD or HFRA Tier1 | Date/Time Contacted
| Alameda County | County Administration | Tier 3, Tier 2 | 07/18/2024 21:41 PDT
| Alameda County | Board President | Tier 3, Tier 2 | 07/18/2024 21:41 PDT
| Alameda County | Board Vice President | Tier 3, Tier 2 | 07/18/2024 21:41 PDT
| Alameda County | County Administrator | Tier 3, Tier 2 | 07/18/2024 21:41 PDT
| Alameda County | County Clerk Recorder | Tier 3, Tier 2 | 07/18/2024 21:41 PDT
| Alameda County | Division Chief | Tier 3, Tier 2 | 07/18/2024 21:42 PDT
| Alameda County | Division Chief of Operations/ Emergency Management | Tier 3, Tier 2 | 07/18/2024 21:41 PDT
| Alameda County | Emergency Medical Services Disaster and WMD Coordinator | Tier 3, Tier 2 | 07/18/2024 21:41 PDT
| Alameda County | Emergency Preparedness Manager | Tier 3, Tier 2 | 07/18/2024 21:41 PDT
| Alameda County | Fire Chief | Tier 3, Tier 2 | 07/18/2024 21:42 PDT
| Alameda County | General | Tier 3, Tier 2 | 07/18/2024 21:42 PDT
| Alameda County | Main Line | Tier 3, Tier 2 | 07/18/2024 21:42 PDT
| Alameda County | Offices of Emergency Services Captain | Tier 3, Tier 2 | 07/18/2024 21:41 PDT
| Alameda County | Office of Emergency Services Emergency Operations Center Lead | Tier 3, Tier 2 | 07/18/2024 21:41 PDT
| Alameda County | President of the Board | Tier 3, Tier 2 | 07/18/2024 21:41 PDT
| Alameda County | Safety & Emergency Preparedness Manager | Tier 3, Tier 2 | 07/18/2024 21:41 PDT
| Alameda County | Senior Emergency Services Coordinator | Tier 3, Tier 2 | 07/18/2024 21:41 PDT
| Alameda County | Sheriff | Tier 3, Tier 2 | 07/18/2024 21:41 PDT
| Alameda County | Superintendent of Water Distribution | Tier 3, Tier 2 | 07/18/2024 21:41 PDT
| Alameda County | Supervisor | Tier 3, Tier 2 | 07/18/2024 21:41 PDT
| Alameda County | Technician | Tier 3, Tier 2 | 07/18/2024 21:41 PDT
| Alameda County | Train Ops | Tier 3, Tier 2 | 07/18/2024 21:42 PDT
| Alameda County | Watch Commander | Tier 3, Tier 2 | 07/18/2024 21:42 PDT
| Alameda County | Water Operations Manager | Tier 3, Tier 2 | 07/18/2024 21:41 PDT
| Alameda County CCA | General | Tier 3, Tier 2 | 07/18/2024 21:41 PDT
| Alameda County Communication Facility | AT&T Services Inc | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/18/2024 21:46 PDT
| Alameda County Communication Facility | Sprint Nextel Corporation | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/18/2024 21:46 PDT
| Alameda County Communication Facility | T-Mobile West Corporation | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/18/2024 21:46 PDT
| Alameda County Communication Facility | T-Mobile West LLC | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/18/2024 21:46 PDT
| Alameda County Communication Facility | TCI Cablevision | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/18/2024 20:31 PDT
| Alameda County Communication Facility | Verizon | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/18/2024 21:46 PDT
| Alameda County Oakland | City Administration | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/19/2024 13:20 PDT
| Alameda County Oakland | Acting Fire Chief | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/19/2024 13:21 PDT
| Alameda County Oakland | Assistant City Administrator | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/19/2024 13:21 PDT
| Alameda County Oakland | Chief of Education & Community Safety | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/19/2024 13:20 PDT
| Alameda County Oakland | City Administrator | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/19/2024 13:21 PDT
| Alameda County Oakland | City Clerk | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/19/2024 13:20 PDT
| Alameda County Oakland | Communications Center | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/19/2024 13:20 PDT
| Alameda County Oakland | Council Member | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/19/2024 13:20 PDT
| Alameda County Oakland | Council President | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/19/2024 13:20 PDT
| Alameda County Oakland | Council Member | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/19/2024 13:20 PDT
| Alameda County Oakland | Council Member At-Large | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/19/2024 13:20 PDT
| Alameda County Oakland | Deputy Mayor | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/19/2024 13:20 PDT
| Alameda County Oakland | Emergency Services Manager | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/19/2024 13:20 PDT
| Alameda County Oakland | Mayor | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/19/2024 13:20 PDT
| Alameda County Oakland | Police Chief (Interim) | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/19/2024 13:21 PDT
| Contra Costa County | City Administration | Tier 3, Tier 2 | 07/18/2024 21:41 PDT
| Contra Costa County | Board Chair | Tier 3, Tier 2 | 07/18/2024 21:41 PDT
| Contra Costa County | Board Vice Chair | Tier 3, Tier 2 | 07/18/2024 21:41 PDT
| Contra Costa County | Chair of the Board | Tier 3, Tier 2 | 07/18/2024 21:41 PDT
| Contra Costa County | Chief of Staff | Tier 3, Tier 2 | 07/18/2024 21:41 PDT
| Contra Costa County | County Administrator | Tier 3, Tier 2 | 07/18/2024 21:41 PDT
| Contra Costa County | County Clerk Recorder | Tier 3, Tier 2 | 07/18/2024 21:41 PDT
| Contra Costa County | Deputy Fire Chief, Mutual Aid Coordinator | Tier 3, Tier 2 | 07/18/2024 21:41 PDT
| Contra Costa County | Duty Officer | Tier 3, Tier 2 | 07/18/2024 21:41 PDT
| Contra Costa County | Duty Officer - 24/7 Staff call line | Tier 3, Tier 2 | 07/18/2024 21:41 PDT
| Contra Costa County | Emergency Manager | Tier 3, Tier 2 | 07/18/2024 21:41 PDT
| Contra Costa County | Emergency Preparedness Manager | Tier 3, Tier 2 | 07/18/2024 21:42 PDT
| Contra Costa County | Fire Chief | Tier 3, Tier 2 | 07/18/2024 21:41 PDT
| Contra Costa County | Fire Chief | Tier 3, Tier 2 | 07/18/2024 21:41 PDT
| Contra Costa County | Office of Emergency Services Warning System | Tier 3, Tier 2 | 07/18/2024 21:41 PDT
| Contra Costa County | Sheriff | Tier 3, Tier 2 | 07/18/2024 21:41 PDT
| Contra Costa County | Supervisor | Tier 3, Tier 2 | 07/18/2024 21:41 PDT
| Contra Costa County Antioch | City Clerk | Tier 2 | 07/18/2024 21:41 PDT
| Contra Costa County Antioch | City Manager | Tier 2 | 07/18/2024 21:41 PDT
| Contra Costa County Antioch | Council Member | Tier 2 | 07/18/2024 21:41 PDT
| Contra Costa County Antioch | Emergency | Tier 2 | 07/18/2024 21:42 PDT
| Contra Costa County Antioch | Mayor | Tier 2 | 07/18/2024 21:41 PDT
| Contra Costa County Antioch | Mayor Pro TEM | Tier 2 | 07/18/2024 21:41 PDT
| Contra Costa County Antioch | Police Chief | Tier 2 | 07/18/2024 21:41 PDT
| Contra Costa County CCA | General | Tier 3, Tier 2 | 07/18/2024 21:41 PDT
| Contra Costa County Communication Facility | AT&T Mobility LLC | Tier 2 | 07/18/2024 21:46 PDT
| Contra Costa County Communication Facility | AT&T Pacific Bell | Tier 2 | 07/18/2024 21:46 PDT
| Contra Costa County Communication Facility | AT&T Services Inc | Tier 2 | 07/18/2024 21:46 PDT
| Contra Costa County Communication Facility | GTE Mobilenet of California LP | Tier 3, Tier 2 | 07/18/2024 21:46 PDT
| Contra Costa County Communication Facility | GTE Mobilenet DBA Verizon Wireless | Tier 2 | 07/18/2024 21:46 PDT
| Contra Costa County Communication Facility | SBA Towers | Tier 2 | 07/18/2024 21:46 PDT
| Contra Costa County Communication Facility | T-Mobile West Corporation | Tier 2 | 07/18/2024 21:46 PDT
| Contra Costa County Communication Facility | T-Mobile West LLC | Tier 2 | 07/18/2024 21:46 PDT
| Contra Costa County Communication Facility | Verizon Wireless | Tier 2 | 07/18/2024 21:46 PDT
| Contra Costa County Other Facility | Contra Costa Water District | Tier 2 | 07/18/2024 21:46 PDT
| Contra Costa County Pittsburg | Chief of Police | Tier 2 | 07/18/2024 21:41 PDT
| Contra Costa County Pittsburg | City Clerk | Tier 2 | 07/18/2024 21:41 PDT
| Contra Costa County Pittsburg | City Manager | Tier 2 | 07/18/2024 21:41 PDT
| Contra Costa County Pittsburg | Council Member | Tier 2 | 07/18/2024 21:41 PDT
| Contra Costa County Pittsburg | Emergency | Tier 2 | 07/18/2024 21:42 PDT
| Contra Costa County Pittsburg | Fire Chief | Tier 2 | 07/18/2024 21:42 PDT
| Contra Costa County Pittsburg | Mayor | Tier 2 | 07/18/2024 21:41 PDT
| Contra Costa County Pittsburg | Non-Emergency | Tier 2 | 07/18/2024 21:42 PDT
| Contra Costa County Pittsburg | Vice Mayor | Tier 2 | 07/18/2024 21:41 PDT
| Fresno County | City Administration | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/18/2024 21:41 PDT
| Fresno County | Board Chair | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/18/2024 21:41 PDT
| Fresno County | Chair of the Board | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/18/2024 21:41 PDT
| Fresno County | City Clerk | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/18/2024 21:41 PDT
| Fresno County | City Manager | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/18/2024 21:42 PDT
| Fresno County | Council Member | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/18/2024 21:41 PDT
| Fresno County | County Administrative Officer | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/18/2024 21:41 PDT
| Fresno County | County Executive Officer | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/18/2024 21:41 PDT
| Fresno County | Emergency | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/18/2024 21:42 PDT
| Fresno County | Emergency Management Specialist | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/18/2024 21:41 PDT
| Fresno County | Facility Services | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/18/2024 21:41 PDT
| Fresno County | Lieutenant | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/18/2024 21:41 PDT
| Fresno County | Medical Health Operational Area Coordinator | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/18/2024 21:41 PDT
| Fresno County | Mayor | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/18/2024 21:41 PDT
| Fresno County | Mayor Pro TEM | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/18/2024 21:41 PDT
| Fresno County | Office of Emergency Services Director of Emergency Services | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/18/2024 21:41 PDT
| Fresno County | Sheriff | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/18/2024 21:41 PDT
| Fresno County | Staff Analyst | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/18/2024 21:41 PDT
| Merced County | County Administration | HFRA | 07/18/2024 21:41 PDT
| Merced County | Battalion Chief | HFRA | 07/18/2024 21:41 PDT
| Merced County | Board Vice Chair | HFRA | 07/18/2024 21:41 PDT
| Merced County | Cal Fire Chief | HFRA | 07/18/2024 21:42 PDT
| Merced County | County Clerk | HFRA | 07/18/2024 21:41 PDT
| Merced County | County Executive Officer | HFRA | 07/18/2024 21:41 PDT
| Merced County | District 4 Supervisor | HFRA | 07/18/2024 21:42 PDT
| Merced County | Duty Chief | HFRA | 07/18/2024 21:41 PDT
| Merced County | Fire Chief | HFRA | 07/18/2024 21:42 PDT
| Merced County | General | HFRA | 07/18/2024 21:41 PDT
| Merced County | Medical Health Operational Area Coordinator | HFRA | 07/18/2024 21:41 PDT
| Merced County | Office of Emergency Services Coordinator | HFRA | 07/18/2024 21:41 PDT
| Merced County | Office of Emergency Services Director | HFRA | 07/18/2024 21:41 PDT
| Merced County | Sheriff | HFRA | 07/18/2024 21:41 PDT
| Merced County | Supervisor | HFRA | 07/18/2024 21:41 PDT
| Merced County | Supervisor District 1 | HFRA | 07/18/2024 21:41 PDT
| Merced County | Unit Chief | HFRA | 07/18/2024 21:41 PDT
| Merced County Communication Facility | AT&T Mobility LLC | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/19/2024 13:27 PDT
| Merced County Communication Facility | AT&T Services Inc | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/18/2024 21:46 PDT
| Merced County Communication Facility | Crown Castle International | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/19/2024 13:27 PDT
| Merced County Communication Facility | Dobson Cellular Inc | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/19/2024 13:27 PDT
| Merced County Communication Facility | MetroPCS Inc | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/19/2024 13:27 PDT
| Merced County Communication Facility | T-Mobile USA Inc | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/19/2024 13:27 PDT
| Merced County Communication Facility | T-Mobile WEST LLC | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/18/2024 21:46 PDT
| Merced County Communication Facility | Verizon | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/18/2024 21:46 PDT
| Merced County Emergency Services Facility | California Department of Forestry | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/18/2024 21:46 PDT
| Merced County Emergency Services Facility | California Highway Patrol | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/19/2024 13:27 PDT
| Merced County Emergency Services Facility | City of Gustine | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/19/2024 13:27 PDT
| Merced County Other Facility | Crown Castle USA Inc | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/18/2024 21:46 PDT
| Merced County Water and Waste Water Facility | City of Gustine | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/19/2024 13:27 PDT
| Merced County Gustine | City Manager | HFRA | 07/18/2024 21:41 PDT
| Merced County Gustine | Emergency | HFRA | 07/18/2024 21:41 PDT
| San Benito County | County Administrative Officer | Tier 2 | 07/18/2024 21:41 PDT
| San Benito County | Emergency Manager | Tier 2 | 07/18/2024 21:41 PDT
| San Benito County | Emergency Services Specialist | Tier 2 | 07/18/2024 21:41 PDT
| San Benito County | Non-Emergency | Tier 2 | 07/18/2024 21:42 PDT
| San Benito County | Sheriff | Tier 2 | 07/18/2024 21:41 PDT
| San Benito County | Staff Analyst | Tier 2 | 07/18/2024 21:41 PDT
| San Benito County | Supervisor | Tier 2 | 07/18/2024 21:41 PDT
| San Benito County CCA | General | Tier 2 | 07/18/2024 21:41 PDT
| San Benito County Communication Facility | AT&T Services Inc | Tier 2 | 07/18/2024 21:46 PDT
| San Benito County Communication Facility | Pinnacles Tel Co | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/18/2024 21:46 PDT
| San Benito County Communication Facility | T-Mobile West Corporation | Tier 2 | 07/18/2024 21:46 PDT
| San Joaquin County | Board Chair | HFRA | 07/18/2024 21:41 PDT
| San Joaquin County | Board Vice Chair | HFRA | 07/18/2024 21:41 PDT
| San Joaquin County | County Administrator | HFRA | 07/18/2024 21:41 PDT
| San Joaquin County | County Clerk | HFRA | 07/18/2024 21:41 PDT
| San Joaquin County | Director of Emergency Operations | HFRA | 07/18/2024 21:41 PDT
| San Joaquin County | EMS Admin | HFRA | 07/18/2024 21:41 PDT
| San Joaquin County | Fire Chief | HFRA | 07/18/2024 21:41 PDT
| San Joaquin County | Sheriff | HFRA | 07/18/2024 21:41 PDT
| San Joaquin County | Supervisor | HFRA | 07/18/2024 21:41 PDT
| San Joaquin County | Supervisor District 3 | HFRA | 07/18/2024 21:41 PDT
| San Joaquin County Communication Facility | AT&T Mobility, LLC | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/18/2024 21:46 PDT
| San Joaquin County Communication Facility | AT&T Services Inc | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/18/2024 21:46 PDT
| San Joaquin County Communication Facility | AT&T Wireless Service LLC | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/19/2024 13:27 PDT
| San Joaquin County Communication Facility | Comcast | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/19/2024 12:48 PDT
| San Joaquin County Communication Facility | Comcast Cable | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/19/2024 13:28 PDT
| San Joaquin County Communication Facility | Comcast Cable Communications Management LLC | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/19/2024 12:48 PDT
| San Joaquin County Communication Facility | Comcast Cable Communications Management LLC | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/19/2024 12:48 PDT
| San Joaquin County Communication Facility | Comcast Cablevision Communications Inc | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/19/2024 12:48 PDT
| San Joaquin County Communication Facility | Comcast Fresno LLC | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/19/2024 12:48 PDT
| San Joaquin County Communication Facility | Comcast Inc | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/19/2024 12:48 PDT
| San Joaquin County Communication Facility | Comcast of California | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/19/2024 12:48 PDT
| San Joaquin County Communication Facility | GTE Mobilenet of California LP | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/19/2024 13:27 PDT
| San Joaquin County Communication Facility | Sprint Corporation | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/18/2024 21:46 PDT
| San Joaquin County Communication Facility | T-Mobile | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/19/2024 13:27 PDT
| San Joaquin County Communication Facility | T-Mobile West LLC | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/18/2024 21:46 PDT
| San Joaquin County Communication Facility | TCI Cablevision | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/19/2024 12:48 PDT
| San Joaquin County Communication Facility | TW Telecom Inc | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/19/2024 13:27 PDT
| San Joaquin County Communication Facility | Verizon | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/18/2024 21:46 PDT
| San Joaquin County Communication Facility | Verizon Services Corporation | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/19/2024 13:27 PDT
| San Joaquin County Energy Sector Facility | Pacific Gas & Electric Company | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/18/2024 21:46 PDT
| San Joaquin County Water and Waste Water Facility | City of Tracy | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/19/2024 13:27 PDT
| San Joaquin County Water and Waste Water Facility | County of San Joaquin | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/19/2024 13:27 PDT
| San Joaquin County Tracy | Police Department | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/18/2024 21:41 PDT
| San Joaquin County Tracy | City Clerk | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/18/2024 21:41 PDT
| San Joaquin County Tracy | City Manager | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/18/2024 21:41 PDT
| San Joaquin County Tracy | Communications Supervisor | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/18/2024 21:41 PDT
| San Joaquin County Tracy | Council Member | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/18/2024 21:41 PDT
| San Joaquin County Tracy | Fire Chief | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/18/2024 21:41 PDT
| San Joaquin County Tracy | Lieutenant | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/18/2024 21:42 PDT
| San Joaquin County Tracy | Mayor | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/18/2024 21:41 PDT
| San Joaquin County Tracy | Mayor Pro TEM | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/18/2024 21:41 PDT
| San Joaquin County Tracy | Sergeant | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/18/2024 21:41 PDT
| Stanislaus County | County Administration | Tier 2 | 07/19/2024 13:20 PDT
| Stanislaus County | Board Chair | Tier 2 | 07/19/2024 13:20 PDT
| Stanislaus County | Board Vice Chair | Tier 2 | 07/19/2024 13:20 PDT
| Stanislaus County | Chief Executive Officer | Tier 2 | 07/19/2024 13:20 PDT
| Stanislaus County | County Clerk Recorder | Tier 2 | 07/19/2024 13:20 PDT
| Stanislaus County | County Fire Warden | Tier 2 | 07/19/2024 13:20 PDT
| Stanislaus County | Emergency Medical Services Duty Officer | Tier 2 | 07/19/2024 13:20 PDT
| Stanislaus County | Emergency Manager | Tier 2 | 07/19/2024 13:20 PDT
| Stanislaus County | Health Officer | Tier 2 | 07/19/2024 13:20 PDT
| Stanislaus County | Medical Health Operational Coordinator | Tier 2 | 07/19/2024 13:21 PDT
| Stanislaus County | Public Health Duty Officer | Tier 2 | 07/19/2024 13:21 PDT
| Stanislaus County | Sheriff | Tier 2 | 07/19/2024 13:20 PDT
| Stanislaus County | Supervisor | Tier 2 | 07/19/2024 13:20 PDT
| Stanislaus County | County Fire Warden | Tier 2 | 07/19/2024 13:21 PDT
| Stanislaus County | Emergency Medical Services Duty Officer | Tier 2 | 07/19/2024 13:21 PDT
| Stanislaus County | Emergency Manager | Tier 2 | 07/19/2024 13:21 PDT
| Stanislaus County | Health Officer | Tier 2 | 07/19/2024 13:30 PDT
| Stanislaus County | Medical Health Operational Coordinator | Tier 2 | 07/19/2024 13:21 PDT
| Stanislaus County Communication Facility | AT&T Mobility LLC | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/19/2024 13:27 PDT
| Stanislaus County Communication Facility | AT&T Mobility LLC | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/19/2024 13:27 PDT
| Stanislaus County Communication Facility | AT&T Services Inc | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/19/2024 13:27 PDT
| Stanislaus County Communication Facility | Comcast Fresno LLC | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/19/2024 12:48 PDT
| Stanislaus County Communication Facility | Comcast of San Joaquin Inc | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/19/2024 12:48 PDT
| Stanislaus County Communication Facility | GTE Mobilenet of California LP | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/19/2024 13:27 PDT
| Stanislaus County Communication Facility | Metro PCS Inc | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/19/2024 13:27 PDT
| Stanislaus County Communication Facility | T-Mobile West LLC | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/19/2024 13:27 PDT
| Stanislaus County Communication Facility | TCI Cablevision of San Joaquin Inc | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/19/2024 12:48 PDT
| Stanislaus County Communication Facility | Televents of San Joaquin Inc | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/19/2024 12:48 PDT
| Stanislaus County Communication Facility | Verizon | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/19/2024 13:27 PDT
| Stanislaus County Emergency Services Facility | City of Newman | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/19/2024 13:28 PDT
| Stanislaus County Other Facility | Comcast Fresno LLC | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/19/2024 13:27 PDT
| Stanislaus County Water and Waste Water Facility | City of Newman | Non-HFTD or Non-HFRA; within PSPS scope (see footnote 2) | 07/19/2024 13:28 PDT
| Stanislaus County Newman | Chief Plant Operator | Tier 2 | 07/19/2024 13:20 PDT
| Stanislaus County Newman | City Manager | Tier 2 | 07/19/2024 13:20 PDT
| Stanislaus County Newman | Council Member | Tier 2 | 07/19/2024 13:20 PDT
| Stanislaus County Newman | Fire Chief | Tier 2 | 07/19/2024 13:20 PDT
| Stanislaus County Newman | Mayor | Tier 2 | 07/19/2024 13:20 PDT
| Stanislaus County Newman | Non-Emergency | Tier 2 | 07/19/2024 13:20 PDT
| Stanislaus County Newman | On Call Officer | Tier 2 | 07/19/2024 13:21 PDT
| Stanislaus County Newman | On-Call Public Works Employee | Tier 2 | 07/19/2024 13:21 PDT
| Stanislaus County Newman | Public Works Director | Tier 2 | 07/19/2024 13:20 PDT
| Stanislaus County Newman | Public Works Superintendent | Tier 2 | 07/19/2024 13:20 PDT
1 Catastrophic Fire Behavior runs both in and outside of High Fire Risk Areas (HFRA). The PG&E Meteorology Team evaluates non-HFRA areas for catastrophic wildfire risk in unusual circumstances.