## Data
Division | Tier | Feeder Name | DATE | Outage Level | Basic Cause | Supplemental Cause | Duration | CESO | Failed Equipment | Sus/Mom | Completed Projects | Forecasted Projects
CENTRAL COAST | Tier 2 | VIEJO-2202 | 2020-02-01 | Distribution Circuit | Vegetation | Tree - branch fell on line | 390 | 182 | Conductor- Overhead | Sus | N/A | N/A
CENTRAL COAST | Tier 2 | VIEJO-2201 | 2020-03-15 | Distribution Circuit | Vegetation | Tree - fell into line | 86 | 82 | Crossarm- Wood | Sus | N/A | N/A
CENTRAL COAST | Tier 2 | LOS OSITOS-2103 | 2020-04-01 | Distribution Circuit | 3rd Party | Vehicle | 190 | 1750 | Pole-Wood | Sus | N/A | 2024, 2025, 2026
CENTRAL COAST | Tier 2 | HATTON-1101 | 2020-04-06 | Distribution Circuit | Vegetation | Tree - fell into line | 216 | 2186 | Conductor- Overhead | Sus | N/A | N/A
CENTRAL COAST | Tier 2 | VIEJO-2204 | 2020-04-20 | Distribution Circuit | Animal | Squirrel | 121 | 277 | Recloser | Sus | N/A | N/A
CENTRAL COAST | Tier 2 | VIEJO-2204 | 2020-05-02 | Distribution Circuit | 3rd Party | Metallic Balloon | 70 | 8658 | Conductor- Overhead | Sus | N/A | N/A
CENTRAL COAST | Tier 2 | VIEJO-2203 | 2020-05-21 | Distribution Circuit | Wildfire Mitigation | Planned - WSIP/System Hardening | 439 | 17 |  | Sus | N/A | N/A
CENTRAL COAST | Tier 2 | HATTON-1102 | 2020-05-27 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 24 | 2147 |  | Sus | N/A | N/A
CENTRAL COAST | Tier 2 | RESERVATION ROAD-1102 | 2020-08-20 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 993 | 520 | Conductor- Overhead | Sus | N/A | N/A
CENTRAL COAST | Tier 2 | JOLON-1103 | 2020-08-29 | Distribution Circuit | 3rd Party | Vehicle | 1204 | 19 | Pole-Wood | Sus | N/A | N/A
CENTRAL COAST | Tier 3 | BURNS-2101 | 2020-10-25 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 1018 | 29 | Conductor- Overhead | Sus | N/A | N/A
CENTRAL COAST | Tier 3 | FELTON-0401 | 2020-10-25 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 1247 | 48 | Conductor- Overhead | Sus | N/A | N/A
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 2020-10-25 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 1119 | 128 | Conductor- Overhead | Sus | N/A | 2023
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 2020-10-25 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 1197 | 333 | Conductor- Overhead | Sus | 2022 | 2023, 2024, 2025
CENTRAL COAST | Tier 3 | BEN LOMOND SUB | 2020-11-08 | Distribution Circuit | 3rd Party | Vehicle | 73 | 759 | Anchor or Guy | Sus | N/A | N/A
CENTRAL COAST | Tier 2 | HATTON-1101 | 2020-11-28 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 146 | 2189 |  | Sus | N/A | N/A
CENTRAL COAST | Tier 3 | FELTON SUB | 2021-01-21 | Distribution Circuit | Vegetation | Tree - branch fell on line | 171 | 48 | Conductor- Overhead | Sus | N/A | N/A
CENTRAL COAST | Tier 2 | HATTON-1101 | 2021-01-27 | Distribution Circuit | Vegetation | Tree - fell into line | 438 | 414 | Conductor- Overhead | Sus | N/A | N/A
CENTRAL COAST | Tier 3 | FELTON SUB | 2021-01-27 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 119 | 48 |  | Sus | N/A | N/A
CENTRAL COAST | Tier 3 | BEN LOMOND SUB | 2021-02-10 | Distribution Circuit | Animal | Bird found | 83 | 759 | Jumper | Sus | N/A | N/A
CENTRAL COAST | Tier 3 | BEN LOMOND SUB | 2021-03-11 | Distribution Circuit | Vegetation | Tree - branch fell on line | 124 | 759 | Conductor- Overhead | Sus | N/A | N/A
CENTRAL COAST | Tier 2 | VIEJO-2201 | 2021-06-15 | Distribution Circuit | Vegetation | Tree - branch fell on line | 80 | 1793 | Conductor- Overhead | Sus | N/A | N/A
CENTRAL COAST | Tier 3 | OTTER-1102 | 2021-08-05 | Distribution Circuit | Equipment Failure/Involved | Overhead | 33 | 738 | Regulator | Sus | N/A | N/A
CENTRAL COAST | Tier 2 | VIEJO-2201 | 2021-10-24 | Distribution Circuit | Vegetation | Tree - branch fell on line | 493 | 1798 | Conductor- Overhead | Sus | N/A | N/A
CENTRAL COAST | Tier 3 | FELTON SUB | 2021-12-14 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 633 | 49 |  | Sus | N/A | N/A
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 2021-12-16 | Distribution Circuit | Vegetation | Tree - fell into line | 967 | 1017 | Conductor- Overhead | Sus | N/A | N/A
CENTRAL COAST | Tier 3 | BEN LOMOND SUB | 2021-12-29 | Distribution Circuit | Environmental/External | Flood/Erosion | 214 | 760 | Conductor- Overhead | Sus | N/A | N/A
CENTRAL COAST | Tier 2 | HATTON-1102 | 2022-04-24 | Distribution Circuit | Equipment Failure/Involved | Overhead | 752 | 2143 | Conductor- Overhead | Sus | N/A | N/A
CENTRAL COAST | Tier 2 | JOLON-1103 | 2022-05-06 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 180 | 20 |  | Sus | N/A | N/A
CENTRAL COAST | Tier 2 | JOLON-1103 | 2022-05-26 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 379 | 20 |  | Sus | N/A | N/A
CENTRAL COAST | Tier 2 | RESERVATION ROAD-1102 | 2022-06-09 | Distribution Circuit | 3rd Party | Aircraft | 474 | 2116 | Conductor- Overhead | Sus | N/A | N/A
CENTRAL COAST | Tier 2 | RESERVATION ROAD-1102 | 2022-07-18 | Distribution Circuit | Animal | Bird found | 259 | 2114 | Conductor- Overhead | Sus | N/A | N/A
CENTRAL COAST | Tier 2 | JOLON-1103 | 2022-07-23 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 238 | 20 |  | Sus | N/A | N/A
CENTRAL COAST | Tier 2 | HATTON-1101 | 2022-09-03 | Distribution Circuit | Animal | Squirrel | 52 | 3538 | Recloser | Sus | N/A | N/A
CENTRAL COAST | Tier 2 | JOLON-1103 | 2022-09-09 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 141 | 20 |  | Sus | N/A | N/A
CENTRAL COAST | Tier 2 | VIEJO-2202 | 2022-09-24 | Distribution Circuit | Company Initiated | Planned- capital | 260 | 63 |  | Sus | N/A | N/A
CENTRAL COAST | Tier 2 | JOLON-1103 | 2022-10-05 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 187 | 20 |  | Sus | N/A | N/A
CENTRAL COAST | Tier 2 | RESERVATION ROAD-1102 | 2022-10-22 | Distribution Circuit | Equipment Failure/Involved | Overhead | 273 | 2114 | Jumper | Sus | N/A | N/A
CENTRAL COAST | Tier 2 | JOLON-1102 | 2022-11-09 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 235 | 608 |  | Sus | N/A | N/A
CENTRAL COAST | Tier 2 | VIEJO-2203 | 2022-12-31 | Distribution Circuit | Vegetation | Tree - fell into line | 849 | 4856 | Conductor- Overhead | Sus | N/A | N/A
DE ANZA | Tier 3 | LOS GATOS-1106 | 2022-08-09 | Substation - Distribution | 3rd Party | Metallic Balloon | 261 | 8118 | Bus | Sus | 2020 | N/A
DIABLO | Tier 2 | MORAGA-1105 | 2020-01-16 | Distribution Circuit | Equipment Failure/Involved | Overhead | 47 | 1732 | Conductor- Overhead | Sus | N/A | N/A
DIABLO | Tier 2 | MORAGA-1105 | 2020-01-16 | Distribution Circuit | Equipment Failure/Involved | Overhead | 174 | 1732 | Conductor- Overhead | Sus | N/A | N/A
DIABLO | Tier 2 | MORAGA-1102 | 2020-02-25 | Distribution Circuit | Equipment Failure/Involved | Overhead | 163 | 2311 | Crossarm- Wood | Sus | 2020 | N/A
DIABLO | Tier 3 | ORINDA-0402 | 2020-05-06 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 8 | 523 | Conductor- Overhead | Sus | N/A | N/A
DIABLO | Tier 2 | SOBRANTE-1101 | 2020-07-12 | Distribution Circuit | Vegetation | Tree - fell into line | 710 | 2124 | Conductor- Overhead | Sus | N/A | N/A
DIABLO | Tier 3 | ORINDA-0402 | 2020-07-20 | Distribution Circuit | Equipment Failure/Involved | Overhead | 181 | 525 | Crossarm- Wood | Sus | N/A | N/A
DIABLO | Tier 2 | SOBRANTE-1101 | 2020-07-25 | Distribution Circuit | Equipment Failure/Involved | Underground | 13 | 2124 | Connector or Splice (UG) | Sus | N/A | N/A
DIABLO | Tier 3 | ORINDA-0402 | 2020-08-08 | Distribution Circuit | Vegetation | Tree - fell into line | 603 | 454 | Conductor- Overhead | Sus | N/A | N/A
DIABLO | Tier 2 | MORAGA-1104 | 2020-09-17 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 736 | 1767 | Crossarm- Wood | Sus | N/A | N/A
DIABLO | Tier 2 | MORAGA-1101 | 2020-09-21 | Distribution Circuit | Animal | Other | 560 | 2003 | Fuse | Sus | 2020 | N/A
DIABLO | Tier 2 | MORAGA-1104 | 2020-11-18 | Distribution Circuit | Equipment Failure/Involved | Overhead | 317 | 536 | Conductor- Overhead | Sus | N/A | N/A
DIABLO | Tier 2 | SOBRANTE-1101 | 2020-11-29 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 91 | 1788 |  | Sus | N/A | N/A
DIABLO | Tier 2 | SOBRANTE-1102 | 2021-01-19 | Distribution Circuit | Vegetation | Tree - branch fell on line | 337 | 1766 | Conductor- Overhead | Sus | N/A | N/A
DIABLO | Tier 3 | ORINDA-0402 | 2021-05-08 | Distribution Circuit | Equipment Failure/Involved | Overhead | 212 | 458 | Connector or Splice (OH) | Sus | N/A | N/A
DIABLO | Tier 2 | MORAGA-1103 | 2021-06-20 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 4858 | Crossarm- Wood | Sus | 2022 | N/A
DIABLO | Tier 2 | SOBRANTE-1102 | 2021-06-30 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 128 | 1824 | Insulator | Sus | N/A | N/A
DIABLO | Tier 2 | SOBRANTE-1101 | 2021-10-20 | Distribution Circuit | Vegetation | Tree - branch fell on line | 85 | 368 | Conductor- Overhead | Sus | N/A | N/A
DIABLO | Tier 2 | MORAGA-1104 | 2021-12-16 | Distribution Circuit | Equipment Failure/Involved | Overhead | 464 | 1766 | Crossarm- Wood | Sus | N/A | N/A
DIABLO | Tier 2 | MORAGA-1102 | 2021-12-23 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 14 | 2471 |  | Sus | 2020 | N/A
DIABLO | Tier 2 | MORAGA-1102 | 2022-05-27 | Distribution Circuit | 3rd Party | Vehicle | 404 | 3091 | Anchor or Guy | Sus | 2020 | N/A
DIABLO | Tier 2 | SOBRANTE-1103 | 2022-07-24 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 264 | 982 |  | Sus | N/A | N/A
DIABLO | Tier 3 | ORINDA-0401 | 2022-07-24 | Distribution Circuit | Vegetation | Tree - branch fell on line | 322 | 292 | Conductor- Overhead | Sus | N/A | N/A
DIABLO | Tier 2 | MORAGA-1105 | 2022-08-06 | Distribution Circuit | 3rd Party | Metallic Balloon | 55 | 1887 | Conductor- Overhead | Sus | N/A | N/A
DIABLO | Tier 2 | SOBRANTE-1103 | 2022-10-29 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 110 | 983 |  | Sus | N/A | N/A
DIABLO | Tier 2 | MORAGA SUB | 2022-11-03 | Distribution Circuit | Vegetation | Tree - grew into line | 765 | 1770 | Fuse | Sus | N/A | N/A
DIABLO | Tier 2 | MORAGA-1105 | 2022-11-26 | Distribution Circuit | Equipment Failure/Involved | Overhead | 416 | 1887 | Transformer (OH) | Sus | N/A | N/A
EAST BAY | Tier 2 | OAKLAND K-1103 | 2020-01-19 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 6 | 3614 |  | Sus | N/A | N/A
EAST BAY | Tier 2 | OAK-0401 | 2020-03-16 | Distribution Circuit | Equipment Failure/Involved | Overhead | 213 | 1017 | Insulator | Sus | N/A | N/A
EAST BAY | Tier 2 | PALO SECO SUB | 2020-04-24 | Distribution Circuit | 3rd Party | Vehicle | 109 | 616 | Other | Sus | N/A | N/A
EAST BAY | Tier 2 | OAKLAND K-1104 | 2020-10-13 | Distribution Circuit | Animal | Bird found | 440 | 2683 | Cutout- fuse holder | Sus | N/A | N/A
EAST BAY | Tier 2 | OAKLAND K-1101 | 2020-10-16 | Distribution Circuit | Vegetation | Tree - branch fell on line | 157 | 2162 | Conductor- Overhead | Sus | N/A | N/A
EAST BAY | Tier 2 | OAKLAND K-1104 | 2020-10-20 | Distribution Circuit | Animal | Squirrel | 84 | 2646 | Conductor- Overhead | Sus | N/A | N/A
EAST BAY | Tier 2 | FLORENCE SUB | 2020-10-26 | Distribution Circuit | Vegetation | Tree - branch fell on line | 168 | 256 | Conductor- Overhead | Sus | N/A | N/A
EAST BAY | Tier 2 | RIDGE SUB | 2020-11-04 | Distribution Circuit | Equipment Failure/Involved | Overhead | 559 | 788 | Transformer (OH) | Sus | N/A | N/A
EAST BAY | Tier 2 | OAKLAND K-1102 | 2021-01-19 | Distribution Circuit | Equipment Failure/Involved | Overhead | 411 | 1340 | Conductor- Overhead | Sus | N/A | N/A
EAST BAY | Tier 2 | RIDGE SUB | 2022-05-03 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 248 | 804 |  | Sus | N/A | N/A
FRESNO | Tier 2 | BALCH NO 1 SUB | 2020-03-04 | Substation - Distribution | Company Initiated | Planned- capital | 136 | 25 |  | Sus | N/A | N/A
FRESNO | Tier 2 | DUNLAP-1102 | 2020-05-02 | Distribution Circuit | Company Initiated | Planned- capital | 553 | 1082 |  | Sus | N/A | N/A
FRESNO | Tier 2 | SAND CREEK-1103 | 2020-05-02 | Distribution Circuit | Company Initiated | Planned- capital | 33 | 931 |  | Sus | N/A | N/A
FRESNO | Tier 2 | AUBERRY-1102 | 2020-07-19 | Distribution Circuit | Animal | Bird found | 315 | 1637 | Fuse | Sus | N/A | N/A
FRESNO | Tier 2 | SAND CREEK-1103 | 2020-08-23 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 160 | 1680 |  | Sus | N/A | N/A
FRESNO | Tier 2 | AUBERRY-1101 | 2020-10-25 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 1046 | 361 | Conductor- Overhead | Sus | 2020 | 2023, 2026
FRESNO | Tier 2 | AUBERRY-1102 | 2020-10-25 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 1107 | 556 | Conductor- Overhead | Sus | N/A | N/A
FRESNO | Tier 2 | SAND CREEK-1103 | 2020-11-05 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 249 | 1680 |  | Sus | N/A | N/A
FRESNO | Tier 2 | BALCH NO 1 SUB | 2020-12-01 | Substation - Distribution | Company Initiated | Planned- maintenance | 512 | 25 |  | Sus | N/A | N/A
FRESNO | Tier 2 | SAND CREEK-1103 | 2021-05-15 | Distribution Circuit | Company Initiated | Planned- capital | 30 | 1680 |  | Sus | N/A | N/A
FRESNO | Tier 3 | WISHON SUB | 2021-06-02 | Distribution Circuit | Wildfire Mitigation | Planned - WSIP/System Hardening | 597 | 15 |  | Sus | N/A | N/A
FRESNO | Tier 2 | KERCKHOFF-1101 | 2021-06-07 | Distribution Circuit | Equipment Failure/Involved | Overhead | 166 | 273 | Lightning Arrestor | Sus | N/A | N/A
FRESNO | Tier 2 | AUBERRY-1101 | 2021-06-16 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 233 | 3185 | Conductor- Overhead | Sus | 2020 | 2023, 2026
FRESNO | Tier 2 | KERCKHOFF-1101 | 2021-07-07 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 230 | 273 |  | Sus | N/A | N/A
FRESNO | Tier 3 | WISHON SUB | 2021-07-31 | Distribution Circuit | Animal | Squirrel | 338 | 15 | Conductor- Overhead | Sus | N/A | N/A
FRESNO | Tier 3 | WISHON SUB | 2022-04-27 | Distribution Circuit | Company Initiated | Planned- capital | 12 | 15 |  | Sus | N/A | N/A
FRESNO | Tier 2 | DUNLAP-1102 | 2022-06-22 | Distribution Circuit | Vegetation | Tree - fell into line | 312 | 700 | Conductor- Overhead | Sus | N/A | N/A
FRESNO | Tier 2 | AUBERRY-1101 | 2022-06-30 | Distribution Circuit | Animal | Squirrel | 191 | 3219 | Conductor- Overhead | Sus | 2020 | 2023, 2026
FRESNO | Tier 2 | AUBERRY-1102 | 2022-08-14 | Distribution Circuit | 3rd Party | Vehicle | 385 | 1658 | Pole-Wood | Sus | N/A | N/A
FRESNO | Tier 2 | AUBERRY-1102 | 2022-09-07 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 275 | 1658 |  | Sus | N/A | N/A
FRESNO | Tier 2 | AUBERRY-1102 | 2022-11-08 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 88 | 1653 |  | Sus | N/A | N/A
FRESNO | Tier 2 | HAAS-2101 | 2022-12-21 | Substation - Distribution | Company Initiated | Personnel- company | 634 | 70 | Relay | Sus | N/A | N/A
HUMBOLDT | Tier 2 | MAPLE CREEK-1101 | 2020-01-16 | Distribution Circuit | Vegetation | Tree - fell into line | 976 | 146 | Conductor- Overhead | Sus | N/A | N/A
HUMBOLDT | Tier 2 | BRIDGEVILLE-1101 | 2020-01-16 | Distribution Circuit | Vegetation | Tree - fell into line | 597 | 94 | Conductor- Overhead | Sus | N/A | N/A
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 2020-01-16 | Distribution Circuit | Vegetation | Tree - fell into line | 517 | 982 | Conductor- Overhead | Sus | 2022 | N/A
HUMBOLDT | Tier 2 | LAYTONVILLE-1102 | 2020-01-16 | Distribution Circuit | Vegetation | Tree - fell into line | 1973 | 601 | Crossarm- Wood | Sus | N/A | N/A
HUMBOLDT | Tier 2 | BRIDGEVILLE-1101 | 2020-01-16 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1602 | 94 | Jumper | Sus | N/A | N/A
HUMBOLDT | Tier 3 | WILLOW CREEK-1103 | 2020-01-16 | Distribution Circuit | Vegetation | Tree - fell into line | 5169 | 2254 | Conductor- Overhead | Sus | N/A | 2023, 2025
HUMBOLDT | Tier 2 | MAPLE CREEK-1101 | 2020-01-17 | Transmission line | Unknown Cause | Patrol - not conducted | 347 | 40 |  | Sus | N/A | N/A
HUMBOLDT | Tier 2 | FRUITLAND-1141 | 2020-01-17 | Transmission line | Vegetation | Tree - fell into line | 3149 | 1096 | Conductor- Overhead | Sus | N/A | N/A
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 2020-02-18 | Distribution Circuit | Animal | Other | 85 | 1279 | Conductor- Overhead | Sus | N/A | N/A
HUMBOLDT | Tier 2 | BRIDGEVILLE-1102 | 2020-02-20 | Distribution Circuit | Wildfire Mitigation | Planned - WSIP/System Hardening | 557 | 104 |  | Sus | N/A | N/A
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 2020-03-15 | Distribution Circuit | Environmental/External | Ice or snow | 800 | 1270 | Conductor- Overhead | Sus | N/A | N/A
HUMBOLDT | Tier 2 | BRIDGEVILLE-1101 | 2020-03-17 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 334 | 94 |  | Sus | N/A | N/A
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 2020-04-22 | Distribution Circuit | Company Initiated | Planned- capital | 404 | 492 |  | Sus | N/A | N/A
HUMBOLDT | Tier 2 | FRUITLAND-1141 | 2020-06-28 | Distribution Circuit | Vegetation | Tree - branch fell on line | 45 | 394 | Conductor- Overhead | Sus | N/A | N/A
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 2020-06-30 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 254 | 1831 | Conductor- Overhead | Sus | 2022 | N/A
HUMBOLDT | Tier 2 | ANNAPOLIS-1101 | 2020-08-14 | Distribution Circuit | Company Initiated | Rotating Outage | 159 | 228 |  | Sus | N/A | N/A
HUMBOLDT | Tier 2 | GUALALA-1111 | 2020-08-14 | Distribution Circuit | Company Initiated | Rotating Outage | 158 | 2477 |  | Sus | N/A | N/A
HUMBOLDT | Tier 2 | GUALALA-1112 | 2020-08-14 | Distribution Circuit | Company Initiated | Rotating Outage | 157 | 1288 |  | Sus | N/A | N/A
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 2020-08-17 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 1276 | Conductor- Overhead | Sus | N/A | N/A
HUMBOLDT | Tier 2 | GARBERVILLE-1103 | 2020-09-10 | Distribution Circuit | Animal | Bird found | 137 | 497 | Transformer (OH) | Sus | N/A | N/A
HUMBOLDT | Tier 2 | MAPLE CREEK-1101 | 2020-09-19 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 148 | Lightning Arrestor | Sus | N/A | N/A
HUMBOLDT | Tier 2 | LOW GAP-1101 | 2020-10-25 | Distribution Circuit | Company Initiated | Coordination failure | 69 | 25 | Conductor- Overhead | Sus | N/A | N/A
HUMBOLDT | Tier 2 | FRUITLAND-1141 | 2020-11-17 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 472 | 393 |  | Sus | N/A | N/A
HUMBOLDT | Tier 2 | REDBUD-1102 | 2020-11-29 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 9 | 3414 |  | Sus | N/A | N/A
HUMBOLDT | Tier 2 | UPPER LAKE-1101 | 2020-12-07 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 113 | 1318 |  | Sus | N/A | 2023, 2025
HUMBOLDT | Tier 2 | GUALALA-1111 | 2020-12-26 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 13 | 2480 |  | Sus | N/A | N/A
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 2021-01-07 | Distribution Circuit | Vegetation | Tree - fell into line | 83 | 576 | Conductor- Overhead | Sus | N/A | N/A
HUMBOLDT | Tier 2 | FRUITLAND-1141 | 2021-01-08 | Distribution Circuit | Vegetation | Tree - fell into line | 230 | 392 | Pole-Wood | Sus | N/A | N/A
HUMBOLDT | Tier 2 | LOW GAP-1101 | 2021-01-27 | Transmission line | Unknown Cause | Patrol - not conducted | 244 | 670 |  | Sus | N/A | N/A
HUMBOLDT | Tier 3 | WILLOW CREEK SUB | 2021-02-08 | Distribution Circuit | Company Initiated | Return Circuit Normal | 28 | 2485 | Conductor- Overhead | Sus | N/A | N/A
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 2021-02-27 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 160 | 1844 |  | Sus | 2022 | N/A
HUMBOLDT | Tier 2 | MAPLE CREEK-1101 | 2021-03-05 | Distribution Circuit | Vegetation | Tree - branch fell on line | 164 | 150 | Conductor- Overhead | Sus | N/A | N/A
HUMBOLDT | Tier 3 | WILLOW CREEK-1101 | 2021-03-05 | Distribution Circuit | Vegetation | Tree - branch fell on line | 320 | 784 | Conductor- Overhead | Sus | N/A | N/A
HUMBOLDT | Tier 2 | FRUITLAND-1141 | 2021-04-19 | Distribution Circuit | Vegetation | Tree - branch fell on line | 333 | 392 | Crossarm- Wood | Sus | N/A | N/A
HUMBOLDT | Tier 2 | REDBUD-1102 | 2021-04-22 | Distribution Circuit | Equipment Failure/Involved | Overhead | 417 | 338 | Jumper | Sus | N/A | N/A
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 2021-04-25 | Distribution Circuit | Vegetation | Tree - branch fell on line | 56 | 1557 | Conductor- Overhead | Sus | 2022 | N/A
HUMBOLDT | Tier 2 | FRUITLAND-1141 | 2021-05-21 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 25 | 392 |  | Sus | N/A | N/A
HUMBOLDT | Tier 2 | POINT ARENA-1101 | 2021-06-12 | Distribution Circuit | Vegetation | Tree - fell into line | 697 | 907 | Conductor- Overhead | Sus | N/A | N/A
HUMBOLDT | Tier 2 | LOW GAP-1101 | 2021-06-20 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 190 | 737 |  | Sus | N/A | N/A
HUMBOLDT | Tier 2 | HIGHLANDS-1103 | 2021-06-21 | Distribution Circuit | 3rd Party | Other | 754 | 2583 | Conductor- Overhead | Sus | N/A | N/A
HUMBOLDT | Tier 2 | LUCERNE-1103 | 2021-06-27 | Distribution Circuit | Animal | Bird found | 285 | 2253 | Crossarm- Wood | Sus | N/A | N/A
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 2021-07-22 | Distribution Circuit | Company Initiated | Planned- maintenance | 420 | 194 |  | Sus | N/A | N/A
HUMBOLDT | Tier 2 | MAPLE CREEK-1101 | 2021-08-04 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 102 | 150 | Conductor- Overhead | Sus | N/A | N/A
HUMBOLDT | Tier 2 | LOW GAP-1101 | 2021-08-12 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 292 | 733 |  | Sus | N/A | N/A
HUMBOLDT | Tier 2 | LOW GAP-1101 | 2021-09-23 | Distribution Circuit | Equipment Failure/Involved | Overhead | 35 | 734 | Recloser | Sus | N/A | N/A
HUMBOLDT | Tier 2 | LOW GAP-1101 | 2021-09-24 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 415 | 734 |  | Sus | N/A | N/A
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 2021-10-09 | Distribution Circuit | Animal | Squirrel | 14 | 1266 | Bushing | Sus | N/A | N/A
HUMBOLDT | Tier 2 | FORT SEWARD-1122 | 2021-10-22 | Distribution Circuit | Vegetation | Tree - fell into line | 262 | 322 | Conductor- Overhead | Sus | N/A | N/A
HUMBOLDT | Tier 2 | LAYTONVILLE-1101 | 2021-12-27 | Transmission line | Unknown Cause | Patrol - not conducted | 614 | 649 |  | Sus | N/A | N/A
HUMBOLDT | Tier 2 | FRUITLAND-1141 | 2022-04-16 | Distribution Circuit | Vegetation | Tree - fell into line | 348 | 384 | Conductor- Overhead | Sus | N/A | N/A
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 2022-04-23 | Distribution Circuit | Animal | Bird found | 330 | 1342 | Insulator | Sus | N/A | N/A
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 2022-04-30 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 24 | 1931 |  | Sus | 2022 | N/A
HUMBOLDT | Tier 2 | LOW GAP-1101 | 2022-05-01 | Distribution Circuit | 3rd Party | Customer Equipment | 22 | 729 | Generator | Sus | N/A | N/A
HUMBOLDT | Tier 2 | FRUITLAND-1141 | 2022-05-07 | Distribution Circuit | Vegetation | Tree - fell into line | 461 | 1192 | Conductor- Overhead | Sus | N/A | N/A
HUMBOLDT | Tier 2 | LOW GAP-1101 | 2022-06-01 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 724 | Conductor- Overhead | Sus | N/A | N/A
HUMBOLDT | Tier 2 | UPPER LAKE-1101 | 2022-06-09 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 255 | 1256 |  | Sus | N/A | 2023, 2025
HUMBOLDT | Tier 2 | LUCERNE-1103 | 2022-07-05 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 85 | 2254 |  | Sus | N/A | N/A
HUMBOLDT | Tier 2 | FRUITLAND SUB | 2022-07-06 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 141 | 1023 | Conductor- Overhead | Sus | N/A | N/A
HUMBOLDT | Tier 2 | FORT SEWARD-1122 | 2022-07-14 | Distribution Circuit | Company Initiated | Planned- capital | 325 | 101 |  | Sus | N/A | N/A
HUMBOLDT | Tier 2 | HIGHLANDS-1103 | 2022-07-20 | Distribution Circuit | 3rd Party | Other | 20 | 2592 | Conductor- Overhead | Sus | N/A | N/A
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 2022-07-21 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 158 | 1936 | Conductor- Overhead | Sus | 2022 | N/A
HUMBOLDT | Tier 2 | HIGHLANDS-1102 | 2022-08-04 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 116 | 3633 | Conductor- Overhead | Sus | N/A | 2023
HUMBOLDT | Tier 2 | HIGHLANDS-1104 | 2022-09-08 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 555 | 2916 | Transformer (OH) | Sus | N/A | 2023
HUMBOLDT | Tier 2 | GUALALA-1111 | 2022-09-10 | Distribution Circuit | Vegetation | Tree - branch fell on line | 216 | 2556 | Conductor- Overhead | Sus | N/A | N/A
HUMBOLDT | Tier 2 | UPPER LAKE-1101 | 2022-09-18 | Distribution Circuit | Equipment Failure/Involved | Overhead | 149 | 1260 | Conductor- Overhead | Sus | N/A | 2023, 2025
HUMBOLDT | Tier 2 | MIDDLETOWN-1101 | 2022-09-19 | Distribution Circuit | Vegetation | Tree - fell into line | 1113 | 2110 | Conductor- Overhead | Sus | 2022 | 2023, 2024, 2025, 2026
HUMBOLDT | Tier 2 | MAPLE CREEK-1101 | 2022-10-04 | Distribution Circuit | Vegetation | Tree - branch fell on line | 131 | 149 | Conductor- Overhead | Sus | N/A | N/A
HUMBOLDT | Tier 2 | FRUITLAND SUB | 2022-10-28 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 115 | 1145 | Conductor- Overhead | Sus | N/A | N/A
HUMBOLDT | Tier 2 | MIDDLETOWN-1102 | 2022-12-04 | Distribution Circuit | Company Initiated | Planned- capital | 430 | 1236 |  | Sus | 2022 | 2024
HUMBOLDT | Tier 2 | LAYTONVILLE-1101 | 2022-12-17 | Distribution Circuit | Company Initiated | Planned- capital | 70 | 1323 |  | Sus | N/A | N/A
HUMBOLDT | Tier 2 | FRUITLAND SUB | 2022-12-26 | Distribution Circuit | Vegetation | Tree - fell into line | 78 | 1145 | Conductor- Overhead | Sus | N/A | N/A
KERN | Tier 2 | SCE TEHACHAPI-1101 | 2020-12-02 | Transformer only | Wildfire Mitigation | Public Safety Power Shut-off | 1324 | 4 | Conductor- Overhead | Sus | N/A | N/A
KERN | Tier 2 | POSO MOUNTAIN-2101 | 2022-06-09 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 179 | 147 |  | Sus | N/A | N/A
KERN | Tier 2 | POSO MOUNTAIN-2101 | 2022-06-10 | Distribution Circuit | Animal | Bird found | 60 | 147 | Recloser | Sus | N/A | N/A
KERN | Tier 2 | POSO MOUNTAIN-2103 | 2022-06-22 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 74 | 27 |  | Sus | N/A | N/A
KERN | Tier 2 | POSO MOUNTAIN-2103 | 2022-06-22 | Distribution Circuit | Environmental/External | Lightning | 720 | 27 | Capacitor | Sus | N/A | N/A
KERN | Tier 2 | POSO MOUNTAIN-2103 | 2022-08-19 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 177 | 27 |  | Sus | N/A | N/A
LOS PADRES | Tier 2 | OCEANO-1105 | 2020-03-20 | Distribution Circuit | 3rd Party | Metallic Balloon | 307 | 6514 | Conductor- Overhead | Sus | N/A | N/A
LOS PADRES | Tier 2 | ZACA-1101 | 2020-04-20 | Distribution Circuit | 3rd Party | Vehicle | 340 | 163 | Anchor or Guy | Sus | N/A | N/A
LOS PADRES | Tier 2 | GOLDTREE-1108 | 2021-01-23 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 52 | 3340 |  | Sus | N/A | N/A
LOS PADRES | Tier 2 | FOOTHILL-1101 | 2021-12-08 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 7 | 379 | Jumper | Sus | N/A | N/A
LOS PADRES | Tier 2 | PURISIMA SUB | 2022-07-03 | Distribution Circuit | 3rd Party | Vehicle | 292 | 2404 | Pole-Wood | Sus | N/A | N/A
LOS PADRES | Tier 2 | FOOTHILL SUB | 2022-08-03 | Distribution Circuit | Equipment Failure/Involved | Overhead | 409 | 380 | Connector or Splice (OH) | Sus | N/A | N/A
LOS PADRES | Tier 2 | CMC-1102 | 2022-08-04 | Distribution Circuit | 3rd Party | Customer Equipment | 105 | 1 | Generator | Sus | N/A | N/A
LOS PADRES | Tier 2 | CMC-1102 | 2022-08-04 | Distribution Circuit | 3rd Party | Customer Equipment | 39 | 1 | Generator | Sus | N/A | N/A
LOS PADRES | Tier 2 | FOOTHILL-1101 | 2022-10-01 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 171 | 379 |  | Sus | N/A | N/A
LOS PADRES | Tier 2 | FOOTHILL SUB | 2022-12-04 | Distribution Circuit | 3rd Party | Vehicle | 674 | 380 | Pole-Wood | Sus | N/A | N/A
MISSION | Tier 2 | NORTH DUBLIN-2103 | 2020-07-03 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 125 | 4822 |  | Sus | N/A | N/A
MISSION | Tier 2 | NORTH DUBLIN-2103 | 2022-06-13 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 377 | 4928 |  | Sus | N/A | N/A
MISSION | Tier 2 | NORTH DUBLIN-2103 | 2022-08-04 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 295 | 4928 |  | Sus | N/A | N/A
MISSION | Tier 2 | NORTH DUBLIN-2103 | 2022-09-06 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 341 | 4934 |  | Sus | N/A | N/A
MISSION | Tier 2 | NORTH DUBLIN-2103 | 2022-09-08 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 265 | 4934 |  | Sus | N/A | N/A
MISSION | Tier 2 | NORTH DUBLIN-2103 | 2022-09-13 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 156 | 4934 |  | Sus | N/A | N/A
NORTH BAY | Tier 3 | WOODACRE-1101 | 2020-01-08 | Distribution Circuit | Company Initiated | Planned- capital | 219 | 8 |  | Sus | N/A | N/A
NORTH BAY | Tier 2 | STAFFORD-1101 | 2020-08-16 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 291 | 3878 |  | Sus | N/A | N/A
NORTH BAY | Tier 2 | STAFFORD-1101 | 2020-12-01 | Distribution Circuit | Equipment Failure/Involved | Overhead | 99 | 2911 | Jumper | Sus | N/A | N/A
NORTH BAY | Tier 3 | WOODACRE-1102 | 2020-12-07 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 105 | 3035 |  | Sus | N/A | N/A
NORTH BAY | Tier 3 | WOODACRE-1101 | 2021-10-24 | Distribution Circuit | Equipment Failure/Involved | Overhead | 157 | 1076 | Secondary | Sus | N/A | N/A
NORTH BAY | Tier 2 | STAFFORD-1101 | 2021-12-15 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 17 | 1080 | Conductor- Overhead | Sus | N/A | N/A
NORTH BAY | Tier 2 | STAFFORD-1101 | 2022-04-01 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 9 | 2541 |  | Sus | N/A | N/A
NORTH BAY | Tier 2 | CALISTOGA-1102 | 2022-05-25 | Distribution Circuit | Company Initiated | Personnel- company | 348 | 2156 | CT | Sus | N/A | N/A
NORTH BAY | Tier 2 | CALISTOGA-1102 | 2022-05-25 | Distribution Circuit | Company Initiated | Personnel- company | 88 | 2156 | CT | Sus | N/A | N/A
NORTH BAY | Tier 2 | CALISTOGA-1102 | 2022-06-21 | Distribution Circuit | Company Initiated | Operating error | 214 | 2154 | Relay | Sus | N/A | N/A
NORTH BAY | Tier 2 | STAFFORD SUB | 2022-07-13 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 77 | 2541 |  | Sus | N/A | N/A
NORTH BAY | Tier 2 | STAFFORD SUB | 2022-07-23 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 421 | 3971 |  | Sus | N/A | N/A
NORTH BAY | Tier 2 | CALISTOGA-1101 | 2022-08-10 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 625 | 1662 |  | Sus | N/A | 2026
NORTH BAY | Tier 2 | MONTICELLO SUB | 2022-09-20 | Distribution Circuit | Company Initiated | Other Circuits | 32 | 1175 | Generator | Sus | N/A | N/A
NORTH VALLEY | Tier 2 | CLARK ROAD-1101 | 2020-01-04 | Substation - Distribution | Wildfire Mitigation | Planned - WSIP/System Hardening | 209 | 1200 | CT | Sus | N/A | N/A
NORTH VALLEY | Tier 2 | WILDWOOD-1101 | 2020-01-31 | Distribution Circuit | Company Initiated | Planned- maintenance | 581 | 146 |  | Sus | N/A | N/A
NORTH VALLEY | Tier 3 | CEDAR CREEK-1101 | 2020-03-08 | Distribution Circuit | Equipment Failure/Involved | Overhead | 584 | 791 | Conductor- Overhead | Sus | N/A | N/A
NORTH VALLEY | Tier 2 | SPANISH CREEK SUB | 2020-03-16 | Distribution Circuit | Equipment Failure/Involved | Overhead | 453 | 921 | Pole-Wood | Sus | N/A | N/A
NORTH VALLEY | Tier 2 | CLARK ROAD-1101 | 2020-03-20 | Distribution Circuit | Company Initiated | Planned- maintenance | 394 | 25 |  | Sus | N/A | N/A
NORTH VALLEY | Tier 2 | ELK CREEK-1101 | 2020-03-28 | Distribution Circuit | Wildfire Mitigation | Planned - WSIP/System Hardening | 214 | 920 |  | Sus | N/A | 2023
NORTH VALLEY | Tier 2 | PIT NO 5-1101 | 2020-04-15 | Distribution Circuit | Wildfire Mitigation | Planned - WSIP/System Hardening | 232 | 1 |  | Sus | N/A | N/A
NORTH VALLEY | Tier 2 | CLARK ROAD-1102 | 2020-05-01 | Distribution Circuit | 3rd Party | Vehicle | 132 | 1190 | Anchor or Guy | Sus | N/A | 2023, 2024, 2025
NORTH VALLEY | Tier 3 | BUCKS CREEK-1101 | 2020-05-05 | Distribution Circuit | Company Initiated | Planned- capital | 433 | 326 |  | Sus | 2021 | 2023
NORTH VALLEY | Tier 2 | FRENCH GULCH-1102 | 2020-06-19 | Distribution Circuit | Wildfire Mitigation | Planned - WSIP/System Hardening | 604 | 37 |  | Sus | N/A | N/A
NORTH VALLEY | Tier 2 | FRENCH GULCH-1102 | 2020-06-28 | Distribution Circuit | Wildfire Mitigation | Planned - WSIP/System Hardening | 397 | 37 |  | Sus | N/A | N/A
NORTH VALLEY | Tier 3 | BIG BEND-1101 | 2020-07-29 | Distribution Circuit | Wildfire Mitigation | Planned - WSIP/System Hardening | 9 | 661 | Conductor- Overhead | Sus | N/A | N/A
NORTH VALLEY | Tier 3 | CHALLENGE-1101 | 2020-08-01 | Transmission line | Equipment Failure/Involved | Overhead | 187 | 1528 | Conductor- Overhead | Sus | N/A | N/A
NORTH VALLEY | Tier 3 | BIG BEND-1102 | 2020-08-15 | Distribution Circuit | Company Initiated | Planned- capital | 93 | 388 |  | Sus | 2021, 2022 | 2023
NORTH VALLEY | Tier 3 | CEDAR CREEK-1101 | 2020-08-23 | Transmission line | Unknown Cause | Patrol - found nothing | 422 | 789 |  | Sus | N/A | N/A
NORTH VALLEY | Tier 2 | WHITMORE-1101 | 2020-08-23 | Transmission line | Unknown Cause | Patrol - found nothing | 489 | 545 |  | Sus | N/A | N/A
NORTH VALLEY | Tier 2 | ELK CREEK-1101 | 2020-08-27 | Distribution Circuit | Equipment Failure/Involved | Overhead | 757 | 903 | Pole-Wood | Sus | N/A | 2023
NORTH VALLEY | Tier 2 | CLARK ROAD-1101 | 2020-09-08 | Distribution Circuit | Equipment Failure/Involved | Underground | 676 | 25 | Cable Termination(live front | Sus | N/A | N/A
NORTH VALLEY | Tier 2 | HAMILTON BRANCH-1101 | 2020-09-12 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 6 | 2389 |  | Sus | N/A | N/A
NORTH VALLEY | Tier 3 | VOLTA-1101 | 2020-09-13 | Distribution Circuit | Equipment Failure/Involved | Overhead | 241 | 1348 | Switch (OH) | Sus | 2022, 2023 | 2023, 2024, 2025, 2026
NORTH VALLEY | Tier 2 | HAMILTON BRANCH-1101 | 2020-09-17 | Substation - Distribution | Equipment Failure/Involved | Substation | 115 | 2388 | Control Circuit/Wiring | Sus | N/A | N/A
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 2020-09-27 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 1140 | 185 | Circuit Breaker | Sus | N/A | N/A
NORTH VALLEY | Tier 3 | VOLTA-1101 | 2020-09-27 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 966 | 63 | Circuit Breaker | Sus | 2022, 2023 | 2023, 2024, 2025, 2026
NORTH VALLEY | Tier 3 | VOLTA-1102 | 2020-09-27 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 852 | 11 |  | Sus | N/A | N/A
NORTH VALLEY | Tier 3 | BIG BEND-1102 | 2020-09-28 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 369 | 9 | Crossarm- Wood | Sus | 2021, 2022 | 2023
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 2020-10-12 | Distribution Circuit | Equipment Failure/Involved | Overhead | 130 | 1522 | Conductor- Overhead | Sus | N/A | N/A
NORTH VALLEY | Tier 2 | OREGON TRAIL-1102 | 2020-10-22 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 826 | 96 | Conductor- Overhead | Sus | N/A | 2026
NORTH VALLEY | Tier 2 | OREGON TRAIL-1103 | 2020-10-22 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 787 | 44 | Conductor- Overhead | Sus | 2022, 2023 | 2024
NORTH VALLEY | Tier 2 | OREGON TRAIL-1104 | 2020-10-22 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 847 | 348 | Conductor- Overhead | Sus | N/A | N/A
NORTH VALLEY | Tier 3 | BUCKS CREEK-1103 | 2020-10-22 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 734 | 8 | Conductor- Overhead | Sus | N/A | N/A
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 2020-10-22 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 707 | 1359 | Conductor- Overhead | Sus | N/A | 2024, 2025, 2026
NORTH VALLEY | Tier 3 | VOLTA-1101 | 2020-10-29 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 269 | 1349 |  | Sus | 2022, 2023 | 2023, 2024, 2025, 2026
NORTH VALLEY | Tier 3 | BUCKS CREEK-1103 | 2020-11-03 | Distribution Circuit | Animal | Squirrel | 399 | 322 | Pothead(Riser Termination) | Sus | N/A | N/A
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 2020-11-06 | Substation - Distribution | Company Initiated | Planned- capital | 95 | 2034 |  | Sus | N/A | 2024, 2025, 2026
NORTH VALLEY | Tier 2 | ELK CREEK-1101 | 2020-11-06 | Distribution Circuit | Animal | Other | 121 | 902 | Recloser | Sus | N/A | 2023
NORTH VALLEY | Tier 3 | CHALLENGE SUB | 2020-11-14 | Distribution Circuit | Company Initiated | Planned- maintenance | 632 | 1522 |  | Sus | N/A | N/A
NORTH VALLEY | Tier 3 | CHALLENGE-1101 | 2020-12-07 | Distribution Circuit | Vegetation | Tree - fell into line | 1018 | 702 | Conductor- Overhead | Sus | N/A | N/A
NORTH VALLEY | Tier 2 | OREGON TRAIL-1104 | 2020-12-11 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 85 | 998 | Recloser | Sus | N/A | N/A
NORTH VALLEY | Tier 3 | CHALLENGE-1101 | 2020-12-14 | Distribution Circuit | Equipment Failure/Involved | Overhead | 205 | 702 | Conductor- Overhead | Sus | N/A | N/A
NORTH VALLEY | Tier 3 | ORO FINO-1101 | 2020-12-18 | Distribution Circuit | Company Initiated | Planned- capital | 352 | 7 |  | Sus | N/A | 2025, 2026
NORTH VALLEY | Tier 3 | VOLTA-1101 | 2021-01-07 | Distribution Circuit | Company Initiated | Operating error | 14 | 3959 | Circuit Breaker | Sus | 2022, 2023 | 2023, 2024, 2025, 2026
NORTH VALLEY | Tier 2 | HAMILTON BRANCH-1101 | 2021-01-18 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 13 | 2388 |  | Sus | N/A | N/A
NORTH VALLEY | Tier 3 | BUCKS CREEK-1101 | 2021-01-22 | Distribution Circuit | Company Initiated | Planned- capital | 85 | 5 |  | Sus | N/A | 2023
NORTH VALLEY | Tier 3 | ORO FINO-1101 | 2021-01-27 | Distribution Circuit | Vegetation | Tree - branch fell on line | 891 | 2336 | Conductor- Overhead | Sus | N/A | 2025, 2026
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 2021-01-27 | Distribution Circuit | Vegetation | Tree - fell into line | 924 | 899 | Crossarm- Wood | Sus | N/A | N/A
NORTH VALLEY | Tier 2 | CLARK ROAD-1101 | 2021-01-30 | Distribution Circuit | Equipment Failure/Involved | Underground | 302 | 25 | Connector or Splice (UG) | Sus | N/A | N/A
NORTH VALLEY | Tier 2 | SPANISH CREEK SUB | 2021-02-17 | Distribution Circuit | Company Initiated | Planned- capital | 299 | 35 |  | Sus | N/A | N/A
NORTH VALLEY | Tier 2 | ELK CREEK-1101 | 2021-02-24 | Transmission line | Equipment Failure/Involved | Overhead | 506 | 902 | Conductor- Overhead | Sus | N/A | 2023
NORTH VALLEY | Tier 3 | BIG BEND-1102 | 2021-03-10 | Distribution Circuit | Vegetation | Tree - fell into line | 532 | 303 | Conductor- Overhead | Sus | 2021, 2022 | 2023
NORTH VALLEY | Tier 3 | BIG BEND-1102 | 2021-04-05 | Distribution Circuit | Company Initiated | Planned- maintenance | 249 | 303 |  | Sus | 2021, 2022 | 2023
NORTH VALLEY | Tier 2 | FRENCH GULCH-1101 | 2021-04-11 | Distribution Circuit | Company Initiated | Planned- capital | 269 | 290 |  | Sus | N/A | N/A
NORTH VALLEY | Tier 3 | KANAKA-1101 | 2021-04-12 | Distribution Circuit | 3rd Party | Vehicle | 723 | 280 | Conductor- Overhead | Sus | 2020, 2022, 2023 | 2023
NORTH VALLEY | Tier 2 | ANTLER-1101 | 2021-04-17 | Substation - Distribution | Company Initiated | Planned- maintenance | 233 | 954 |  | Sus | 2021 | 2026
NORTH VALLEY | Tier 2 | GRAYS FLAT-0401 | 2021-05-18 | Distribution Circuit | Company Initiated | Planned- capital | 501 | 125 |  | Sus | N/A | 2023
NORTH VALLEY | Tier 2 | GRAYS FLAT-0401 | 2021-06-04 | Distribution Circuit | Company Initiated | Planned- capital | 259 | 125 |  | Sus | N/A | 2023
NORTH VALLEY | Tier 2 | PIT NO 3-2101 | 2021-06-22 | Distribution Circuit | Animal | Other | 169 | 154 | Circuit Breaker | Sus | N/A | 2024, 2025
NORTH VALLEY | Tier 3 | VOLTA-1101 | 2021-07-16 | Distribution Circuit | Wildfire Mitigation | Planned - WSIP/System Hardening | 571 | 1349 |  | Sus | 2022, 2023 | 2023, 2024, 2025, 2026
NORTH VALLEY | Tier 2 | SPANISH CREEK SUB | 2021-07-19 | Transmission line | Environmental/External | Fire- Forest/Grass | 168 | 914 | Footings- Tower or Pole | Sus | N/A | N/A
NORTH VALLEY | Tier 3 | CHALLENGE-1101 | 2021-08-20 | Distribution Circuit | Company Initiated | Planned- capital | 296 | 1597 |  | Sus | N/A | N/A
NORTH VALLEY | Tier 3 | CEDAR CREEK-1101 | 2021-08-27 | Distribution Circuit | Company Initiated | Planned- maintenance | 555 | 782 |  | Sus | N/A | N/A
NORTH VALLEY | Tier 2 | PIT NO 1-1101 | 2021-09-10 | Distribution Circuit | Animal | Other | 785 | 883 | Conductor- Overhead | Sus | N/A | N/A
NORTH VALLEY | Tier 2 | ANTLER-1101 | 2021-09-24 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 156 | 32 | Conductor- Overhead | Sus | 2021 | 2026
NORTH VALLEY | Tier 3 | CEDAR CREEK-1101 | 2021-10-01 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 159 | 782 |  | Sus | N/A | N/A
NORTH VALLEY | Tier 3 | BUCKS CREEK-1103 | 2021-10-08 | Distribution Circuit | Company Initiated | Planned- capital | 778 | 322 |  | Sus | N/A | N/A
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 2021-10-17 | Distribution Circuit | Equipment Failure/Involved | Overhead | 407 | 898 | Conductor- Overhead | Sus | N/A | N/A
NORTH VALLEY | Tier 2 | WILDWOOD SUB | 2021-11-14 | Transmission line | Equipment Failure/Involved | Overhead | 180 | 139 | Insulator | Sus | N/A | N/A
NORTH VALLEY | Tier 2 | PIT NO 1-1101 | 2021-11-18 | Transmission line | Company Initiated | Planned- capital | 854 | 883 |  | Sus | N/A | N/A
NORTH VALLEY | Tier 3 | VOLTA-1101 | 2021-11-24 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 114 | 1340 |  | Sus | 2022, 2023 | 2023, 2024, 2025, 2026
NORTH VALLEY | Tier 2 | CLARK ROAD-1101 | 2021-11-30 | Transmission line | Animal | Bird found | 80 | 1249 | Conductor- Overhead | Sus | N/A | N/A
NORTH VALLEY | Tier 3 | ORO FINO-1101 | 2021-11-30 | Transmission line | Company Initiated | Coordination failure | 69 | 3754 | Other | Sus | N/A | 2025, 2026
NORTH VALLEY | Tier 2 | ELK CREEK-1101 | 2021-12-18 | Distribution Circuit | Company Initiated | Planned- capital | 238 | 900 |  | Sus | N/A | 2023
NORTH VALLEY | Tier 3 | BIG BEND-1102 | 2022-04-11 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 326 | 152 |  | Sus | 2021, 2022 | 2023
NORTH VALLEY | Tier 2 | PIT NO 1-1101 | 2022-04-12 | Distribution Circuit | Company Initiated | Planned- capital | 582 | 883 |  | Sus | N/A | N/A
NORTH VALLEY | Tier 3 | KESWICK-1101 | 2022-05-03 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 17 | 531 | Conductor- Overhead | Sus | 2022 | 2023, 2026
NORTH VALLEY | Tier 3 | ORO FINO-1101 | 2022-05-19 | Distribution Circuit | Animal | Squirrel | 186 | 2379 | Fuse | Sus | N/A | 2025, 2026
NORTH VALLEY | Tier 3 | KANAKA SUB | 2022-05-20 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 477 | 539 |  | Sus | N/A | N/A
NORTH VALLEY | Tier 3 | BIG BEND-1102 | 2022-05-21 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 337 | 202 |  | Sus | 2021, 2022 | 2023
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 2022-06-03 | Distribution Circuit | Company Initiated | Planned- capital | 732 | 157 |  | Sus | N/A | N/A
NORTH VALLEY | Tier 3 | CHALLENGE-1101 | 2022-06-11 | Distribution Circuit | Equipment Failure/Involved | Overhead | 278 | 703 | Conductor- Overhead | Sus | N/A | N/A
NORTH VALLEY | Tier 3 | ORO FINO-1101 | 2022-06-17 | Distribution Circuit | Equipment Failure/Involved | Overhead | 239 | 2379 | Lightning Arrestor | Sus | N/A | 2025, 2026
NORTH VALLEY | Tier 2 | FRENCH GULCH-1102 | 2022-06-18 | Distribution Circuit | Company Initiated | Planned- capital | 292 | 38 |  | Sus | N/A | N/A
NORTH VALLEY | Tier 2 | PIT NO 3-2101 | 2022-06-21 | Distribution Circuit | Equipment Failure/Involved | Overhead | 868 | 152 | Conductor- Overhead | Sus | N/A | 2024, 2025
NORTH VALLEY | Tier 2 | BIG MEADOWS SUB | 2022-06-22 | Distribution Circuit | Animal | Other | 9 | 1389 | Conductor- Overhead | Sus | N/A | N/A
NORTH VALLEY | Tier 2 | ELK CREEK-1101 | 2022-07-01 | Distribution Circuit | Equipment Failure/Involved | Overhead | 211 | 901 | Conductor- Overhead | Sus | N/A | 2023
NORTH VALLEY | Tier 2 | PIT NO 1-1101 | 2022-07-08 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 378 | 999 |  | Sus | N/A | N/A
NORTH VALLEY | Tier 2 | RISING RIVER-1101 | 2022-07-10 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 121 | 725 |  | Sus | N/A | N/A
NORTH VALLEY | Tier 2 | PIT NO 5-1101 | 2022-07-22 | Distribution Circuit | Company Initiated | Planned- capital | 522 | 7 |  | Sus | N/A | N/A
NORTH VALLEY | Tier 3 | BIG BEND-1102 | 2022-07-25 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 146 | 325 |  | Sus | 2021, 2022 | 2023
NORTH VALLEY | Tier 3 | ORO FINO-1101 | 2022-08-23 | Distribution Circuit | Equipment Failure/Involved | Overhead | 310 | 1910 | Crossarm- Wood | Sus | N/A | 2025, 2026
NORTH VALLEY | Tier 3 | BUCKS CREEK SUB | 2022-08-30 | Generation | Company Initiated | Personnel- company | 29 | 322 | Circuit Breaker | Sus | N/A | N/A
NORTH VALLEY | Tier 2 | CHESTER-1102 | 2022-09-29 | Distribution Circuit | Equipment Failure/Involved | Overhead | 89 | 90 | Recloser | Sus | N/A | N/A
NORTH VALLEY | Tier 2 | RISING RIVER-1101 | 2022-10-20 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 117 | 725 |  | Sus | N/A | N/A
NORTH VALLEY | Tier 2 | WHITMORE-1101 | 2022-10-28 | Distribution Circuit | Company Initiated | Planned- maintenance | 311 | 541 |  | Sus | N/A | N/A
NORTH VALLEY | Tier 3 | KANAKA SUB | 2022-11-01 | Distribution Circuit | Vegetation | Tree - fell into line | 296 | 548 | Conductor- Overhead | Sus | N/A | N/A
NORTH VALLEY | Tier 2 | ELK CREEK-1101 | 2022-11-05 | Distribution Circuit | Company Initiated | Planned- maintenance | 409 | 725 |  | Sus | N/A | 2023
NORTH VALLEY | Tier 3 | BIG BEND-1101 | 2022-11-06 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 112 | 311 |  | Sus | N/A | N/A
NORTH VALLEY | Tier 3 | BIG BEND-1101 | 2022-11-18 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1206 | 312 | Other | Sus | N/A | N/A
NORTH VALLEY | Tier 2 | HAMILTON BRANCH-1101 | 2022-12-01 | Distribution Circuit | Vegetation | Tree - branch fell on line | 61 | 2598 | Conductor- Overhead | Sus | N/A | N/A
NORTH VALLEY | Tier 3 | BIG BEND-1101 | 2022-12-10 | Distribution Circuit | Vegetation | Tree - fell into line | 545 | 312 | Conductor- Overhead | Sus | N/A | N/A
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 2022-12-10 | Distribution Circuit | Vegetation | Tree - fell into line | 448 | 888 | Crossarm- Wood | Sus | N/A | N/A
PENINSULA | Tier 2 | EMERALD LAKE-0402 | 2020-12-14 | Distribution Circuit | Company Initiated | Planned- capital | 12 | 290 |  | Sus | N/A | N/A
PENINSULA | Tier 2 | EMERALD LAKE SUB | 2021-06-20 | Distribution Circuit | Wildfire Mitigation | Planned - WSIP/System Hardening | 218 | 3 |  | Sus | N/A | N/A
PENINSULA | Tier 2 | EMERALD LAKE-0401 | 2022-06-29 | Distribution Circuit | Equipment Failure/Involved | Overhead | 297 | 1137 | Conductor- Overhead | Sus | N/A | N/A
PENINSULA | Tier 2 | EMERALD LAKE-0401 | 2022-07-11 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 161 | 1140 |  | Sus | N/A | N/A
PENINSULA | Tier 2 | EMERALD LAKE-0401 | 2022-08-16 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 184 | 975 | Circuit Breaker | Sus | N/A | N/A
PENINSULA | Tier 2 | EMERALD LAKE-0401 | 2022-08-17 | Distribution Circuit | Company Initiated | Operating error | 15 | 975 | Circuit Breaker | Sus | N/A | N/A
SACRAMENTO | Tier 2 | DOBBINS-1101 | 2020-08-17 | Distribution Circuit | Equipment Failure/Involved | Overhead | 65 | 918 | Switch (OH) | Sus | N/A | N/A
SACRAMENTO | Tier 2 | NARROWS-2102 | 2020-11-07 | Distribution Circuit | Environmental/External | Lightning | 85 | 3436 | Recloser | Sus | N/A | 2026
SACRAMENTO | Tier 2 | NARROWS SUB | 2020-12-26 | Substation - Distribution | Animal | Other | 265 | 4235 | Bus | Sus | N/A | N/A
SACRAMENTO | Tier 2 | NARROWS SUB | 2021-01-12 | Substation - Distribution | Animal | Other | 108 | 4235 | Insulator | Sus | N/A | N/A
SACRAMENTO | Tier 2 | NARROWS-2102 | 2022-12-10 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 179 | 3446 |  | Sus | N/A | 2026
SAN JOSE | Tier 2 | MORGAN HILL-2111 | 2021-12-24 | Distribution Circuit | Equipment Failure/Involved | Overhead | 688 | 395 | Connector or Splice (OH) | Sus | N/A | N/A
SIERRA | Tier 2 | ALLEGHANY-1101 | 2020-01-07 | Distribution Circuit | Wildfire Mitigation | Planned - WSIP/System Hardening | 6 | 555 |  | Sus | N/A | N/A
SIERRA | Tier 3 | EL DORADO PH-2102 | 2020-01-18 | Distribution Circuit | Equipment Failure/Involved | Overhead | 438 | 2 | Crossarm- Wood | Sus | N/A | 2025, 2026
SIERRA | Tier 2 | ALLEGHANY-1101 | 2020-01-18 | Distribution Circuit | Company Initiated | Return Circuit Normal | 7 | 555 | Other | Sus | N/A | N/A
SIERRA | Tier 2 | GRASS VALLEY SUB | 2020-01-28 | Substation - Distribution | Company Initiated | Operating error | 93 | 3709 | Circuit Breaker | Sus | N/A | N/A
SIERRA | Tier 2 | APPLE HILL-2102 | 2020-02-03 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 118 | 4509 |  | Sus | N/A | 2024, 2025, 2026
SIERRA | Tier 3 | DRUM-1101 | 2020-03-15 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 181 | 198 |  | Sus | N/A | N/A
SIERRA | Tier 3 | EL DORADO PH-2102 | 2020-03-15 | Distribution Circuit | Vegetation | Tree - fell into line | 865 | 773 | Conductor- Overhead | Sus | N/A | 2025, 2026
SIERRA | Tier 3 | ALLEGHANY-1102 | 2020-04-05 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2063 | 165 | Conductor- Overhead | Sus | N/A | 2025, 2026
SIERRA | Tier 2 | APPLE HILL-1103 | 2020-05-06 | Distribution Circuit | 3rd Party | Vehicle | 528 | 1288 | Pole-Wood | Sus | N/A | N/A
SIERRA | Tier 2 | NARROWS-2101 | 2020-05-10 | Substation - Distribution | Animal | Other | 9 | 532 | Bus | Sus | N/A | N/A
SIERRA | Tier 3 | DRUM-1101 | 2020-05-28 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 149 | 199 | Conductor- Overhead | Sus | N/A | N/A
SIERRA | Tier 3 | WASHINGTON CITY SUB | 2020-06-22 | Generation | Equipment Failure/Involved | Electrical Overload | 145 | 165 | Circuit Breaker | Sus | N/A | N/A
SIERRA | Tier 2 | SUMMIT-1102 | 2020-06-22 | Distribution Circuit | Equipment Failure/Involved | Underground | 394 | 294 | Conductor- Underground | Sus | N/A | N/A
SIERRA | Tier 3 | ALLEGHANY SUB | 2020-06-22 | Generation | Company Initiated | Other Circuits | 1393 | 519 | Generator | Sus | N/A | N/A
SIERRA | Tier 2 | SUMMIT-1102 | 2020-08-14 | Distribution Circuit | Company Initiated | Rotating Outage | 50 | 295 |  | Sus | N/A | N/A
SIERRA | Tier 3 | ALLEGHANY SUB | 2020-09-04 | Substation - Distribution | Company Initiated | Planned- maintenance | 8 | 142 |  | Sus | N/A | N/A
SIERRA | Tier 3 | ALLEGHANY-1102 | 2020-09-09 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 148 | Pole-Wood | Sus | N/A | 2025, 2026
SIERRA | Tier 2 | WEIMAR-1101 | 2020-09-25 | Distribution Circuit | Animal | Squirrel | 114 | 1649 | Cutout- fuse holder | Sus | N/A | N/A
SIERRA | Tier 3 | PIKE CITY-1102 | 2020-09-27 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 1177 | 27 | Conductor- Overhead | Sus | N/A | N/A
SIERRA | Tier 3 | PIKE CITY-1101 | 2020-09-27 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 1244 | 241 | Conductor- Overhead | Sus | N/A | 2025, 2026
SIERRA | Tier 3 | ALLEGHANY-1101 | 2020-10-04 | Distribution Circuit | Wildfire Mitigation | Planned - WSIP/System Hardening | 53 | 520 | Recloser | Sus | N/A | N/A
SIERRA | Tier 2 | ALLEGHANY SUB | 2020-10-04 | Substation - Distribution | Wildfire Mitigation | Planned - WSIP/System Hardening | 6 | 555 | Generator | Sus | N/A | N/A
SIERRA | Tier 2 | GRASS VALLEY-1103 | 2020-11-02 | Distribution Circuit | Vegetation | Tree - fell into line | 186 | 1478 | Conductor- Overhead | Sus | N/A | N/A
SIERRA | Tier 2 | PLACERVILLE-1110 | 2020-11-02 | Distribution Circuit | Vegetation | Tree - fell into line | 495 | 1592 | Conductor- Overhead | Sus | N/A | N/A
SIERRA | Tier 3 | PIKE CITY-1101 | 2020-12-04 | Distribution Circuit | Wildfire Mitigation | Planned - WSIP/System Hardening | 464 | 440 |  | Sus | N/A | 2025, 2026
SIERRA | Tier 2 | ALLEGHANY SUB | 2020-12-05 | Transmission line | Wildfire Mitigation | Planned - WSIP/System Hardening | 6 | 556 |  | Sus | N/A | N/A
SIERRA | Tier 2 | APPLE HILL-1103 | 2020-12-16 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 25 | 1538 |  | Sus | N/A | N/A
SIERRA | Tier 3 | ALLEGHANY-1102 | 2021-01-18 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 22 | 165 |  | Sus | N/A | 2025, 2026
SIERRA | Tier 3 | DRUM-1101 | 2021-01-19 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 16 | 199 |  | Sus | N/A | N/A
SIERRA | Tier 3 | ALLEGHANY-1102 | 2021-01-28 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 643 | 165 |  | Sus | N/A | 2025, 2026
SIERRA | Tier 3 | ALLEGHANY-1102 | 2021-01-28 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 6 | 165 |  | Sus | N/A | 2025, 2026
SIERRA | Tier 3 | BONNIE NOOK-1102 | 2021-01-28 | Distribution Circuit | Vegetation | Tree - fell into line | 1052 | 362 | Conductor- Overhead | Sus | N/A | 2024, 2025, 2026
SIERRA | Tier 3 | FORESTHILL-1101 | 2021-01-29 | Distribution Circuit | Vegetation | Tree - fell into line | 1041 | 581 | Insulator | Sus | N/A | 2023, 2024, 2025, 2026
SIERRA | Tier 3 | WASHINGTON CITY SUB | 2021-02-05 | Substation - Distribution | Company Initiated | Return Circuit Normal | 20 | 142 | Generator | Sus | N/A | N/A
SIERRA | Tier 3 | BONNIE NOOK-1102 | 2021-03-11 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 518 | Conductor- Overhead | Sus | N/A | 2024, 2025, 2026
SIERRA | Tier 3 | COLUMBIA HILL-1101 | 2021-03-13 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 341 | 1153 | Pole-Wood | Sus | 2020 | N/A
SIERRA | Tier 2 | ALLEGHANY SUB | 2021-04-02 | Distribution Circuit | Company Initiated | Planned- capital | 7 | 605 |  | Sus | N/A | N/A
SIERRA | Tier 2 | ALLEGHANY SUB | 2021-04-26 | Distribution Circuit | Company Initiated | Planned- capital | 10 | 564 |  | Sus | N/A | N/A
SIERRA | Tier 3 | COLUMBIA HILL-1101 | 2021-04-28 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 61 | 93 |  | Sus | 2020 | N/A
SIERRA | Tier 3 | SHINGLE SPRINGS-2108 | 2021-05-02 | Distribution Circuit | Vegetation | Tree - fell into line | 134 | 2887 | Conductor- Overhead | Sus | N/A | N/A
SIERRA | Tier 3 | SHINGLE SPRINGS-1103 | 2021-06-02 | Distribution Circuit | 3rd Party | Vehicle | 52 | 1147 | Anchor or Guy | Sus | N/A | N/A
SIERRA | Tier 3 | COLUMBIA HILL-1101 | 2021-06-21 | Distribution Circuit | 3rd Party | Vehicle | 424 | 1160 | Pole-Wood | Sus | 2020 | N/A
SIERRA | Tier 2 | NARROWS-2105 | 2021-07-10 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 848 | 4048 |  | Sus | N/A | N/A
SIERRA | Tier 3 | SHINGLE SPRINGS-2108 | 2021-07-27 | Distribution Circuit | Animal | Squirrel | 197 | 2891 | Recloser | Sus | N/A | N/A
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 2021-08-02 | Distribution Circuit | Equipment Failure/Involved | Substation | 6 | 3694 | Other | Sus | 2022 | 2023, 2024
SIERRA | Tier 2 | APPLE HILL-1104 | 2021-08-06 | Distribution Circuit | Vegetation | Tree - fell into line | 347 | 2485 | Crossarm- Wood | Sus | N/A | 2024, 2025
SIERRA | Tier 2 | GRASS VALLEY-1102 | 2021-08-25 | Distribution Circuit | Animal | Squirrel | 294 | 1468 | Transformer (OH) | Sus | N/A | N/A
SIERRA | Tier 3 | SHINGLE SPRINGS-2110 | 2021-09-05 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 773 | 1221 |  | Sus | N/A | N/A
SIERRA | Tier 2 | WEIMAR-1102 | 2021-09-05 | Distribution Circuit | 3rd Party | Vehicle | 655 | 640 | Pole-Wood | Sus | N/A | N/A
SIERRA | Tier 2 | HALSEY-1102 | 2021-09-07 | Distribution Circuit | Vegetation | Tree - fell into line | 456 | 2117 | Conductor- Overhead | Sus | N/A | N/A
SIERRA | Tier 3 | ALLEGHANY-1102 | 2021-09-09 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 528 | 164 |  | Sus | N/A | 2025, 2026
SIERRA | Tier 2 | SHADY GLEN-1101 | 2021-09-14 | Distribution Circuit | Animal | Bird found | 328 | 487 | Recloser | Sus | 2021, 2022 | 2024, 2026
SIERRA | Tier 3 | ALLEGHANY-1102 | 2021-09-22 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 397 | 164 |  | Sus | N/A | 2025, 2026
SIERRA | Tier 3 | SHINGLE SPRINGS-2110 | 2021-09-26 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 258 | 1293 |  | Sus | N/A | N/A
SIERRA | Tier 3 | SHINGLE SPRINGS-2108 | 2021-10-08 | Distribution Circuit | Company Initiated | Planned- capital | 259 | 3 |  | Sus | N/A | N/A
SIERRA | Tier 3 | SHINGLE SPRINGS-2105 | 2021-10-21 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 3156 | Other | Sus | N/A | N/A
SIERRA | Tier 2 | SIERRA CITY DIESEL SUB | 2021-10-26 | Substation - Distribution | Company Initiated | Return Circuit Normal | 7 | 357 | Generator | Sus | N/A | N/A
SIERRA | Tier 3 | COLUMBIA HILL-1101 | 2021-12-14 | Distribution Circuit | Vegetation | Tree - fell into line | 721 | 93 | Conductor- Overhead | Sus | 2020 | N/A
SIERRA | Tier 2 | SHADY GLEN-1102 | 2022-04-13 | Distribution Circuit | 3rd Party | Vehicle | 41 | 927 | Conductor- Overhead | Sus | N/A | 2025, 2026
SIERRA | Tier 3 | ALLEGHANY-1102 | 2022-05-17 | Distribution Circuit | Company Initiated | Planned- maintenance | 12 | 142 |  | Sus | N/A | 2025, 2026
SIERRA | Tier 2 | WEIMAR-1101 | 2022-05-19 | Distribution Circuit | Vegetation | Tree - fell into line | 89 | 2169 | Conductor- Overhead | Sus | N/A | N/A
SIERRA | Tier 3 | ALLEGHANY-1101 | 2022-06-13 | Distribution Circuit | Company Initiated | Planned- maintenance | 41 | 520 |  | Sus | N/A | N/A
SIERRA | Tier 2 | WISE-1101 | 2022-06-15 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 181 | 2793 |  | Sus | N/A | N/A
SIERRA | Tier 3 | COLUMBIA HILL-1101 | 2022-06-22 | Distribution Circuit | Company Initiated | Planned- maintenance | 594 | 1163 |  | Sus | 2020 | N/A
SIERRA | Tier 3 | BONNIE NOOK-1102 | 2022-06-22 | Distribution Circuit | 3rd Party | Vehicle | 281 | 535 | Pole-Wood | Sus | N/A | 2024, 2025, 2026
SIERRA | Tier 3 | WASHINGTON CITY SUB | 2022-06-22 | Substation - Distribution | Company Initiated | Planned- capital | 16 | 142 |  | Sus | N/A | N/A
SIERRA | Tier 3 | DRUM-1101 | 2022-06-25 | Distribution Circuit | 3rd Party | Other | 522 | 203 | Conductor- Overhead | Sus | N/A | N/A
SIERRA | Tier 2 | GRASS VALLEY-1103 | 2022-06-27 | Distribution Circuit | Company Initiated | Planned- capital | 575 | 79 |  | Sus | N/A | N/A
SIERRA | Tier 3 | ALLEGHANY SUB | 2022-06-29 | Distribution Circuit | Equipment Failure/Involved | Substation | 386 | 520 | Generator | Sus | N/A | N/A
SIERRA | Tier 3 | DOWNIEVILLE DIESEL SUB | 2022-07-01 | Distribution Circuit | Equipment Failure/Involved | Substation | 110 | 520 | Generator | Sus | N/A | N/A
SIERRA | Tier 2 | SIERRA CITY DIESEL SUB | 2022-07-02 | Distribution Circuit | Company Initiated | Return Circuit Normal | 11 | 556 | Conductor- Overhead | Sus | N/A | N/A
SIERRA | Tier 3 | WASHINGTON CITY SUB | 2022-07-19 | Distribution Circuit | Company Initiated | Planned- capital | 10 | 142 |  | Sus | N/A | N/A
SIERRA | Tier 3 | DRUM-1101 | 2022-07-28 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 218 | 203 |  | Sus | N/A | N/A
SIERRA | Tier 3 | WASHINGTON CITY SUB | 2022-08-01 | Distribution Circuit | Company Initiated | Planned- capital | 10 | 142 |  | Sus | N/A | N/A
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 2022-08-11 | Distribution Circuit | Animal | Squirrel | 219 | 3698 | Conductor- Overhead | Sus | 2022 | 2023, 2024
SIERRA | Tier 3 | DRUM-1101 | 2022-08-13 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 249 | 202 |  | Sus | N/A | N/A
SIERRA | Tier 2 | NARROWS SUB | 2022-08-18 | Substation - Distribution | Animal | Other | 103 | 3984 | Bus | Sus | N/A | N/A
SIERRA | Tier 2 | SUMMIT-1102 | 2022-08-22 | Distribution Circuit | 3rd Party | Dig in- 3rd party | 272 | 296 | Conductor- Underground | Sus | N/A | N/A
SIERRA | Tier 3 | ALLEGHANY-1102 | 2022-08-23 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 312 | 164 |  | Sus | N/A | 2025, 2026
SIERRA | Tier 3 | WASHINGTON CITY SUB | 2022-08-23 | Distribution Circuit | Company Initiated | Return Circuit Normal | 11 | 142 | Conductor- Overhead | Sus | N/A | N/A
SIERRA | Tier 3 | BONNIE NOOK-1102 | 2022-09-05 | Distribution Circuit | Animal | Squirrel | 253 | 535 | Cutout- fuse holder | Sus | N/A | 2024, 2025, 2026
SIERRA | Tier 3 | BONNIE NOOK-1101 | 2022-09-13 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 233 | 492 | Conductor- Overhead | Sus | N/A | 2025, 2026
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 2022-09-20 | Distribution Circuit | Equipment Failure/Involved | Overhead | 382 | 3703 | Connector or Splice (OH) | Sus | 2022 | 2023, 2024
SIERRA | Tier 2 | WEIMAR-1101 | 2022-09-24 | Substation - Distribution | Animal | Squirrel | 70 | 1786 | Bus | Sus | N/A | N/A
SIERRA | Tier 3 | BRUNSWICK-1102 | 2022-09-25 | Distribution Circuit | Animal | Bird found | 84 | 1465 | Conductor- Overhead | Sus | N/A | 2024, 2025, 2026
SIERRA | Tier 3 | DRUM-1101 | 2022-10-21 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 873 | 202 |  | Sus | N/A | N/A
SIERRA | Tier 3 | FORESTHILL-1101 | 2022-10-22 | Distribution Circuit | Vegetation | Tree - branch fell on line | 91 | 2274 | Conductor- Overhead | Sus | N/A | 2023, 2024, 2025, 2026
SIERRA | Tier 3 | SHINGLE SPRINGS-2108 | 2022-10-23 | Distribution Circuit | 3rd Party | Vehicle | 911 | 3138 | Pole-Wood | Sus | N/A | N/A
SIERRA | Tier 2 | NARROWS-2101 | 2022-10-25 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 205 | 4310 |  | Sus | N/A | N/A
SIERRA | Tier 3 | BONNIE NOOK-1102 | 2022-11-02 | Distribution Circuit | Vegetation | Tree - fell into line | 91 | 535 | Conductor- Overhead | Sus | N/A | 2024, 2025, 2026
SIERRA | Tier 3 | BONNIE NOOK-1102 | 2022-11-09 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 15 | 355 |  | Sus | N/A | 2024, 2025, 2026
SIERRA | Tier 3 | WASHINGTON CITY SUB | 2022-11-12 | Distribution Circuit | Company Initiated | Return Circuit Normal | 9 | 142 | Conductor- Overhead | Sus | N/A | N/A
SIERRA | Tier 3 | COLUMBIA HILL-1101 | 2022-12-10 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 15 | 1166 |  | Sus | 2020 | N/A
SONOMA | Tier 3 | MONTE RIO-1113 | 2020-01-29 | Distribution Circuit | Vegetation | Tree - fell into line | 573 | 3919 | Pole-Wood | Sus | N/A | N/A
SONOMA | Tier 2 | COTATI-1103 | 2020-03-29 | Distribution Circuit | Equipment Failure/Involved | Overhead | 239 | 1455 | Transformer (OH) | Sus | N/A | N/A
SONOMA | Tier 2 | COTATI-1103 | 2020-05-01 | Distribution Circuit | Animal | Bird found | 802 | 1460 | Conductor- Overhead | Sus | N/A | N/A
SONOMA | Tier 2 | RINCON-1104 | 2020-05-11 | Distribution Circuit | 3rd Party | Vehicle | 489 | 3016 | Pole-Wood | Sus | 2021 | N/A
SONOMA | Tier 3 | MONTE RIO-1113 | 2020-06-28 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 122 | 3919 |  | Sus | N/A | N/A
SONOMA | Tier 2 | COTATI-1102 | 2020-08-14 | Distribution Circuit | Company Initiated | Rotating Outage | 169 | 5596 |  | Sus | N/A | N/A
SONOMA | Tier 2 | COTATI-1103 | 2020-08-14 | Distribution Circuit | Company Initiated | Rotating Outage | 151 | 1463 |  | Sus | N/A | N/A
SONOMA | Tier 2 | COTATI-1104 | 2020-08-14 | Distribution Circuit | Company Initiated | Rotating Outage | 150 | 2019 |  | Sus | N/A | N/A
SONOMA | Tier 2 | COTATI-1105 | 2020-08-14 | Distribution Circuit | Company Initiated | Rotating Outage | 150 | 3084 |  | Sus | N/A | N/A
SONOMA | Tier 3 | MONTE RIO-1111 | 2020-08-14 | Distribution Circuit | Company Initiated | Rotating Outage | 164 | 1754 |  | Sus | N/A | N/A
SONOMA | Tier 3 | MONTE RIO-1112 | 2020-08-14 | Distribution Circuit | Company Initiated | Rotating Outage | 187 | 1155 |  | Sus | 2019 | N/A
SONOMA | Tier 3 | MONTE RIO-1113 | 2020-08-14 | Distribution Circuit | Company Initiated | Rotating Outage | 163 | 3918 |  | Sus | N/A | N/A
SONOMA | Tier 2 | RINCON-1104 | 2020-09-08 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 1119 | 1253 | Conductor- Overhead | Sus | 2021 | N/A
SONOMA | Tier 2 | RINCON-1104 | 2020-10-17 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 111 | 3469 |  | Sus | 2021 | N/A
SONOMA | Tier 2 | MOLINO-1102 | 2020-10-26 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 601 | Conductor- Overhead | Sus | N/A | 2024
SONOMA | Tier 2 | RINCON-1104 | 2020-11-28 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 100 | 3469 |  | Sus | 2021 | N/A
SONOMA | Tier 3 | MONTE RIO-1113 | 2021-01-27 | Distribution Circuit | Vegetation | Tree - branch fell on line | 181 | 3918 | Conductor- Overhead | Sus | N/A | N/A
SONOMA | Tier 2 | COTATI-1103 | 2021-07-30 | Distribution Circuit | Equipment Failure/Involved | Overhead | 601 | 1459 | Insulator | Sus | N/A | N/A
SONOMA | Tier 3 | MONTE RIO-1113 | 2022-08-21 | Distribution Circuit | Vegetation | Tree - branch fell on line | 106 | 3919 | Conductor- Overhead | Sus | N/A | N/A
SONOMA | Tier 2 | CLOVERDALE-1102 | 2022-09-14 | Distribution Circuit | 3rd Party | Other | 85 | 2598 | Conductor- Overhead | Sus | N/A | N/A
STOCKTON | Tier 3 | WEST POINT-1102 | 2020-01-09 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 60 | 2999 | Conductor- Overhead | Sus | N/A | 2025, 2026
STOCKTON | Tier 2 | PINE GROVE-1101 | 2020-02-23 | Distribution Circuit | Vegetation | Tree - fell into line | 329 | 1379 | Conductor- Overhead | Sus | N/A | 2025, 2026
STOCKTON | Tier 3 | WEST POINT-1102 | 2020-03-16 | Distribution Circuit | Vegetation | Tree - fell into line | 210 | 959 | Conductor- Overhead | Sus | N/A | 2025, 2026
STOCKTON | Tier 2 | IONE-1101 | 2020-07-23 | Distribution Circuit | 3rd Party | Vehicle | 166 | 854 | Conductor- Overhead | Sus | N/A | N/A
STOCKTON | Tier 2 | ELECTRA-1101 | 2020-08-05 | Distribution Circuit | 3rd Party | Vandalism | 89 | 1912 | Switch (OH) | Sus | N/A | 2025, 2026
STOCKTON | Tier 2 | FROGTOWN-1702 | 2020-08-19 | Distribution Circuit | 3rd Party | Customer Equipment | 86 | 4180 | Customer Equipment | Sus | N/A | 2023
STOCKTON | Tier 3 | WEST POINT-1101 | 2020-08-31 | Distribution Circuit | Company Initiated | Planned- capital | 320 | 4 |  | Sus | N/A | 2025, 2026
STOCKTON | Tier 2 | SALT SPRINGS-2101 | 2020-09-27 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 1176 | 273 | Conductor- Overhead | Sus | N/A | N/A
STOCKTON | Tier 2 | SALT SPRINGS-2102 | 2020-09-27 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 1120 | 1742 | Conductor- Overhead | Sus | N/A | 2026
STOCKTON | Tier 3 | WEST POINT-1101 | 2020-09-27 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 949 | 6 | Conductor- Overhead | Sus | N/A | 2025, 2026
STOCKTON | Tier 3 | WEST POINT-1102 | 2020-09-27 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 916 | 468 | Conductor- Overhead | Sus | N/A | 2025, 2026
STOCKTON | Tier 3 | TIGER CREEK-0201 | 2020-09-27 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 1036 | 14 | Conductor- Overhead | Sus | N/A | 2024
STOCKTON | Tier 2 | CLAY-1102 | 2020-11-18 | Distribution Circuit | 3rd Party | Customer Equipment | 146 | 2 | Recloser | Sus | N/A | N/A
STOCKTON | Tier 2 | PINE GROVE-1101 | 2021-01-25 | Distribution Circuit | Vegetation | Tree - fell into line | 883 | 1376 | Pole-Wood | Sus | N/A | 2025, 2026
STOCKTON | Tier 2 | FROGTOWN-1702 | 2021-02-06 | Substation - Distribution | Equipment Failure/Involved | Substation | 130 | 6142 | PT/CCVT | Sus | N/A | 2023
STOCKTON | Tier 3 | WEST POINT-1102 | 2021-04-16 | Transmission line | Equipment Failure/Involved | Overhead | 99 | 905 | Connector or Splice (OH) | Sus | N/A | 2025, 2026
STOCKTON | Tier 2 | NORTH BRANCH-1101 | 2021-05-14 | Distribution Circuit | Equipment Failure/Involved | Overhead | 257 | 1321 | Lightning Arrestor | Sus | N/A | 2024
STOCKTON | Tier 3 | TIGER CREEK-0201 | 2021-06-29 | Distribution Circuit | Company Initiated | Planned- capital | 564 | 14 |  | Sus | N/A | 2024
STOCKTON | Tier 2 | SALT SPRINGS-2101 | 2021-07-01 | Distribution Circuit | Equipment Failure/Involved | Underground | 204 | 937 | Conductor- Underground | Sus | N/A | N/A
STOCKTON | Tier 2 | SALT SPRINGS-2101 | 2021-07-01 | Distribution Circuit | Equipment Failure/Involved | Underground | 7 | 56 | Conductor- Underground | Sus | N/A | N/A
STOCKTON | Tier 2 | CLAY-1102 | 2021-07-21 | Distribution Circuit | 3rd Party | Customer Equipment | 153 | 3 | Connector or Splice (OH) | Sus | N/A | N/A
STOCKTON | Tier 2 | SALT SPRINGS-2101 | 2021-07-27 | Distribution Circuit | Company Initiated | Return Circuit Normal | 34 | 984 | Conductor- Underground | Sus | N/A | N/A
STOCKTON | Tier 2 | NORTH BRANCH-1101 | 2021-07-27 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 585 | 1444 |  | Sus | N/A | 2024
STOCKTON | Tier 2 | CLAY-1102 | 2021-09-21 | Distribution Circuit | 3rd Party | Customer Equipment | 73 | 3 | Customer Equipment | Sus | N/A | N/A
STOCKTON | Tier 3 | WEST POINT-1101 | 2021-10-07 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 107 | 1761 |  | Sus | N/A | 2025, 2026
STOCKTON | Tier 2 | NORTH BRANCH-1101 | 2021-10-24 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 103 | 1301 |  | Sus | N/A | 2024
STOCKTON | Tier 2 | NORTH BRANCH-1101 | 2021-10-24 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 52 | 1301 |  | Sus | N/A | 2024
STOCKTON | Tier 3 | WEST POINT-1102 | 2021-11-02 | Distribution Circuit | Company Initiated | Planned- capital | 7 | 2987 |  | Sus | N/A | 2025, 2026
STOCKTON | Tier 2 | MARTELL-1101 | 2021-12-13 | Distribution Circuit | Vegetation | Tree - bark fell into line | 369 | 2275 | Conductor- Overhead | Sus | 2022, 2023 | 2024
STOCKTON | Tier 3 | PINE GROVE SUB | 2022-05-27 | Distribution Circuit | Company Initiated | Planned- capital | 6 | 4402 |  | Sus | N/A | N/A
STOCKTON | Tier 2 | PINE GROVE SUB | 2022-05-27 | Distribution Circuit | Company Initiated | Planned- capital | 7 | 1373 |  | Sus | N/A | N/A
STOCKTON | Tier 3 | WEST POINT SUB | 2022-05-27 | Distribution Circuit | Company Initiated | Planned- capital | 12 | 2403 |  | Sus | N/A | N/A
STOCKTON | Tier 2 | CLAY-1102 | 2022-05-30 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 14 | 3 |  | Sus | N/A | N/A
STOCKTON | Tier 2 | CLAY-1102 | 2022-05-31 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 25 | 3 |  | Sus | N/A | N/A
STOCKTON | Tier 2 | CLAY-1102 | 2022-07-04 | Distribution Circuit | 3rd Party | Customer Equipment | 91 | 3 | Conductor- Overhead | Sus | N/A | N/A
STOCKTON | Tier 3 | TIGER CREEK-0201 | 2022-07-07 | Distribution Circuit | Company Initiated | Return Circuit Normal | 7 | 14 | Conductor- Overhead | Sus | N/A | 2024
STOCKTON | Tier 2 | CLAY-1102 | 2022-09-16 | Distribution Circuit | 3rd Party | Customer Equipment | 62 | 3 | Customer Equipment | Sus | N/A | N/A
STOCKTON | Tier 2 | CLAY-1101 | 2022-09-18 | Distribution Circuit | Vegetation | Tree - grew into line | 186 | 1730 | Conductor- Overhead | Sus | N/A | N/A
STOCKTON | Tier 2 | PINE GROVE-1102 | 2022-09-19 | Distribution Circuit | Equipment Failure/Involved | Overhead | 524 | 4403 | Crossarm- Wood | Sus | 2022 | 2023, 2024, 2025, 2026
STOCKTON | Tier 2 | CLAY-1101 | 2022-09-28 | Distribution Circuit | Animal | Bird found | 228 | 1730 | Transformer (OH) | Sus | N/A | N/A
STOCKTON | Tier 2 | OLETA-1101 | 2022-11-01 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 43 | 1740 |  | Sus | N/A | N/A
STOCKTON | Tier 2 | IONE-1101 | 2022-11-08 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 165 | 1007 |  | Sus | N/A | N/A
STOCKTON | Tier 2 | CLAY-1103 | 2022-12-13 | Distribution Circuit | Equipment Failure/Involved | Overhead | 879 | 1655 | Connector or Splice (OH) | Sus | N/A | N/A
YOSEMITE | Tier 2 | SAN JOAQUIN #3 PH-1103 | 2020-02-09 | Distribution Circuit | Vegetation | Tree - fell into line | 456 | 743 | Conductor- Overhead | Sus | N/A | N/A
YOSEMITE | Tier 3 | MIWUK-1702 | 2020-02-11 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 61 | 3756 | Service conductor | Sus | 2021 | N/A
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 2020-05-17 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 23 | 1279 |  | Sus | N/A | N/A
YOSEMITE | Tier 2 | COARSEGOLD-2102 | 2020-05-17 | Distribution Circuit | Animal | Other | 118 | 1337 | Regulator | Sus | N/A | N/A
YOSEMITE | Tier 3 | OAKHURST-1101 | 2020-07-29 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 140 | 3025 | Connector or Splice (OH) | Sus | 2022 | N/A
YOSEMITE | Tier 2 | INDIAN FLAT-1104 | 2020-07-30 | Distribution Circuit | Company Initiated | Planned- capital | 504 | 561 |  | Sus | N/A | 2026
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 2020-08-24 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 231 | 1106 |  | Sus | N/A | N/A
YOSEMITE | Tier 3 | MIWUK-1701 | 2020-08-24 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 82 | 3718 | Conductor- Overhead | Sus | N/A | N/A
YOSEMITE | Tier 3 | OAKHURST-1102 | 2020-09-22 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 50 | 1105 |  | Sus | N/A | N/A
YOSEMITE | Tier 2 | COARSEGOLD-2102 | 2020-10-25 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 1084 | 63 | Conductor- Overhead | Sus | N/A | N/A
YOSEMITE | Tier 2 | SAN JOAQUIN #3 PH-1101 | 2020-10-25 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 1380 | 9 | Conductor- Overhead | Sus | N/A | N/A
YOSEMITE | Tier 3 | SAN JOAQUIN POWER HOUSE NO 2 | 2020-10-25 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 1255 | 804 | Conductor- Overhead | Sus | N/A | N/A
YOSEMITE | Tier 3 | OAKHURST-1101 | 2020-10-25 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 1065 | 517 | Conductor- Overhead | Sus | 2022 | N/A
YOSEMITE | Tier 2 | SAN JOAQUIN #3 PH-1103 | 2020-10-25 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 1348 | 446 | Conductor- Overhead | Sus | N/A | N/A
YOSEMITE | Tier 3 | OAKHURST-1102 | 2020-10-25 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 1070 | 309 | Conductor- Overhead | Sus | N/A | N/A
YOSEMITE | Tier 3 | OAKHURST-1103 | 2020-10-25 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 1165 | 1067 | Conductor- Overhead | Sus | N/A | N/A
YOSEMITE | Tier 3 | MIWUK-1702 | 2020-11-11 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 45 | 3839 |  | Sus | 2021 | N/A
YOSEMITE | Tier 2 | SAN JOAQUIN #3 PH-1103 | 2020-11-13 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 46 | 906 |  | Sus | N/A | N/A
YOSEMITE | Tier 3 | OAKHURST-1102 | 2021-01-17 | Distribution Circuit | Animal | Squirrel | 81 | 1105 | Transformer (OH) | Sus | N/A | N/A
YOSEMITE | Tier 2 | RACETRACK-1703 | 2021-01-23 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 54 | 3530 |  | Sus | N/A | N/A
YOSEMITE | Tier 3 | MIWUK-1701 | 2021-03-01 | Distribution Circuit | Equipment Failure/Involved | Overhead | 90 | 3726 | Crossarm- Steel | Sus | N/A | N/A
YOSEMITE | Tier 3 | OAKHURST-1102 | 2021-03-10 | Distribution Circuit | Animal | Squirrel | 134 | 1105 | Transformer (OH) | Sus | N/A | N/A
YOSEMITE | Tier 3 | OAKHURST-1102 | 2021-05-07 | Distribution Circuit | Animal | Bird found | 200 | 1102 | Transformer (OH) | Sus | N/A | N/A
YOSEMITE | Tier 2 | MARIPOSA-2101 | 2021-05-13 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 54 | 3816 |  | Sus | N/A | 2023, 2024, 2025, 2026
YOSEMITE | Tier 2 | MARIPOSA-2102 | 2021-05-17 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 8 | 3321 | Conductor- Overhead | Sus | N/A | 2023
YOSEMITE | Tier 3 | MIWUK-1701 | 2021-05-25 | Distribution Circuit | Company Initiated | Personnel- company | 6 | 3727 | Transformer (OH) | Sus | N/A | N/A
YOSEMITE | Tier 2 | PEORIA FLAT-1701 | 2021-08-01 | Transmission line | Equipment Failure/Involved | Fire- pole | 666 | 1912 | Pole - Tower- steel | Sus | N/A | N/A
YOSEMITE | Tier 2 | PEORIA FLAT-1704 | 2021-08-01 | Transmission line | Equipment Failure/Involved | Fire- pole | 341 | 3297 | Pole - Tower- steel | Sus | N/A | N/A
YOSEMITE | Tier 2 | PEORIA FLAT-1701 | 2021-08-08 | Distribution Circuit | Animal | Bird found | 170 | 1912 | Recloser | Sus | N/A | N/A
YOSEMITE | Tier 3 | MIWUK-1701 | 2021-08-26 | Transmission line | Environmental/External | Fire- Forest/Grass | 269 | 3729 | Pole-Wood | Sus | N/A | N/A
YOSEMITE | Tier 3 | MIWUK-1702 | 2021-08-26 | Transmission line | Environmental/External | Fire- Forest/Grass | 355 | 3834 | Pole-Wood | Sus | 2021 | N/A
YOSEMITE | Tier 2 | PEORIA FLAT-1701 | 2021-08-26 | Transmission line | Environmental/External | Fire- Forest/Grass | 319 | 1912 | Pole-Wood | Sus | N/A | N/A
YOSEMITE | Tier 2 | PEORIA FLAT-1704 | 2021-08-26 | Transmission line | Environmental/External | Fire- Forest/Grass | 229 | 3300 | Pole-Wood | Sus | N/A | N/A
YOSEMITE | Tier 2 | PEORIA FLAT-1705 | 2021-08-26 | Transmission line | Environmental/External | Fire- Forest/Grass | 417 | 2331 | Pole-Wood | Sus | N/A | N/A
YOSEMITE | Tier 3 | SPRING GAP SUB | 2021-10-01 | Generation | Animal | Other | 308 | 1707 | Bus | Sus | N/A | N/A
YOSEMITE | Tier 2 | SAN JOAQUIN #3 PH-1103 | 2021-10-08 | Distribution Circuit | Equipment Failure/Involved | Overhead | 386 | 899 | Connector or Splice (OH) | Sus | N/A | N/A
YOSEMITE | Tier 2 | SAN JOAQUIN #3 PH-1101 | 2021-10-08 | Distribution Circuit | Equipment Failure/Involved | Overhead | 192 | 704 | PT/CCVT | Sus | N/A | N/A
YOSEMITE | Tier 2 | PEORIA FLAT-1701 | 2021-10-11 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 235 | 1912 |  | Sus | N/A | N/A
YOSEMITE | Tier 3 | MIWUK-1701 | 2021-10-24 | Distribution Circuit | Vegetation | Tree - branch fell on line | 69 | 3730 | Conductor- Overhead | Sus | N/A | N/A
YOSEMITE | Tier 2 | SAN JOAQUIN #3 PH-1102 | 2021-12-23 | Distribution Circuit | Vegetation | Tree - fell into line | 398 | 262 | Crossarm- Wood | Sus | N/A | N/A
YOSEMITE | Tier 2 | MARIPOSA-2102 | 2022-04-11 | Distribution Circuit | Equipment Failure/Involved | Overhead | 666 | 3314 | Pole-Wood | Sus | N/A | 2023
YOSEMITE | Tier 2 | SAN JOAQUIN #3 PH SUB | 2022-05-14 | Substation - Transmission | Company Initiated | Personnel- company | 6 | 1286 | Relay | Sus | N/A | N/A
YOSEMITE | Tier 2 | COARSEGOLD-2104 | 2022-05-16 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 106 | 4382 | Jumper | Sus | N/A | N/A
YOSEMITE | Tier 3 | OAKHURST-1103 | 2022-06-03 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 272 | 3958 |  | Sus | N/A | N/A
YOSEMITE | Tier 3 | OAKHURST-1102 | 2022-06-04 | Distribution Circuit | Animal | Bird found | 307 | 3185 | Transformer (OH) | Sus | N/A | N/A
YOSEMITE | Tier 2 | SAN JOAQUIN #3 PH-1102 | 2022-06-14 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 199 | 262 |  | Sus | N/A | N/A
YOSEMITE | Tier 2 | SAN JOAQUIN #3 PH-1102 | 2022-06-22 | Distribution Circuit | Vegetation | Tree - fell into line | 317 | 262 | Conductor- Overhead | Sus | N/A | N/A
YOSEMITE | Tier 2 | STANISLAUS-1701 | 2022-07-23 | Distribution Circuit | 3rd Party | Vehicle | 1005 | 2188 | Pole-Wood | Sus | N/A | 2023, 2024
YOSEMITE | Tier 2 | PEORIA FLAT-1704 | 2022-08-05 | Distribution Circuit | Equipment Failure/Involved | Underground | 574 | 3342 | Conductor- Underground | Sus | N/A | N/A
YOSEMITE | Tier 2 | INDIAN FLAT-1104 | 2022-08-30 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 211 | 626 |  | Sus | N/A | 2026
YOSEMITE | Tier 2 | MARIPOSA-2101 | 2022-09-10 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 97 | 3825 |  | Sus | N/A | 2023, 2024, 2025, 2026
YOSEMITE | Tier 2 | STANISLAUS-1701 | 2022-09-18 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 183 | 2190 |  | Sus | N/A | 2023, 2024
YOSEMITE | Tier 2 | COARSEGOLD-2103 | 2022-11-03 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 213 | 2053 |  | Sus | N/A | N/A
YOSEMITE | Tier 3 | SPRING GAP-1702 | 2022-12-03 | Distribution Circuit | Company Initiated | Personnel- company | 33 | 1705 | Circuit Breaker | Sus | N/A | N/A
YOSEMITE | Tier 3 | SPRING GAP-1702 | 2022-12-03 | Distribution Circuit | Equipment Failure/Involved | Overhead | 246 | 1705 | Other | Sus | N/A | N/A