## Random PG&E Outages
Footnote | Outages | County | Circuit | CPZ | Cause | FNL | Protective Function | Phase MTT (A) | Ground MTT (A) | Time Delay (s) | Max load (phase current) 2019-2023 | Max Ground Current 2019-2023 | 3 wire or 4 wire
| 23-0106454 | Madera | COARSEGOLD 2104 | COARSEGOLD 210410400 | Environmental/External | 2023-08-19 18:46 | 50N | 300 | 110 | 0.02 | 187 | 17.5 | 3W
1,2 | 23-0109487 | Sonoma | DUNBAR 1102 | DUNBAR 1102386158 | Unknown Cause | 2023-08-27 06:27 | 50P | 40 | N/A- FuseSaver | 0 | 7 | no SCADA ground record | 3W
| 23-0108633 | Lake | HARTLEY 1101 | HARTLEY 1101738 | Animal | 2023-08-24 12:17 | 50P | 340 | 125 | 0.01 | 228 | 10.2 | 3W
1,2,3 | 23-0100413 | Santa Cruz | GREEN VALLEY 2101 | GREEN VALLEY 2101942143 | Unknown Cause | 2023-08-04 06:55 | 50P | 50 | N/A- FuseSaver | 0 | no SCADA phase record | no SCADA ground record | 4W
| 23-0102789 | Santa Clara | SARATOGA 1106 | SARATOGA 1106340986 | Vegetation | 2023-08-10 13:54 | 50N | 380 | 120 | 0.02 | 94 | 25.3 | 3W
| 23-0106390 | El Dorado | CLARKSVILLE 2104 | CLARKSVILLE 210413352 | Animal | 2023-08-19 14:15 | 50P | 480 | 160 | 0.07 | 126 | 31.8 | 4W
| 23-0106496 | Calaveras | SALT SPRINGS 2102 | SALT SPRINGS 21023118 | Environmental/External | 2023-08-19 21:11 | 50P | 280 | 110 | 0.09 | 149 | 2.8 | 3W
| 23-0099935 | Contra Costa | ROSSMOOR 1108 | ROSSMOOR 110845268 | Unknown Cause | 2023-08-03 07:55 | 50N | 600 | 120 | 0.04 | 374 | 20.5 | 4W
| 23-0104770 | Tuolumne | CURTIS 1703 | CURTIS 170384944 | Unknown Cause | 2023-08-15 17:27 | DCD | 500 | 120 | 0.08 | 394 | 31.5 | 3W
| 23-0106875 | Humboldt | HOOPA 1101 | HOOPA 11013174 | Equipment Failure/Involved | 2023-08-21 08:38 | 50P | 100 | 40 | 0.03 | 54 | 4.8 | 3W
| 23-0100927 | Amador | OLETA 1101 | OLETA 1101928252 | Unknown Cause | 2023-08-05 16:05 | 50P | 210 | 100 | 0.03 | 90 | 17.5 | 3W
| 23-0102136 | Shasta | KESWICK 1101 | KESWICK 11011590 | Unknown Cause | 2023-08-09 11:10 | DCD | 200 | 80 | 0 | 93 | 25.4 | 3W
3 | 23-0105878 | Amador | MARTELL 1101 | MARTELL 110111244 | Animal | 2023-08-18 07:16 | 50P | 300 | 140 | 0.05 | 102 | 4.1 | 3W
| 23-0107214 | Placer | PENRYN 1107 | PENRYN 1107CB | Vegetation | 2023-08-21 15:59 | 50P | 900 | 180 | 0.05 | 685 | 0 | 3W
1,2 | 23-0101152 | Napa | CALISTOGA 1102 | CALISTOGA 1102141073 | Unknown Cause | 2023-08-07 08:28 | 50P | 65 | N/A- FuseSaver | 0 | 20 | no SCADA ground record | 3W
1 | 23-0106473 | Kern | DEVILS DEN 1101 | DEVILS DEN 1101CB | Unknown Cause | 2023-08-19 20:07 | Trip - No Targets | 300 | 180 | 0.05 | 107 | no SCADA ground record | 3W
| 23-0103775 | Tuolumne | MIWUK 1701 | MIWUK 170110600 | Environmental/External | 2023-08-13 17:49 | 50P | 180 | 120 | 0 | 82 | 9.3 | 3W
| 23-0106827 | Sonoma | GEYSERVILLE 1102 | GEYSERVILLE 1102776178 | Unknown Cause | 2023-08-21 07:04 | 50P | 30 | 30 | 0 | 1.73 | 1.6 | 3W
1 | 23-0105266 | Alameda | CAYETANO 2111 | CAYETANO 2111CB | Equipment Failure/Involved | 2023-08-16 17:02 | 50P | 960 | 240 | 0.1 | 366 | no SCADA ground record | 4W
| 23-0107466 | Napa | NAPA 1112 | NAPA 11121302 | Unknown Cause | 2023-08-22 09:39 | 50P | 270 | 120 | 0.05 | 108 | 5.4 | 3W
| 23-0108102 | Sonoma | MOLINO 1101 | MOLINO 1101322 | Unknown Cause | 2023-08-23 12:41 | 50N | 200 | 60 | 0.037 | 55 | 4 | 3W
| 23-0107149 | Marin | SAN RAFAEL 1107 | SAN RAFAEL 11071276 | Vegetation | 2023-08-21 14:27 | 50P | 280 | 110 | 0 | 65 | 2.9 | 3W
| 23-0101981 | Tulare | REEDLEY 1104 | REEDLEY 1104887932 | Unknown Cause | 2023-08-09 04:26 | 50N | 90 | 50 | 0 | 6.73 | 1.6 | 3W
| 23-0109295 | Santa Barbara | CABRILLO 1103 | CABRILLO 1103Y46 | Equipment Failure/Involved | 2023-08-25 16:52 | 50P | 200 | 90 | 0.01 | 107 | 1.4 | 3W
| 23-0101002 | Kern | POSO MOUNTAIN 2101 | POSO MOUNTAIN 21012181 | 3rd Party | 2023-08-06 10:25 | 50N | 320 | 110 | 0.1 | 111 | 4.6 | 3W
| Footnote | Reference
| 1 | SCADA records not available for all devices
| 2 | FuseSavers are single phase reclosers with no ground MTT setting
| 3 | update to the Circuit/CPZ to better reflect Outage report