## Slide 2 - Inspections per Year
# Unique SAP inspected per year
| Column1 | Total | Non-HFTD | HFTD | Tier 3 | Tier 2 | Zone 1/Buffer | (null) | Column1 | # ILIS A tags (Non-Major Event WTC)
| 2015 | 553574 | 421949 | 131625 | 43734 | 87719 | 168 | 4 | 2014 | 851
| 2016 | 577538 | 433452 | 144086 | 50232 | 93726 | 124 | 4 | 2015 | 1735
| 2017 | 564695 | 416562 | 148133 | 44351 | 103720 | 58 | 4 | 2016 | 2655
| 2018 | 525376 | 384964 | 140412 | 45208 | 95164 | 26 | 14 | 2017 | 2626
| 2019 | 1102034 | 414554 | 687480 | 215545 | 466140 | 2030 | 3765 | 2018 | 2536
| 2020 | 762952 | 353674 | 409278 | 198128 | 152270 | 498 | 58382 | 2019 | 3405
| 2021 | 947655 | 428344 | 519311 | 199862 | 249039 | 440 | 69970 | 2020 | 4322
| 2022 | 864024 | 407976 | 456048 | 205251 | 190158 | 426 | 60213 | 2021 | 4586
| Average 2015-2018 | 555295.75 | 414231.75 | 141064 |  |  |  |  | 2022 | 4342
| Average 2019-2022 | 919166.25 | 401137 | 518029.25

## Slide 5 - Etag Pop. Analysis
Object | E-tag Damage | Year | Total # of E-tag with Object "object" and given Damage with ILIS Transformer A-tag | Total # of E-tag with Object "Transformer" and given Damage | E-tag Failure Rate by Damage | % of Structures with an Open "Pole" INSP Tag | Total # of HFRA/HFTD E-tag with Object "Transformer" and given Damage with ILIS A-tag | Total # of HFRA/HFTD E-tag with Object "Transformer" and given Damage | HFRA/HFTD E-tag Failure Rate by Damage | Average E-tag Failure Rate by Damage | Average HFRA/HFTD E-tag Failure Rate by Damage
Transformer | Corroded | 2018 | 2 | 487 | 0.4107% |  | 0 | 120 | 0% | 0.3812% | 0.2183%
Transformer | Corroded | 2019 | 3 | 2023 | 0.1483% |  | 1 | 854 | 0.1171% | 0.3812% | 0.2183%
Transformer | Corroded | 2020 | 15 | 3690 | 0.4065% |  | 1 | 1632 | 0.06127% | 0.3812% | 0.2183%
Transformer | Corroded | 2021 | 31 | 5212 | 0.5948% |  | 15 | 1942 | 0.7724% | 0.3812% | 0.2183%
Transformer | Corroded | 2022 | 25 | 7226 | 0.346% |  | 3 | 2135 | 0.1405% | 0.3812% | 0.2183%
Transformer | Leaks/Seeps/ Weeps | 2018 | 1 | 563 | 0.1776% |  | 1 | 128 | 0.7812% | 0.4399% | 0.5679%
Transformer | Leaks/Seeps/ Weeps | 2019 | 2 | 672 | 0.2976% |  | 2 | 284 | 0.7042% | 0.4399% | 0.5679%
Transformer | Leaks/Seeps/ Weeps | 2020 | 9 | 1484 | 0.6065% |  | 2 | 628 | 0.3185% | 0.4399% | 0.5679%
Transformer | Leaks/Seeps/ Weeps | 2021 | 15 | 2339 | 0.6413% |  | 3 | 818 | 0.3667% | 0.4399% | 0.5679%
Transformer | Leaks/Seeps/ Weeps | 2022 | 17 | 3568 | 0.4765% |  | 7 | 1047 | 0.6686% | 0.4399% | 0.5679%
Transformer | Broken/ Damaged | 2018 | 0 | 368 | 0% |  | 0 | 163 | 0% | 0.1698% | 0.2199%
Transformer | Broken/ Damaged | 2019 | 0 | 625 | 0% |  | 0 | 351 | 0% | 0.1698% | 0.2199%
Transformer | Broken/ Damaged | 2020 | 3 | 962 | 0.3119% |  | 3 | 622 | 0.4823% | 0.1698% | 0.2199%
Transformer | Broken/ Damaged | 2021 | 4 | 1039 | 0.385% |  | 3 | 645 | 0.4651% | 0.1698% | 0.2199%
Transformer | Broken/ Damaged | 2022 | 2 | 1313 | 0.1523% |  | 1 | 657 | 0.1522% | 0.1698% | 0.2199%
Conductor | Improper Connection | 2018 | 0 | 212 | 0% |  | 0 | 54 | 0% | 0.03424% | 0.03557%
Conductor | Improper Connection | 2019 | 1 | 2821 | 0.03545% |  | 1 | 1106 | 0.09042% | 0.03424% | 0.03557%
Conductor | Improper Connection | 2020 | 1 | 7752 | 0.0129% |  | 0 | 3326 | 0% | 0.03424% | 0.03557%
Conductor | Improper Connection | 2021 | 6 | 10195 | 0.05885% |  | 2 | 4239 | 0.04718% | 0.03424% | 0.03557%
Conductor | Improper Connection | 2022 | 25 | 39078 | 0.06397% |  | 5 | 12428 | 0.04023% | 0.03424% | 0.03557%
Conductor | Broken/ Damaged | 2018 | 0 | 1357 | 0% |  | 0 | 283 | 0% | 0.02193% | 0.01366%
Conductor | Broken/ Damaged | 2019 | 0 | 2628 | 0% |  | 0 | 1191 | 0% | 0.02193% | 0.01366%
Conductor | Broken/ Damaged | 2020 | 0 | 5076 | 0% |  | 0 | 2577 | 0% | 0.02193% | 0.01366%
Conductor | Broken/ Damaged | 2021 | 9 | 16166 | 0.05567% |  | 3 | 6487 | 0.04625% | 0.02193% | 0.01366%
Conductor | Broken/ Damaged | 2022 | 16 | 29629 | 0.054% |  | 2 | 9070 | 0.02205% | 0.02193% | 0.01366%
Conductor | Clearance Impaired | 2018 | 1 | 758 | 0.1319% |  | 1 | 270 | 0.3704% | 0.04705% | 0.07407%
Conductor | Clearance Impaired | 2019 | 0 | 1164 | 0% |  | 0 | 578 | 0% | 0.04705% | 0.07407%
Conductor | Clearance Impaired | 2020 | 0 | 3938 | 0% |  | 0 | 2070 | 0% | 0.04705% | 0.07407%
Conductor | Clearance Impaired | 2021 | 5 | 6065 | 0.08244% |  | 0 | 3112 | 0% | 0.04705% | 0.07407%
Conductor | Clearance Impaired | 2022 | 2 | 9567 | 0.02091% |  | 0 | 4351 | 0% | 0.04705% | 0.07407%
Conductor | Sag/ Clearance | 2018 | 0 | 787 | 0% |  | 0 | 249 | 0% | 0.02073% | 0.01413%
Conductor | Sag/ Clearance | 2019 | 0 | 2038 | 0% |  | 0 | 1003 | 0% | 0.02073% | 0.01413%
Conductor | Sag/ Clearance | 2020 | 0 | 3679 | 0% |  | 0 | 1647 | 0% | 0.02073% | 0.01413%
Conductor | Sag/ Clearance | 2021 | 5 | 5956 | 0.08395% |  | 1 | 2395 | 0.04175% | 0.02073% | 0.01413%
Conductor | Sag/ Clearance | 2022 | 2 | 10140 | 0.01972% |  | 1 | 3461 | 0.02889% | 0.02073% | 0.01413%
Conductor | Burnt | 2018 | 0 | (numerator = 0) | 0% |  | 0 | (numerator = 0) | 0% | 0.05051% | 0.08368%
Conductor | Burnt | 2019 | 0 | (numerator = 0) | 0% |  | 0 | (numerator = 0) | 0% | 0.05051% | 0.08368%
Conductor | Burnt | 2020 | 0 | (numerator = 0) | 0% |  | 0 | (numerator = 0) | 0% | 0.05051% | 0.08368%
Conductor | Burnt | 2021 | 1 | 396 | 0.2525% |  | 1 | 239 | 0.4184% | 0.05051% | 0.08368%
Conductor | Burnt | 2022 | 0 | (numerator = 0) | 0% |  | 0 | (numerator = 0) | 0% | 0.05051% | 0.08368%
Crossarm | Decayed/ Rotten | 2018 | 3 | 6565 | 0.0457% |  | 0 | 1363 | 0% | 0.0813% | 0.02966%
Crossarm | Decayed/ Rotten | 2019 | 7 | 11396 | 0.06143% |  | 0 | 2965 | 0% | 0.0813% | 0.02966%
Crossarm | Decayed/ Rotten | 2020 | 12 | 14281 | 0.08403% |  | 1 | 3545 | 0.02821% | 0.0813% | 0.02966%
Crossarm | Decayed/ Rotten | 2021 | 31 | 21377 | 0.145% |  | 4 | 4568 | 0.08757% | 0.0813% | 0.02966%
Crossarm | Decayed/ Rotten | 2022 | 23 | 32712 | 0.07031% |  | 2 | 6149 | 0.03253% | 0.0813% | 0.02966%
Crossarm | Broken/ Damaged | 2018 | 2 | 4234 | 0.04724% |  | 0 | 1346 | 0% | 0.06743% | 0.0357%
Crossarm | Broken/ Damaged | 2019 | 5 | 9227 | 0.05419% |  | 1 | 4931 | 0.02028% | 0.06743% | 0.0357%
Crossarm | Broken/ Damaged | 2020 | 10 | 10781 | 0.09276% |  | 5 | 5154 | 0.09701% | 0.06743% | 0.0357%
Crossarm | Broken/ Damaged | 2021 | 10 | 14673 | 0.06815% |  | 1 | 6247 | 0.01601% | 0.06743% | 0.0357%
Crossarm | Broken/ Damaged | 2022 | 15 | 20052 | 0.07481% |  | 3 | 6638 | 0.04519% | 0.06743% | 0.0357%
Pole | Decayed/ Rotten | 2018 | 0 | 5687 | 0% |  | 0 | 1956 | 0% | 0.03188% | 0.02173%
Pole | Decayed/ Rotten | 2019 | 8 | 17633 | 0.04537% |  | 3 | 8923 | 0.03362% | 0.03188% | 0.02173%
Pole | Decayed/ Rotten | 2020 | 6 | 35016 | 0.01714% |  | 1 | 15906 | 0.006287% | 0.03188% | 0.02173%
Pole | Decayed/ Rotten | 2021 | 32 | 55102 | 0.05807% |  | 11 | 23001 | 0.04782% | 0.03188% | 0.02173%
Pole | Decayed/ Rotten | 2022 | 34 | 87549 | 0.03884% |  | 7 | 33472 | 0.02091% | 0.03188% | 0.02173%
Pole | Broken/ Damaged | 2018 | 0 | 6061 | 0% |  | 0 | 3271 | 0% | 0.02111% | 0.01459%
Pole | Broken/ Damaged | 2019 | 1 | 13861 | 0.007214% |  | 1 | 9969 | 0.01003% | 0.02111% | 0.01459%
Pole | Broken/ Damaged | 2020 | 4 | 21517 | 0.01859% |  | 3 | 15074 | 0.0199% | 0.02111% | 0.01459%
Pole | Broken/ Damaged | 2021 | 13 | 30764 | 0.04226% |  | 4 | 20111 | 0.01989% | 0.02111% | 0.01459%
Pole | Broken/ Damaged | 2022 | 17 | 45319 | 0.03751% |  | 6 | 25947 | 0.02312% | 0.02111% | 0.01459%
Pole | Leaning | 2018 | 0 | 532 | 0% |  | 0 | 145 | 0% | 0.05857% | 0.0645%
Pole | Leaning | 2019 | 2 | 2673 | 0.07482% |  | 1 | 1149 | 0.08703% | 0.05857% | 0.0645%
Pole | Leaning | 2020 | 5 | 6456 | 0.07745% |  | 3 | 2389 | 0.1256% | 0.05857% | 0.0645%
Pole | Leaning | 2021 | 4 | 9832 | 0.04068% |  | 2 | 3323 | 0.06019% | 0.05857% | 0.0645%
Pole | Leaning | 2022 | 14 | 14011 | 0.09992% |  | 2 | 4025 | 0.04969% | 0.05857% | 0.0645%
Pole | Overloaded | 2018 | 0 | 274 | 0% |  | 0 | 66 | 0% | 0.04198% | 0.04828%
Pole | Overloaded | 2019 | 0 | 2498 | 0% |  | 0 | 1349 | 0% | 0.04198% | 0.04828%
Pole | Overloaded | 2020 | 3 | 5164 | 0.05809% |  | 3 | 2391 | 0.1255% | 0.04198% | 0.04828%
Pole | Overloaded | 2021 | 7 | 7866 | 0.08899% |  | 4 | 3450 | 0.1159% | 0.04198% | 0.04828%
Pole | Overloaded | 2022 | 7 | 11140 | 0.06284% |  | 0 | 4482 | 0% | 0.04198% | 0.04828%
Pole | Woodpecker Damage | 2018 | 0 | 5774 | 0% |  | 0 | 4401 | 0% | 0.00557% | 0.004825%
Pole | Woodpecker Damage | 2019 | 0 | 5759 | 0% |  | 0 | 4457 | 0% | 0.00557% | 0.004825%
Pole | Woodpecker Damage | 2020 | 0 | 13365 | 0% |  | 0 | 9980 | 0% | 0.00557% | 0.004825%
Pole | Woodpecker Damage | 2021 | 5 | 24850 | 0.02012% |  | 3 | 18028 | 0.01664% | 0.00557% | 0.004825%
Pole | Woodpecker Damage | 2022 | 3 | 38824 | 0.007727% |  | 2 | 26715 | 0.007486% | 0.00557% | 0.004825%

## Slide 5 - Avg. Failure Rate
Failure Mode | Calendar Year | Failure Rate of Structures with an Open INSP Tag | Failure Rate of Structures with No Open INSP Tag(s) | Failure Rate Difference w/ Open INSP Tag - w/o No Open INSP Tag | 95% Confidence Interval | Statistically Significant Difference | Failure Ratio w/ Open Tag : w/o Open Tag | Failure Rate of Structures with an Open INSP Tag2 | Failure Rate of Structures with No Open INSP Tag(s)3 | Category | Year | Total # Object A-tag failures | Total # HFTD/HFRA Object A-tag Failures | Number of Structures that had an Open "Object" INSP Tag** | Number of HFTD/HFRA Structures that had an Open "Object" INSP Tag** | # of A-tag Failures on Structures with an Open INSP Tag | # of A-tag Failures on HFTD/HFRA Structures with an Open INSP Tag | Failure Rate of Structures with an Open INSP Tag | Failure Rate of Structures with No Open INSP Tag(s) | Failure Rate of HFTD/HFRA Structures with an Open INSP Tag | Failure Rate of HFTD/HFRA Structures with No Open INSP Tag(s)
Overall | Corroded | 0.0010465 | 0.0010947 | -0.00482% | (-0.035%, 0.025%) | No | 1:1 | 0.1805% | 0.1845% | Overall | 2018
Overall | Corroded | 0.0016393 | 0.0018257 | -0.01864% | (-0.057%, 0.02%) | No | 1:1 | 0.1805% | 0.1845% | Overall | 2019
Overall | Corroded | 0.0016785 | 0.0018937 | -0.02152% | (-0.061%, 0.018%) | No | 1:1 | 0.1805% | 0.1845% | Overall | 2020
Overall | Corroded | 0.0025015 | 0.0024526 | 0.004882% | (-0.04%, 0.05%) | No | 1:1 | 0.1805% | 0.1845% | Overall | 2021
Overall | Corroded | 0.0021592 | 0.0019566 | 0.02026% | (-0.02%, 0.061%) | No | 1:1 | 0.1805% | 0.1845% | Overall | 2022
Overall | Leaks/Seeps/ Weeps | 0 | 9.1334e-05 |  |  |  |  | 0.02858% | 0.01512% | Poles | 2018 | 245 | 14 | 22592 | 12721 | 0 | 0 | 0 | 9.1334e-05 | 0 | 1.8615e-05
Overall | Leaks/Seeps/ Weeps | 0.00028542 | 0.00017311 | 0.01123% | (-0.006%, 0.028%) | No | 2:1 | 0.02858% | 0.01512% | Poles | 2019 | 473 | 93 | 42043 | 25608 | 12 | 6 | 0.00028542 | 0.00017311 | 0.0002343 | 0.0001177
Overall | Leaks/Seeps/ Weeps | 0.00024112 | 0.00012147 | 0.01197% | (-0.003%, 0.027%) | No | 2:1 | 0.02858% | 0.01512% | Poles | 2020 | 338 | 72 | 78799 | 43427 | 19 | 10 | 0.00024112 | 0.00012147 | 0.00023027 | 8.5947e-05
Overall | Leaks/Seeps/ Weeps | 0.0005052 | 0.00022439 | 0.02808% | (0.008%, 0.048%) | Yes | 2:1 | 0.02858% | 0.01512% | Poles | 2021 | 642 | 107 | 124703 | 64441 | 63 | 24 | 0.0005052 | 0.00022439 | 0.00037243 | 0.00011851
Overall | Leaks/Seeps/ Weeps | 0.00039706 | 0.00014575 | 0.02513% | (0.008%, 0.042%) | Yes | 3:1 | 0.02858% | 0.01512% | Poles | 2022 | 443 | 72 | 193925 | 91981 | 77 | 18 | 0.00039706 | 0.00014575 | 0.00019569 | 8.026e-05
Overall | Broken/ Damaged | 0.00029481 | 0.00021653 | 0.007828% | (-0.041%, 0.057%) | No | 1:1 | 0.03456% | 0.0397% | Conductors | 2018 | 586 | 86 | 3392 | 1107 | 1 | 1 | 0.00029481 | 0.00021653 | 0.00090334 | 0.0001113
Overall | Broken/ Damaged | 0.00011586 | 0.00042723 | -0.03114% | (-0.1%, 0.038%) | No | 1:4 | 0.03456% | 0.0397% | Conductors | 2019 | 1153 | 208 | 8631 | 3915 | 1 | 1 | 0.00011586 | 0.00042723 | 0.00025543 | 0.00027205
Overall | Broken/ Damaged | 9.878e-05 | 0.00037992 | -0.02811% | (-0.093%, 0.037%) | No | 1:4 | 0.03456% | 0.0397% | Conductors | 2020 | 1022 | 168 | 20247 | 9584 | 2 | 0 | 9.878e-05 | 0.00037992 | 0 | 0.00022245
Overall | Broken/ Damaged | 0.00061275 | 0.00056157 | 0.005117% | (-0.074%, 0.084%) | No | 1:1 | 0.03456% | 0.0397% | Conductors | 2021 | 1521 | 338 | 37536 | 15790 | 23 | 6 | 0.00061275 | 0.00056157 | 0.00037999 | 0.00044325
Overall | Broken/ Damaged | 0.00060602 | 0.00039999 | 0.0206% | (-0.047%, 0.088%) | No | 2:1 | 0.03456% | 0.0397% | Conductors | 2022 | 1099 | 193 | 82505 | 27734 | 50 | 8 | 0.00060602 | 0.00039999 | 0.00028845 | 0.000251
Transformer | Improper Connection | 0.0016086 | 0.0018229 | -0.02143% | (-0.215%, 0.172%) | No | 1:1 | 0.354% | 0.3162% | Transformer | 2018 | 1177 | 288 | 1865 | 674 | 3 | 1 | 0.0016086 | 0.0018229 | 0.0014837 | 0.0014748
Transformer | Improper Connection | 0.0016911 | 0.0027477 | -0.1057% | (-0.342%, 0.131%) | No | 1:2 | 0.354% | 0.3162% | Transformer | 2019 | 1771 | 548 | 3548 | 1623 | 6 | 4 | 0.0016911 | 0.0027477 | 0.0024646 | 0.0028091
Transformer | Improper Connection | 0.005138 | 0.0037052 | 0.1433% | (-0.132%, 0.418%) | No | 1:1 | 0.354% | 0.3162% | Transformer | 2020 | 2403 | 617 | 6812 | 3153 | 35 | 8 | 0.005138 | 0.0037052 | 0.0025373 | 0.0031698
Transformer | Improper Connection | 0.0054037 | 0.0039138 | 0.149% | (-0.134%, 0.432%) | No | 1:1 | 0.354% | 0.3162% | Transformer | 2021 | 2542 | 693 | 9438 | 3635 | 51 | 22 | 0.0054037 | 0.0039138 | 0.0060523 | 0.0035013
Transformer | Improper Connection | 0.0038566 | 0.0036227 | 0.0234% | (-0.249%, 0.296%) | No | 1:1 | 0.354% | 0.3162% | Transformer | 2022 | 2343 | 532 | 13224 | 4072 | 51 | 11 | 0.0038566 | 0.0036227 | 0.0027014 | 0.0027248
Transformer | Broken/ Damaged | 0.00045126 | 0.00010394 | 0.03473% | (0.016%, 0.054%) | Yes | 4:1 | 0.0822% | 0.01686% | CrossArm | 2018 | 285 | 54 | 11080 | 2881 | 5 | 0 | 0.00045126 | 0.00010394 | 0 | 7.0874e-05
Transformer | Broken/ Damaged | 0.00082512 | 0.00016838 | 0.06567% | (0.041%, 0.09%) | Yes | 5:1 | 0.0822% | 0.01686% | CrossArm | 2019 | 469 | 93 | 20603 | 7885 | 17 | 1 | 0.00082512 | 0.00016838 | 0.00012682 | 0.00012155
Transformer | Broken/ Damaged | 0.00089932 | 0.00016346 | 0.07359% | (0.049%, 0.098%) | Yes | 6:1 | 0.0822% | 0.01686% | CrossArm | 2020 | 461 | 82 | 25575 | 9082 | 23 | 6 | 0.00089932 | 0.00016346 | 0.00066065 | 0.00010057
Transformer | Broken/ Damaged | 0.00115 | 0.0002492 | 0.09008% | (0.06%, 0.12%) | Yes | 5:1 | 0.0822% | 0.01686% | CrossArm | 2021 | 707 | 148 | 36522 | 10919 | 42 | 5 | 0.00115 | 0.0002492 | 0.00045792 | 0.00018969
Transformer | Broken/ Damaged | 0.0007845 | 0.00015802 | 0.06265% | (0.038%, 0.087%) | Yes | 5:1 | 0.0822% | 0.01686% | CrossArm | 2022 | 461 | 82 | 53537 | 12900 | 42 | 5 | 0.0007845 | 0.00015802 | 0.0003876 | 0.00010241
Transformer | Clearance Impaired
Transformer | Clearance Impaired
Transformer | Clearance Impaired
Transformer | Clearance Impaired
Transformer | Clearance Impaired
Transformer | Sag/ Clearance
Transformer | Sag/ Clearance
Transformer | Sag/ Clearance
Transformer | Sag/ Clearance
Transformer | Sag/ Clearance
Burnt
Burnt
Burnt
Burnt
Burnt
Decayed/ Rotten
Decayed/ Rotten
Decayed/ Rotten
Decayed/ Rotten
Decayed/ Rotten
Broken/ Damaged
Broken/ Damaged
Broken/ Damaged
Broken/ Damaged
Broken/ Damaged
Decayed/ Rotten
Decayed/ Rotten
Decayed/ Rotten
Decayed/ Rotten
Decayed/ Rotten
Broken/ Damaged
Broken/ Damaged
Broken/ Damaged
Broken/ Damaged
Broken/ Damaged
Leaning
Leaning
Leaning
Leaning
Leaning
Overloaded
Overloaded
Overloaded
Overloaded
Overloaded
Woodpecker Damage
Woodpecker Damage
Woodpecker Damage
Woodpecker Damage
Woodpecker Damage

## Slide 6 - Duration from E to A
Count of notification, Month | Count of notification, # Etags Associated with Failures | Open all E at end of X months, # Open Etags | Open all E at end of X months | Running total Etags with Atag as X months, # Etags Associated with Failures | Running total Etags with Atag as X months, % Etags Associated with Failures | # Etags Not Associated with Failures | % Etags Not Associated with Failures
0 | 44 | 525809 | 8.3681e-05 | 44 | 2.161% | 525765 | 99.99%
1 | 119 | 522291 | 0.00022784 | 163 | 8.006% | 525646 | 99.97%
2 | 134 | 520205 | 0.00025759 | 297 | 14.59% | 525512 | 99.94%
3 | 120 | 516889 | 0.00023216 | 417 | 20.48% | 525392 | 99.92%
4 | 125 | 513403 | 0.00024347 | 542 | 26.62% | 525267 | 99.9%
5 | 103 | 510197 | 0.00020188 | 645 | 31.68% | 525164 | 99.88%
6 | 91 | 506639 | 0.00017962 | 736 | 36.15% | 525073 | 99.86%
7 | 103 | 502802 | 0.00020485 | 839 | 41.21% | 524970 | 99.84%
8 | 94 | 497964 | 0.00018877 | 933 | 45.83% | 524876 | 99.82%
9 | 90 | 488310 | 0.00018431 | 1023 | 50.25% | 524786 | 99.81%
10 | 64 | 466908 | 0.00013707 | 1087 | 53.39% | 524722 | 99.79%
11 | 64 | 443498 | 0.00014431 | 1151 | 56.53% | 524658 | 99.78%
12 | 63 | 407519 | 0.00015459 | 1214 | 59.63% | 524595 | 99.77%
13 | 70 | 357742 | 0.00019567 | 1284 | 63.06% | 524525 | 99.76%
14 | 55 | 314236 | 0.00017503 | 1339 | 65.77% | 524470 | 99.75%
15 | 55 | 284118 | 0.00019358 | 1394 | 68.47% | 524415 | 99.73%
16 | 63 | 260841 | 0.00024153 | 1457 | 71.56% | 524352 | 99.72%
17 | 66 | 251434 | 0.00026249 | 1523 | 74.8% | 524286 | 99.71%
18 | 56 | 246543 | 0.00022714 | 1579 | 77.55% | 524230 | 99.7%
19 | 45 | 241629 | 0.00018624 | 1624 | 79.76% | 524185 | 99.69%
20 | 45 | 233836 | 0.00019244 | 1669 | 81.97% | 524140 | 99.68%
21 | 39 | 219808 | 0.00017743 | 1708 | 83.89% | 524101 | 99.68%
22 | 36 | 204692 | 0.00017587 | 1744 | 85.66% | 524065 | 99.67%
23 | 28 | 190781 | 0.00014677 | 1772 | 87.03% | 524037 | 99.66%
24 | 24 | 174029 | 0.00013791 | 1796 | 88.21% | 524013 | 99.66%
25 | 20 | 155989 | 0.00012821 | 1816 | 89.19% | 523993 | 99.65%
26 | 34 | 139089 | 0.00024445 | 1850 | 90.86% | 523959 | 99.65%
27 | 26 | 124622 | 0.00020863 | 1876 | 92.14% | 523933 | 99.64%
28 | 23 | 110943 | 0.00020731 | 1899 | 93.27% | 523910 | 99.64%
29 | 21 | 106628 | 0.00019695 | 1920 | 94.3% | 523889 | 99.63%
30 | 13 | 104447 | 0.00012447 | 1933 | 94.94% | 523876 | 99.63%
31 | 12 | 102552 | 0.00011701 | 1945 | 95.53% | 523864 | 99.63%
32 | 7 | 99672 | 7.023e-05 | 1952 | 95.87% | 523857 | 99.63%
33 | 5 | 91583 | 5.4595e-05 | 1957 | 96.12% | 523852 | 99.63%
34 | 8 | 83919 | 9.533e-05 | 1965 | 96.51% | 523844 | 99.63%
35 | 11 | 74335 | 0.00014798 | 1976 | 97.05% | 523833 | 99.62%
36 | 8 | 57442 | 0.00013927 | 1984 | 97.45% | 523825 | 99.62%
37 | 8 | 43944 | 0.00018205 | 1992 | 97.84% | 523817 | 99.62%
38 | 5 | 32683 | 0.00015298 | 1997 | 98.08% | 523812 | 99.62%
39 | 7 | 26385 | 0.0002653 | 2004 | 98.43% | 523805 | 99.62%
40 | 10 | 24764 | 0.00040381 | 2014 | 98.92% | 523795 | 99.62%
41 | 5 | 24183 | 0.00020676 | 2019 | 99.17% | 523790 | 99.62%
42 | 3 | 23863 | 0.00012572 | 2022 | 99.31% | 523787 | 99.62%
43 | 6 | 23602 | 0.00025422 | 2028 | 99.61% | 523781 | 99.61%
44 | 2 | 22680 | 8.8183e-05 | 2030 | 99.71% | 523779 | 99.61%
45 | 2 | 21045 | 9.5034e-05 | 2032 | 99.8% | 523777 | 99.61%
46 |  | 19654 | 0 | 2032 | 99.8% | 523777 | 99.61%
47 | 1 | 17740 | 5.637e-05 | 2033 | 99.85% | 523776 | 99.61%
48 | 1 | 15956 | 6.2672e-05 | 2034 | 99.9% | 523775 | 99.61%
49 |  | 14222 | 0 | 2034 | 99.9% | 523775 | 99.61%
50 |  | 12070 | 0 | 2034 | 99.9% | 523775 | 99.61%
51 | 1 | 7870 | 0.00012706 | 2035 | 99.95% | 523774 | 99.61%
52 | 1 | 3702 | 0.00027012 | 2036 | 100% | 523773 | 99.61%
53 |  | 2032 | 0 | 2036 | 100% | 523773 | 99.61%
54 |  | 1837 | 0 | 2036 | 100% | 523773 | 99.61%
55 |  | 1693 | 0 | 2036 | 100% | 523773 | 99.61%
56 |  | 1670 | 0 | 2036 | 100% | 523773 | 99.61%
57 |  | 1631 | 0 | 2036 | 100% | 523773 | 99.61%
58 |  | 1584 | 0 | 2036 | 100% | 523773 | 99.61%
59 |  | 1545 | 0 | 2036 | 100% | 523773 | 99.61%
60 |  | 1473 | 0 | 2036 | 100% | 523773 | 99.61%
61 |  |  |  | 2036 | 100% | 523773 | 99.61%
62 |  |  |  | 2036 | 100% | 523773 | 99.61%
63 |  |  |  | 2036 | 100% | 523773 | 99.61%
64 |  | 1172 | 0 | 2036 | 100% | 523773 | 99.61%

## Slide 8 - Pareto by Object
Abbreviated FDAs
Column1 | Row Labels | Count of notification | Running total | Total %
1 | Transformer | 9841 | 9841 | 40.39%
2 | Conductor | 5149 | 14990 | 61.53%
3 | Crossarm | 2299 | 17289 | 70.96%
4 | Pole | 2082 | 19371 | 79.51%
5 | Cutout | 1703 | 21074 | 86.5%
6 | Jumper | 1379 | 22453 | 92.16%
7 | Connector | 623 | 23076 | 94.72%
8 | Insulator | 562 | 23638 | 97.02%
9 | Hardware/Framing | 187 | 23825 | 97.79%
10 | Tie Wire | 87 | 23912 | 98.15%
| Other | 451 | 24363 | 100%