## Summary
Category | Investigation Count |  |  | Transformer Count | Comments
| Non-HFTD | HFTD2/3 | Total
Successful Intervention - Replaced Transformer | 29 | 9 | 38 | 44 | Incipient transformer failures - remediation initated through IONA1
Successful Prediction - Replaced Transformer | 14 | 4 | 18 | 18 | Transformer Failures - remediation initiated independent of IONA
Sub-total - Transformer Remediation | 43 | 13 | 56 | 62
Successful Intervention - Non-TX Remediation | 81 | 23 | 104 |  | Non-transformer risks - remediation initiated through IONA
Successful Prediction - Non-TX Remediation | 11 | 4 | 15 |  | Non-transformer risks - remediation initiated independent of IONA
Sub-total - Non Transformer Remediation | 92 | 27 | 119
Non-Risk Issue | 80 | 21 | 101 |  | Outages, SmartMeter data issues etc
False Positive Prediction | 5 | 1 | 6 |  | False positive prediction by model
Total | 220 | 62 | 282
Notes:
Successful Intervention - IONA predicted issue, remediated through IONA workflow
Successful Prediction - IONA predicted issue, remediation was initated independent of IONA workflow
1 - Transformer count higher than investigation count since some locations involved transformer banks
Risk Reduction Category | Risk Reduction Calculated using WDRM v4
Transformer Unit Replacements (44 Transformers) | 1.1924
Additional Equipment Replaced (Pole, crossarm) | 0.00038005
Total Risk Reduction | 1.1928

## Pivot
Row Labels | Count of outcome | Sum of Transformers Replaced Count
False Positive Prediction | 6
5
[Tier 2 - Elevated] | 1
Non-Risk Issue | 101
80
[Tier 2 - Elevated] | 11
[Tier 3 - Extreme] | 10
Successful Intervention - Non-TX Remediation | 104
81
[Tier 2 - Elevated] | 9
[Tier 3 - Extreme] | 14
Successful Intervention - Replaced Transformer | 38 | 44
| 29 | 35
[Tier 2 - Elevated] | 5 | 5
[Tier 3 - Extreme] | 4 | 4
Successful Prediction - Non-TX Remediation | 15
11
[Tier 2 - Elevated] | 4
(blank)
(blank)
Successful Prediction - Replaced Transformer | 18 | 18
[Tier 3 - Extreme] | 4 | 4
(blank) | 14 | 14
Grand Total | 282 | 62

## IONA-2024-Closed Investigations
field_notification_id | field_ec_notification_id | initial_review_date | review_outcome | Category | field_inspection_outcome | outcome | status | field_inspection_status | hftd | Transformers Replaced Count | Transformer Risk Reduction | Additional Equipment Replaced | Additional Equipment Replaced Risk Reduction
40116742 |  | 2024-05-15 13:32:12 | Suspect Blown Fuse | Fuse Failures | Fuse Failure | Successful Intervention - Non-TX Remediation | Closed | Closed - No EC tag
40119004 |  | 2024-08-21 14:00:04 | Suspect Blown Fuse | Fuse Failures | Fuse Failure | Successful Intervention - Non-TX Remediation | Closed | Closed - No EC tag
|  | 2024-02-16 13:42:47 | Suspected Loose Neutral | Intervention through another department |  | Successful Prediction - Non-TX Remediation | Closed
|  | 2024-02-14 09:18:44 | Suspect Incorrect displayed values | Meter Program Error |  | Non-Risk Issue | Closed |  | [Tier 2 - Elevated]
|  | 2024-06-03 11:24:27 | Suspect Broken Jumper | Intervention through another department |  | Successful Prediction - Non-TX Remediation | Closed |  | [Tier 2 - Elevated]
|  | 2024-04-03 13:59:35 | Suspect Blown Fuse | Intervention through another department | Not Complete | Successful Prediction - Non-TX Remediation | Closed | Not Initiated
40120218 |  | 2024-10-16 08:53:46 | Suspect Blown Fuse | Fuse Failures | Blown Fuse | Successful Intervention - Non-TX Remediation | Closed | Closed - No EC tag
|  | 2024-04-10 14:14:10 | Suspect Incorrect displayed values | Meter Program Error |  | Non-Risk Issue | Closed | Not Initiated
|  | 2024-02-06 14:02:13 | Suspect Overload - No Bypass | Intervention through another department | Suspect Overload - No Bypass | Successful Prediction - Replaced Transformer | Closed | Not Initiated | [Tier 3 - Extreme] | 1
|  | 2024-08-08 16:14:06 | Suspect Incorrect displayed values | Meter Program Error |  | Non-Risk Issue | Closed
40113085 |  | 2024-02-08 21:55:52 | Suspected Meter Issue | Meter Issue | Mismapped Meter | Non-Risk Issue | Closed | False Positive | [Tier 3 - Extreme]
|  |  |  | Meter Issue | Mismapped Meter | Non-Risk Issue | Closed |  | [Tier 3 - Extreme]
40112461 |  | 2024-01-02 11:50:19 | Suspect Blown Fuse | Fuse Failures | Fuse Failure | Successful Intervention - Non-TX Remediation | Closed | Closed - No EC tag
40121511 |  | 2024-12-25 00:51:12 | Suspect Blown Fuse | Fuse Failures | Customer's Equipment | Successful Intervention - Non-TX Remediation | Closed | Closed - No EC tag
40120980 | 129834628 | 2024-11-19 09:17:12 | Suspect Blown Fuse | Fuse Failures | Windings Failure | Successful Intervention - Non-TX Remediation | Closed | Closed - EC tag
40120536 |  | 2024-10-29 11:02:05 | Suspect Blown Fuse | Fuse Failures | Blown Fuse | Successful Intervention - Non-TX Remediation | Closed | Closed - No EC tag
40113700 | OIS# 2391998 | 2024-02-21 13:56:52 | Suspect Blown Fuse | Fuse Failures | Fuse Failure | Successful Intervention - Non-TX Remediation | Closed | Closed - EC tag
|  | 2024-03-12 12:41:25 | Suspect Incorrect displayed values | Meter Program Error |  | Non-Risk Issue | Closed | Not Initiated
|  | 2024-01-24 08:17:42 | Suspect Incorrect displayed values | Meter Program Error |  | Non-Risk Issue | Closed | Not Initiated
|  | 2024-04-11 01:27:01 | Suspect Incorrect displayed values | Meter Program Error |  | Non-Risk Issue | Closed | Flagged for Inspection | [Tier 3 - Extreme]
40121524 |  | 2024-12-31 09:56:45 | Suspect Blown Fuse | Fuse Failures | Loose Neutral | Successful Intervention - Non-TX Remediation | Closed | Closed - No EC tag | [Tier 2 - Elevated]
|  | 2024-02-21 09:48:02 | Suspect Windings Failure | Intervention through another department | Not Complete | Successful Prediction - Replaced Transformer | Closed | Not Initiated |  | 1
40117167 |  | 2024-06-04 10:54:01 | Suspect Blown Fuse | Fuse Failures | Fuse Failure | Successful Intervention - Non-TX Remediation | Closed | Closed - No EC tag
|  | 2024-02-26 16:14:41 | Suspect Primary Issue |  | Not Complete | Non-Risk Issue | Closed | Not Initiated | [Tier 3 - Extreme]
|  | 2024-02-07 13:43:33 | Suspect Overload - No Bypass | Intervention through another department | Not Complete | Successful Prediction - Replaced Transformer | Closed | Not Initiated | [Tier 3 - Extreme] | 1
|  | 2024-02-09 14:24:54 | Suspect Windings Failure | Intervention through another department | Not Complete | Successful Prediction - Replaced Transformer | Closed | Not Initiated | [Tier 3 - Extreme] | 1
|  | 2024-07-31 16:16:34 | Circuit Outage | Circuit Outage | Not Complete | Non-Risk Issue | Closed | Not Initiated | [Tier 2 - Elevated]
40112462 |  | 2024-01-10 14:33:01 | Suspect Blown Fuse | Fuse Failures | Fuse Failure | Successful Intervention - Non-TX Remediation | Closed | Closed - No EC tag
|  | 2024-06-26 11:13:48 | Circuit Outage | Circuit Outage | Not Complete | Non-Risk Issue | Closed | Not Initiated
40119742 |  | 2024-09-24 16:21:11 | Suspect Broken Jumper | Broken Jumpers | Broken Jumper | Successful Intervention - Non-TX Remediation | Closed | Ad-hoc Notification Created
40121374 |  | 2024-12-18 08:52:44 | Suspect Broken Jumper | Broken Jumpers | Severely Corroded Connecter | Successful Intervention - Non-TX Remediation | Closed | Closed - No EC tag
40121157 | 129895089 | 2024-12-03 22:07:57 | Suspect Broken Jumper | Broken Jumpers | Broken Jumper | Successful Intervention - Non-TX Remediation | Closed | Closed - EC tag
40113083 |  | 2024-02-06 11:39:11 | Suspect Broken Jumper | Broken Jumpers | Broken Jumper | Successful Intervention - Non-TX Remediation | Closed |  | [Tier 3 - Extreme]
|  | 2024-09-27 12:57:07 | Circuit Outage | Circuit Outage | Not Complete | Non-Risk Issue | Closed | Not Initiated
|  | 2024-05-13 15:37:35 | Suspect Primary Issue | Intervention through another department | Not Complete | Successful Prediction - Non-TX Remediation | Closed | Not Initiated
|  | 2024-05-14 12:50:08 | Suspect Windings Failure | Intervention through another department | Not Complete | Successful Prediction - Replaced Transformer | Closed | Not Initiated |  | 1
40119330 |  | 2024-09-03 14:57:39 | Suspect Broken Jumper | Broken Jumpers | Customer's Equipment | Successful Intervention - Non-TX Remediation | Closed | Ad-hoc Notification Created | [Tier 3 - Extreme]
|  | 2024-08-08 13:57:50 | Suspect Customer's Drop Design Constraints | Customer's Equipment Limitation - Secondary Conductor |  | Non-Risk Issue | Closed
|  | 2024-04-16 11:48:01 | Suspect Incorrect displayed values | Meter Program Error |  | Non-Risk Issue | Closed | Not Initiated
40120713 |  | 2024-11-06 16:41:16 | Suspect Broken Jumper | Broken Jumpers | Broken Jumper | Successful Intervention - Non-TX Remediation | Closed | Ad-hoc Notification Created
|  | 2024-08-01 15:57:21 | Suspect Customer's Drop Design Constraints | Customer's Equipment Limitation - Secondary Conductor |  | Non-Risk Issue | Closed
|  | 2024-05-02 08:34:53 | Suspect Incorrect displayed values | Meter Program Error |  | Non-Risk Issue | Closed | Not Initiated
40121451 |  | 2024-12-23 13:59:25 | Suspect Broken Jumper | Broken Jumpers | Loose Chance Clamp | Successful Intervention - Non-TX Remediation | Closed | Closed - No EC tag
|  | 2024-11-27 08:41:33 | Suspect Equipment Arcing | Intervention through another department |  | Successful Prediction - Non-TX Remediation | Closed
40118585 |  | 2024-03-12 16:41:12 | Suspect Broken Jumper | Broken Jumpers | Broken Jumper | Successful Intervention - Non-TX Remediation | Closed | Ad-hoc Notification Created
40120405 | 129733827 | 2024-10-23 08:25:19 | Suspect Broken Jumper | Broken Jumpers | Broken Jumper | Successful Intervention - Non-TX Remediation | Closed | Closed - EC tag
40121591 |  | 2025-01-03 15:52:05 | Suspect Broken Jumper | Broken Jumpers | Loose Chance Clamp | Successful Intervention - Non-TX Remediation | Closed | Closed - No EC tag
|  | 2024-04-11 10:04:00 | Suspect Primary Issue |  | Not Complete | Non-Risk Issue | Closed | Not Initiated | [Tier 2 - Elevated]
|  | 2024-08-08 15:56:15 | Suspect Incorrect displayed values | Meter Program Error |  | Non-Risk Issue | Closed
40116511 |  | 2024-04-24 13:08:15 | Suspect Customer's Equipment | Customer’s equipment issues | Customer's Equipment | Successful Intervention - Non-TX Remediation | Closed | Ad-hoc Notification Created
40119114 |  | 2024-08-23 11:33:59 | Suspect Customer's Equipment | Customer’s equipment issues | Customer's Equipment | Successful Intervention - Non-TX Remediation | Closed | Ad-hoc Notification Created
40117084 |  | 2024-05-30 13:44:37 | Suspect Customer's Equipment | Customer’s equipment issues | Customer's Equipment | Successful Intervention - Non-TX Remediation | Closed | Ad-hoc Notification Created
|  | 2024-04-23 14:24:00 | Circuit Outage | Circuit Outage | Not Complete | Non-Risk Issue | Closed | Not Initiated | [Tier 2 - Elevated]
|  | 2024-12-27 16:58:09 | Suspect Windings Failure | Intervention through another department |  | Successful Prediction - Replaced Transformer | Closed |  |  | 1
40117249 |  | 2024-06-04 10:39:21 | Suspect Customer's Equipment | Customer’s equipment issues | Customer's Equipment | Successful Intervention - Non-TX Remediation | Closed | Ad-hoc Notification Created
|  | 2024-08-19 16:40:58 | Suspect Incorrect displayed values | Meter Program Error |  | Non-Risk Issue | Closed
40113093 |  | 2024-03-04 09:19:50 | False Positive Prediction | False Positive | False Positive | False Positive Prediction | Closed | Ad-hoc Notification Created
40120714 |  | 2024-11-06 17:19:47 | Suspect Equipment Arcing | Broken Jumpers | Equipment Arcing | Successful Intervention - Non-TX Remediation | Closed | Closed - No EC tag
|  | 2024-04-26 10:58:28 | Suspect Incorrect displayed values | Meter Program Error |  | Non-Risk Issue | Closed | Not Initiated
|  | 2024-05-07 10:02:00 | Suspect Incorrect displayed values | Meter Program Error |  | Non-Risk Issue | Closed | Not Initiated
|  | 2024-09-18 10:48:05 | Suspect Primary Issue |  |  | Non-Risk Issue | Closed
40121279 |  | 2024-12-12 16:49:46 | Suspect Equipment Arcing | Broken Jumpers | Equipment Arcing | Successful Intervention - Non-TX Remediation | Closed | Closed - No EC tag
Sent to Revenue Assurance |  | 2024-03-05 11:49:09 | Suspect Overload - Bypass | Overload - Bypass (Energy Theft) | Overload - Bypass | Successful Intervention - Non-TX Remediation | Closed | Meter Field Inspection | [Tier 2 - Elevated]
|  | 2024-05-29 14:30:10 | Suspect Incorrect displayed values | Meter Program Error |  | Non-Risk Issue | Closed | Not Initiated
Sent to Revenue Assurance |  | 2024-07-22 16:51:42 | Suspect Overload - Bypass | Overload - Bypass (Energy Theft) | Overload - Bypass | Successful Intervention - Non-TX Remediation | Closed | Meter Field Inspection
|  | 2024-04-24 12:47:02 | Suspect Incorrect displayed values | Meter Program Error |  | Non-Risk Issue | Closed | Not Initiated
|  | 2024-04-05 10:15:22 | Suspect Short Term Overload - No Bypass |  |  | Non-Risk Issue | Closed
|  | 2024-04-29 13:53:10 | Suspect Incorrect displayed values | Meter Program Error |  | Non-Risk Issue | Closed | Not Initiated
|  | 2024-05-08 15:27:44 | Suspect Incorrect displayed values | Meter Program Error |  | Non-Risk Issue | Closed | Not Initiated
Sent to Revenue Assurance |  | 2024-07-31 11:37:41 | Suspect Overload - Bypass | Overload - Bypass (Energy Theft) | Overload - Bypass | Successful Intervention - Non-TX Remediation | Closed | Meter Field Inspection
40113089 | 116827493 | 2024-02-07 11:04:34 | Suspect Overload - Bypass | Overload - Bypass (Energy Theft) | Overload - Bypass | Successful Intervention - Non-TX Remediation | Closed | Meter Field Inspection | [Tier 3 - Extreme]
Sent to Revenue Assurance |  | 2024-02-26 15:47:55 | Suspect Overload - Bypass | Overload - Bypass (Energy Theft) | Overload - Bypass | Successful Intervention - Non-TX Remediation | Closed | Meter Field Inspection | [Tier 3 - Extreme]
|  | 2024-03-29 16:31:14 | Suspect Incorrect displayed values | Meter Program Error |  | Non-Risk Issue | Closed | Not Initiated
|  | 2024-05-08 14:44:01 | Suspect Incorrect displayed values | Meter Program Error |  | Non-Risk Issue | Closed | Not Initiated
Sent to Revenue Assurance |  | 2024-02-07 11:38:48 | Suspect Overload - Bypass | Overload - Bypass (Energy Theft) | Overload - Bypass | Successful Intervention - Non-TX Remediation | Closed | Meter Field Inspection | [Tier 3 - Extreme]
40113092 |  | 2024-01-08 10:28:58 | Suspect Overload - Bypass | Overload - Bypass (Energy Theft) | Overload - Bypass | Successful Intervention - Non-TX Remediation | Closed | Meter Field Inspection
|  | 2024-05-01 18:41:05 | Suspect Wiring Issue | Intervention through another department | Not Complete | Successful Prediction - Non-TX Remediation | Closed | Not Initiated
Sent to Revenue Assurance |  | 2024-11-13 15:48:44 | Suspect Overload - Bypass | Overload - Bypass (Energy Theft) | Overload - Bypass | Successful Intervention - Non-TX Remediation | Closed | Meter Field Inspection | [Tier 3 - Extreme]
|  | 2024-04-04 09:23:41 | Suspect Incorrect displayed values | Meter Program Error |  | Non-Risk Issue | Closed | Not Initiated
Sent to Revenue Assurance |  | 2024-02-01 16:04:03 | Suspect Overload - Bypass | Overload - Bypass (Energy Theft) | Overload - Bypass | Successful Intervention - Non-TX Remediation | Closed | Meter Field Inspection | [Tier 3 - Extreme]
40112589 |  | 2024-01-18 13:51:20 | Suspect Overload - Bypass | Overload - Bypass (Energy Theft) | Overload - Bypass | Successful Intervention - Non-TX Remediation | Closed | Meter Field Inspection
Sent to Revenue Assurance |  | 2024-09-12 | Suspect Overload - Bypass | Overload - Bypass (Energy Theft) | Overload - Bypass | Successful Intervention - Non-TX Remediation | Closed | Meter Field Inspection | [Tier 3 - Extreme]
40113449 |  | 2024-02-14 14:22:37 | Suspected Meter Issue | Meter Issue | Meter Issue | Non-Risk Issue | Closed | Ad-hoc Notification Created | [Tier 2 - Elevated]
|  | 2024-03-15 09:44:29 | False Positive Prediction | False Positive | False Positive | False Positive Prediction | Closed | Not Initiated | [Tier 2 - Elevated]
|  | 2024-02-28 14:21:24 | Suspect Primary Issue | Intervention through another department | Not Complete | Successful Prediction - Non-TX Remediation | Closed | Flagged for Inspection | [Tier 2 - Elevated]
|  | 2024-01-31 07:15:55 | Suspect Windings Failure | Intervention through another department | Not Complete | Successful Prediction - Replaced Transformer | Closed | Not Initiated |  | 1
40115906 |  | 2024-04-15 15:01:00 | Suspect Overload - No Bypass | Overload - No Bypass Customer Notified | Overload - No Bypass | Successful Intervention - Non-TX Remediation | Closed | Ad-hoc Notification Created
|  | 2024-06-14 17:13:01 | Suspect Customer's Equipment |  | Not Complete | Non-Risk Issue | Closed | Not Initiated | [Tier 2 - Elevated]
40120002 |  | 2024-10-04 16:33:40 | Suspect Overload - No Bypass | Overload - No Bypass Customer Notified | Customer Usage | Successful Intervention - Non-TX Remediation | Closed | Closed - No EC tag
40120004 |  | 2024-10-09 14:15:36 | Suspect Overload - No Bypass | Overload - No Bypass Customer Notified | Overloaded - Single Service Point | Successful Intervention - Non-TX Remediation | Closed | Ad-hoc Notification Created
40121687 |  | 2024-08-06 16:48:49 | Suspected Loose Neutral | Intervention through another department | Loose Neutral | Successful Prediction - Non-TX Remediation | Closed | Ad-hoc Notification Created
|  | 2024-04-11 01:22:43 | Suspect Incorrect displayed values | Meter Program Error |  | Non-Risk Issue | Closed | Not Initiated
|  | 2024-04-03 14:53:36 | Suspect Incorrect displayed values | Meter Program Error |  | Non-Risk Issue | Closed | Not Initiated
Sent to Planning | 122422537 | 2024-01-04 12:52:30 | Suspect Overload - No Bypass | Transformer Replacement | Overload - No Bypass | Successful Intervention - Replaced Transformer | Closed | Closed - EC tag | [Tier 3 - Extreme] | 1 | 0.034952
40115080 | 128778926 | 2024-03-01 15:11:13 | Suspect Overload - No Bypass | Transformer Replacement | Overload - No Bypass | Successful Intervention - Replaced Transformer | Closed | Closed - EC tag | [Tier 3 - Extreme] | 1 | 0.047798 | Crossarm/Pole | 0.00012099
|  | 2024-09-25 11:02:13 | Circuit Outage | Circuit Outage | Not Complete | Non-Risk Issue | Closed | Not Initiated | [Tier 3 - Extreme]
40120341 | 129844858 | 2024-10-21 10:28:19 | Suspect Overload - No Bypass | Transformer Replacement | Overload - No Bypass | Successful Intervention - Replaced Transformer | Closed | Closed - EC tag |  | 1 | 0.0075092
|  | 2024-02-16 08:58:40 | Suspect Windings Failure | Intervention through another department | Not Complete | Successful Prediction - Replaced Transformer | Closed | Not Initiated |  | 1
40118933 | 129400618 | 2024-06-14 16:22:38 | Suspect Overload - No Bypass | Transformer Replacement | Overload - No Bypass | Successful Intervention - Replaced Transformer | Closed | Closed - EC tag |  | 1 | 0.0075376 | Crossarm | 3.6698e-05
40113448 | 128228734 | 2024-02-21 15:33:06 | Suspect Parallel Secondary Blown Fuse | Fuse Failures | Parallel Bank Fuse Failure | Successful Intervention - Non-TX Remediation | Closed | Closed - EC tag
128228734 | 128228734 | 2024-02-28 12:00:07 | Suspect Parallel Secondary Blown Fuse | Fuse Failures | Wiring issue | Successful Intervention - Non-TX Remediation | Closed | Closed - EC tag
40117390 | 129172514 | 2024-06-14 14:17:50 | Suspect Parallel TXs Failure | Transformer Replacement | Parallel TX Failure | Successful Intervention - Replaced Transformer | Closed | Closed - EC tag |  | 1 | 0.0076659
|  | 2024-07-22 22:38:12 | Suspect Primary Issue |  | Not Complete | Non-Risk Issue | Closed | Not Initiated
40119853 | 129633800 | 2024-07-11 11:29:24 | Suspect Parallel TXs Failure | Transformer Replacement | Parallel TX Failure | Successful Intervention - Replaced Transformer | Closed | Closed - EC tag |  | 1 | 0.0077288
40119485 | 129532069 | 2024-06-04 16:37:01 | Suspect Parallel TXs Failure | Transformer Replacement | Parallel TX Failure | Successful Intervention - Replaced Transformer | Closed | Closed - EC tag |  | 1 | 0.0076041
|  | 2024-04-29 12:04:01 | Suspect Incorrect displayed values | Meter Program Error |  | Non-Risk Issue | Closed | Not Initiated
40120060 | 129669656 | 2024-10-04 12:34:42 | Suspect Parallel TXs Failure | Transformer Replacement | Parallel TX Failure | Successful Intervention - Replaced Transformer | Closed | Closed - EC tag |  | 1 | 0.0076509
|  | 2024-04-30 16:48:04 | Suspect Incorrect displayed values | Meter Program Error |  | Non-Risk Issue | Closed | Not Initiated | [Tier 2 - Elevated]
40119572 | 129551678 | 2024-09-17 15:50:54 | Suspect Parallel TXs Failure | Transformer Replacement | Parallel TX Failure | Successful Intervention - Replaced Transformer | Closed | Closed - EC tag |  | 1 | 0.0076608
|  | 2024-09-06 14:32:49 | Suspect Windings Failure | Intervention through another department |  | Successful Prediction - Replaced Transformer | Closed |  |  | 1
Sent to Distribution Ops |  | 2024-03-21 11:04:53 | Suspect Primary Issue | Primary issues | Not Complete | Successful Intervention - Non-TX Remediation | Closed | Not Initiated | [Tier 2 - Elevated]
Sent to Distribution Ops |  | 2024-12-19 13:15:40 | Suspect Primary Issue | Primary issues | Regulator Bypassed | Successful Intervention - Non-TX Remediation | Closed | Flagged for inspection | [Tier 2 - Elevated]
|  | 2024-05-01 10:17:53 | Suspected Cycling AG load |  | Not Complete | Non-Risk Issue | Closed | Not Initiated
Sent to Distribution Ops |  | 2024-11-27 08:15:35 | Suspect Primary Issue | Primary issues | Reactive - Cap. Bank Issue | Successful Intervention - Non-TX Remediation | Closed | Flagged for inspection
40116247 |  | 2024-04-30 16:58:50 | Suspected Meter Issue | Meter Issue | Meter Issue | Non-Risk Issue | Closed | Ad-hoc Notification Created
|  | 2024-02-27 11:47:28 | Suspect Incorrect displayed values | Meter Program Error |  | Non-Risk Issue | Closed | Not Initiated
|  | 2024-02-27 11:24:24 | Suspect Incorrect displayed values | Meter Program Error |  | Non-Risk Issue | Closed | Not Initiated
40121000 |  | 2024-11-20 13:49:30 | Suspect Primary Issue | Primary issues | Primary Issue | Successful Intervention - Non-TX Remediation | Closed | Ad-hoc Notification Created | [Tier 2 - Elevated]
|  | 2024-03-11 15:33:11 | Suspect Incorrect displayed values | Meter Program Error |  | Non-Risk Issue | Closed | Not Initiated | [Tier 2 - Elevated]
Sent to Distribution Ops |  | 2024-05-07 15:33:53 | Suspect Primary Issue | Primary issues | Not Complete | Successful Intervention - Non-TX Remediation | Closed | Not Initiated
40116866 |  | 2024-05-20 16:42:03 | Suspect Primary Issue | Primary issues | Other | Successful Intervention - Non-TX Remediation | Closed | Ad-hoc Notification Created | [Tier 3 - Extreme]
Sent to Distribution Ops |  | 2024-05-28 10:39:28 | Suspect Primary Issue | Primary issues | Not Complete | Successful Intervention - Non-TX Remediation | Closed | Not Initiated
|  | 2024-03-04 14:26:23 | Suspect Primary Issue |  | Not Complete | Non-Risk Issue | Closed | Not Initiated | [Tier 3 - Extreme]
Sent to Distribution Ops |  | 2024-05-14 12:13:37 | Suspect Primary Issue | Primary issues | Not Complete | Successful Intervention - Non-TX Remediation | Closed | Not Initiated
|  | 2024-02-20 13:17:25 | Suspect Primary Issue |  | Not Complete | Non-Risk Issue | Closed | Not Initiated | [Tier 2 - Elevated]
|  | 2024-01-16 15:54:31 | Suspect Windings Failure | Intervention through another department | Not Complete | Successful Prediction - Replaced Transformer | Closed | Not Initiated |  | 1
Sent to Distribution Ops |  | 2024-12-17 16:51:32 | Suspect Primary Issue | Primary issues | Regulator's Settings | Successful Intervention - Non-TX Remediation | Closed | Flagged for inspection
Sent to Distribution Ops |  | 2024-02-01 17:57:10 | Suspect Primary Issue | Primary issues | Not Complete | Successful Intervention - Non-TX Remediation | Closed | Not Initiated | [Tier 3 - Extreme]
Sent to Distribution Ops |  | 2024-12-18 16:08:53 | Suspect Primary Issue | Primary issues |  | Successful Intervention - Non-TX Remediation | Closed
|  | 2024-08-02 14:21:25 | Suspect Incorrect displayed values | Meter Program Error |  | Non-Risk Issue | Closed
|  | 2024-06-17 16:24:08 | Suspect Incorrect displayed values | Meter Program Error |  | Non-Risk Issue | Closed | Not Initiated
Sent to Distribution Ops |  | 2024-04-09 15:45:55 | Suspect Primary Issue | Primary issues | Not Complete | Successful Intervention - Non-TX Remediation | Closed | Not Initiated
|  | 2024-06-04 16:36:14 | Suspect Parallel TXs Failure | Intervention through another department |  | Successful Prediction - Replaced Transformer | Closed |  |  | 1
|  | 2024-04-22 19:58:54 | Suspect Incorrect displayed values | Meter Program Error |  | Non-Risk Issue | Closed | Not Initiated
|  | 2024-07-11 14:26:31 | Suspect Incorrect displayed values | Meter Program Error |  | Non-Risk Issue | Closed | Not Initiated
|  | 2024-05-20 13:58:14 | Suspect Equipment Arcing | Intervention through another department |  | Successful Prediction - Non-TX Remediation | Closed
|  | 2024-06-11 15:39:08 | Suspect Incorrect displayed values | Meter Program Error |  | Non-Risk Issue | Closed | Not Initiated
|  | 2024-05-08 15:26:35 | Suspect Incorrect displayed values | Meter Program Error |  | Non-Risk Issue | Closed | Not Initiated
|  | 2024-08-23 12:01:53 | Suspect Customer's Drop Design Constraints | Customer's Equipment Limitation - Secondary Conductor |  | Non-Risk Issue | Closed
40116741 | 128782860 | 2024-04-23 16:19:54 | Suspect Windings Failure | Transformer Replacement | Tree Fell on Pole | Successful Intervention - Replaced Transformer | Closed | Closed - EC tag |  | 3 | 0.11568
|  | 2024-05-09 13:29:25 | Suspect Incorrect displayed values | Meter Program Error |  | Non-Risk Issue | Closed | Not Initiated
|  | 2024-02-21 09:13:39 | Suspect Windings Failure | Intervention through another department | Not Complete | Successful Prediction - Replaced Transformer | Closed | Not Initiated |  | 1
|  | 2024-03-04 10:42:52 | Suspect Incorrect displayed values | Meter Program Error | Display shows incorrect values | Non-Risk Issue | Closed | Not Initiated | [Tier 2 - Elevated]
|  | 2024-06-14 17:04:20 | Suspect Incorrect displayed values | Meter Program Error |  | Non-Risk Issue | Closed | Not Initiated
40113091 | 128124123 | 2024-01-24 15:42:44 | Suspect Windings Failure | Transformer Replacement | Windings Failure | Successful Intervention - Replaced Transformer | Closed | Closed - EC tag |  | 1 | 0.0069828
|  | 2024-02-16 09:01:25 | Suspect Incorrect displayed values | Meter Program Error |  | Non-Risk Issue | Closed | Not Initiated
40121125 | 129897242 | 2024-12-04 14:09:44 | Suspect Windings Failure | Transformer Replacement | Windings Failure | Successful Intervention - Replaced Transformer | Closed | Closed - EC tag | [Tier 2 - Elevated] | 1 | 0.10679
40115093 | 128350715 | 2024-02-27 10:00:08 | Suspect Windings Failure | Transformer Replacement | Windings Failure | Successful Intervention - Replaced Transformer | Closed | Closed - EC tag | [Tier 2 - Elevated] | 1 | 0.33603
40116743 | Disconnected | 2024-05-10 14:55:15 | Suspect Broken Jumper | Broken Jumpers | Broken Jumper | Successful Intervention - Non-TX Remediation | Closed | Closed - EC tag
40120981 | 129834893 | 2024-11-23 00:47:34 | Suspect Windings Failure | Transformer Replacement | Windings Failure | Successful Intervention - Replaced Transformer | Closed | Closed - EC tag |  | 1 | 0.0074887 | Crossarm/Pole | 2.2893e-05
|  | 2024-04-22 16:50:16 | Suspect Blown Fuse | Intervention through another department | Not Complete | Successful Prediction - Non-TX Remediation | Closed | Not Initiated | [Tier 2 - Elevated]
40116090 | 128624306 | 2024-04-04 10:46:51 | Suspect Windings Failure | Transformer Replacement | Windings Failure | Successful Intervention - Replaced Transformer | Closed | Closed - EC tag |  | 2 | 0.0075085
40120690 | 129784685 | 2024-11-05 11:24:43 | Suspect Windings Failure | Transformer Replacement | Windings Failure | Successful Intervention - Replaced Transformer | Closed | Closed - EC tag |  | 1 | 0.0074509
40115082 | 128298392 | 2024-03-11 15:08:35 | Suspect Windings Failure | Transformer Replacement | Windings Failure | Successful Intervention - Replaced Transformer | Closed | Closed - EC tag | [Tier 3 - Extreme] | 1 | 0.094013
40121590 | 130710537 | 2025-01-03 15:21:59 | Suspect Windings Failure | Transformer Replacement | Windings Failure | Successful Intervention - Replaced Transformer | Closed | Closed - EC tag | [Tier 2 - Elevated] | 1 | 0.019195
|  | 2024-03-12 16:04:08 | Suspect Incorrect displayed values | Meter Program Error |  | Non-Risk Issue | Closed | Not Initiated
40115083 | 128299305 | 2024-03-07 11:44:42 | Suspect Windings Failure | Transformer Replacement | Windings Failure | Successful Intervention - Replaced Transformer | Closed | Closed - EC tag |  | 1 | 0.0069059
40116562 | 128744254 | 2024-04-30 16:09:56 | Suspect Windings Failure | Transformer Replacement | Windings Failure | Successful Intervention - Replaced Transformer | Closed | Closed - EC tag | [Tier 2 - Elevated] | 1 | 0.046452
|  | 2024-08-21 12:25:53 | Suspect Primary Issue |  |  | Non-Risk Issue | Closed
|  | 2024-08-01 14:51:08 | Suspect Incorrect displayed values | Meter Program Error |  | Non-Risk Issue | Closed
40121124 | 129896633 | 2024-12-04 12:35:00 | Suspect Windings Failure | Transformer Replacement | Windings Failure | Successful Intervention - Replaced Transformer | Closed | Closed - EC tag |  | 1 | 0.0069387
|  | 2024-07-18 13:03:34 | Suspect Broken Jumper | Intervention through another department | Not Complete | Successful Prediction - Non-TX Remediation | Closed | Not Initiated
|  | 2024-04-22 15:20:29 | Suspect Primary Issue |  | Not Complete | Non-Risk Issue | Closed | Not Initiated
|  | 2024-03-05 10:19:53 | Suspect Customer's Equipment |  | Not Complete | Non-Risk Issue | Closed | Not Initiated
|  | 2024-06-04 11:04:56 | Suspect Customer's Equipment |  | Not Complete | Non-Risk Issue | Closed | Not Initiated
40115907 | 128571765 | 2024-04-03 14:21:06 | Suspect Windings Failure | Transformer Replacement | Windings Failure | Successful Intervention - Replaced Transformer | Closed | Closed - EC tag |  | 1 | 0.0073819
|  | 2024-01-03 09:18:11 | Suspect Incorrect displayed values | Meter Program Error |  | Non-Risk Issue | Closed | Not Initiated
40120579 | 129762003 | 2024-10-31 16:41:26 | Suspect Windings Failure | Transformer Replacement | Windings Failure | Successful Intervention - Replaced Transformer | Closed | Closed - EC tag |  | 1 | 0.0075042
40115084 | 128300151 | 2024-03-04 16:18:32 | Suspect Windings Failure | Transformer Replacement | Windings Failure | Successful Intervention - Replaced Transformer | Closed | Closed - EC tag | [Tier 2 - Elevated] | 1 | 0.17308
40120406 |  | 2024-10-23 14:10:59 | Suspected Meter Issue | Meter Issue | Meter Issue | Non-Risk Issue | Closed | Ad-hoc Notification Created | [Tier 3 - Extreme]
40121002 | 129848116 | 2024-11-20 15:02:44 | Suspect Windings Failure | Transformer Replacement | Windings Failure | Successful Intervention - Replaced Transformer | Closed | Closed - EC tag | [Tier 3 - Extreme] | 1 | 0.013295
|  | 2024-03-06 15:15:26 | Suspect Incorrect displayed values | Meter Program Error |  | Non-Risk Issue | Closed | Not Initiated | [Tier 3 - Extreme]
40115533 | 128464925 | 2024-04-03 10:06:31 | Suspect Windings Failure | Transformer Replacement | Windings Failure | Successful Intervention - Replaced Transformer | Closed | Closed - EC tag |  | 2 | 0.0050819
|  | 2024-05-08 15:43:51 | Suspect Windings Failure | Intervention through another department | Not Complete | Successful Prediction - Replaced Transformer | Closed | Not Initiated |  | 1
|  | 2024-05-24 14:31:11 | Suspect Blown Fuse | Intervention through another department | Not Complete | Successful Prediction - Non-TX Remediation | Closed | Not Initiated
40120995 |  | 2024-11-20 23:11:59 | Suspect Incorrect displayed values | Meter Program Error | Display shows incorrect values | Non-Risk Issue | Closed | False Positive
|  | 2024-05-30 13:39:44 | Suspect Incorrect displayed values | Meter Program Error |  | Non-Risk Issue | Closed | Not Initiated
40120403 | 129733926 | 2024-10-25 10:29:08 | Suspect Windings Failure | Transformer Replacement | Windings Failure | Successful Intervention - Replaced Transformer | Closed | Closed - EC tag |  | 1 | 0.0050858
40118546 |  | 2024-02-23 16:10:07 | Suspect Customer's Equipment |  | Customer's Equipment | Non-Risk Issue | Closed | Ad-hoc Notification Created
|  | 2024-04-15 11:05:12 | Suspect Incorrect displayed values | Meter Program Error |  | Non-Risk Issue | Closed | Not Initiated
|  | 2024-02-15 21:17:26 | False Positive Prediction | False Positive | False Positive | False Positive Prediction | Closed | Not Initiated
40120792 | 129809305 | 2024-11-12 15:36:02 | Suspect Windings Failure | Transformer Replacement | Windings Failure | Successful Intervention - Replaced Transformer | Closed | Closed - EC tag |  | 1 | 0.0075205
40116084 | 128697497 | 2024-04-23 15:21:04 | Suspect Windings Failure | Transformer Replacement | Windings Failure | Successful Intervention - Replaced Transformer | Closed | Closed - EC tag |  | 1 | 0.0076394
40120991 | 129844434 | 2024-11-20 11:36:08 | Suspect Windings Failure | Transformer Replacement | Windings Failure | Successful Intervention - Replaced Transformer | Closed | Closed - EC tag |  | 1 | 0.0076202
40119815 | 129597724 | 2024-09-26 14:18:17 | Suspect Windings Failure | Transformer Replacement | Windings Failure | Successful Intervention - Replaced Transformer | Closed | Closed - EC tag |  | 1 | 0.0075481
40113082 |  | 2024-02-02 00:45:33 | Suspected Meter Issue | Meter Issue | Meter Issue | Non-Risk Issue | Closed | Ad-hoc Notification Created | [Tier 3 - Extreme]
40118170 | 129243080 | 2024-07-17 13:45:30 | Suspect Windings Failure | Transformer Replacement | Windings Failure | Successful Intervention - Replaced Transformer | Closed | Closed - EC tag |  | 1 | 0.0075531
|  | 2024-02-22 14:59:03 | Suspect Incorrect displayed values | Meter Program Error |  | Non-Risk Issue | Closed | Not Initiated
|  | 2024-02-26 10:49:26 | Suspect Windings Failure | Intervention through another department | Not Complete | Successful Prediction - Replaced Transformer | Closed | Not Initiated |  | 1
40120372 | 129725182 | 2023-07-28 14:53 | Suspect Windings Failure | Transformer Replacement | Windings Failure | Successful Intervention - Replaced Transformer | Closed | Closed - EC tag |  | 1 | 0.0076023 | Crossarm | 0.00014351
40117207 | 129064109 | 2024-06-11 15:38:06 | Suspect Windings Failure | Transformer Replacement | Windings Failure | Successful Intervention - Replaced Transformer | Closed | Closed - EC tag |  | 1 | 0.0075677
40115086 | 128300294 | 2024-02-27 15:09:41 | Suspect Windings Failure | Transformer Replacement | Windings Failure | Successful Intervention - Replaced Transformer | Closed | Closed - EC tag |  | 3 | 0.0075486 | Pole | 5.5959e-05
|  | 2024-03-29 12:51:28 | Suspect Incorrect displayed values | Meter Program Error |  | Non-Risk Issue | Closed | Not Initiated
|  | 2024-04-25 14:06:23 | Suspect Incorrect displayed values | Meter Program Error |  | Non-Risk Issue | Closed | Not Initiated
40115085 |  | 2024-02-27 10:42:34 | Suspected Meter Issue | Meter Issue | Meter Issue | Non-Risk Issue | Closed | Ad-hoc Notification Created
40121381 | 130114300 | 2024-12-17 15:29:58 | Suspect Windings Failure | Transformer Replacement | Windings Failure | Successful Intervention - Replaced Transformer | Closed | Closed - EC tag |  | 1 | 0.0075622
|  | 2024-04-22 18:50:29 | Suspect Incorrect displayed values | Meter Program Error |  | Non-Risk Issue | Closed
S000933122 |  | 2024-06-04 15:57:03 | Suspect Parallel Secondary Blown Fuse | Intervention through another department | Fuse Failure | Successful Prediction - Non-TX Remediation | Closed | Closed - No EC tag
|  | 2024-10-21 13:56:44 | Suspect Incorrect displayed values | Meter Program Error |  | Non-Risk Issue | Closed
|  | 2024-10-25 16:43:07 | Suspect Incorrect displayed values | Meter Program Error |  | Non-Risk Issue | Closed
40115253 | 128402326 | 2024-03-04 14:47:24 | Suspect Windings Failure | Wiring Issues | Wiring Issue | Successful Intervention - Non-TX Remediation | Closed | Closed - EC tag | [Tier 2 - Elevated]
|  | 2024-10-25 16:38:46 | Suspect Incorrect displayed values | Meter Program Error |  | Non-Risk Issue | Closed
40121319 | 130112044 | 2024-12-17 09:07:23 | Suspect Windings Failure | Transformer Replacement | Windings Failure | Successful Intervention - Replaced Transformer | Closed | Closed - EC tag |  | 1 | 0.0076674
|  | 2024-03-21 14:28:51 | Suspect Incorrect displayed values | Meter Program Error |  | Non-Risk Issue | Closed | Not Initiated
40120980 | 129834628 | 2024-11-19 09:19 | Suspect Windings Failure | Transformer Replacement | Windings Failure | Successful Intervention - Replaced Transformer | Closed | Closed - EC tag |  | 1 | 0.0076506
40113095 |  | 2024-01-31 13:39:39 | Suspected Loose Neutral | Loose/Broken Neutrals | Loose Neutral | Successful Intervention - Non-TX Remediation | Closed | Closed - No EC tag | [Tier 3 - Extreme]
|  | 2024-08-08 13:48:06 | Suspect Incorrect displayed values | Meter Program Error |  | Non-Risk Issue | Closed
40119395 | 129516953 | 2024-09-04 14:34:59 | Suspect Wiring Issue | Wiring Issues | Wiring issue | Successful Intervention - Non-TX Remediation | Closed | Closed - EC tag
40115661 |  | 2024-04-04 11:40:46 | Suspect Wiring Issue | Wiring Issues | Wiring issue | Successful Intervention - Non-TX Remediation | Closed | Closed - No EC tag
40121523 |  | 2024-12-31 12:15:14 | Suspect Wiring Issue | Wiring Issues | Wiring Issue | Successful Intervention - Non-TX Remediation | Closed | Closed - No EC tag
40117086 |  | 2024-05-30 14:36:46 | Suspect Wiring Issue | Wiring Issues | Customer's Equipment | Successful Intervention - Non-TX Remediation | Closed | Closed - No EC tag
40120237 | 129700554 | 2024-10-17 14:52:13 | Suspect Wiring Issue | Wiring Issues | Wiring issue | Successful Intervention - Non-TX Remediation | Closed | Closed - No EC tag
40120754 |  | 2024-11-13 11:15:08 | Suspect Wiring Issue | Wiring Issues | Wiring issue | Successful Intervention - Non-TX Remediation | Closed | Closed - No EC tag
40118583 |  | 2024-06-04 10:06:40 | Suspected Meter Issue | Meter Issue | Meter Issue | Non-Risk Issue | Closed | Closed - No EC tag
|  | 2024-12-25 00:59:47 | Circuit Outage | Circuit Outage | Not Complete | Non-Risk Issue | Closed | Not Initiated | [Tier 2 - Elevated]
2370545510 |  | 2024-06-03 14:41:13 | Suspect Wiring Issue | Wiring Issues | Wiring issue | Successful Intervention - Non-TX Remediation | Closed | Closed - No EC tag
|  | 2024-02-01 11:42:42 | Suspect Incorrect displayed values | Meter Program Error |  | Non-Risk Issue | Closed | Not Initiated | [Tier 3 - Extreme]
40115255 |  | 2024-03-05 09:37:38 | Suspect Wiring Issue | Wiring Issues | Wiring issue | Successful Intervention - Non-TX Remediation | Closed | Closed - No EC tag
40116383 | 128707982 | 2024-04-25 10:47:03 | Suspect Wiring Issue | Wiring Issues | Wiring issue | Successful Intervention - Non-TX Remediation | Closed | Closed - EC tag
40117168 |  | 2024-06-04 16:13:59 | Suspect Wiring Issue | Wiring Issues | Wiring issue | Successful Intervention - Non-TX Remediation | Closed | Closed - No EC tag
40113180 |  | 2024-02-09 11:43:00 | Suspect Wiring Issue | Wiring Issues | Wiring Issue | Successful Intervention - Non-TX Remediation | Closed | Closed - No EC tag | [Tier 3 - Extreme]
|  | 2024-03-04 11:05:14 | Suspect Windings Failure | Intervention through another department | Not Complete | Successful Prediction - Replaced Transformer | Closed | Not Initiated | [Tier 3 - Extreme] | 1
40116563 |  | 2024-05-09 09:12:20 | Suspect Wiring Issue | Wiring Issues | Wiring issue | Successful Intervention - Non-TX Remediation | Closed | Closed - No EC tag
|  | 2024-06-14 13:31:31 | Circuit Outage | Circuit Outage | Not Complete | Non-Risk Issue | Closed | Not Initiated
|  | 2024-08-15 12:00:47 | Suspect Incorrect displayed values | Meter Program Error |  | Non-Risk Issue | Closed
40121526 |  | 2024-12-31 12:11:28 | Suspect Wiring Issue | Wiring Issues | NG PG connector | Successful Intervention - Non-TX Remediation | Closed | Closed - No EC tag
|  | 2024-07-09 14:25:58 | Suspect Incorrect displayed values | Meter Program Error |  | Non-Risk Issue | Closed | Not Initiated
|  | 2024-10-25 16:36:10 | Suspected Cycling AG load |  |  | Non-Risk Issue | Closed
|  | 2024-07-29 09:32:15 | Suspect Customer's Equipment |  | Not Complete | Non-Risk Issue | Closed | Not Initiated
|  | 2024-03-29 12:11:47 | Suspect Incorrect displayed values | Meter Program Error |  | Non-Risk Issue | Closed | Not Initiated
40120342 | 129714447 | 2024-10-21 13:23:51 | Suspect Wiring Issue | Wiring Issues | Wiring issue | Successful Intervention - Non-TX Remediation | Closed | Closed - EC tag
40121376 |  | 2024-12-20 08:50:17 | Suspect Wiring Issue | Wiring Issues | Wiring issue | Successful Intervention - Non-TX Remediation | Closed | Closed - No EC tag
40121450 |  | 2024-12-23 13:37:52 | Suspect Wiring Issue | Wiring Issues | Burnt Wiring | Successful Intervention - Non-TX Remediation | Closed | Closed - No EC tag
40116461 | 128728148 | 2024-05-06 16:42:34 | Suspect Wiring Issue | Wiring Issues | Wiring issue | Successful Intervention - Non-TX Remediation | Closed | Closed - EC tag
40116384 |  | 2024-04-25 11:59:32 | Suspect Wiring Issue | Wiring Issues | Wiring issue | Successful Intervention - Non-TX Remediation | Closed | Closed - No EC tag
|  | 2024-07-18 09:42:41 | Suspect Primary Issue |  | Not Complete | Non-Risk Issue | Closed | Not Initiated
40120344 |  | 2024-10-23 07:39:27 | Suspect Wiring Issue | Wiring Issues | Wiring issue | Successful Intervention - Non-TX Remediation | Closed | Closed - No EC tag
40117682 |  | 2024-06-26 07:24:38 | Suspected Loose Neutral | Loose/Broken Neutrals | Loose Neutral | Successful Intervention - Non-TX Remediation | Closed | Closed - No EC tag | [Tier 2 - Elevated]
40121724 | 130741072 | 2024-11-27 08:45:16 | Suspected Loose Neutral | Loose/Broken Neutrals | Loose Neutral | Successful Intervention - Non-TX Remediation | Closed | Closed - No EC tag
40121227 |  | 2024-11-27 08:40:38 | Suspected Loose Neutral | Loose/Broken Neutrals | Loose Neutral | Successful Intervention - Non-TX Remediation | Closed | Closed - No EC tag
|  | 2024-05-21 15:56:30 | Circuit Outage | Circuit Outage | Not Complete | Non-Risk Issue | Closed | Not Initiated
40120545 |  | 2024-10-30 09:50:50 | Suspected Loose Neutral | Loose/Broken Neutrals | Loose Neutral | Successful Intervention - Non-TX Remediation | Closed | Closed - No EC tag
|  | 2024-04-11 14:30:46 | Suspect Incorrect displayed values | Meter Program Error |  | Non-Risk Issue | Closed | Not Initiated
|  | 2024-03-26 10:41:47 | Suspect Incorrect displayed values | Meter Program Error |  | Non-Risk Issue | Closed | Not Initiated
40112587 |  | 2024-02-29 10:22:00 | Suspected Loose Neutral | Loose/Broken Neutrals | Windings Failure | Successful Intervention - Non-TX Remediation | Closed | Closed - No EC tag
|  | 2024-03-25 14:19:20 | Suspect Incorrect displayed values | Meter Program Error |  | Non-Risk Issue | Closed | Not Initiated
|  | 2024-04-12 12:31:38 | Suspect Incorrect displayed values | Meter Program Error |  | Non-Risk Issue | Closed | Flagged for Inspection
40115256 |  | 2024-03-25 15:56:22 | Suspected Loose Neutral | Loose/Broken Neutrals | Loose Neutral | Successful Intervention - Non-TX Remediation | Closed | Closed - No EC tag
|  | 2024-02-26 15:47:03 | Suspect Primary Issue | Intervention through another department | Not Complete | Successful Prediction - Non-TX Remediation | Closed | Not Initiated | [Tier 2 - Elevated]
40117083 |  | 2024-05-30 13:42:28 | Suspected Loose Neutral | Loose/Broken Neutrals | Loose Neutral | Successful Intervention - Non-TX Remediation | Closed | Closed - No EC tag
40120337 |  | 2024-10-23 07:01:57 | Suspected Loose Neutral | Loose/Broken Neutrals | Loose Neutral | Successful Intervention - Non-TX Remediation | Closed | Closed - No EC tag
40117085 |  | 2024-05-30 14:57:13 | Suspected Loose Neutral | Loose/Broken Neutrals | Loose Neutral | Successful Intervention - Non-TX Remediation | Closed | Closed - No EC tag
40120547 |  | 2024-04-11 10:32:57 | False Positive Prediction | False Positive | False Positive | False Positive Prediction | Closed | Ad-hoc Notification Created
40121527 |  | 2024-12-31 09:12:37 | Suspected Loose Neutral | Loose/Broken Neutrals | Loose Neutral | Successful Intervention - Non-TX Remediation | Closed | Closed - No EC tag
40116085 |  | 2024-04-22 18:59:13 | Suspected Loose Neutral | Loose/Broken Neutrals | Loose Neutral | Successful Intervention - Non-TX Remediation | Closed | Closed - No EC tag
40120575 |  | 2024-10-30 11:33:37 | Suspected Loose Neutral | Loose/Broken Neutrals | Loose Neutral | Successful Intervention - Non-TX Remediation | Closed | Closed - No EC tag
40121296 |  | 2024-12-19 14:56:34 | Suspected Loose Neutral | Loose/Broken Neutrals | Corroded Neutral Splice | Successful Intervention - Non-TX Remediation | Closed | Closed - No EC tag
40121528 |  | 2024-12-31 09:09:54 | Suspected Loose Neutral | Loose/Broken Neutrals | Loose Neutral | Successful Intervention - Non-TX Remediation | Closed | Closed - No EC tag
|  | 2024-04-03 15:10:34 | False Positive Prediction | False Positive | False Positive | False Positive Prediction | Closed | Not Initiated
S000933122 |  | 2024-05-21 16:16:14 | Suspect Parallel Secondary Blown Fuse | Intervention through another department | Fuse Failure | Successful Prediction - Non-TX Remediation | Closed | Closed - No EC tag
40115254 |  | 2024-02-14 11:04:25 | Suspected Loose Neutral | Loose/Broken Neutrals | Loose Neutral | Successful Intervention - Non-TX Remediation | Closed | Closed - No EC tag | [Tier 2 - Elevated]
|  | 2024-12-31 11:25:36 | Circuit Outage | Circuit Outage | Not Complete | Non-Risk Issue | Closed | Not Initiated
|  | 2024-12-31 11:28:26 | Circuit Outage | Circuit Outage | Not Complete | Non-Risk Issue | Closed | Not Initiated
40118840 | 129373532 | 2024-08-08 16:38:56 | Suspected Loose Neutral | Loose/Broken Neutrals | Loose Neutral | Successful Intervention - Non-TX Remediation | Closed | Closed - EC tag | [Tier 3 - Extreme]
40120793 |  | 2024-11-12 17:47:49 | Suspected Loose Neutral | Loose/Broken Neutrals | Burnt Lug/Neutral | Successful Intervention - Non-TX Remediation | Closed | Closed - No EC tag
|  | 2024-04-03 15:38:23 | False Positive Prediction | False Positive | False Positive | False Positive Prediction | Closed | Not Initiated
|  | 2024-06-03 13:46:31 | Suspect Customer's Equipment |  | Not Complete | Non-Risk Issue | Closed | Not Initiated
40121449 |  | 2024-12-26 16:53:13 | Suspected Loose Neutral | Loose/Broken Neutrals | Loose Neutral | Successful Intervention - Non-TX Remediation | Closed | Closed - No EC tag
|  | 2024-03-22 12:35:56 | Suspect Windings Failure | Intervention through another department | Not Complete | Successful Prediction - Replaced Transformer | Closed | Not Initiated |  | 1
|  | 2024-10-17 13:48:05 | Suspect Incorrect displayed values | Meter Program Error |  | Non-Risk Issue | Closed
|  | 2024-02-16 09:29:50 | Suspect Windings Failure | Intervention through another department | Not Complete | Successful Prediction - Replaced Transformer | Closed | Not Initiated |  | 1
|  | 2024-05-01 13:48:01 | Suspect Windings Failure | Intervention through another department | Not Complete | Successful Prediction - Replaced Transformer | Closed | Not Initiated |  | 1
40116385 | 128721088 | 2024-05-02 12:23:23 | Suspected Loose Neutral | Loose/Broken Neutrals | Loose Neutral | Successful Intervention - Non-TX Remediation | Closed | Closed - EC tag
40121447 |  | 2024-12-26 09:49:52 | Suspected Loose Neutral | Loose/Broken Neutrals | Severely Corroded Neutral | Successful Intervention - Non-TX Remediation | Closed | Closed - No EC tag
40117208 |  | 2024-06-11 15:35:01 | Suspected Loose Neutral | Loose/Broken Neutrals | Loose Neutral | Successful Intervention - Non-TX Remediation | Closed | Closed - No EC tag
40117657 |  | 2024-06-26 07:55:30 | Suspected Loose Neutral | Loose/Broken Neutrals | Loose Neutral | Successful Intervention - Non-TX Remediation | Closed | Closed - No EC tag
40113086 |  | 2024-02-12 08:35:22 | Suspected Loose Neutral | Loose/Broken Neutrals | Loose Neutral | Successful Intervention - Non-TX Remediation | Closed | Ad-hoc Notification Created | [Tier 3 - Extreme]
40117209 |  | 2024-06-11 15:35:55 | Suspected Loose Neutral | Loose/Broken Neutrals | Loose Neutral | Successful Intervention - Non-TX Remediation | Closed | Closed - No EC tag
40118476 | 2533199 | 2024-08-01 14:49:55 | Suspected Loose Neutral | Loose/Broken Neutrals | Loose Neutral | Successful Intervention - Non-TX Remediation | Closed | Closed - EC tag | [Tier 2 - Elevated]
40118171 |  | 2024-07-17 13:44:47 | Suspected Loose Neutral | Loose/Broken Neutrals | Loose Neutral | Successful Intervention - Non-TX Remediation | Closed | Closed - No EC tag
40118384 |  | 2024-07-25 09:48:12 | Suspected Loose Neutral | Loose/Broken Neutrals | Loose Neutral | Successful Intervention - Non-TX Remediation | Closed | Closed - No EC tag
40119118 |  | 2024-08-23 16:04:33 | Suspected Meter Issue | Meter Issue | Meter Issue | Non-Risk Issue | Closed | Meter Field Inspection