## Table of Contents
Post-Event Report Data: PG&E August 17 - 19, 2021 De-energization Event
File Description:
This file includes all tables from the Post Event Report submitted following the August 17-19, 2021 De-energization Event
Table of Contents
Section 1 Tables
Section 2 Tables
Section 5 Tables
Section 6 Tables
Section 7 Tables
Section 8 Tables
Section 10 Tables
Section 11 Tables
Section 12 Tables
Appendix

## Section 1 ->
Post-Event Report Data: PG&E August 17 - 19, 2021 De-energization Event
Section 1 Tables
Table 1: Customers Notified and De-energized

## Table 1
Post-Event Report Data: PG&E August 17 - 19, 2021 De-energization Event
Table 1: Customers Notified and De-energized
Total Customers |  |  | Medical Baseline (MBL) Customers | Number of Counties | Number of Tribes | Number of Circuits |  |  | Damage / Hazard Count | Critical Facilities and Infrastructure
Notified | De-energized | Cancelled | De-energized | De-energized | De-energized | Transmission De-energized | Unique Distribution Circuits in Any Version of Scope | Distribution Circuits De-energized
65861 | 48155 | 17,669[1] | 3856 | 13 | 3 | 3 | 139 | 95 | 6 damages | 936
4 hazards
[1] Of the customers who received cancellation notifications, approximately 40 were ultimately de-energized. Please see page 43 regarding PG&E’s Explanation of De-energization after receiving a Cancellation Notification.

## Section 2 ->
Post-Event Report Data: PG&E August 17 - 19, 2021 De-energization Event
Section 2 Tables
Table 2: Modeling Considerations

## Table 2
Post-Event Report Data: PG&E August 17 - 19, 2021 De-energization Event
Table 2: Modeling Considerations
Risk Type | Wildfire Risk Modeling Considerations | PSPS Risk Modeling Considerations
Safety | Calculated based on maximum population impacts derived from Technosylva wildfire simulation models and a fatality ratio based on National Fire Protection Association (NFPA) data. | Calculated from an estimate of Equivalent Fatalities (EF) per Million Customer Minutes Interrupted (MMCI). EF/MMCI ratio is estimated from previous PG&E PSPS and other large external outage events[1].
Reliability | N/A | Calculated directly from the potential number of customers impacted and outage duration based on customer minutes interrupted
Financial | Calculated based on maximum building impacts derived from Technosylva wildfire simulation models and a cost per structure burned previously evaluated in 2020 RAMP report[2] | Calculated based on two financial estimates 1) distribution of a lump sum cost of execution across all relevant circuits and 2) an estimated proxy cost per customer per PSPS event[3]
[1] Previous PG&E PSPS events include 2019-2020 events, and other large external outage events include 2003 Northeast Blackout in New York City, 2011 Southwest Blackout in San Diego, 2012 Derecho Windstorms, 2012 Superstorm Sandy, and 2017 Hurricane Irma.
[2] See A.20-06-012.
[3] The assumptions used in these calculations, including the proxy cost of $250 per customer per PSPS event, are subject to be updated and are not intended to prejudge or create precedent with regard to the development of more precise values of resiliency or cost of PSPS metrics being considered in other ongoing proceedings at the California Public Utilities Commission, such as the Risk-Based Decision-Making Rulemaking [R.20.07.013] and the Microgrid and Resiliency Strategies Rulemaking (R.19-09-009). PG&E is temporarily using the $250 proxy metric for the cost per customer of a PSPS event to align with the proxy value adopted by the other Investor-Owned Utilities and to respond to the Commission’s requirement that PG&E’s 10-day reports provide a quantified assessment of the relative costs and benefits of PSPS events prior to the development of a full record in other proceedings on this issue. By using the proxy metric for this limited purpose, PG&E does not concede that any particular customer has or will incur costs of this amount due to a particular PSPS event or waive its ability to argue in any particular dispute that the particular costs incurred by a customer due to a PSPS event are different than this proxy. PG&E expects that this cost assumption may be updated as the aforementioned proceedings progress.

## Section 5 ->
Post-Event Report Data: PG&E August 17 - 19, 2021 De-energization Event
Section 5 Tables
Table 3: Notification Descriptions
Table 4: Customer Notification Timeline Summary Prior to De-energization for August 17, 2021 PSPS Event
Table 5: Notifications to customers where positive or affirmative notification was attempted

## Table 3
Post-Event Report Data: PG&E August 17 - 19, 2021 De-energization Event
Table 3: Notification Descriptions
Type of Notification | Recipients | Description
ADVANCED NOTIFICATION: 48-72 hours in advance de-energization | Public Safety Partners and Transmission-level Customers | On Sunday, August 15, PG&E’s Meteorology Team noted a potential weather event. Following PG&E’s activation of its EOC for a potential PSPS event, PG&E completed the following: • Submitted a PSPS State Notification Form to Cal OES and sent an email to the CPUC notifying them that PG&E’s EOC has been activated and that PG&E is monitoring for a potential PSPS event. • Sent notifications to other Public Safety Partners[1], and transmission-level customers via call, text, and email; these notifications include the following information: o Estimated window of the de-energization time. o When weather is anticipated to pass. o Estimated time of restoration (ETOR). o Links to the PSPS Portal and website where event-specific maps and information are available (for Public Safety Partners only). o Links to pge.com/psps and pge.com/pspsweather (for transmission-level customers only).
WATCH NOTIFICATION: 24-48 hours in advance of anticipated de-energization | Public Safety Partners, All Customers (including Medical Baseline program customers and Self-Identified Vulnerable (SIV)[2] customers), and Transmission-level Customers | During this time, PG&E completed the following: • Submitted a PSPS State Notification Form to Cal OES and sent an email to the CPUC to notify them that power is in the process of being shut off. • Sent notifications to other Public Safety Partners, transmission-level customers, and all customers via call, text, and email; these notifications include the following information: o Potentially impacted addresses (for customers only). o Transmission Substation Name and Line name serving substation (for transmission-level customers only). o Estimated window of the de-energization time. o When weather is anticipated to pass. o Estimated time of restoration (ETOR). o Links to the PSPS Portal and website where event-specific maps and information is available (for Public Safety Partners only). o Links to PSPS updates webpage with Community Resource Center information, and resources for customers with access and functional needs, including but not limited to information on the Medical Baseline program, Meals on Wheels, language support and the Portal Battery Program (for customers only). • Sent notifications to Medical Baseline program customers, including tenants of master metered accounts, and Self-Identified Vulnerable (SIV) customers every hour until the customer confirms receipt of the notification (up to 21:00 PDT or when PG&E halts notifications ). • Sent cancellation notifications to Public Safety Partners and customers removed from scope; this was to inform them that their power would not be shut off. Customer notifications were provided in English, with information on how to get event information in 15 non-English languages, referred to herein as “translated languages”. Customers with their language preference set received in-language (translated) notifications. Public Safety Partner notifications were provided in English.
WARNING NOTIFICATION: 1-4 hours in advance of de-energization, if possible | Public Safety Partners, All Customers (including Medical Baseline program customers and Self-Identified Vulnerable (SIV) customers) | When forecasted weather conditions showed that a safety shutoff was confirmed, and power would be de-energized soon, PG&E completed the following: • Submitted a PSPS State Notification Form to Cal OES and sent an email to the CPUC notifying them that PG&E has made the decision to de-energize. • Sent notifications to other Public Safety Partners and customers; these notifications include the same key event timing information and resource links as the “Watch Notification”. • Sent notifications to Medical Baseline program customers, including tenants of master metered accounts, and SIV customers every hour until the customer confirms receipt of the notification (up to 21:00 PDT or when PG&E halts notifications[3]). • Sent cancellation notifications to Public Safety Partners and customers removed from scope; this was to inform them that power would not be shut off. Customer notifications were provided in English, with information on how to get event information in translated languages[4]. Customers with their language preference set received in-language (translated) notifications. Public Safety Partner notifications were provided in English
POWER OFF NOTIFICATION: When de-energization is initiated | Public Safety Partners, All Customers (including Medical Baseline program customers and Self-Identified Vulnerable (SIV) customers), and Transmission-level customers | When shut off was initiated, PG&E completed the following: • Submitted a PSPS State Notification Form to Cal OES and sent an email to the CPUC to notify them that power is in the process of being shut off. • Agency Representatives conducted a live call and/or sent an email, as appropriate, to County OES that were within the potential PSPS scope area and select cities and tribes to inform them that customers within their jurisdiction were beginning to be de-energized. • PG&E Grid Control Center (GCC) conducted live agent calls to impacted transmission-level customers. • Sent notification to other Public Safety Partners and customers via phone, text, and email, that included: o Impacted addresses (for customers only). o De-energization time. o When weather is anticipated to pass. o Estimated time of restoration (ETOR). o Links to PSPS updates webpage with Community Resource Center information, and resources for customers with access and functional needs, including but not limited to information on the Medical Baseline program, Meals on Wheels, language support and the Portal Battery Program (for customers only). Customer notifications were provided in English, with information on how to get event information in translated languages. Customers with their language preference set received in-language (translated) notifications. Public Safety Partner notifications were provided in English
WEATHER “ALL-CLEAR”/ETOR UPDATE NOTIFICATION: Immediately before re-energization begins | Public Safety Partners, All Customers (including Medical Baseline program customers and Self-Identified Vulnerable (SIV) customers), and Transmission-level Customers | After the weather event had passed and the area is deemed safe to begin patrols and restoration, PG&E completed the following: • Submitted a PSPS State Notification Form to Cal OES and sent an email to the CPUC notifying them that PG&E is initiating re-energization patrols. • Sent notifications to other Public Safety Partners, transmission-level customers[5] ,and customers via phone, text, and email; these notifications included the ETOR. o Note: Customers can opt out of receiving event update notifications after de-energization has occurred. • Sent “event update” notifications to customers if their ETOR changed; two ways that an ETOR may change include: o New field or meteorology conditions. o Damage was found during patrols and repair is needed. Customer notifications were provided in English, with information on how to get event information in translated languages. Customers with their language preference set received in-language (translated) notifications. Public Safety Partner notifications were provided in English.
RESTORATION NOTIFICATION: When re-energization is complete | Public Safety Partners, All Customers (including Medical Baseline program customers and Self-Identified Vulnerable (SIV) customers), and Transmission-level Customers | PG&E Grid Control Center (GCC) conducted live agent calls to notify impacted transmission-level customers of restoration. Once customers, including Medical Baseline program customers and SIV customers, were restored, they received notifications via phone, text, and email. This was done using an automated process that issued customer notifications every 15 minutes upon restoration of service. Customer notifications were provided in English, with information on how to get event information in translated languages. Customers with their language preference set received in-language (translated) notifications. Once all customers were restored, PG&E submitted the final PSPS State Notification Form to Cal OES, sent an email to the CPUC, and sent a notification to Public Safety Partners via phone, text, and email. Public Safety Partner notifications were provided in English.
[1] Other Public Safety partners refers to first/emergency responders at the local, state and federal level, water, wastewater and communication service providers, affected community choice aggregators, publicly-owned utilities/electrical cooperatives, the CPUC, the California Governor’s Office of Emergency Services, and the California Department of Forestry and Fire Protection.
[2] In accordance with D.12-03-054, customers that are not enrolled or qualify for the Medical Baseline program can “certify that they have a serious illness or condition that could become life threatening if service is disconnected.” PG&E uses this designation to make an in-person visit prior to disconnection. This designation remains on their account temporarily for 90 days and can be extended to 12 months if the customers submit an application.
[3] For customers potentially impacted by PSPS late at night or overnight, PG&E, did not send automated notifications to customers between the hours of 2100 and 0800 in order to prevent waking up the customers in the middle of the night as a courtesy. PG&E will send notifications during the hours of 2100 and 0800 on a case-by-case basis (e.g., calls to Medical Baseline due to suddenly changing conditions).
[4] Translated languages refers to Spanish, Chinese (Mandarin and Cantonese), Vietnamese, Tagalog, Korean, Russian, Arabic, Punjabi, Farsi, Japanese, Khmer, Hmong, Thai, Hindi, and Portuguese. A language is prevalent if it is spoken by 1,000 or more persons in the utility’s territory or if it’s spoken by 5 percent or more of the population within a “public safety answering point” in the utility territory (D.20-03-004). Details on the community outreach efforts for PSPS and wildfire-related outreach including efforts to reach all languages prevalent in PG&E’s territory can be found in Section 8.4 of PG&E’s 2021 Wildfire Mitigation Plan Report.
[5] Transmission lines serving impacted Transmission-level Customers may cut across multiple Fire Index Areas (FIAs) and will only be notified when all those FIAs that the line cuts across have been given the all-clear.

## Table 4
Post-Event Report Data: PG&E August 17 - 19, 2021 De-energization Event
Table 4: Customer Notification Timeline Summary Prior to De-energization for August 17, 2021 PSPS Event
Event Order | Minimum Timeline[1] | Notification Sent to: | Approximate Time Sent | Message | Notes
Pre-De-energization (Prior) | 72-48 hours | Local/Tribal Governments and CCAs* | 8/15/2021 17:43 PDT | Advanced |  | #VALUE!
|  | Public Safety Partners** | 8/15/2021 17:53 PDT | Advanced |  | #VALUE!
| 48-24 hours | Local/Tribal Governments and CCAs* | 8/16/2021 19:08 PDT | Watch |  | #VALUE!
|  | Local/Tribal Governments and CCAs* | 8/17/2021 10:07 PDT | Watch |  | #VALUE!
|  | Local/Tribal Governments and CCAs* | 8/17/2021 10:50 PDT | Cancel | Only Local/Tribal Governments and CCAs removed from scope received the cancel notification. | #VALUE!
|  | Public Safety Partners** | 8/15/2021 21:07 PDT | Watch |  | #VALUE!
|  | Public Safety Partners** | 8/16/2021 19:29 PDT | Watch |  | #VALUE!
|  | Public Safety Partners** | 8/16/2021 20:55 PDT | Cancel | Only Public Safety Partners removed from scope received the cancel notification. | #VALUE!
|  | Public Safety Partners** | 8/17/2021 10:44 PDT | Watch |  | #VALUE!
|  | Public Safety Partners** | 8/17/2021 11:07 PDT | Cancel | Only Public Safety Partners removed from scope received the cancel notification. | #VALUE!
|  | All Customers*** | 8/15/2021 21:07 PDT | Watch |  | #VALUE!
|  | All Customers*** | 8/16/2021 19:29 PDT | Watch |  | #VALUE!
|  | All Customers*** | 8/16/2021 20:55 PDT | Cancel | Only Customers removed from scope received the cancel notification. | #VALUE!
|  | All Customers*** | 8/17/2021 10:44 PDT | Watch |  | #VALUE!
|  | All Customers*** | 8/17/2021 11:07 PDT | Cancel | Only Customers removed from scope received the cancel notification. | #VALUE!
|  | Transmission-level Customers | 8/17/2021 11:15 PDT | Watch |  | #VALUE!
| 4-1 hours | Local/Tribal Governments and CCAs* | 8/17/2021 15:17 PDT | Warning |  | #VALUE!
|  | Public Safety Partners** | 8/17/2021 15:46 PDT | Warning |  | #VALUE!
|  | Public Safety Partners** | 8/18/2021 10:50 PDT | Cancel | Only Public Safety Partners removed from scope received the cancel notification | #VALUE!
|  | All Customers*** | 8/17/2021 15:46 PDT | Warning |  | #VALUE!
|  | All Customers*** | 8/18/2021 10:50 PDT | Cancel | Only Customers removed from scope received the cancel notification | #VALUE!
Initiation (During) | When the de-energization was initiated | Public Safety Partners** | 8/17/2021 20:55 PDT | Power Off |  | #VALUE!
|  | All Customers*** | 8/17/2021 20:55 PDT | Power Off |  | #VALUE!
|  | Transmission-level Customers | 8/17/2021 15:56 PDT | Power Off |  | #VALUE!
| Immediately before re-energization | Local/Tribal Governments and CCAs* | 8/18/2021 13:36 PDT | Weather All-Clear |  | #VALUE!
|  | Local/Tribal Governments and CCAs* | 8/18/2021 17:04 PDT | Weather All-Clear |  | #VALUE!
|  | Local/Tribal Governments and CCAs* | 8/18/2021 16:48 PDT | Cancel | Only Local/Tribal Governments and CCAs removed from scope received the cancel notification | #VALUE!
|  | Public Safety Partners** | 8/18/2021 12:53 PDT | Weather All-Clear |  | #VALUE!
|  | Public Safety Partners** | 8/18/2021 12:59 PDT | ETOR Update |  | #VALUE!
|  | All Customers*** | 8/18/2021 12:53 PDT | Weather All-Clear |  | #VALUE!
|  | All Customers*** | 8/18/2021 12:59 PDT | ETOR Update |  | #VALUE!
|  | Transmission-level Customers | 8/18/2021 13:24 PDT | Weather All-Clear
Restoration (After) | After re-energization was completed | Local/Tribal Governments and CCAs* | 8/19/2021 18:57 PDT | Restore
|  | Public Safety Partners** | 8/18/2021 12:51 PDT | Restore
|  | All Customers*** | 8/18/2021 12:51 PDT | Restore
|  | Transmission-level Customers | 8/19/2021 13:10 PDT | Restore
*A subset of Public Safety Partners, including cities, counties, tribes, and community choice aggregators **A subset of Public Safety Partners, including water, wastewater, communication service providers and publicly owned utilities/electrical cooperatives ***All Customers, including Medical Baseline program customers and SIV customers
[1] Decision 19-05-042, Appendix A, Timing of Notification.

## Table 5
Post-Event Report Data: PG&E August 17 - 19, 2021 De-energization Event
Table 5: Notifications to customers where positive or affirmative notification was attempted
Category | Total Number of customers[1] | Notification Attempts Made[2] | Timing of Attempts[3] | Who made the Notification Attempt | Successful Positive Notification[4]
Medical Baseline[5] | 5220 | 13,886 Watch Notifications | 08/15/2021 21:07 PDT | PG&E | 4,789 Watch Notifications
|  | 4,810 Warning Notifications | 8/15/2021 21:11 PDT |  | 3,401 Warning Notifications
|  | 18,696 Overall Notifications | 08/15/2021 21:07 PDT |  | 8,190 Overall Notifications
MBL behind a master meter | 76 | 201 Watch Notifications | 08/15/2021 21:07 PDT | PG&E | 36 Watch Notifications
|  | 65 Warning Notifications | 8/15/2021 21:11 PDT |  | 27 Warning Notifications
|  | 266 Overall Notifications | 08/15/2021 21:07 PDT |  | 63 Overall Notifications
Access and Functional Needs (AFN)[6] | 10,101 | 16,496 Watch Notifications | 08/15/2021 21:07 PDT | PG&E | 4,357 Watch Notifications
|  | 9,436 Warning Notifications | 8/15/2021 21:11 PDT |  | 2,956 Warning Notifications
|  | 25,932 Overall Notifications | 08/15/2021 21:07 PDT |  | 7,313 Overall Notifications
[1] Total number of customers notified where notification was attempted.
[2] Count of Warning Notifications includes doorbell rings and Live Agent phone calls.
[3] Initial start time notification was sent.
[4] PG&E considers successful positive notifications as those in which the notification was successfully delivered to the customer (i.e., no bounce back) and the customer acknowledges receipt of the notification.
[5] Residential tenants of master-metered customers can also qualify for Medical Baseline Quantities. The Medical Baseline category for the purposes of Table 5. Notifications to customers where positive or affirmative notification was attempted does not include Medical Baseline program customers who are master meter tenants.
[6] Access and Functional Needs category includes customers enrolled in CARE or FERA; customers that self-identify to receive an in-person visit before disconnection for non-payment (e.g., vulnerable), customers that self-identify has having a person with a disability in the household (e.g., disabled); customers who self-select to receive utility communications in a non-standard format (e.g., in braille or large print); and customers who indicate a non-English language preference. Although Medical Baseline program customers are considered AFN, for the purposes of Table 5: Notifications to customers where positive or affirmative notification was attempted Medical Baseline program customers are reflected in separate categories.

## Section 6 ->
Post-Event Report Data: PG&E August 17 - 19, 2021 De-energization Event
Section 6 Tables
Table 6: PSPS Portal Time & Date for Map Sharing
Table 7: Customer Notifications Based on Language Preference
Table 8: Call Center Support Services[1]
Table 9: PG&E Website Traffic for 8-17-21 PSPS Event
Table 10: Unique Visitors to the Translated Versions of PG&E’s Website for the 8-17-21 PSPS Event
Table 11: Unique Visitors to the Translated Versions of PG&E’s Emergency Website for the 8-17-21 PSPS Event
Table 12: Generators available for critical facilities and infrastructure customers
Table 13: Critical Facility and Infrastructure Customers Energized with Backup Generation

## Table 6
Post-Event Report Data: PG&E August 17 - 19, 2021 De-energization Event
Table 6: PSPS Portal Time & Date for Map Sharing
Date | Time PDF Maps Shared | Time GIS Layers Shared
2021-08-15 | 13:26 PDT | 13:27 PDT
2021-08-15 | 16:50 PDT | 16:44 PDT
2021-08-16 | 17:49 PDT | 17:42 PDT
2021-08-17 | 08:24 PDT | 08:19 PDT
2021-08-17 | 14:38 PDT | 14:33 PDT
2021-08-18 | 06:40 PDT | 06:30 PDT

## Table 7
Post-Event Report Data: PG&E August 17 - 19, 2021 De-energization Event
Table 7: Customer Notifications Based on Language Preference
Language | Total Notifications[1] | Percent
English | 1110241 | 99.41%
Spanish | 5237 | 0.469%
Chinese (Mandarin) | 748 | 0.067%
Chinese (Cantonese) | 490 | 0.044%
Vietnamese | 62 | 0.006%
Hmong | 48 | 0.004%
Tagalog | 19 | 0.002%
Russian | 16 | 0.001%
Total | 1116861 | 100%
[1] Total notifications do not include door rings and Live Agent phone calls.

## Table 8
Post-Event Report Data: PG&E August 17 - 19, 2021 De-energization Event
Table 8: Call Center Support Services[1]
Total Calls Handled | PSPS Calls Handled | Average Response Time for PSPS-related Calls | Number of calls handled by Call Center Translation Services | Number of languages Supported by Call Center Translation Services
(seconds)
68996 | 2591 | 22 | 1161 | 32
[1] Metrics are provided from August 16, 2021 through August 19, 2021.

## Table 9
Post-Event Report Data: PG&E August 17 - 19, 2021 De-energization Event
Table 9: PG&E Website Traffic for 8-17-21 PSPS Event
Web Page | Unique Visitors | Visits | Total Page Views
PG&E’s Website (pge.com) | 1037462 | 1629247 | 4334099
PG&E’s Emergency Website (pgealerts.alerts.pge.com) [1], [2] | 370820 | 573031 | 1125014
[1] The PSPS Event Updates page is at the following link: pgealerts.alerts.pge.com/updates. PG&E also uses the following shortened URL for the same site: www.pge.com/pspsupdates.
[2] The emergency website metrics are a subset of the pge.com website traffic reported.

## Table 10
Post-Event Report Data: PG&E August 17 - 19, 2021 De-energization Event
Table 10: Unique Visitors to the Translated Versions of PG&E’s Website for the 8-17-21 PSPS Event
Language | Unique Visitors[1] | Percent
English | 1000406 | 96.43%
Spanish | 33129 | 3.19%
Chinese | 1907 | 0.18%
Russian | 596 | 0.06%
Korean | 483 | 0.05%
Vietnamese | 295 | 0.03%
Tagalog | 96 | 0.01%
Portuguese | 77 | 0.01%
Khmer | 70 | 0.01%
Farsi | 68 | 0.01%
Thai | 59 | 0.01%
Japanese | 57 | 0.01%
Arabic | 57 | 0.01%
Hindi | 55 | 0.01%
Punjabi | 54 | 0.01%
Hmong | 53 | 0.01%
Grand Total | 1037462 | 100%
[1] There is some overlap in unique visitors by language because some visitors viewed webpages in different languages.

## Table 11
Post-Event Report Data: PG&E August 17 - 19, 2021 De-energization Event
Table 11: Unique Visitors to the Translated Versions of PG&E’s Emergency Website for the 8-17-21 PSPS Event
Language | Unique Visitors[1] | Percent
English | 369262 | 99.5%
Spanish | 1256 | 0.34%
Chinese | 367 | 0.1%
Russian | 37 | 0.01%
Vietnamese | 33 | 0.01%
Tagalog | 29 | 0.01%
Arabic | 19 | 0.01%
Portuguese | 18 | 0%
Punjabi | 16 | 0%
Thai | 16 | 0%
Korean | 16 | 0%
Khmer | 15 | 0%
Hmong | 14 | 0%
Hindi | 12 | 0%
Farsi | 12 | 0%
Japanese | 10 | 0%
Grand Total | 371132 | 100%
[1] There is some overlap in unique visitors by language because some visitors viewed webpages in different languages.

## Table 12
Post-Event Report Data: PG&E August 17 - 19, 2021 De-energization Event
Table 12: Generators available for critical facilities and infrastructure customers
Generator Type | # of Units | Size (MW) | Run Time (Hrs.)[1] | Description
Diesel Generator | 5 | 0.125 | 36 | 5 units on reserve in Sacramento
Diesel Generator | 6 | 0.15 | 30 | 1 unit pre-staged at ICU Hospital, 5 units on reserve in Sacramento
Diesel Generator | 5 | 0.2 | 29 | 1 unit pre-staged at ICU Hospital, 4 units on reserve in Sacramento
Diesel Generator | 2 | 0.3 | 29 | 2 units staged at two ICU Hospitals
Diesel Generator | 4 | 0.35 | 25 | Reserve in Sacramento
Diesel Generator | 1 | 0.4 | 21 | 1 unit pre-staged at ICU Hospital
Diesel Generator | 13 | 0.5 | 23 | 6 units pre-staged at two ICU Hospitals, 7 units on reserve in Sacramento
Diesel Generator | 3 | 1 | 21 | 3 units pre-staged at ICU Hospitals
Diesel Generator | 9 | 1.25 | 20 | 1 unit pre-staged at ICU Hospital, 8 on reserve in Sacramento
Diesel Generator | 1 | 1.5 | 14 | 1 unit pre-staged at ICU Hospital
Diesel Generator | 7 | 2 | 11 | Reserve in Santa Rosa
[1] Estimated based on a 75% load, barring mechanical failure and refueling the temporary generators have the ability to operate continuously throughout a typical PSPS event.

## Table 13
Post-Event Report Data: PG&E August 17 - 19, 2021 De-energization Event
Table 13: Critical Facility and Infrastructure Customers Energized with Backup Generation
County | Site Type | Generation Deployed | Duration of Operation | Reason Deployed
Tehama | Water District | 0.2 MW | 56.25 hours | High risk to environment

## Section 7 ->
Post-Event Report Data: PG&E August 17 - 19, 2021 De-energization Event
Section 7 Tables
Table 14: Number and Nature of Complaints as a result of 8-17-21 PSPS Event
Table 15: Count and Type of Claims Received

## Table 14
Post-Event Report Data: PG&E August 17 - 19, 2021 De-energization Event
Table 14: Number and Nature of Complaints as a result of 8-17-21 PSPS Event
Nature of Complaints | Number of Complaints
Communications/Notifications: Including, but not limited to complaints regarding lack of notice, excessive notices, confusing notice, false alarm notice, problems with getting up-to-date information, inaccurate information provided, not being able to get information in the prevalent languages and/or information accessibility, complaints about website, Public Safety Partner Portal, Representational State Transfer (REST)/Digital Asset Manager (DAM) sites (as applicable). | 193
PSPS Frequency/Duration: Including, but not limited to complaints regarding the frequency and/or duration of PSPS events, including delays in restoring power, scope of PSPS and dynamic of weather conditions. | 89
Safety/Health Concern: Including, but not limited to complaints regarding difficulties experienced by AFN/MBL populations, traffic accidents due to non-operating traffic lights, inability to get medical help, well water or access to clean water, inability to keep property cool/warm during outage raising health concern. | 108
General PSPS Dissatisfaction/Other: Including, but not limited to complaints about being without power during PSPS event and related hardships such as food loss, income loss, inability to work/attend school, plus any PSPS-related complaints that do not fall into any other category. | 174
Outreach/Assistance: Including, but not limited to complaints regarding Community Resource Centers, community crew vehicles, backup power, hotel vouchers, other assistance provided by utility to mitigate impact of PSPS. | 9

## Table 15
Post-Event Report Data: PG&E August 17 - 19, 2021 De-energization Event
Table 15: Count and Type of Claims Received
Description of Claims | Number of Claims
Business Interruption / Economic Loss | 3
Food Loss Only | 11
Property Damage | 2

## Section 8 ->
Post-Event Report Data: PG&E August 17 - 19, 2021 De-energization Event
Section 8 Tables
Table 16: Weather All Clear Times
Table 17: Circuits PG&E was Unable to Restore within 24 Hours of the Weather All Clear

## Table 16
Post-Event Report Data: PG&E August 17 - 19, 2021 De-energization Event
Table 16: Weather All Clear Times
All-Clear Zones | Weather All-Clear Date and Time
154C, 154E, 180C, 180D, 180H, 180I, 249, 255, 280C, 285, 290 | 8/18/2021 07:58 PDT
170, 175A, 175B, 175C, 175D, 177D, 180J, 241B, 241C, 244B, 245C, 280B | 8/18/2021 09:29 PDT
117C, 241A | 8/18/2021 10:20 PDT
154D, 248B, 248C | 8/18/2021 11:38 PDT
175E, 175F | 8/18/2021 12:39 PDT
177B | 8/18/2021 14:45 PDT
177A, 244A, 245A, 246A, 246C, 247A | 8/18/2021 15:24 PDT
245B, 247B | 8/18/2021 16:41 PDT
246B, 246E, 246F, 246G | 8/18/2021 17:08 PDT
244C, 246D, 247C, 248A, 280G, 282A | 8/19/2021 05:17 PDT

## Table 17
Post-Event Report Data: PG&E August 17 - 19, 2021 De-energization Event
Table 17: Circuits PG&E was Unable to Restore within 24 Hours of the Weather All Clear
Circuit Name | Primary Reason the Utility was Unable to Restore the Circuit Within 24 Hours
REDBUD 1101 | Unable to gain access due to the Cache fire.
HIGHLANDS 1102 | Unable to gain access due to the Cache fire.
HIGHLANDS 1103 | Unable to gain access due to the Cache fire.
BUCKS CREEK 1103 | Unable to energize the non-PG&E owned portions of the line prior to customer providing positive confirmation that the lines were safe to restore, for customer-owner primary lines[1] One PG&E customer (powerhouse facility) also required a delayed re-energization, pending completion of inspections required in the facility.
MC ARTHUR 1101 | Unable to energize the non-PG&E owned portions of the line prior to customer providing positive confirmation that the lines were safe to restore, for customer-owner primary lines
STILLWATER 1102 | Unable to complete air patrol due to visibility resulting in switching to ground patrol
[1] For customer owner primary Facilities fed by PG&E assets, it is PG&E’s process to receive positive confirmation that the lines downstream of any PG&E asset are safe to re-energize prior to restoring power to the customer’s line.

## Section 10 ->
Post-Event Report Data: PG&E August 17 - 19, 2021 De-energization Event
Section 10 Tables
Table 18: Temporary Microgrids

## Table 18
Post-Event Report Data: PG&E August 17 - 19, 2021 De-energization Event
Table 18: Temporary Microgrids
Temporary Microgrid | Generation Deployed | Customers Energized
Shingletown (Shasta County) | 1.5 MW | 83
Magalia (Butte County) | 1.5 MW | 34
Calistoga (Napa County) | 5.13 MW | 1556
Angwin (Napa County) | 0.5 MW | 48

## Section 11 ->
Post-Event Report Data: PG&E August 17 - 19, 2021 De-energization Event
Section 11 Tables
Table 19: Lessons Learned from PSPS Event

## Table 19
Post-Event Report Data: PG&E August 17 - 19, 2021 De-energization Event
Table 19: Lessons Learned from PSPS Event
Lessons Learned from PSPS Event
Issue | Discussion | Resolution
There was confusion on the nomenclature used for All Clear Zones. | In 2021, PG&E adopted a method of calling Weather “All-Clears” based on reviewing and calling on clears from pre-defined Fire Index Areas. This is known as the All-Clear Zone methodology. Due to the large geographic span of some Fire Index Areas (FIA), PG&E further divided FIAs into pre-defined boundaries, or All Clear Zones, to allow for varying geographic weather conditions within a FIA. These All-Clear Zones align with known meteorological phenomena, such as mountain tops and wind gaps which may experience longer periods of extreme weather. This allows for further granularity in calling weather “all clears”, thereby helping areas less prone to wind gusts or adverse conditions to be cleared and then restored more quickly. While these process and changes were trained on earlier, there was still confusion on the nomenclature used for these All-Clear Zones and in some cases the field personnel misunderstood the suffixes to mean segments of the circuit, thereby causing some uncertainty in the restoration process. | PG&E recognized the need for additional training for field personnel on this process change for calling “All-Clears” to make them more familiar with the process. After the PSPS Event, PG&E practiced this process during the second full scale exercise of 2021 and going forward PG&E plans to undertake more training for field personnel in the short term.
PG&E faced issues when creating Restoration Playbooks after each All Clear Declaration meeting. | During the PSPS event, the technical teams faced issues transferring data from between systems to build out the restoration playbook. A temporary tech down procedure had to be followed to manually enter All Clear information into the Restoration Playbook. This resulted in delay in creating the Restoration Playbooks. | PG&E has recognized that contingency plans need to be implemented to build out a tech down solution for future PSPS events. PG&E plans to rectify the issues associated with the automation process in Foundry, reduce the cycle time for creating the Restoration Playbooks after each All Clear is declared, and further reduce the risk of errors and delays in cascading the Restoration Playbook to Field Operations teams. PG&E tested these processes during the second PSPS full scale exercise has updated the automated and tech down tools so that they can both be utilized during a PSPS event
PG&E faced issues producing the event scope and subsequent files in a timely manner | Due to further systems integration and the addition of new scoping requirements e.g. tags, PG&E faced issues building the PSPS event scope in a timely manner and noticed that processing and production time for relatively quick items had increased from 2020 to 2021. | PG&E has identified performance issues arising from leaving multiple datasets in our ‘live production environment’ and since removed non-critical datasets from the production environment so that all the computing power can be focused on the items that necessitate immediate processing needs. PG&E has tested these processes during the second full scale exercise of 2021 and performed an analysis on the processing time for each of the sub-process steps so that we can further identify areas for improvement.

## Section 12 ->
Post-Event Report Data: PG&E August 17 - 19, 2021 De-energization Event
Section 12 Tables
Table 20: Maximum Wind Gusts Recorded 08/17/2021 in Impacted Counties

## Table 20
Post-Event Report Data: PG&E August 17 - 19, 2021 De-energization Event
Table 20: Maximum Wind Gusts Recorded 08/17/2021 in Impacted Counties
County | Maximum Wind Gust (mph) | Station ID | Station Name
Butte | 56 | JBGC1 | JARBO GAP
Tehama | 55 | TCKC1 | THOMES CREEK
Sonoma | 54 | PG132 | MT ST HELENA WEST
Yolo | 53 | PG490 | BALD MOUNTAIN TOWER
Shasta | 48 | PG313 | WILSON HILL ROAD - SHASTA
Lake | 46 | WISC1 | COUNTY LINE
Mendocino | 44 | PG990 | CAHTO PEAK
Napa | 43 | PG358 | KNOXVILLE
Glenn | 42 | PG662 | CHROME
Solano | 39 | PG880 | BLUE RIDGE ROAD SOUTH
Colusa | 37 | PG557 | SILLS ROAD
Lassen | 35 | HDVC1 | HIDDEN VALLEY
Plumas | 34 | PIEC1 | PIERCE

## Appendix ->
Post-Event Report Data: PG&E August 17 - 19, 2021 De-energization Event
Appendix
Table A-1.1: Factors Considered in the Decision to Shut Off Power for Each Distribution Circuit De-energized During the August 17-21, 2021 PSPS Event
Table A-1.2: Description, Units, and Value provided for Factors Considered in the Decision to Shut Off Power for Each Distribution Circuit De-energized During the August 17-21, 2021 PSPS Event
Table A-2.1: Factors Considered in the Decision to Shut Off Power for Each Transmission Circuit De-energized During the August 17-21, 2021 PSPS Event
Table A-2.2: Description, Units, and Value provided for Factors Considered in the Decision to Shut Off Power for Each Transmission Circuit De-energized During the August 17-21, 2021 PSPS Event
Appendix B: Distribution Circuits De-Energized During the August 17 - 19 PSPS Event
Appendix C: DAMAGES & HAZARDS FOUND WITHIN THE DE-ENERGIZED AREAS
Appendix E: Local Community Representatives Contacted
Appendix G: Community Resource Centers Provided by PG&E

## Appendix A-1.1
Post-Event Report Data: PG&E August 17 - 19, 2021 De-energization Event
Table A-1.1: Factors Considered in the Decision to Shut Off Power for Each Distribution Circuit De-energized During the August 17-21, 2021 PSPS Event
* Please see Table A-1.2 for the description of each column header, as well as the unit and value provided.
** Note: PSPS decision making on Distribution does not occur at a per-circuit level, and instead occurs at the level of our 2 x 2 km weather and fuels model grid. These outputs are used in a GIS system to visualize the areas of concern by area, which meteorologists and Distribution Assets Health Specialists review to scope the event. The data provided here is representative of our high-resolution weather model data, which is driven by the Weather Research and Forecasting model. It is not inclusive of other model information reviewed by meteorologists that include external, public global and high-resolution weather models. This temporal and areal review of the risk, the operational time-line required to create the scope as well as any areas that were added based on subject matter expertise of meteorologists may lead to some circuits being de-energized that do not strictly exceed PSPS guidance.
Circuit Name | cfpd | flame_ | rate_of_ | area_ | ws_ | wg_ | ws_ | temp_ | rh_ | vpd2m_ | dfm_ | dfm_ | dfm_ | lfm_ | lfm_ | lfm_ | prob_ | prob_ | prob_ | sum_ | prob_ | RFW | GACC_ | open_ | transmission_
|  | length_ | spread_ | acres_ | mph | ec_ | mph_ | 2m_f | 2m | mb | 10hr | 100hr | 1000hr | herb | chamise_ | woody | large | cat | large_ | tree_ | ignition |  | HighRisk | psps_ | impacts_
|  | ft_2hr | chhr_2hr | 8hr |  | mph | 50m | [7 empty] | new |  |  |  | or_cat | ovr |  |  |  | tags | yes_no
ANDERSON 1101 | 20.72 | 6.92 | 43.3 | 3946.1 | 26.47 | 50.06 | 34.52 | 96.6 | 9.84 | 53.13 | 0.034 | 0.055 | 0.051 | 54.27 | 68.65 | 68.56 | 0.46 | 0.65 | 0.89 | 3074.9 | 0.00341 | YES | YES | YES | NO
ANDERSON 1103 | 14.76 | 7.97 | 59.9 | 5983.4 | 25.97 | 47.43 | 31.57 | 83.55 | 13.66 | 32.77 | 0.035 | 0.057 | 0.052 | 32.34 | 68.57 | 79.74 | 0.42 | 0.61 | 0.87 | 1094.9 | 0.00242 | YES | YES | YES | NO
ANTLER 1101 | 19.52 | 32.97 | 25.5 | 400.3 | 22.9 | 53.42 | 33.35 | 80.22 | 14.63 | 29.04 | 0.037 | 0.06 | 0.053 | 38.46 | 65.83 | 72.34 | 0.41 | 0.78 | 0.92 | 49813.6 | 0.00273 | YES | YES | YES | NO
ARBUCKLE 1101 | 13.96 | 8.7 | 54.93 | 5535.6 | 21.02 | 44.05 | 31.17 | 94.91 | 8.88 | 51.25 | 0.038 | 0.058 | 0.056 | 31.96 | 69.24 | 61.06 | 0.39 | 0.8 | 0.92 |  | 0.00191 | YES | YES | NO | NO
ARBUCKLE 1104 | 12.65 | 8.82 | 53.04 | 6252.1 | 21.2 | 44.21 | 30.96 | 94.76 | 9 | 50.94 | 0.039 | 0.057 | 0.053 | 30.99 | 68.83 | 60.48 | 0.38 | 0.87 | 0.97 | 477.9 | 0.00163 | YES | YES | YES | NO
BIG BEND 1101 | 37 | 20.62 | 68.65 | 3804.2 | 22.93 | 53.52 | 38.94 | 91.89 | 10.72 | 45.62 | 0.042 | 0.056 | 0.048 | 32.35 | 65.96 | 67 | 0.38 | 0.87 | 0.97 | 88659.2 | 0.00579 | YES | YES | YES | NO
BUCKS CREEK 1101 | 9.05 | 30.25 | 25.9 | 417.4 | 19.12 | 45.71 | 29.85 | 80.77 | 13.18 | 31.17 | 0.043 | 0.057 | 0.05 | 35.66 | 65.4 | 73.28 | 0.42 | 0.8 | 0.94 | 5025.3 | 0.00137 | YES | YES | YES | NO
BURNEY 1101 | 11.93 | 29.1 | 20.23 | 629.5 | 21.64 | 51.84 | 30.9 | 69.73 | 19.1 | 19.95 | 0.046 | 0.07 | 0.058 | 55.53 | 62.9 | 85.87 | 0.5 | 0.42 | 0.76 | 30933.3 | 0.0032 | YES | NO | YES | NO
BUTTE 1105 | 7.99 | 9.12 | 40.31 | 2057.2 | 18.22 | 42.3 | 29.16 | 91.19 | 9.14 | 45.59 | 0.04 | 0.056 | 0.05 | 31.7 | 69.42 | 73.59 | 0.36 | 0.82 | 0.96 | 22497.4 | 0.00111 | YES | YES | YES | NO
CALISTOGA 1101 | 31.94 | 70.99 | 64.92 | 3436.3 | 32.17 | 66.78 | 46.62 | 94.13 | 8.55 | 49.84 | 0.041 | 0.057 | 0.052 | 36.04 | 66.69 | 62.25 | 0.47 | 0.89 | 0.98 | 69278.3 | 0.00397 | YES | YES | YES | YES
CALISTOGA 1102 | 23.37 | 21.65 | 38.62 | 754.1 | 22.53 | 52.9 | 34.05 | 95.15 | 9.09 | 51.46 | 0.047 | 0.074 | 0.068 | 39.01 | 67.29 | 60.27 | 0.4 | 0.85 | 0.97 | 69278.3 | 0.00317 | YES | YES | YES | YES
CALPINE 1144 | 29.54 | 36.57 | 62.44 | 2638.4 | 23.9 | 52.4 | 36.21 | 90.59 | 7.43 | 45.49 | 0.037 | 0.053 | 0.049 | 35.96 | 66.74 | 62.09 | 0.38 | 0.88 | 0.98 | 3736.7 | 0.00393 | YES | YES | YES | NO
CALPINE 1146 | 7.52 | 13.74 | 38.87 | 1353.4 | 18.05 | 42.99 | 28.07 | 85.57 | 8.8 | 38.24 | 0.04 | 0.06 | 0.054 | 42.26 | 68.53 | 66.25 | 0.34 | 0.83 | 0.96 |  | 0.00103 | YES | YES | YES | NO
CEDAR CREEK 1101 | 30.54 | 75.56 | 53.98 | 1220.7 | 32.43 | 72.94 | 48.7 | 80.84 | 13.89 | 30.71 | 0.037 | 0.057 | 0.05 | 38.61 | 64.21 | 66.71 | 0.49 | 0.68 | 0.87 | 87136.2 | 0.00567 | YES | YES | YES | NO
CLARK ROAD 1102 | 31.56 | 15.08 | 50.75 | 6961.4 | 27.14 | 53.52 | 39.09 | 94.24 | 9.33 | 49.49 | 0.041 | 0.055 | 0.048 | 31.61 | 68.33 | 66.19 | 0.39 | 0.91 | 0.98 | 21285.1 | 0.00416 | YES | YES | YES | NO
CLOVERDALE 1102 | 14.59 | 14.13 | 66.51 | 1651.3 | 24.92 | 51.68 | 37.35 | 94.76 | 8.44 | 50.85 | 0.04 | 0.058 | 0.053 | 44.4 | 65.88 | 66.11 | 0.42 | 0.81 | 0.95 | 5638 | 0.00217 | YES | YES | YES | NO
CORNING 1101 | 20.76 | 8.74 | 102 | 15221.5 | 29.68 | 53.74 | 37.62 | 97.35 | 9.49 | 54.69 | 0.032 | 0.052 | 0.052 | 30.06 | 68.81 | 67.77 | 0.39 | 0.86 | 0.95 | 6259.9 | 0.0026 | YES | YES | YES | NO
CORNING 1102 | 19.4 | 59.77 | 110.75 | 19625.6 | 33.72 | 74.18 | 45.09 | 96.63 | 9.35 | 53.49 | 0.03 | 0.048 | 0.047 | 30 | 67.95 | 59.22 | 0.4 | 0.9 | 0.98 | 1979 | 0.00244 | YES | YES | YES | NO
CORTINA 1101 | 11.38 | 14.37 | 87.14 | 8907.5 | 23.15 | 48.87 | 34.2 | 91.12 | 8.88 | 45.55 | 0.038 | 0.054 | 0.049 | 30.37 | 70.15 | 61.21 | 0.29 | 0.9 | 0.98 | 18.4 | 0.00145 | YES | YES | NO | NO
COTTONWOOD 1101 | 16.45 | 11.37 | 80.73 | 9265 | 22.65 | 48.06 | 32.89 | 96.23 | 9.81 | 52.42 | 0.033 | 0.053 | 0.051 | 30.99 | 67.96 | 78.44 | 0.42 | 0.84 | 0.94 | 9930 | 0.00303 | YES | YES | YES | NO
COTTONWOOD 1102 | 23.69 | 8.8 | 48.81 | 4919.6 | 24.29 | 50.97 | 34.38 | 96.18 | 9.64 | 52.21 | 0.033 | 0.054 | 0.05 | 32.67 | 68.35 | 62.46 | 0.41 | 0.82 | 0.95 | 8310.6 | 0.00313 | YES | YES | YES | NO
COTTONWOOD 1103 | 18.64 | 9.69 | 65.02 | 5783.1 | 24.28 | 48.11 | 33.52 | 97.61 | 9.79 | 54.94 | 0.034 | 0.055 | 0.052 | 33.11 | 68.07 | 76.67 | 0.42 | 0.86 | 0.96 | 9930 | 0.00315 | YES | YES | YES | NO
CRESCENT MILLS 2101 | 2.49 | 6.14 | 20.08 | 950 | 12.92 | 31.91 | 17.96 | 75.05 | 15.11 | 25.25 | 0.044 | 0.064 | 0.055 | 46.35 | 65.9 | 75.4 | 0.5 | 0.54 | 0.81 | 38601 | 0.0005 | YES | YES | YES | NO
CRESTA 1101 | 10.81 | 6.08 | 21.79 | 535.3 | 20.16 | 47.97 | 29.95 | 83.9 | 12.85 | 34.77 | 0.042 | 0.056 | 0.049 | 47.9 | 70.91 | 73.92 | 0.34 | 0.78 | 0.94 | 3924.9 | 0.00154 | YES | YES | NO | NO
DESCHUTES 1101 | 27.83 | 11.31 | 66.76 | 9134.6 | 22.85 | 47.7 | 34.42 | 86.15 | 10.7 | 38.26 | 0.034 | 0.055 | 0.05 | 31.52 | 67.1 | 73.91 | 0.45 | 0.71 | 0.88 | 47373.6 | 0.00541 | YES | YES | YES | NO
DESCHUTES 1104 | 17.66 | 7.97 | 59.9 | 7116.7 | 25.97 | 44.99 | 31.57 | 86.87 | 10.6 | 39.38 | 0.033 | 0.056 | 0.051 | 32.34 | 68.36 | 78.21 | 0.42 | 0.65 | 0.89 | 7094.3 | 0.00284 | YES | YES | YES | NO
DUNBAR 1101 | 25.86 | 16.45 | 51.95 | 2351.6 | 24.16 | 50.3 | 35.53 | 90.7 | 11.5 | 42.47 | 0.047 | 0.069 | 0.061 | 41.43 | 66.83 | 59.76 | 0.42 | 0.86 | 0.97 | 23643.9 | 0.00349 | YES | YES | YES | NO
DUNBAR 1102 | 2.8 | 6.47 | 17.5 | 325.5 | 14.08 | 29.62 | 20.58 | 91.9 | 10.81 | 43.78 | 0.053 | 0.079 | 0.078 | 39.41 | 68.75 | 64.13 | 0.39 | 0.78 | 0.93 | 29286.9 | 0.00038 | YES | YES | YES | NO
DUNBAR 1103 | 16.91 | 26.04 | 55.53 | 2100 | 24.78 | 51.58 | 36.1 | 91.67 | 10.87 | 43.63 | 0.047 | 0.064 | 0.055 | 39.45 | 65.56 | 61.53 | 0.41 | 0.91 | 0.97 | 75579.7 | 0.00221 | YES | YES | YES | NO
ELK CREEK 1101 | 17.27 | 20.22 | 126.66 | 25697.6 | 31.37 | 59.51 | 38.67 | 96.05 | 7.76 | 53.23 | 0.03 | 0.048 | 0.048 | 30 | 68.32 | 56.14 | 0.4 | 0.92 | 0.98 | 13262.9 | 0.00211 | YES | YES | YES | NO
GEYSERVILLE 1101 | 2.04 | 7.28 | 20.68 | 384.6 | 18.64 | 37.35 | 24.81 | 91.53 | 10.74 | 45.14 | 0.05 | 0.074 | 0.067 | 56.91 | 65.71 | 62.9 | 0.43 | 0.69 | 0.91 | 20051.8 | 0.00039 | YES | YES | YES | NO
GEYSERVILLE 1102 | 27.86 | 12.11 | 61.04 | 1198 | 26.64 | 55.24 | 39.81 | 96.86 | 8.08 | 54.65 | 0.038 | 0.058 | 0.053 | 42.96 | 68.01 | 62.25 | 0.42 | 0.88 | 0.98 | 5234.6 | 0.00357 | YES | YES | YES | NO
GIRVAN 1101 | 30.21 | 16.26 | 47.72 | 5108.1 | 24.9 | 55.44 | 36.41 | 95.65 | 9.43 | 50.72 | 0.032 | 0.051 | 0.049 | 30.03 | 66.92 | 63.22 | 0.42 | 0.91 | 0.99 | 23867.7 | 0.00393 | YES | YES | YES | NO
GIRVAN 1102 | 18.43 | 10.8 | 55.87 | 5258.1 | 22.02 | 48.02 | 32.02 | 96.4 | 10.32 | 52.19 | 0.032 | 0.051 | 0.048 | 37.32 | 66.96 | 61.2 | 0.43 | 0.86 | 0.97 | 20596.5 | 0.0027 | YES | YES | YES | NO
GLENN 1101 | 12.79 | 7.84 | 75.56 | 12471.1 | 33 | 61.89 | 42.49 | 95.72 | 9.35 | 52.08 | 0.031 | 0.05 | 0.049 | 30.01 | 69.67 | 60.54 | 0.4 | 0.77 | 0.92 | 14.6 | 0.00177 | YES | YES | YES | NO
HIGHLANDS 1102 | 14.25 | 16.41 | 83.81 | 7979.3 | 24.08 | 56.76 | 40.14 | 91.37 | 7.47 | 46.61 | 0.037 | 0.057 | 0.052 | 30.51 | 68.55 | 57.86 | 0.34 | 0.91 | 0.98 | 927.8 | 0.00175 | YES | YES | YES | NO
HIGHLANDS 1103 | 24.24 | 13.23 | 64.82 | 5456.5 | 28.31 | 66.95 | 41.39 | 93.29 | 7.09 | 49.57 | 0.036 | 0.055 | 0.05 | 32.09 | 68.24 | 57.69 | 0.4 | 0.92 | 0.99 | 22328.7 | 0.00326 | YES | YES | YES | NO
JAMESON 1102 | 9.91 | 17.93 | 40.07 | 2200.6 | 24.76 | 49.98 | 36.34 | 90.84 | 11.1 | 42.8 | 0.051 | 0.078 | 0.067 | 38.03 | 60.73 | 61.5 | 0.38 | 0.9 | 0.98 | 5722.9 | 0.0013 | NO | YES | YES | NO
JAMESON 1105 | 11.42 | 7.03 | 40.26 | 2840.3 | 24.76 | 49.98 | 36.34 | 95.18 | 9.92 | 50.65 | 0.047 | 0.065 | 0.058 | 34.62 | 60.43 | 61.23 | 0.39 | 0.9 | 0.98 | 3018.1 | 0.00158 | YES | YES | YES | NO
JESSUP 1101 | 20.4 | 11.99 | 51.55 | 4203.4 | 22.7 | 48.26 | 33.35 | 96.25 | 10.61 | 52.14 | 0.033 | 0.054 | 0.05 | 31.58 | 68.16 | 70.66 | 0.44 | 0.91 | 0.98 | 16151 | 0.00331 | YES | YES | YES | NO
JESSUP 1102 | 25.97 | 11.59 | 51.55 | 4754.8 | 23.67 | 50.19 | 34.27 | 96.25 | 10.25 | 52.14 | 0.034 | 0.055 | 0.051 | 35.64 | 68.29 | 68.56 | 0.44 | 0.85 | 0.95 | 16151 | 0.00426 | YES | YES | YES | NO
JESSUP 1103 | 18.12 | 6.65 | 37.38 | 3109.9 | 20.76 | 44.35 | 29.22 | 95.77 | 10.61 | 51.19 | 0.034 | 0.056 | 0.052 | 51.92 | 68.93 | 82.79 | 0.39 | 0.64 | 0.88 | 2361.8 | 0.0029 | YES | YES | YES | NO
KESWICK 1101 | 21.9 | 13.85 | 68.85 | 5258.1 | 20.97 | 49.65 | 33.55 | 94.56 | 10.51 | 48.85 | 0.032 | 0.052 | 0.048 | 36.77 | 66.04 | 58.96 | 0.42 | 0.88 | 0.98 | 8683.8 | 0.00286 | YES | YES | YES | NO
KONOCTI 1108 | 3.67 | 12.39 | 45.09 | 2534 | 13.5 | 35.15 | 17.66 | 89.34 | 7.74 | 43.59 | 0.036 | 0.053 | 0.05 | 40.64 | 68.07 | 61.03 | 0.41 | 0.66 | 0.89 | 5193.5 | 0.00059 | YES | YES | YES | NO
LAKEVILLE 1102 | 6.28 | 5.76 | 43.25 | 2756.8 | 22.44 | 46.46 | 32.13 | 86.26 | 14.85 | 34.27 | 0.052 | 0.068 | 0.058 | 38.52 | 68.86 | 64.82 | 0.39 | 0.72 | 0.9 | 4259.6 | 0.00102 | YES | YES | YES | NO
LOGAN CREEK 2102 | 14.32 | 9.92 | 102.3 | 24409.9 | 24.85 | 49.75 | 33.66 | 97.17 | 8.3 | 55.16 | 0.031 | 0.052 | 0.052 | 30 | 69.03 | 60.49 | 0.36 | 0.79 | 0.91 | 547 | 0.00196 | YES | YES | YES | NO
MADISON 1105 | 16.64 | 6.08 | 51.95 | 6869.3 | 21.45 | 46.43 | 28.67 | 95.79 | 8.75 | 52.69 | 0.038 | 0.057 | 0.057 | 30.11 | 68.95 | 59.77 | 0.32 | 0.72 | 0.9 | 13.4 | 0.00236 | YES | YES | YES | NO
MADISON 2101 | 17.16 | 10.57 | 66.51 | 8024.6 | 26.86 | 51.61 | 38.92 | 95.58 | 8.47 | 52.21 | 0.036 | 0.051 | 0.047 | 30.05 | 69.52 | 57.99 | 0.41 | 0.89 | 0.98 | 639.3 | 0.00226 | YES | YES | YES | NO
MAXWELL 1105 | 14.03 | 8.68 | 92.06 | 17713.2 | 28.21 | 52.53 | 36.31 | 95.75 | 8.29 | 52.93 | 0.035 | 0.052 | 0.051 | 30 | 68.89 | 59.65 | 0.38 | 0.85 | 0.95 | 261 | 0.00176 | YES | YES | YES | NO
MC ARTHUR 1101 | 17.85 | 9.19 | 62.48 | 1979 | 29.34 | 53.94 | 38.8 | 71.4 | 19.5 | 20.96 | 0.046 | 0.07 | 0.06 | 40.04 | 63.51 | 68.49 | 0.47 | 0.55 | 0.82 | 20944 | 0.00329 | YES | YES | YES | NO
MIDDLETOWN 1101 | 27.6 | 75.34 | 55.28 | 2686.6 | 28.83 | 59.94 | 42.73 | 92.61 | 7.06 | 48.65 | 0.036 | 0.051 | 0.049 | 34.28 | 67.64 | 63.73 | 0.4 | 0.91 | 0.98 | 140703.8 | 0.00413 | YES | YES | YES | NO
MIDDLETOWN 1102 | 11.48 | 9.25 | 42.55 | 3373.2 | 21.87 | 45.65 | 33.79 | 93.34 | 6.87 | 49.87 | 0.036 | 0.056 | 0.054 | 32.27 | 69.39 | 60.29 | 0.38 | 0.8 | 0.93 | 4340.2 | 0.00168 | YES | YES | YES | NO
MONTICELLO 1101 | 25.33 | 17.05 | 75.54 | 9764.8 | 24.25 | 50.84 | 38.58 | 95.32 | 8.03 | 51.97 | 0.041 | 0.061 | 0.054 | 30.21 | 59.9 | 57.5 | 0.4 | 0.92 | 0.99 | 16907.7 | 0.00353 | YES | YES | YES | NO
NAPA 1112 | 10.19 | 14.46 | 77.8 | 2855.1 | 20.09 | 48.05 | 31.39 | 88.24 | 10.88 | 39.85 | 0.048 | 0.065 | 0.057 | 37.33 | 62.79 | 61.41 | 0.47 | 0.84 | 0.94 | 3811.4 | 0.00142 | YES | YES | YES | NO
OREGON TRAIL 1102 | 15.37 | 6.72 | 37.43 | 2180.2 | 20.87 | 44.52 | 29.75 | 82.97 | 12.29 | 34.33 | 0.034 | 0.056 | 0.052 | 40.82 | 70.26 | 73.68 | 0.39 | 0.58 | 0.84 | 9578.3 | 0.00279 | YES | YES | YES | NO
OREGON TRAIL 1103 | 18.95 | 12.75 | 60.65 | 6203.6 | 23.06 | 47.57 | 31.08 | 84.96 | 11.17 | 36.67 | 0.033 | 0.054 | 0.05 | 31.91 | 67.62 | 68.22 | 0.41 | 0.76 | 0.91 | 14535.1 | 0.00336 | YES | YES | YES | NO
OREGON TRAIL 1104 | 18.95 | 6.55 | 37.98 | 2370.3 | 20.73 | 44.3 | 29.41 | 84.03 | 11.58 | 35.87 | 0.034 | 0.056 | 0.052 | 37.42 | 69.41 | 76.78 | 0.38 | 0.61 | 0.87 | 16831.8 | 0.00336 | YES | YES | YES | NO
ORO FINO 1101 | 23.81 | 44.62 | 22.12 | 826.3 | 18.94 | 44.09 | 30.77 | 86.57 | 10.18 | 38.58 | 0.042 | 0.056 | 0.049 | 33.4 | 66.86 | 68.88 | 0.38 | 0.75 | 0.92 | 527261.7 | 0.00408 | YES | YES | YES | NO
ORO FINO 1102 | 43.17 | 72.69 | 37.88 | 1202 | 22.29 | 52.72 | 35.01 | 87.89 | 9.77 | 40.62 | 0.041 | 0.055 | 0.049 | 32.37 | 64.52 | 73.2 | 0.44 | 0.76 | 0.92 | 527261.7 | 0.00617 | YES | YES | YES | NO
PANORAMA 1101 | 15.43 | 7.5 | 65.02 | 5274.7 | 21.96 | 47.49 | 31.11 | 97.61 | 9.93 | 54.94 | 0.035 | 0.056 | 0.053 | 42.43 | 68.84 | 83.65 | 0.4 | 0.74 | 0.9 | 301.6 | 0.00223 | YES | YES | YES | NO
PANORAMA 1102 | 8.18 | 7.38 | 75.01 | 8693.4 | 23.72 | 43.32 | 30.08 | 83.94 | 11.65 | 34.43 | 0.036 | 0.056 | 0.051 | 30.18 | 68.66 | 80.81 | 0.42 | 0.67 | 0.87 | 1797.4 | 0.00201 | YES | YES | YES | NO
PARADISE 1104 | 30.27 | 7.47 | 37.38 | 3035.7 | 21.07 | 47.98 | 35.93 | 92.06 | 9.4 | 46.72 | 0.042 | 0.055 | 0.049 | 31.06 | 67.51 | 72.04 | 0.41 | 0.9 | 0.97 | 63796 | 0.00629 | YES | YES | YES | NO
PARADISE 1105 | 30.27 | 44.62 | 27.74 | 826.3 | 19.4 | 45.14 | 32.87 | 87.89 | 9.77 | 40.62 | 0.041 | 0.055 | 0.049 | 32.23 | 66.86 | 68.88 | 0.41 | 0.75 | 0.92 | 316958.4 | 0.00629 | YES | YES | YES | NO
PARADISE 1106 | 6.17 | 22.08 | 27.74 | 764.7 | 16.01 | 37.6 | 27.95 | 87.07 | 9.91 | 39.67 | 0.042 | 0.056 | 0.049 | 32.66 | 67.48 | 74.23 | 0.41 | 0.64 | 0.87 | 61401.6 | 0.00145 | YES | YES | YES | NO
PHILO 1101 | 2.47 | 36.68 | 31.42 | 1030.9 | 19.6 | 40.6 | 27.83 | 92.74 | 9.23 | 46.83 | 0.048 | 0.067 | 0.061 | 46.2 | 59.87 | 66.74 | 0.46 | 0.73 | 0.91 | 21323.6 | 0.00043 | NO | YES | YES | NO
PIT NO 7 1101 | 23.3 | 27.83 | 17.4 | 244.1 | 21.02 | 49.06 | 33.87 | 77.58 | 16.08 | 27.05 | 0.038 | 0.06 | 0.053 | 46.78 | 65.57 | 79.47 | 0.39 | 0.63 | 0.84 | 36647 | 0.00372 | YES | YES | YES | NO
PUEBLO 1104 | 19.77 | 15.21 | 71.78 | 3406.7 | 23.59 | 51.44 | 35.78 | 93.03 | 9.59 | 46.31 | 0.044 | 0.062 | 0.057 | 35.58 | 61.87 | 57.73 | 0.47 | 0.91 | 0.97 | 4277.3 | 0.00269 | YES | YES | YES | NO
PUEBLO 1105 | 23.33 | 10.61 | 56.45 | 2766.3 | 24.84 | 51.53 | 37.27 | 94.48 | 9.46 | 49 | 0.048 | 0.068 | 0.061 | 36.46 | 65.64 | 58.55 | 0.41 | 0.89 | 0.98 | 3127.2 | 0.00307 | YES | YES | YES | NO
PUEBLO 2102 | 5.67 | 26.04 | 89.08 | 1275.5 | 18.22 | 41.22 | 28.3 | 91.6 | 10.13 | 45.24 | 0.047 | 0.071 | 0.064 | 40.38 | 65.56 | 61.96 | 0.41 | 0.85 | 0.96 | 75579.7 | 0.00083 | YES | YES | YES | NO
PUEBLO 2103 | 17.08 | 32.94 | 42.05 | 1326.3 | 19.72 | 46.62 | 30.18 | 91.08 | 10.4 | 43.94 | 0.05 | 0.065 | 0.055 | 40.09 | 65.56 | 62.49 | 0.42 | 0.88 | 0.97 | 107640.9 | 0.00214 | YES | YES | YES | NO
PUTAH CREEK 1102 | 9.76 | 6.23 | 51.05 | 2973.9 | 22.28 | 46.14 | 35.31 | 96.65 | 8.58 | 54.2 | 0.038 | 0.054 | 0.049 | 30.37 | 64.98 | 58.76 | 0.39 | 0.89 | 0.98 | 4835.7 | 0.00176 | YES | YES | YES | NO
PUTAH CREEK 1103 | 11.08 | 5.82 | 44.19 | 6043.8 | 20.01 | 42.87 | 27.87 | 96.85 | 8.54 | 54.56 | 0.041 | 0.062 | 0.059 | 30.1 | 69.28 | 59.04 | 0.37 | 0.78 | 0.92 | 289.8 | 0.00176 | YES | YES | YES | NO
PUTAH CREEK 1105 | 5.15 | 6.49 | 67.41 | 6251.2 | 24.87 | 42.08 | 34.59 | 96.13 | 8.66 | 53.3 | 0.038 | 0.056 | 0.053 | 30.33 | 69.11 | 59.63 | 0.33 | 0.64 | 0.85 | 39.8 | 0.00092 | YES | YES | YES | NO
RED BLUFF 1101 | 16.89 | 7.97 | 81.42 | 12448.9 | 27.55 | 48.29 | 33.8 | 97.35 | 9.14 | 54.76 | 0.034 | 0.054 | 0.052 | 30.84 | 68.64 | 68.07 | 0.38 | 0.81 | 0.92 | 2955.8 | 0.00224 | YES | YES | YES | NO
RED BLUFF 1103 | 15.41 | 7.57 | 84.21 | 12528.2 | 27.55 | 51.54 | 33.68 | 97.2 | 9.14 | 54.49 | 0.034 | 0.054 | 0.052 | 31.51 | 69.12 | 81.1 | 0.41 | 0.69 | 0.9 | 2592.8 | 0.00265 | YES | YES | YES | NO
RED BLUFF 1104 | 19.23 | 8.36 | 79.83 | 8763.4 | 24.24 | 48.11 | 34.47 | 98.3 | 8.96 | 56.34 | 0.034 | 0.055 | 0.051 | 32.12 | 68.07 | 68.07 | 0.4 | 0.86 | 0.96 | 2575.6 | 0.00258 | YES | YES | YES | NO
RED BLUFF 1105 | 17.66 | 7.97 | 63.53 | 4255.8 | 23.11 | 47.29 | 33.57 | 97.97 | 8.05 | 55.78 | 0.033 | 0.052 | 0.05 | 32.34 | 68.29 | 80.47 | 0.43 | 0.82 | 0.92 | 1126.1 | 0.00316 | YES | YES | YES | NO
REDBUD 1101 | 17.71 | 15.81 | 72.63 | 7447.4 | 27.33 | 57.47 | 42.23 | 90.91 | 7.36 | 45.81 | 0.035 | 0.053 | 0.05 | 30.65 | 68.32 | 57.86 | 0.38 | 0.91 | 0.98 | 2121.2 | 0.00221 | YES | YES | YES | NO
REDBUD 1102 | 11.21 | 13.25 | 65.62 | 6418.5 | 21.88 | 45.31 | 36.74 | 89.78 | 7.64 | 44.27 | 0.038 | 0.061 | 0.055 | 34.06 | 66.79 | 61.5 | 0.36 | 0.9 | 0.98 | 2285.8 | 0.00149 | YES | YES | YES | NO
RINCON 1101 | 9.4 | 4.06 | 18.14 | 160.9 | 18.45 | 42.89 | 30.01 | 90.65 | 12.38 | 42.81 | 0.048 | 0.076 | 0.07 | 41.53 | 69.13 | 59.54 | 0.4 | 0.86 | 0.97 | 25519.6 | 0.0014 | YES | YES | YES | NO
RINCON 1103 | 9.4 | 7.27 | 25.7 | 711.5 | 19.94 | 42.89 | 31.45 | 89.62 | 11.1 | 42.03 | 0.046 | 0.07 | 0.064 | 42.68 | 68.06 | 58.9 | 0.41 | 0.85 | 0.95 | 99846.7 | 0.00142 | YES | YES | YES | NO
SILVERADO 2102 | 24.26 | 42.35 | 47.07 | 1557.4 | 25.02 | 53.82 | 36.39 | 94.81 | 7.99 | 51.58 | 0.045 | 0.073 | 0.071 | 33.03 | 62.79 | 57.59 | 0.42 | 0.92 | 0.98 | 6713.5 | 0.00318 | YES | YES | YES | NO
SILVERADO 2103 | 3.18 | 16.45 | 41.66 | 846.3 | 21.13 | 35.58 | 29.98 | 87.12 | 11.7 | 38.92 | 0.047 | 0.065 | 0.059 | 41.58 | 66.36 | 61.06 | 0.34 | 0.8 | 0.94 | 3255.9 | 0.00057 | YES | YES | YES | NO
SILVERADO 2104 | 34.97 | 76.43 | 65.91 | 2703.6 | 23.74 | 55.8 | 36.54 | 95.39 | 7.43 | 52.82 | 0.039 | 0.058 | 0.057 | 32.12 | 63 | 57.3 | 0.43 | 0.92 | 0.99 | 100456.3 | 0.00535 | YES | YES | YES | NO
SONOMA 1103 | 17.08 | 8.69 | 32.06 | 883.1 | 24.78 | 51.58 | 35.99 | 90.13 | 11.3 | 41.8 | 0.051 | 0.077 | 0.07 | 39.82 | 68.02 | 62.94 | 0.4 | 0.88 | 0.97 | 9832.1 | 0.00221 | YES | YES | YES | NO
SONOMA 1104 | 4.66 | 6.69 | 31.81 | 1828.6 | 20.01 | 41.35 | 29.58 | 91.74 | 10.81 | 43.43 | 0.049 | 0.062 | 0.054 | 39.37 | 66.63 | 64.15 | 0.41 | 0.78 | 0.93 | 10511.2 | 0.00097 | YES | YES | YES | NO
STILLWATER 1101 | 22.18 | 12.28 | 36.34 | 1744.1 | 21.52 | 50.18 | 31.79 | 82.56 | 12.57 | 33.66 | 0.034 | 0.056 | 0.051 | 37.87 | 66.26 | 72.16 | 0.39 | 0.74 | 0.91 | 36401.9 | 0.00323 | YES | YES | YES | NO
STILLWATER 1102 | 19.77 | 9.85 | 44.39 | 3239.1 | 21.02 | 44.89 | 29.88 | 84.66 | 11.66 | 36.18 | 0.033 | 0.054 | 0.05 | 36.16 | 67.61 | 66.01 | 0.39 | 0.78 | 0.92 | 26610.9 | 0.00317 | YES | YES | YES | NO
TYLER 1105 | 17.15 | 8.13 | 94.89 | 12744.5 | 27.71 | 52.2 | 34.39 | 96.96 | 9.61 | 54.03 | 0.033 | 0.052 | 0.051 | 30.13 | 68.71 | 68.31 | 0.44 | 0.8 | 0.91 | 2404.3 | 0.00265 | YES | YES | YES | NO
VACA DIXON 1105 | 11.79 | 6 | 43.55 | 4530.5 | 23.44 | 45.02 | 28.43 | 96.85 | 8.54 | 54.56 | 0.04 | 0.059 | 0.053 | 30.1 | 68.23 | 58.99 | 0.38 | 0.8 | 0.94 | 4563.2 | 0.00231 | YES | YES | YES | NO
VACAVILLE 1104 | 10.31 | 5.07 | 28.24 | 503.9 | 22.6 | 46.91 | 34.57 | 94.72 | 10.43 | 49.99 | 0.044 | 0.064 | 0.057 | 33.32 | 64.26 | 60.37 | 0.37 | 0.85 | 0.95 | 7433.8 | 0.0013 | YES | YES | YES | NO
VACAVILLE 1108 | 9.6 | 6 | 34.75 | 1566.8 | 23.51 | 48.71 | 36.48 | 96.33 | 8.26 | 53.64 | 0.039 | 0.056 | 0.05 | 31.13 | 65.41 | 58 | 0.4 | 0.87 | 0.96 | 7433.8 | 0.00137 | YES | YES | YES | NO
VOLTA 1101 | 26.35 | 57.54 | 50.06 | 5525.9 | 24.6 | 55.6 | 37.92 | 84.9 | 11.25 | 35.38 | 0.036 | 0.055 | 0.048 | 30.88 | 65.27 | 59.88 | 0.52 | 0.78 | 0.94 | 96081.9 | 0.00424 | YES | YES | YES | NO
VOLTA 1102 | 48.6 | 38.17 | 122.53 | 1923.7 | 23.65 | 55.54 | 39.12 | 80.88 | 12.47 | 31.57 | 0.038 | 0.057 | 0.049 | 35.13 | 64.71 | 65.59 | 0.46 | 0.74 | 0.9 | 156058.2 | 0.01268 | YES | YES | YES | NO
WHITMORE 1101 | 53.96 | 82.98 | 51.1 | 1896.2 | 26.47 | 61.73 | 43.26 | 79.98 | 13.32 | 30.12 | 0.036 | 0.056 | 0.049 | 43.98 | 66.9 | 82.33 | 0.46 | 0.63 | 0.86 | 125249.6 | 0.00912 | YES | YES | YES | NO
WILDWOOD 1101 | 2.54 | 9.9 | 35.49 | 2383.5 | 14.34 | 33.27 | 20.53 | 90.38 | 12.11 | 42.89 | 0.035 | 0.053 | 0.049 | 30.33 | 68.56 | 63.11 | 0.38 | 0.91 | 0.97 | 942.1 | 0.00028 | YES | YES | YES | NO

## Appendix A-1.2
Post-Event Report Data: PG&E August 17 - 19, 2021 De-energization Event
Table A-1.2: Description, Units, and Value provided for Factors Considered in the Decision to Shut Off Power for Each Distribution Circuit De-energized During the August 17-21, 2021 PSPS Event
Value | Unit | Value provided | Description
cfpd | Scaled Probability | max | The product of probability of catastrophic fire (Prob_Cat) and IPW - probability of ignition (prob_ignition).
This product is called the (CFPd) Catastrophic Fire Probability distribution model.
Scaled by 103 to covert to an integer value.
flame_length_ft_2hr | ft | max | Flame length in feet on fire front for first 2 hours of fire spread simulation from Technoslyva.
rate_of_spread_chhr_2hr | Ch/hr | max | Rate of fire spread in chains per hour for first 2 hours of fire spread simulation from Technoslyva.
area_acres_8hr | acres | max | Acres burned in the 8 hour fire spread simulation from Technoslyva.
ws_mph | mph | max | Sustained windspeed in miles per hour at 10 meters above ground level.
wg_ec_mph | mph | max | Wind gust in miles per hour at 10 meters above ground level.
ws_mph_50m | mph | max | Sustained windspeed in miles per hour at 50 meters above ground level.
temp_2m_f | F | max | Temperature in Fahrenheit at 2 meters above ground level.
rh_2m | % | min | Relative Humidity in percent at 2 meters above ground level.
vpd2m_mb | mb | max | Vapor pressure deficit at 2 meters above ground level in millibars.
dfm_10hr | fuel moisture fraction | min | Dead Fuel Moisture in 10-hour fuel moisture class.
Can be scaled to percentage by multiplying by 100.
dfm_100hr | fuel moisture fraction | min | Dead Fuel Moisture in 100-hour moisture class.
Can be scaled to percentage by multiplying by 100.
dfm_1000hr | fuel moisture fraction | min | Dead Fuel Moisture in 1000-hour moisture class.
Can be scaled to percentage by multiplying by 100.
lfm_herb | % | min | Live Fuel Moisture Percentage of herbaceous plant species. (% of species that is comprised of water)
lfm_chamise_new | % | min | Live Fuel Moisture Percentage of Chamise (shrub) plant species. (% of species that is comprised of water)
lfm_woody | % | min | Live Fuel Moisture Percentage of woody plant species. (% of species that is comprised of water)
prob_large | Probability | max | Fire Potential Index (FPI) Model Output - Probability of a large fire if an ignition were to occur.
prob_cat | Probability | max | Fire Potential Index (FPI) Model Output - Probability of a catastrophic fire if an ignition were to occur. FPI component of the CFPD model.
prob_large_or_cat | Probability | max | Fire Potential Index (FPI) Model Output - Probability of a large or catastrophic fire if an ignition were to occur. Utilized in the minimum fire potential conditions.
sum_tree_ovr | ft | max | Sum of tree overstrike in a 2 x 2 km grid cell area in ft.
prob_ignition | Probability | max | 2021 Ignition Probability Weather (IPW) Model Output - Probability of Ignition based on the probability of outages by cause. Ignition component of the CFPd model.
RFW | N/A | Yes/No during event | Red Flag Warning from the Federal National Weather Service.
GACC_HighRisk | N/A | Yes/No during event | High Risk issued by the Federal North or South Operations Predictive Services.
open_psps_tags | N/A | Yes/No During Event | PSPS-Qualified Tags include P1 (tree represents an immediate risk) and P2 (tree is damaged or diseased and could fall into nearby power lines) tree tags and Electric Corrective tags (Priority A - emergency, B - urgent, E - risk-based, and H - hardening projects)
transmission_impacts_yes_no | N/A | Yes/No During Event | Distribution lines that would have been de-energized due to de-energization of upstream transmission lines, regardless of whether those distribution lines would have also been de-energized due to direct distribution PSPS.

## Appendix A-2.1
Post-Event Report Data: PG&E August 17 - 19, 2021 De-energization Event
Table A-2.1: Factors Considered in the Decision to Shut Off Power for Each Transmission Circuit De-energized During the August 17-21, 2021 PSPS Event
* Please see Table A-2.1 for the description of each column header, as well as the unit and value provided.
** Note: PSPS decision making on Transmission does not occur at a per-circuit level, and instead occurs at the granularity of each transmission structure. These outputs are used in a GIS system and dashboard to visualize the areas of concern by area, which meteorologists and Transmission Asset Health Specialists review to scope the event. This includes a review of lines that have little to no impact to customers and electric grid reliability. The data provided here is representative of our high resolution weather model data, which is driven by the Weather Research and Forecasting model. It is not inclusive of other model information reviewed by meteorologists that include external, public global and high resolution weather models. This temporal and areal review of the risk, the operational time-line required to create the scope as well as any areas that were added based on subject matter expertise of meteorologists may lead to some circuits being de-energized that do not strictly exceed PSPS guidance.
Transmission Line Name | Segment | High Fire Risk Area (Y/N) | High Risk Vegetation Present on Circuit (Y/N) | Dead Fuel Moisture 1,000-hr. (%) | Dead Fuel Moisture 100-hr. (%) | Dead Fuel Moisture 10-hr. (%) | FPI | Prob. of Large Fire | Prob. Of Failure | Relative Humidity (%) | Wind Gust (mph)
LOWER LAKE-HOMESTAKE | N/A | YES | NO | 5.5 | 5.9 | 4.5 | 0.3684 | 0.005136 | 0.013958 | 18 | 50
ROCK CREEK-POE | N/A | YES | NO | 5.5 | 6.3 | 5.5 | 0.2941 | 7.5e-05 | 0.000258 | 26 | 35.3
FULTON-CALISTOGA | CALISTOGA JCT SW 17 --> MIDDLETOWN SW 49 | YES | YES | 6.4 | 6.6 | 5.2 | 0.3183 | 0.04759 | 0.1624 | 17 | 43.3
FULTON-CALISTOGA | CALISTOGA JCT SW 19 --> FULTON --> DUNBAR SW 69(NO) (via Lakeville #1) | YES | YES | 9.9 | 10.1 | 7.4 | 0.283 | 0.009508 | 0.035765 | 15 | 41.5

## Appendix A-2.2
Post-Event Report Data: PG&E August 17 - 19, 2021 De-energization Event
Table A-2.2: Description, Units, and Value provided for Factors Considered in the Decision to Shut Off Power for Each Transmission Circuit De-energized During the August 17-21, 2021 PSPS Event
Value | Unit | Value provided | Description
High Fire Risk Area (Y/N) | N/A | Yes/No During Event | Yes when Circuit goes through High Fire Risk Area.
High Risk Vegetation Present on Circuit (Y/N) | N/A | Yes/No During Event | High risk vegetation present on the circuit
Dead Fuel Moisture 1,000-hr. | % | Min | Dead Fuel Moisture in 1000-hour moisture class.
Dead Fuel Moisture 100-hr. | % | Min | Dead Fuel Moisture in 100-hour moisture class.
Dead Fuel Moisture 10-hr. | % | Min | Dead Fuel Moisture in 10-hour fuel moisture class.
FPI | Probability | Max | Fire Potential Index (FPI) Model Output - Probability of a catastrophic fire if an ignition were to occur. FPI component of the CFPD model.
Prob. of Large Fire | Probability | Max | Fire Potential Index (FPI) Model Output - Probability of a large fire if an ignition were to occur.
Prob. Of Failure | Probability | Max | The probability of failure of an individual asset at the forecasted windspeed based on the Operability Assessment fragility curve for that asset.
Relative Humidity | % | Min | Relative Humidity at 2 meters above ground level
Wind Gust (mph) | mph | Max | Wind gust in at 10 meters above ground level

## Appendix B
Post-Event Report Data: PG&E August 17 - 19, 2021 De-energization Event
Appendix B: Distribution Circuits De-Energized During the August 17 - 19 PSPS Event
Circuits labeled as “non-HFTD” are located outside of the CPUC High Fire-Threat District (HFTD). These circuits or portions of circuits are impacted for one of two reasons: (1) indirect impacts from transmission lines being de-energized or (2) the non-HFTD portion of the circuit are conductive to the HFTD at some point in the path to service. Circuits with an asterisk (*) were sectionalized during the event to further reduce customer impact. The de-energization date and time represents the time the first customer was de-energized on the circuit and the restoration time represents the date and time of the last customer restored on a circuit by circuit
Distribution / Transmission | Circuit Name | De-Energization Date and Time (PDT) | Restoration Date and Time (PDT) | Counties | HFTD Tier(s) | Total Customers | Residential Customers | Commercial / Industrial Customers | Medical Baseline Customers | Other Customers
DISTRIBUTION | ANDERSON 1101* | 2021-08-17 18:04 | 2021-08-18 20:11 | SHASTA | Partially Outside HFTD, Tier 2 | 460 | 361 | 96 | 33 | 3
DISTRIBUTION | ANDERSON 1103* | 2021-08-17 18:50 | 2021-08-18 20:40 | SHASTA | Partially Outside HFTD, Tier 2 | 68 | 63 | 2 | 7 | 3
DISTRIBUTION | ANTLER 1101* | 2021-08-17 18:21 | 2021-08-18 17:19 | SHASTA | Partially Outside HFTD, Tier 3, Tier 2 | 346 | 307 | 32 | 30 | 7
DISTRIBUTION | ARBUCKLE 1101* | 2021-08-17 18:34 | 2021-08-18 16:14 | COLUSA | Outside HFTD | 3 | 2 | 0 | 0 | 1
DISTRIBUTION | ARBUCKLE 1104* | 2021-08-17 18:33 | 2021-08-18 16:45 | YOLO, COLUSA | Partially Outside HFTD, Tier 2 | 12 | 8 | 3 | 0 | 1
DISTRIBUTION | BIG BEND 1101 | 2021-08-17 19:20 | 2021-08-19 10:54 | BUTTE | Tier 3, Tier 2 | 259 | 233 | 24 | 19 | 2
DISTRIBUTION | BUCKS CREEK 1103 | 2021-08-17 19:51 | 2021-08-20 10:30 | PLUMAS | Partially Outside HFTD, Tier 3, Tier 2 | 316 | 265 | 51 | 4 | 0
DISTRIBUTION | BURNEY 1101* | 2021-08-17 17:32 | 2021-08-18 11:40 | SHASTA | Partially Outside HFTD, Tier 3, Tier 2 | 131 | 100 | 25 | 16 | 6
DISTRIBUTION | BUTTE 1105* | 2021-08-17 19:00 | 2021-08-18 14:25 | BUTTE | Tier 3 | 53 | 51 | 2 | 3 | 0
DISTRIBUTION | CALISTOGA 1101* | 2021-08-17 18:40 | 2021-08-18 19:56 | NAPA, SONOMA | Partially Outside HFTD, Tier 3, Tier 2 | 1603 | 1256 | 240 | 64 | 107
DISTRIBUTION | CALISTOGA 1102 | 2021-08-17 19:15 | 2021-08-18 20:35 | NAPA | Partially Outside HFTD, Tier 3, Tier 2 | 2076 | 1592 | 422 | 63 | 62
DISTRIBUTION | CALPINE 1144 | 2021-08-17 20:00 | 2021-08-19 09:11 | SONOMA, LAKE | Partially Outside HFTD, Tier 3, Tier 2 | 15 | 2 | 13 | 0 | 0
DISTRIBUTION | CALPINE 1146 | 2021-08-17 20:00 | 2021-08-19 09:11 | SONOMA, LAKE | Outside HFTD | 0 | 0 | 0 | 0 | 0
DISTRIBUTION | CEDAR CREEK 1101 | 2021-08-17 17:34 | 2021-08-19 13:34 | SHASTA | Partially Outside HFTD, Tier 3, Tier 2 | 721 | 641 | 74 | 54 | 6
DISTRIBUTION | CLARK ROAD 1102* | 2021-08-17 19:06 | 2021-08-19 10:11 | BUTTE | Partially Outside HFTD, Tier 3, Tier 2 | 490 | 428 | 55 | 50 | 7
DISTRIBUTION | CLOVERDALE 1102* | 2021-08-17 19:23 | 2021-08-18 17:39 | SONOMA, MENDOCINO | Tier 3, Tier 2 | 70 | 46 | 9 | 7 | 15
DISTRIBUTION | CORNING 1101* | 2021-08-17 19:16 | 2021-08-19 11:46 | TEHAMA | Partially Outside HFTD, Tier 2 | 840 | 772 | 65 | 101 | 3
DISTRIBUTION | CORNING 1102* | 2021-08-17 19:08 | 2021-08-19 12:00 | TEHAMA | Partially Outside HFTD, Tier 2 | 286 | 228 | 48 | 13 | 10
DISTRIBUTION | CORTINA 1101* | 2021-08-17 18:42 | 2021-08-18 17:22 | COLUSA | Tier 2 | 8 | 4 | 4 | 1 | 0
DISTRIBUTION | COTTONWOOD 1101* | 2021-08-17 17:38 | 2021-08-19 13:19 | SHASTA, TEHAMA | Partially Outside HFTD, Tier 2 | 895 | 831 | 46 | 75 | 18
DISTRIBUTION | COTTONWOOD 1102* | 2021-08-17 17:28 | 2021-08-19 12:08 | SHASTA | Partially Outside HFTD, Tier 2 | 962 | 895 | 52 | 97 | 15
DISTRIBUTION | COTTONWOOD 1103* | 2021-08-17 17:29 | 2021-08-19 13:04 | SHASTA, TEHAMA | Partially Outside HFTD, Tier 2 | 2435 | 2284 | 117 | 230 | 34
DISTRIBUTION | CRESCENT MILLS 2101* | 2021-08-17 18:52 | 2021-08-18 11:26 | PLUMAS | Partially Outside HFTD, Tier 2 | 92 | 79 | 5 | 8 | 8
DISTRIBUTION | CRESTA 1101* | 2021-08-17 19:18 | 2021-08-19 12:34 | BUTTE | Tier 2 | 1 | 0 | 1 | 0 | 0
DISTRIBUTION | DESCHUTES 1101* | 2021-08-17 17:47 | 2021-08-18 19:56 | SHASTA | Partially Outside HFTD, Tier 3, Tier 2 | 253 | 227 | 21 | 18 | 5
DISTRIBUTION | DESCHUTES 1104* | 2021-08-17 18:39 | 2021-08-19 10:24 | SHASTA | Partially Outside HFTD, Tier 2 | 389 | 368 | 17 | 26 | 4
DISTRIBUTION | DUNBAR 1101* | 2021-08-17 18:41 | 2021-08-18 15:15 | SONOMA | Partially Outside HFTD, Tier 3, Tier 2 | 131 | 104 | 21 | 6 | 6
DISTRIBUTION | DUNBAR 1102* | 2021-08-17 18:51 | 2021-08-18 12:08 | SONOMA | Partially Outside HFTD, Tier 3, Tier 2 | 144 | 123 | 14 | 10 | 7
DISTRIBUTION | DUNBAR 1103* | 2021-08-17 18:53 | 2021-08-18 13:22 | SONOMA | Partially Outside HFTD, Tier 3, Tier 2 | 253 | 197 | 41 | 7 | 15
DISTRIBUTION | ELK CREEK 1101* | 2021-08-17 12:51 | 2021-08-19 12:22 | COLUSA, GLENN | Partially Outside HFTD, Tier 2 | 856 | 696 | 132 | 53 | 28
DISTRIBUTION | GEYSERVILLE 1101* | 2021-08-17 19:05 | 2021-08-18 18:57 | SONOMA | Partially Outside HFTD, Tier 2 | 26 | 17 | 6 | 1 | 3
DISTRIBUTION | GEYSERVILLE 1102* | 2021-08-17 18:45 | 2021-08-18 16:37 | SONOMA | Partially Outside HFTD, Tier 3, Tier 2 | 297 | 191 | 65 | 5 | 41
DISTRIBUTION | GIRVAN 1101 | 2021-08-17 17:24 | 2021-08-19 10:47 | SHASTA | Partially Outside HFTD, Tier 3, Tier 2 | 1207 | 1079 | 124 | 102 | 4
DISTRIBUTION | GIRVAN 1102* | 2021-08-17 17:35 | 2021-08-19 09:18 | SHASTA | Tier 3, Tier 2 | 581 | 560 | 20 | 46 | 1
DISTRIBUTION | GLENN 1101* | 2021-08-17 19:17 | 2021-08-18 19:39 | GLENN | Partially Outside HFTD, Tier 2 | 5 | 3 | 1 | 0 | 1
DISTRIBUTION | HIGHLANDS 1102* | 2021-08-17 19:18 | 2021-08-19 15:10 | LAKE | Tier 3, Tier 2 | 10 | 7 | 3 | 0 | 0
DISTRIBUTION | HIGHLANDS 1103* | 2021-08-17 19:13 | 2021-08-19 15:31 | LAKE | Partially Outside HFTD, Tier 2 | 1325 | 1204 | 91 | 110 | 30
DISTRIBUTION | JAMESON 1102* | 2021-08-17 19:36 | 2021-08-18 12:48 | SOLANO | Tier 2 | 217 | 200 | 17 | 14 | 0
DISTRIBUTION | JAMESON 1105* | 2021-08-17 20:00 | 2021-08-18 12:50 | SOLANO | Partially Outside HFTD, Tier 2 | 66 | 46 | 13 | 3 | 7
DISTRIBUTION | JESSUP 1101* | 2021-08-17 17:51 | 2021-08-19 13:31 | SHASTA | Partially Outside HFTD, Tier 3, Tier 2 | 1459 | 1408 | 49 | 147 | 2
DISTRIBUTION | JESSUP 1102* | 2021-08-17 17:35 | 2021-08-19 16:07 | SHASTA | Partially Outside HFTD, Tier 2 | 1504 | 1448 | 55 | 158 | 1
DISTRIBUTION | JESSUP 1103* | 2021-08-17 17:28 | 2021-08-18 20:56 | SHASTA | Partially Outside HFTD, Tier 2 | 113 | 108 | 5 | 4 | 0
DISTRIBUTION | KESWICK 1101 | 2021-08-17 18:42 | 2021-08-19 10:04 | SHASTA | Partially Outside HFTD, Tier 3, Tier 2 | 501 | 404 | 94 | 22 | 3
DISTRIBUTION | KONOCTI 1108* | 2021-08-17 19:02 | 2021-08-18 19:04 | LAKE | Partially Outside HFTD, Tier 2 | 707 | 671 | 34 | 57 | 2
DISTRIBUTION | LAKEVILLE 1102* | 2021-08-17 19:20 | 2021-08-18 12:57 | SONOMA | Tier 2 | 20 | 10 | 6 | 2 | 4
DISTRIBUTION | LOGAN CREEK 2102* | 2021-08-17 19:03 | 2021-08-18 18:05 | GLENN | Partially Outside HFTD, Tier 2 | 8 | 3 | 3 | 0 | 2
DISTRIBUTION | MADISON 1105* | 2021-08-17 19:06 | 2021-08-18 16:43 | YOLO | Partially Outside HFTD, Tier 2 | 31 | 20 | 7 | 1 | 4
DISTRIBUTION | MADISON 2101* | 2021-08-17 18:30 | 2021-08-18 19:34 | YOLO | Partially Outside HFTD, Tier 2 | 222 | 144 | 32 | 5 | 46
DISTRIBUTION | MAXWELL 1105* | 2021-08-17 18:37 | 2021-08-18 17:59 | COLUSA | Partially Outside HFTD, Tier 2 | 44 | 29 | 9 | 1 | 6
DISTRIBUTION | MC ARTHUR 1101* | 2021-08-17 17:46 | 2021-08-19 16:12 | LASSEN, SHASTA | Partially Outside HFTD, Tier 2 | 59 | 46 | 13 | 1 | 0
DISTRIBUTION | MIDDLETOWN 1101* | 2021-08-17 19:00 | 2021-08-19 12:13 | NAPA, SONOMA, LAKE | Partially Outside HFTD, Tier 3, Tier 2 | 1216 | 1086 | 120 | 62 | 10
DISTRIBUTION | MIDDLETOWN 1102* | 2021-08-17 18:45 | 2021-08-18 16:31 | LAKE | Partially Outside HFTD, Tier 2 | 691 | 674 | 15 | 67 | 2
DISTRIBUTION | MONTICELLO 1101* | 2021-08-17 18:32 | 2021-08-18 19:34 | NAPA, SOLANO | Partially Outside HFTD, Tier 3, Tier 2 | 932 | 718 | 165 | 54 | 49
DISTRIBUTION | NAPA 1112* | 2021-08-17 18:38 | 2021-08-18 13:47 | NAPA | Partially Outside HFTD, Tier 2 | 28 | 19 | 6 | 4 | 3
DISTRIBUTION | OREGON TRAIL 1102* | 2021-08-17 18:35 | 2021-08-18 20:01 | SHASTA | Tier 2 | 242 | 238 | 4 | 22 | 0
DISTRIBUTION | OREGON TRAIL 1103* | 2021-08-17 18:44 | 2021-08-19 15:16 | SHASTA | Partially Outside HFTD, Tier 2 | 1130 | 1051 | 71 | 87 | 8
DISTRIBUTION | OREGON TRAIL 1104* | 2021-08-17 18:37 | 2021-08-18 20:42 | SHASTA | Partially Outside HFTD, Tier 2 | 325 | 314 | 11 | 25 | 0
DISTRIBUTION | ORO FINO 1101* | 2021-08-17 18:28 | 2021-08-18 17:57 | BUTTE | Tier 3 | 2290 | 2215 | 70 | 288 | 5
DISTRIBUTION | ORO FINO 1102* | 2021-08-17 19:01 | 2021-08-18 18:17 | BUTTE | Partially Outside HFTD, Tier 3, Tier 2 | 1185 | 1134 | 49 | 118 | 2
DISTRIBUTION | PANORAMA 1101* | 2021-08-17 17:38 | 2021-08-18 19:39 | SHASTA, TEHAMA | Partially Outside HFTD, Tier 2 | 791 | 777 | 14 | 93 | 0
DISTRIBUTION | PANORAMA 1102* | 2021-08-17 19:45 | 2021-08-19 11:56 | SHASTA, TEHAMA | Tier 2 | 19 | 11 | 5 | 0 | 3
DISTRIBUTION | PARADISE 1104* | 2021-08-17 19:15 | 2021-08-18 16:23 | BUTTE | Partially Outside HFTD, Tier 3, Tier 2 | 1301 | 1210 | 91 | 130 | 0
DISTRIBUTION | PARADISE 1105* | 2021-08-17 18:28 | 2021-08-18 14:45 | BUTTE | Partially Outside HFTD, Tier 3 | 881 | 802 | 79 | 81 | 0
DISTRIBUTION | PARADISE 1106* | 2021-08-17 18:56 | 2021-08-18 13:28 | BUTTE | Tier 3 | 107 | 91 | 16 | 9 | 0
DISTRIBUTION | PHILO 1101* | 2021-08-17 19:28 | 2021-08-18 11:27 | MENDOCINO | Partially Outside HFTD, Tier 2 | 146 | 108 | 23 | 4 | 15
DISTRIBUTION | PIT NO 7 1101 | 2021-08-17 17:57 | 2021-08-18 21:44 | SHASTA | Tier 2 | 2 | 1 | 1 | 0 | 0
DISTRIBUTION | PUEBLO 1104* | 2021-08-17 18:30 | 2021-08-18 13:58 | NAPA | Partially Outside HFTD, Tier 2 | 257 | 189 | 49 | 16 | 19
DISTRIBUTION | PUEBLO 1105* | 2021-08-17 18:31 | 2021-08-18 15:01 | NAPA | Partially Outside HFTD, Tier 2 | 117 | 71 | 27 | 5 | 19
DISTRIBUTION | PUEBLO 2102* | 2021-08-17 18:21 | 2021-08-18 18:28 | NAPA | Partially Outside HFTD, Tier 3 | 66 | 51 | 14 | 1 | 1
DISTRIBUTION | PUEBLO 2103* | 2021-08-17 18:46 | 2021-08-18 19:25 | NAPA | Tier 3, Tier 2 | 216 | 145 | 38 | 4 | 33
DISTRIBUTION | PUTAH CREEK 1102* | 2021-08-17 20:51 | 2021-08-18 17:29 | YOLO, SOLANO | Partially Outside HFTD, Tier 2 | 159 | 114 | 35 | 7 | 10
DISTRIBUTION | PUTAH CREEK 1103* | 2021-08-17 18:29 | 2021-08-18 15:25 | YOLO, SOLANO | Partially Outside HFTD, Tier 2 | 41 | 35 | 2 | 1 | 4
DISTRIBUTION | PUTAH CREEK 1105* | 2021-08-17 18:32 | 2021-08-18 16:42 | YOLO | Partially Outside HFTD, Tier 2 | 9 | 3 | 5 | 0 | 1
DISTRIBUTION | RED BLUFF 1101* | 2021-08-17 17:55 | 2021-08-19 13:05 | TEHAMA | Partially Outside HFTD, Tier 2 | 685 | 648 | 27 | 73 | 10
DISTRIBUTION | RED BLUFF 1103* | 2021-08-17 17:40 | 2021-08-19 16:55 | TEHAMA | Partially Outside HFTD, Tier 2 | 214 | 199 | 14 | 23 | 1
DISTRIBUTION | RED BLUFF 1104* | 2021-08-17 17:43 | 2021-08-19 13:00 | YOLO, TEHAMA | Partially Outside HFTD, Tier 2 | 865 | 753 | 85 | 76 | 27
DISTRIBUTION | RED BLUFF 1105* | 2021-08-17 17:29 | 2021-08-19 11:50 | TEHAMA | Partially Outside HFTD, Tier 2 | 981 | 918 | 49 | 119 | 14
DISTRIBUTION | REDBUD 1101* | 2021-08-17 18:52 | 2021-08-19 15:10 | LAKE | Partially Outside HFTD, Tier 3, Tier 2 | 560 | 513 | 32 | 54 | 15
DISTRIBUTION | REDBUD 1102* | 2021-08-17 18:45 | 2021-08-18 16:44 | LAKE | Partially Outside HFTD, Tier 2 | 59 | 41 | 13 | 4 | 5
DISTRIBUTION | RINCON 1101* | 2021-08-17 19:21 | 2021-08-18 16:01 | SONOMA | Tier 3 | 21 | 14 | 7 | 2 | 0
DISTRIBUTION | RINCON 1103* | 2021-08-17 18:55 | 2021-08-19 02:31 | SONOMA | Tier 3 | 281 | 234 | 40 | 12 | 7
DISTRIBUTION | SILVERADO 2102* | 2021-08-17 18:38 | 2021-08-18 14:49 | NAPA | Partially Outside HFTD, Tier 3, Tier 2 | 182 | 112 | 38 | 2 | 32
DISTRIBUTION | SILVERADO 2103* | 2021-08-17 19:41 | 2021-08-18 16:33 | SONOMA | Tier 3 | 3 | 0 | 3 | 0 | 0
DISTRIBUTION | SILVERADO 2104* | 2021-08-17 18:22 | 2021-08-18 23:55 | NAPA | Partially Outside HFTD, Tier 3, Tier 2 | 1815 | 1516 | 174 | 93 | 125
DISTRIBUTION | SONOMA 1103* | 2021-08-17 19:19 | 2021-08-18 12:43 | SONOMA | Tier 3 | 37 | 30 | 3 | 3 | 4
DISTRIBUTION | SONOMA 1104* | 2021-08-17 19:27 | 2021-08-18 13:23 | SONOMA | Partially Outside HFTD, Tier 2 | 184 | 162 | 20 | 6 | 2
DISTRIBUTION | STILLWATER 1101* | 2021-08-17 18:56 | 2021-08-19 11:59 | SHASTA | Partially Outside HFTD, Tier 2 | 706 | 601 | 99 | 57 | 6
DISTRIBUTION | STILLWATER 1102 | 2021-08-17 18:27 | 2021-08-19 17:13 | SHASTA | Partially Outside HFTD, Tier 2 | 1384 | 1338 | 46 | 117 | 0
DISTRIBUTION | TYLER 1105* | 2021-08-17 18:22 | 2021-08-19 08:05 | TEHAMA | Partially Outside HFTD, Tier 2 | 765 | 653 | 70 | 73 | 42
DISTRIBUTION | VACA DIXON 1105* | 2021-08-17 18:26 | 2021-08-18 16:36 | SOLANO | Partially Outside HFTD, Tier 2 | 384 | 336 | 41 | 40 | 7
DISTRIBUTION | VACAVILLE 1104* | 2021-08-17 20:36 | 2021-08-18 14:45 | SOLANO | Tier 2 | 25 | 24 | 1 | 2 | 0
DISTRIBUTION | VACAVILLE 1108* | 2021-08-17 18:28 | 2021-08-19 09:36 | SOLANO | Partially Outside HFTD, Tier 2 | 295 | 212 | 63 | 18 | 20
DISTRIBUTION | VOLTA 1101 | 2021-08-17 18:20 | 2021-08-19 16:28 | SHASTA, TEHAMA | Partially Outside HFTD, Tier 3, Tier 2 | 1126 | 927 | 165 | 69 | 34
DISTRIBUTION | VOLTA 1102 | 2021-08-17 18:23 | 2021-08-19 18:27 | SHASTA | Partially Outside HFTD, Tier 3, Tier 2 | 2584 | 2393 | 180 | 242 | 11
DISTRIBUTION | WHITMORE 1101* | 2021-08-17 18:43 | 2021-08-18 19:00 | SHASTA | Tier 3, Tier 2 | 271 | 241 | 25 | 19 | 5
DISTRIBUTION | WILDWOOD 1101* | 2021-08-17 17:44 | 2021-08-18 21:45 | SHASTA, TEHAMA | Tier 2 | 6 | 3 | 3 | 0 | 0
TRANSMISSION | FULTON-CALISTOGA | 2021-08-17 18:31 | Line Remained De-energized for Planned Project Work | Transmission Line | Tier 2, Tier 3 | 0 | 0 | 0 | 0 | 0
TRANSMISSION | LOWER LAKE-HOMESTAKE | 2021-08-17 18:32 | 2021-08-19 13:31 | Transmission Line | Tier 2 | 1[1] | 0 | 1 | 0 | 0
TRANSMISSION | ROCK CREEK-POE | 2021-08-17 18:38 | 2021-08-19 12:48 | Transmission Line | Tier 2, Tier 3 | 0 | 0 | 0 | 0 | 0
Total | [5 empty] | 48155 | 42686 | 4388 | 3856 | 1081
[1] PG&E defines Transmission level customers as customers being served by 60 kV assets or higher. The customer impacted in this event was not under CAISO Control, thus would not meet the definition of a Transmission Customer per D. 21.06.034.

## Appendix C
Post-Event Report Data: PG&E August 17 - 19, 2021 De-energization Event
Appendix C: DAMAGES & HAZARDS FOUND WITHIN THE DE-ENERGIZED AREAS
Circuit Name | County | Structure Identifier | Tier 2/3 or Non-HFTD | Damage / Hazard | Type of Damage / Hazard | Description of Damage
PUEBLO 2103 | Napa | 103781539 | Tier 3 | Hazard | Vegetation | Tree on primary line removed.
PUEBLO 2103 | Napa | 102270992 | Tier 3 | Hazard | Wind Related | Conductor on crossarm.
MIDDLETOWN 1101 | Lake | 102166579 | Tier 3 | Hazard | Vegetation | Dead Tree Leaning toward line in between 2 poles. The line is not damaged but this is a hazard.
KESWICK 1101 | Shasta | 103923363 | Tier 3 | Damage | Wind Related | Broken tree wire has snapped and uncurled.
KESWICK 1101 | Shasta | 103920243 | Tier 3 | Damage | Wind Related | Wind caused tree wire to break.
PUEBLO 2103 | Napa | 102269654 | Tier 3 | Damage | Wind Related | The ground was loose and came off pole.
PUEBLO 2103 | Napa | 102269729 | Tier 3 | Hazard | Vegetation | Limb fell on line. The line does not appear to be damaged.
ANDERSON 1101 | Shasta | 101493379 | Tier 2 | Damage | Vegetation | Service wire broke off service meter, tree branches contacting service.
STILLWATER 1102 | Shasta | 101474634 | Tier 2 | Damage | Vegetation | Tree limb on service removed broke neutral. Neutral was repaired.
CEDAR CREEK 1101 | Shasta | 101474218 | Tier 2 | Damage | Wind Related | Conductor wire separated from the conductor. Could arc with high winds, possible separated because of the winds. There was no vegetation on or near the pole.

## Appendix E
Post-Event Report Data: PG&E August 17 - 19, 2021 De-energization Event
Appendix E: Local Community Representatives Contacted
Organization/Jurisdiction | Title | HFTD TIER | DATE/TIME CONTACTED
Alameda County | County Administrator | Tier 2, Tier 3, Zone 1 | 8/17/2021 10:07 PDT
Alameda County | Customer Care Manager | Tier 2, Tier 3, Zone 1 | 8/17/2021 10:07 PDT
Alameda County | Dublin Police - Technician | Tier 2, Tier 3, Zone 1 | 8/17/2021 10:07 PDT
Alameda County | Emergency Preparedness Manager | Tier 2, Tier 3, Zone 1 | 8/17/2021 10:07 PDT
Alameda County | Emergency Preparedness Manager | Tier 2, Tier 3, Zone 1 | 8/17/2021 10:07 PDT
Alameda County | EMS Disaster and WMD Coordinator | Tier 2, Tier 3, Zone 1 | 8/17/2021 10:07 PDT
Alameda County | Fire Division Chief | Tier 2, Tier 3, Zone 1 | 8/17/2021 10:07 PDT
Alameda County | General | Tier 2, Tier 3, Zone 1 | 8/17/2021 10:07 PDT
Alameda County | General | Tier 2, Tier 3, Zone 1 | 8/17/2021 10:07 PDT
Alameda County | Local Cal Fire | Tier 2, Tier 3, Zone 1 | 8/17/2021 10:07 PDT
Alameda County | OES Coordinator | Tier 2, Tier 3, Zone 1 | 8/17/2021 10:07 PDT
Alameda County | OES EOC Lead | Tier 2, Tier 3, Zone 1 | 8/17/2021 10:07 PDT
Alameda County | President of the Board | Tier 2, Tier 3, Zone 1 | 8/17/2021 10:07 PDT
Alameda County | Sheriff | Tier 2, Tier 3, Zone 1 | 8/17/2021 10:07 PDT
Alameda County | Superintendent of Water Distribution | Tier 2, Tier 3, Zone 1 | 8/17/2021 10:07 PDT
Alameda County | Watch Commander | Tier 2, Tier 3, Zone 1 | 8/17/2021 10:07 PDT
Berry Creek Rancheria | Chairman | Tier 2, Tier 3, Zone 1 | 8/15/2021 14:45 PDT
Butte County | Assistant Director | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Butte County | CAO | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Butte County | Director | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Butte County | General | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Butte County | General | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Butte County | General | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Butte County | General | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Butte County | General | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Butte County | General | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Butte County | General | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Butte County | General | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Butte County | General | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Butte County | General | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Butte County | General | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Butte County | General | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Butte County | General | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Butte County | General CAL FIRE | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Butte County | General Services Director | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Butte County | OES Director | Tier 2, Tier 3, Zone 1 | 8/15/2021 15:45 PDT
Butte County | Probation Officer | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Butte County | Public Health Director | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Butte County | Public Safety Answering Point | Tier 2, Tier 3, Zone 1 | 8/15/2021 18:25 PDT
Butte County | Public Safety Answering Point | Tier 2, Tier 3, Zone 1 | 8/15/2021 18:27 PDT
Butte County | Public Safety Answering Point | Tier 2, Tier 3, Zone 1 | 8/15/2021 18:29 PDT
Butte County | Public Safety Answering Point | Tier 2, Tier 3, Zone 1 | 8/15/2021 18:31 PDT
Butte County | Public Safety Answering Point | Tier 2, Tier 3, Zone 1 | 8/15/2021 18:33 PDT
Butte County | Public Safety Answering Point | Tier 2, Tier 3, Zone 1 | 8/15/2021 18:35 PDT
Butte County | Public Safety Answering Point | Tier 2, Tier 3, Zone 1 | 8/15/2021 18:23 PDT
Butte County | Sheriff | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Butte Tribal Council | Chairman | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Colusa County | Deputy Chief | Tier 2 | 8/16/2021 19:08 PDT
Colusa County | Director | Tier 2 | 8/16/2021 19:08 PDT
Colusa County | Division Chief | Tier 2 | 8/16/2021 19:08 PDT
Colusa County | General | Tier 2 | 8/16/2021 9:00 PDT
Colusa County | MHOAC | Tier 2 | 8/16/2021 19:08 PDT
Colusa County | OES Lieutenant | Tier 2 | 8/16/2021 9:00 PDT
Colusa Rancheria | Chairman | Tier 2 | 8/16/2021 08:38 PDT
Contra Costa County | Battalion Chief | Tier 2, Tier 3 | 8/17/2021 10:07 PDT
Contra Costa County | CEO | Tier 2, Tier 3 | 8/17/2021 10:07 PDT
Contra Costa County | Chair of the Board | Tier 2, Tier 3 | 8/17/2021 10:07 PDT
Contra Costa County | County Administrator | Tier 2, Tier 3 | 8/17/2021 10:07 PDT
Contra Costa County | Duty Officer | Tier 2, Tier 3 | 8/17/2021 10:07 PDT
Contra Costa County | Emergency Planning Coordinator | Tier 2, Tier 3 | 8/17/2021 10:07 PDT
Contra Costa County | Fire Chief | Tier 2, Tier 3 | 8/17/2021 10:07 PDT
Contra Costa County | OES Director | Tier 2, Tier 3 | 8/15/2021 16:30 PDT
Cortina Rancheria | Chairperson | Tier 2 | 8/16/2021 19:08 PDT
Glenn County | County Administrative Officer | Tier 2 | 8/15/2021 17:43 PDT
Glenn County | Deputy Director OES | Tier 2 | 8/15/2021 18:30 PDT
Glenn County | Fire Chief | Tier 2 | 8/15/2021 17:43 PDT
Glenn County | General | Tier 2 | 8/15/2021 17:43 PDT
Glenn County | Public Safety Answering Point | Tier 2 | 8/15/2021 16:54 PDT
Glenn County | Public Safety Answering Point | Tier 2 | 8/15/2021 18:36 PDT
Glenn County | Sheriff | Tier 2 | 8/15/2021 17:43 PDT
Glenn County | Unit Chief Tehama-Glenn | Tier 2 | 8/15/2021 17:43 PDT
Grindstone Rancheria | Chairman | Tier 2 | 8/16/2021 08:38 PDT
Grindstone Rancheria | Tribal Secretary | Tier 2 | 8/16/2021 19:08 PDT
Humboldt County | Account Services Manager | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Humboldt County | Corrections Lieutenant | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Humboldt County | County Administrative Officer | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Humboldt County | Director of Power Resources | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Humboldt County | Fire Chief | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Humboldt County | Fire Safe Council | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Humboldt County | General | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Humboldt County | Local Cal Fire | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Humboldt County | MHOAC | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Humboldt County | OES Manager | Tier 2, Tier 3, Zone 1 | 8/15/2021 15:30 PDT
Humboldt County | Public Safety Answering Point | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:05 PDT
Humboldt County | Public Safety Answering Point | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:11 PDT
Humboldt County | Public Safety Answering Point | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:11 PDT
Humboldt County | Public Safety Answering Point | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:20 PDT
Humboldt County | Public Safety Answering Point | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:21 PDT
Humboldt County | Public Safety Answering Point | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:22 PDT
Humboldt County | Public Safety Answering Point | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:22 PDT
Humboldt County | Public Safety Answering Point | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:22 PDT
Humboldt County | Public Safety Answering Point | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:33 PDT
Humboldt County | State Assembly member | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Humboldt County | State Senator | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Lake County | Battalion Chief | Tier 2, Tier 3 | 8/15/2021 17:43 PDT
Lake County | Chair of the Board | Tier 2, Tier 3 | 8/15/2021 17:43 PDT
Lake County | County Administrative Officer | Tier 2, Tier 3 | 8/15/2021 17:43 PDT
Lake County | Deputy Chief | Tier 2, Tier 3 | 8/15/2021 17:43 PDT
Lake County | Dispatch | Tier 2, Tier 3 | 8/15/2021 17:43 PDT
Lake County | Division Chief | Tier 2, Tier 3 | 8/15/2021 17:43 PDT
Lake County | Lieutenant | Tier 2, Tier 3 | 8/15/2021 16:00 PDT
Lake County | MHOAC | Tier 2, Tier 3 | 8/15/2021 17:43 PDT
Lake County | OES Emergency Director; Designated POC | Tier 2, Tier 3 | 8/15/2021 16:00 PDT
Lake County | Public Safety Answering Point | Tier 2, Tier 3 | 8/15/2021 17:38 PDT
Lake County | Public Safety Answering Point | Tier 2, Tier 3 | 8/15/2021 17:40 PDT
Lake County | Public Safety Answering Point | Tier 2, Tier 3 | 8/15/2021 17:40 PDT
Lake County | Public Safety Answering Point | Tier 2, Tier 3 | 8/15/2021 17:40 PDT
Lake County | Public Safety Answering Point | Tier 2, Tier 3 | 8/15/2021 17:45 PDT
Lake County | Sheriff | Tier 2, Tier 3 | 8/15/2021 17:43 PDT
Lake County | Special Districts Administrator | Tier 2, Tier 3 | 8/15/2021 17:43 PDT
Lassen County | CAL FIRE | Tier 2, Zone 1 | 8/15/2021 17:43 PDT
Lassen County | CAO; Designated POC | Tier 2, Zone 1 | 8/15/2021 17:43 PDT
Lassen County | General | Tier 2, Zone 1 | 8/15/2021 17:43 PDT
Lassen County | General | Tier 2, Zone 1 | 8/15/2021 18:30 PDT
Lassen County | MHOAC | Tier 2, Zone 1 | 8/15/2021 17:43 PDT
Lassen County | Public Safety Answering Point | Tier 2, Zone 1 | 8/15/2021 17:43 PDT
Lassen County | Public Safety Answering Point | Tier 2, Zone 1 | 8/15/2021 17:43 PDT
Lassen County | Public Safety Answering Point | Tier 2, Zone 1 | 8/15/2021 17:43 PDT
Lassen County | Public Safety Answering Point | Tier 2, Zone 1 | 8/15/2021 17:47 PDT
Mendocino County | Account Executive | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Mendocino County | CEO | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Mendocino County | Commander | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Mendocino County | Director of Customer Care | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Mendocino County | Fire Chief | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Mendocino County | Fire Chief | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Mendocino County | Local Cal Fire | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Mendocino County | OES Manager | Tier 2, Tier 3, Zone 1 | 8/15/2021 15:30 PDT
Mendocino County | Public Safety Answering Point | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:49 PDT
Mendocino County | Public Safety Answering Point | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:49 PDT
Mendocino County | Public Safety Answering Point | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:51 PDT
Mendocino County | Public Safety Answering Point | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:55 PDT
Mendocino County | Public Safety Answering Point | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:57 PDT
Mendocino County | Public Safety Answering Point | Tier 2, Tier 3, Zone 1 | 8/15/2021 18:45 PDT
Mishewal-Wappo Of Alexander Valley | Chairperson | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Mooretown Rancheria | Casino Operations | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Mooretown Rancheria | Chairman | Tier 2, Tier 3, Zone 1 | 8/15/2021 14:45 PDT
Napa County | Captain | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Napa County | Captain | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Napa County | Emergency Management | Tier 2, Tier 3, Zone 1 | 8/15/2021 14:06 PDT
Napa County | Emergency Services Manager | Tier 2, Tier 3, Zone 1 | 8/15/2021 14:06 PDT
Napa County | General | Tier 2, Tier 3, Zone 1 | 8/15/2021 14:06 PDT
Napa County | GIS | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Napa County | LNU Command Center | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Napa County | MHOAC | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Napa County | MHOAC | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Napa County | Napa County Fire Chief | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Napa County | Napa County Fire Operations Chief | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Napa County | Public Safety Answering Point | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:59 PDT
Napa County | Public Safety Answering Point | Tier 2, Tier 3, Zone 1 | 8/15/2021 18:00 PDT
Napa County | Public Safety Answering Point | Tier 2, Tier 3, Zone 1 | 8/15/2021 18:04 PDT
Napa County | Public Safety Answering Point | Tier 2, Tier 3, Zone 1 | 8/15/2021 18:06 PDT
Napa County | Sheriff | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Napa County | Under-Sheriff | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Nevada County | Division Chief | Tier 2, Tier 3, Zone 1 | 8/16/2021 19:08 PDT
Nevada County | General | Tier 2, Tier 3, Zone 1 | 8/16/2021 19:08 PDT
Nevada County | General | Tier 2, Tier 3, Zone 1 | 8/16/2021 19:08 PDT
Nevada County | Health Officer | Tier 2, Tier 3, Zone 1 | 8/16/2021 19:08 PDT
Nevada County | OES Director | Tier 2, Tier 3, Zone 1 | 8/16/2021 19:08 PDT
Nevada County | OES Manager; Designated POC | Tier 2, Tier 3, Zone 1 | 8/15/2021 15:46 PDT
Pit River Tribes | Chairperson | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Pit River Tribes | OES Director | Tier 2, Tier 3, Zone 1 | 8/15/2021 14:45 PDT
Pit River Tribes | Tribal Housing Authority | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Plumas County | CAL FIRE | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Plumas County | CAO; Designated POC | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Plumas County | Director | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Plumas County | Dispatch | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Plumas County | Division Chief | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Plumas County | General | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Plumas County | Main Office | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Plumas County | MHOAC | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Plumas County | OES Director | Tier 2, Tier 3, Zone 1 | 8/15/2021 15:55 PDT
Plumas County | Public Safety Answering Point | Tier 2, Tier 3, Zone 1 | 8/15/2021 18:11 PDT
Plumas County | Public Safety Answering Point | Tier 2, Tier 3, Zone 1 | 8/15/2021 18:12 PDT
Plumas County | Public Works Director | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Plumas County | USFS PNF Dispatch | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Round Valley Reservation | Chief of Police | Tier 2, Tier 3, Zone 1 | 8/17/2021 15:27 PDT
Round Valley Reservation | Tribal Business Administrator | Tier 2, Tier 3, Zone 1 | 8/17/2021 15:27 PDT
Shasta County | CEO; Designated POC | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Shasta County | Chief, County Fire Warden | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Shasta County | Chief, Northern Operations | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Shasta County | District Director | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Shasta County | ECC | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Shasta County | General | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Shasta County | General | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Shasta County | General | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Shasta County | General | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Shasta County | Lieutenant | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Shasta County | MHOAC | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Shasta County | OES | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Shasta County | OES Assistant Director | Tier 2, Tier 3, Zone 1 | 8/15/2021 18:30 PDT
Shasta County | Public Safety Answering Point | Tier 2, Tier 3, Zone 1 | 8/15/2021 18:15 PDT
Shasta County | Public Safety Answering Point | Tier 2, Tier 3, Zone 1 | 8/15/2021 18:19 PDT
Shasta County | Public Safety Answering Point | Tier 2, Tier 3, Zone 1 | 8/15/2021 18:22 PDT
Shasta County | Public Safety Answering Point | Tier 2, Tier 3, Zone 1 | 8/15/2021 18:22 PDT
Shasta County | Public Safety Answering Point | Tier 2, Tier 3, Zone 1 | 8/15/2021 18:22 PDT
Shasta County | Sheriff | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Shasta County | Supervisor | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Shasta County | Supervisor | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Shasta County | Undersheriff | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Shebelna Band Of Mendocino Coast Pomo Indians | Chairperson | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Sierra County | Chair of the Board | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Sierra County | Dispatch Supervisor | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Sierra County | Fire Chief | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Sierra County | Fire Chief | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Sierra County | OES Coordinator; Designated POC | Tier 2, Tier 3, Zone 1 | 8/15/2021 15:46 PDT
Sierra County | Public Safety Answering Point | Tier 2, Tier 3, Zone 1 | 8/15/2021 18:21 PDT
Sierra County | Public Safety Answering Point | Tier 2, Tier 3, Zone 1 | 8/15/2021 18:28 PDT
Sierra County | Public Safety Answering Point | Tier 2, Tier 3, Zone 1 | 8/15/2021 18:28 PDT
Sierra County | Public Safety Answering Point | Tier 2, Tier 3, Zone 1 | 8/15/2021 18:28 PDT
Sierra County | Sheriff | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Sierra County | Superintendent | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Sierra County | Supervisor | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Solano County | County Administrator | Tier 2 | 8/15/2021 17:43 PDT
Solano County | Emergency | Tier 2 | 8/15/2021 17:43 PDT
Solano County | Emergency | Tier 2 | 8/15/2021 17:43 PDT
Solano County | Emergency | Tier 2 | 8/15/2021 15:32 PDT
Solano County | Fire Chief | Tier 2 | 8/15/2021 17:43 PDT
Solano County | Local Cal Fire | Tier 2 | 8/15/2021 17:43 PDT
Solano County | Local Cal Fire | Tier 2 | 8/16/2021 19:08 PDT
Solano County | Public Safety Answering Point | Tier 2 | 8/15/2021 17:51 PDT
Solano County | Public Safety Answering Point | Tier 2 | 8/15/2021 18:13 PDT
Solano County | Public Safety Answering Point | Tier 2 | 8/15/2021 18:28 PDT
Solano County | Public Safety Answering Point | Tier 2 | 8/15/2021 18:29 PDT
Solano County | Public Safety Answering Point | Tier 2 | 8/15/2021 18:30 PDT
Solano County | Public Safety Answering Point | Tier 2 | 8/15/2021 18:42 PDT
Solano County | Public Safety Answering Point | Tier 2 | 8/15/2021 18:48 PDT
Solano County | Public Safety Answering Point | Tier 2 | 8/15/2021 18:49 PDT
Sonoma County | CEO | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Sonoma County | Communications & Engagement Coordinator | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Sonoma County | Communications & Engagement Coordinator | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Sonoma County | Community Alert & Warning Manager | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Sonoma County | Costal Valleys EMS | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Sonoma County | County Administrator | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Sonoma County | Deputy Director | Tier 2, Tier 3, Zone 1 | 8/15/2021 16:20 PDT
Sonoma County | Director of Customer Care | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Sonoma County | Emergency Coordinator | Tier 2, Tier 3, Zone 1 | 8/15/2021 16:20 PDT
Sonoma County | Emergency Manager | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Sonoma County | EMS Dispatch | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Sonoma County | General | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Sonoma County | Local Cal Fire | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Sonoma County | Main Office | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Sonoma County | MHOAC | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Sonoma County | OES Director | Tier 2, Tier 3, Zone 1 | 8/15/2021 16:20 PDT
Sonoma County | Public Health Officer | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Sonoma County | Public Safety Answering Point | Tier 2, Tier 3, Zone 1 | 8/15/2021 18:24 PDT
Sonoma County | Public Safety Answering Point | Tier 2, Tier 3, Zone 1 | 8/15/2021 18:24 PDT
Sonoma County | Public Safety Answering Point | Tier 2, Tier 3, Zone 1 | 8/15/2021 18:29 PDT
Sonoma County | Public Safety Answering Point | Tier 2, Tier 3, Zone 1 | 8/15/2021 18:29 PDT
Sonoma County | Public Safety Answering Point | Tier 2, Tier 3, Zone 1 | 8/15/2021 18:33 PDT
Sonoma County | Public Safety Answering Point | Tier 2, Tier 3, Zone 1 | 8/15/2021 18:35 PDT
Sonoma County | Public Safety Answering Point | Tier 2, Tier 3, Zone 1 | 8/15/2021 18:38 PDT
Sonoma County | Public Safety Answering Point | Tier 2, Tier 3, Zone 1 | 8/15/2021 18:43 PDT
Sonoma County | Public Safety Answering Point | Tier 2, Tier 3, Zone 1 | 8/15/2021 18:45 PDT
Sonoma County | Public Safety Answering Point | Tier 2, Tier 3, Zone 1 | 8/15/2021 18:52 PDT
Sonoma County | Public Safety Answering Point | Tier 2, Tier 3, Zone 1 | 8/15/2021 18:57 PDT
Sonoma County | Public Safety Answering Point | Tier 2, Tier 3, Zone 1 | 8/15/2021 18:59 PDT
Sonoma County | Sheriff | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Sonoma County | Sheriff Dispatch | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Sonoma County | Sheriff's Liaison | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Tehama County | Administrative Analyst | Tier 2 | 8/15/2021 17:43 PDT
Tehama County | CAO; Designated POC | Tier 2 | 8/15/2021 17:43 PDT
Tehama County | Communications Supervisor | Tier 2 | 8/15/2021 17:43 PDT
Tehama County | OES Deputy Director | Tier 2 | 8/15/2021 17:43 PDT
Tehama County | OES Director | Tier 2 | 8/15/2021 17:43 PDT
Tehama County | Public Safety Answering Point | Tier 2 | 8/15/2021 18:17 PDT
Tehama County | Public Safety Answering Point | Tier 2 | 8/15/2021 18:29 PDT
Tehama County | Public Safety Answering Point | Tier 2 | 8/15/2021 18:29 PDT
Tehama County | Public Safety Answering Point | Tier 2 | 8/15/2021 18:32 PDT
Tehama County | Public Safety Answering Point | Tier 2 | 8/15/2021 18:41 PDT
Tehama County | Public Safety Answering Point | Tier 2 | 8/15/2021 18:58 PDT
the City of Anderson | City Manager | Tier 2 | 8/15/2021 17:43 PDT
the City of Anderson | Deputy Public Works Director | Tier 2 | 8/15/2021 17:43 PDT
the City of Anderson | Fire Chief | Tier 2 | 8/15/2021 17:43 PDT
the City of Anderson | Lieutenant | Tier 2 | 8/15/2021 17:43 PDT
the City of Anderson | MOT Director | Tier 2 | 8/15/2021 17:43 PDT
the City of Anderson | Public Works Superintendent | Tier 2 | 8/15/2021 17:43 PDT
the City of Calistoga | City Manager; Designated POC | Tier 2, Tier 3 | 8/17/2021 15:27 PDT
the City of Calistoga | Fire Chief | Tier 2, Tier 3 | 8/17/2021 15:27 PDT
the City of Calistoga | Mayor | Tier 2, Tier 3 | 8/17/2021 15:27 PDT
the City of Calistoga | Police Chief | Tier 2, Tier 3 | 8/17/2021 15:27 PDT
the City of Clearlake | Chief of Police | Tier 2 | 8/15/2021 17:43 PDT
the City of Clearlake | City Manager; Designated POC | Tier 2 | 8/15/2021 17:43 PDT
the City of Clearlake | Fire Chief | Tier 2 | 8/15/2021 17:43 PDT
the City of Clearlake | Mayor | Tier 2 | 8/15/2021 17:43 PDT
the City of Clearlake | Non-Emergency | Tier 2 | 8/15/2021 17:43 PDT
the City of Corning |  | N/A | 8/16/2021 19:08 PDT
the City of Oakley | City Engineer | N/A | 8/17/2021 10:07 PDT
the City of Oakley | City Manager | N/A | 8/17/2021 10:07 PDT
the City of Oakley | Fire Chief | N/A | 8/17/2021 10:07 PDT
the City of Oakley | General Manager | N/A | 8/17/2021 10:07 PDT
the City of Oakley | General Manager | N/A | 8/17/2021 10:07 PDT
the City of Oroville | City Manager; Designated POC | Tier 2 | 8/15/2021 17:43 PDT
the City of Oroville | Deputy Chief | Tier 2 | 8/15/2021 17:43 PDT
the City of Oroville | Mayor | Tier 2 | 8/15/2021 17:43 PDT
the City of Oroville | Police Chief | Tier 2 | 8/15/2021 17:43 PDT
the City of Oroville | Vice Mayor | Tier 2 | 8/15/2021 17:43 PDT
the City of Red Bluff | City Manager; Designated POC | N/A | 8/17/2021 15:27 PDT
the City of Red Bluff | Fire Chief | N/A | 8/17/2021 15:27 PDT
the City of Red Bluff | Unit Chief | N/A | 8/17/2021 15:27 PDT
the City of Saint Helena | City Manager; Designated POC | Tier 2, Tier 3 | 8/17/2021 15:27 PDT
the City of Saint Helena | Fire Chief | Tier 2, Tier 3 | 8/17/2021 15:27 PDT
the City of Saint Helena | Police Chief | Tier 2, Tier 3 | 8/17/2021 15:27 PDT
the City of Santa Rosa | Admin Sergeant | Tier 2, Tier 3 | 8/17/2021 15:27 PDT
the City of Santa Rosa | Assistant Fire Marshal | Tier 2, Tier 3 | 8/17/2021 15:27 PDT
the City of Santa Rosa | Battalion Chief | Tier 2, Tier 3 | 8/17/2021 15:27 PDT
the City of Santa Rosa | Deputy Emergency Preparedness Coordinator | Tier 2, Tier 3 | 8/17/2021 15:27 PDT
the City of Santa Rosa | Deputy Fire Chief | Tier 2, Tier 3 | 8/17/2021 15:27 PDT
the City of Santa Rosa | Emergency Preparedness Coordinator; Designated POC | Tier 2, Tier 3 | 8/17/2021 15:27 PDT
the City of Santa Rosa | Fire | Tier 2, Tier 3 | 8/17/2021 15:27 PDT
the City of Santa Rosa | Lieutenant | Tier 2, Tier 3 | 8/17/2021 15:27 PDT
the City of Santa Rosa | Police Chief | Tier 2, Tier 3 | 8/17/2021 15:27 PDT
the City of Santa Rosa | Public Information Officer | Tier 2, Tier 3 | 8/17/2021 15:27 PDT
the City of Vacaville | Assistant City Manager | Tier 2 | 8/17/2021 15:27 PDT
the City of Vacaville | Emergency | Tier 2 | 8/17/2021 15:27 PDT
the City of Vacaville | General | Tier 2 | 8/17/2021 15:27 PDT
the City of West Sacramento | Fire Chief | N/A | 8/16/2021 19:08 PDT
the City of West Sacramento | Fire Marshal | N/A | 8/16/2021 19:08 PDT
the City of West Sacramento | General | N/A | 8/16/2021 19:08 PDT
the City of West Sacramento | Non-Emergency | N/A | 8/16/2021 19:08 PDT
the City of West Sacramento | Non-Emergency | N/A | 8/16/2021 19:08 PDT
the City of Willows | City Manager; Designated POC | N/A | 8/15/2021 17:43 PDT
the City of Willows | Non-Emergency | N/A | 8/15/2021 17:43 PDT
the City of Yountville | Public Works Director | Tier 3 | 8/17/2021 15:27 PDT
the City of Yountville | Town Manager; Designated POC | Tier 3 | 8/17/2021 15:27 PDT
the City of Yountville | Town Manager; Designated POC | Tier 3 | 8/17/2021 15:27 PDT
the Town of Paradise | Council Member | Tier 2, Tier 3 | 8/15/2021 17:43 PDT
the Town of Paradise | Council Member | Tier 2, Tier 3 | 8/15/2021 17:43 PDT
the Town of Paradise | Division Chief, Paradise Fire Chief | Tier 2, Tier 3 | 8/15/2021 17:43 PDT
the Town of Paradise | General | Tier 2, Tier 3 | 8/15/2021 17:43 PDT
the Town of Paradise | General | Tier 2, Tier 3 | 8/15/2021 17:43 PDT
the Town of Paradise | General | Tier 2, Tier 3 | 8/15/2021 17:43 PDT
the Town of Paradise | Mayor | Tier 2, Tier 3 | 8/15/2021 17:43 PDT
the Town of Paradise | Town Manager; Designated POC | Tier 2, Tier 3 | 8/15/2021 17:43 PDT
the Town of Paradise | Vice Mayor | Tier 2, Tier 3 | 8/15/2021 17:43 PDT
Trina Marine Ruano Family | Representative | Tier 2, Tier 3 | 8/17/2021 10:07 PDT
Trinity County | CAO; Designated POC | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Trinity County | Health Officer | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Trinity County | Program Manager | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Trinity County | Public Safety Answering Point | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:30 PDT
Tsungwe Council | Vice Chairman | Tier 2, Tier 3, Zone 1 | 8/15/2021 17:43 PDT
Yolo County | Board Clerk/Administrative Analyst | Tier 2 | 8/15/2021 17:43 PDT
Yolo County | Director Customer Care and Marketing | Tier 2 | 8/15/2021 17:43 PDT
Yolo County | Dispatch | Tier 2 | 8/15/2021 17:43 PDT
Yolo County | EMS Administrator | Tier 2 | 8/15/2021 17:43 PDT
Yolo County | Fire Chief | Tier 2 | 8/15/2021 17:43 PDT
Yolo County | Non-Emergency | Tier 2 | 8/15/2021 17:43 PDT
Yolo County | OES Coordinator | Tier 2 | 8/15/2021 17:43 PDT
Yolo County | Public Safety Answering Point | Tier 2, Tier 3 | 8/15/2021 18:38 PDT
Yolo County | Public Safety Answering Point | Tier 2 | 8/15/2021 18:47 PDT
Yolo County | Public Safety Answering Point | Tier 2 | 8/15/2021 18:48 PDT
Yolo County | Public Safety Answering Point | Tier 2 | 8/15/2021 18:55 PDT
Yolo County | N/A | Tier 2 | 8/15/2021 15:30 PDT
Yuba County | Board Supervisor | Tier 2, Tier 3 | 8/15/2021 17:43 PDT
Yuba County | Chief | Tier 2, Tier 3 | 8/15/2021 17:43 PDT
Yuba County | County Executive Officer | Tier 2, Tier 3 | 8/15/2021 17:43 PDT
Yuba County | Director | Tier 2, Tier 3 | 8/15/2021 17:43 PDT
Yuba County | Emergency Manager ; Designated POC | Tier 2, Tier 3 | 8/15/2021 17:43 PDT
Yuba County | General | Tier 2, Tier 3 | 8/15/2021 17:43 PDT
Yuba County | Health Administrator | Tier 2, Tier 3 | 8/15/2021 17:43 PDT
Yuba County | Health Officer | Tier 2, Tier 3 | 8/15/2021 17:43 PDT
Yuba County | Interim Emergency Operations Manager | Tier 2, Tier 3 | 8/15/2021 17:43 PDT
Yuba County | Public Safety Answering Point | Tier 2, Tier 3 | 8/15/2021 17:35 PDT
Yuba County | Public Safety Answering Point | Tier 2, Tier 3 | 8/15/2021 18:33 PDT
Yuba County | Public Safety Answering Point | Tier 2, Tier 3 | 8/15/2021 18:36 PDT
Yuba County | Public Safety Answering Point | Tier 2, Tier 3 | 8/16/2021 18:16 PDT
Yuba County | Public Safety Answering Point | Tier 2, Tier 3 | 8/16/2021 18:16 PDT
ALAMEDA County Communication Facility | SPRINT CORPORATION | N/A | 8/14/2021 21:11 PDT
ALAMEDA County Communication Facility | T-MOBILE WEST LLC | N/A | 8/14/2021 21:11 PDT
BUTTE County Communication Facility | AT&T MOBILITY | Tier 3 | 8/14/2021 17:54 PDT
BUTTE County Communication Facility | AT&T MOBILITY LLC | Tier 3 | 8/14/2021 17:54 PDT
BUTTE County Communication Facility | AT&T SERVICES INC | Tier 2, Tier 3 | 8/14/2021 17:54 PDT
BUTTE County Communication Facility | GTE MOBILE NET | Tier 3 | 8/14/2021 17:54 PDT
BUTTE County Communication Facility | GTE MOBILNET OF CALIFORNIA LIMITED PARTNERSHIP | Tier 3 | 8/14/2021 17:54 PDT
BUTTE County Communication Facility | GTE MOBILNET OF CALIFORNIA LP | Tier 3 | 8/14/2021 17:54 PDT
BUTTE County Communication Facility | METRO PCS INC | Tier 3 | 8/14/2021 17:54 PDT
BUTTE County Communication Facility | SPRINT CORPORATION | Tier 2, Tier 3 | 8/14/2021 17:54 PDT
BUTTE County Communication Facility | SPRINT NEXTEL CORPORATION | Tier 2, Tier 3 | 8/14/2021 17:54 PDT
BUTTE County Communication Facility | T-MOBILE WEST LLC | Tier 3 | 8/14/2021 17:54 PDT
BUTTE County Water and Waste Water Facility | ENTERPRISE RANCHERIA | Tier 2 | 8/14/2021 17:54 PDT
COLUSA County Communication Facility | AT&T | N/A | 8/14/2021 21:11 PDT
COLUSA County Communication Facility | AT&T MOBILITY LLC | Tier 2 | 8/14/2021 21:11 PDT
COLUSA County Communication Facility | AT&T SERVICES INC | Tier 2 | 8/14/2021 21:11 PDT
COLUSA County Communication Facility | CITIZENS TELECOMMUNICATIONS OF CALIFORNIA INC. | Tier 2 | 8/14/2021 21:11 PDT
COLUSA County Communication Facility | FRONTIER COMMUNICATIONS CORPORATION DIP | Tier 2 | 8/14/2021 21:11 PDT
COLUSA County Communication Facility | GTE MOBILNET OF CALIFORNIA LP | Tier 2 | 8/14/2021 21:11 PDT
COLUSA County Water and Waste Water Facility | COUNTY OF COLUSA | Tier 2 | 8/14/2021 21:11 PDT
CONTRA COSTA County Communication Facility | AT&T SERVICES INC | Tier 3 | 8/14/2021 21:11 PDT
CONTRA COSTA County Communication Facility | COUNTY OF CONTRA COSTA | Tier 3 | 8/14/2021 21:11 PDT
CONTRA COSTA County Communication Facility | U S COAST GUARD | Tier 3 | 8/14/2021 21:11 PDT
GLENN County Communication Facility | AMERICAN TOWER CORPORATION | Tier 2 | 8/14/2021 21:11 PDT
GLENN County Communication Facility | AT&T MOBILITY | Tier 2 | 8/14/2021 21:11 PDT
GLENN County Communication Facility | AT&T SERVICES INC | Tier 2 | 8/14/2021 21:11 PDT
GLENN County Communication Facility | GTE MOBILE NET | Tier 2 | 8/14/2021 21:11 PDT
GLENN County Water and Waste Water Facility | ELK CREEK COMMUNITY SERVICE | Tier 2 | 8/14/2021 21:11 PDT
HUMBOLDT County Communication Facility | AT&T SERVICES INC | Tier 2 | 8/14/2021 17:54 PDT
HUMBOLDT County Communication Facility | EDGE WIRELESS LLC | Tier 2 | 8/14/2021 17:54 PDT
HUMBOLDT County Communication Facility | FRONTIER COMMUNICATIONS CORPORATION DIP | Tier 2 | 8/14/2021 17:54 PDT
HUMBOLDT County Communication Facility | GTE MOBILNET OF CALIFORNIA LIMITED PARTNERSHIP | Tier 2 | 8/14/2021 17:54 PDT
HUMBOLDT County Communication Facility | UNITED STATES CELLULAR CORP | Tier 2 | 8/14/2021 17:54 PDT
LAKE County Communication Facility | AT&T MOBILITY LLC | Tier 2 | 8/14/2021 17:54 PDT
LAKE County Communication Facility | AT&T SERVICES INC | Tier 2, Tier 3 | 8/14/2021 17:54 PDT
LAKE County Communication Facility | GTE MOBILNET OF CALIFORNIA LIMITED PARTNERSHIP | Tier 2 | 8/14/2021 21:11 PDT
LAKE County Communication Facility | GTE MOBILNET OF CALIFORNIA LP | Tier 3 | 8/14/2021 17:54 PDT
LAKE County Communication Facility | MEDIACOM CALIFORNIA LLC | N/A | 8/14/2021 17:54 PDT
LAKE County Communication Facility | US CELLULAR | Tier 2 | 8/14/2021 21:11 PDT
LASSEN County Communication Facility | FRONTIER COMMUNICATIONS CORPORATION DIP | Tier 2 | 8/14/2021 21:11 PDT
MENDOCINO County Communication Facility | AT&T SERVICES INC | Tier 2, Tier 3 | 8/14/2021 21:11 PDT
MENDOCINO County Communication Facility | EDGE WIRELESS LLC | Tier 2 | 8/14/2021 21:11 PDT
MENDOCINO County Communication Facility | FRONTIER COMMUNICATIONS CORPORATION DIP | Tier 2 | 8/14/2021 17:54 PDT
MENDOCINO County Communication Facility | GTE MOBILNET OF CALIFORNIA LIMITED PARTNERSHIP | N/A | 8/14/2021 17:54 PDT
MENDOCINO County Communication Facility | GTE MOBILNET OF CALIFORNIA LP | Tier 2 | 8/14/2021 21:11 PDT
MENDOCINO County Communication Facility | T MOBILE OMNI POINT COMMUNICATIONS | Tier 2 | 8/14/2021 17:54 PDT
MENDOCINO County Communication Facility | T-MOBILE CO NISC | Tier 2 | 8/14/2021 21:11 PDT
MENDOCINO County Communication Facility | T-MOBILE USA INC | Tier 2 | 8/14/2021 21:11 PDT
MENDOCINO County Communication Facility | US CELLULAR | Tier 2 | 8/14/2021 21:11 PDT
NAPA County Communication Facility | AT&T MOBILITY LLC | Tier 2, Tier 3 | 8/14/2021 17:54 PDT
NAPA County Communication Facility | AT&T SERVICES INC | Tier 2, Tier 3 | 8/14/2021 17:54 PDT
NAPA County Communication Facility | CALIFORNIA HIGHWAY PATROL | Tier 2 | 8/14/2021 17:54 PDT
NAPA County Communication Facility | CITY OF NAPA | Tier 3 | 8/14/2021 17:54 PDT
NAPA County Communication Facility | GTE MOBILNET OF CALIFORNIA LIMITED PARTNERSHIP | N/A | 8/14/2021 21:11 PDT
NAPA County Communication Facility | GTE MOBILNET OF CALIFORNIA LP | Tier 2 | 8/14/2021 21:11 PDT
NAPA County Communication Facility | SPRINT CORPORATION | Tier 2 | 8/14/2021 21:11 PDT
NAPA County Communication Facility | SPRINT NEXTEL CORPORATION | Tier 3 | 8/14/2021 21:11 PDT
NAPA County Communication Facility | T-MOBILE WEST CORPORATION | Tier 3 | 8/14/2021 17:54 PDT
NAPA County Water and Waste Water Facility | CITY OF CALISTOGA | N/A | 8/14/2021 21:11 PDT
NEVADA County Communication Facility | AT&T SERVICES INC | Tier 3 | 8/14/2021 21:11 PDT
PLUMAS County Communication Facility | AT&T SERVICES INC | Tier 2, Tier 3 | 8/14/2021 17:54 PDT
PLUMAS County Communication Facility | CALIFORNIA HIGHWAY PATROL | Tier 2 | 8/14/2021 17:54 PDT
PLUMAS County Communication Facility | FRONTIER COMMUNICATIONS CORPORATION DIP | Tier 2 | 8/14/2021 21:11 PDT
PLUMAS County Communication Facility | SPRINT CORPORATION | Tier 3 | 8/14/2021 17:54 PDT
PLUMAS County Communication Facility | US DEPARTMENT OF AGRICULTURE | Tier 2 | 8/14/2021 17:54 PDT
SHASTA County Communication Facility | AT&T | Tier 3 | 8/14/2021 17:54 PDT
SHASTA County Communication Facility | AT&T MOBILITY LLC | Tier 2, Tier 3 | 8/14/2021 17:54 PDT
SHASTA County Communication Facility | AT&T SERVICES INC | Tier 2, Tier 3 | 8/14/2021 17:54 PDT
SHASTA County Communication Facility | CHARTER COMMUNICATIONS HOLDING COMPANY LLC | Tier 2, Tier 3 | 8/14/2021 17:54 PDT
SHASTA County Communication Facility | CINGULAR WIRELESS SERVICES, INC | Tier 2 | 8/14/2021 17:54 PDT
SHASTA County Communication Facility | FRONTIER COMMUNICATIONS | Tier 2 | 8/14/2021 21:11 PDT
SHASTA County Communication Facility | FRONTIER COMMUNICATIONS CORPORATION DIP | Tier 2, Tier 3 | 8/14/2021 17:54 PDT
SHASTA County Communication Facility | GTE MOBILNET OF CALIFORNIA LIMITED PARTNERSHIP | Tier 2 | 8/14/2021 17:54 PDT
SHASTA County Communication Facility | GTE MOBILNET OF CALIFORNIA LP | Tier 2, Tier 3 | 8/14/2021 17:54 PDT
SHASTA County Communication Facility | HAPPY VALLEY TELEPHONE CO | Tier 2 | 8/14/2021 17:54 PDT
SHASTA County Communication Facility | METRO PCS INC | Tier 2 | 8/14/2021 17:54 PDT
SHASTA County Communication Facility | SPRINT CORPORATION | Tier 2, Tier 3 | 8/14/2021 17:54 PDT
SHASTA County Communication Facility | SPRINT NEXTEL CORPORATION | Tier 2 | 8/14/2021 17:54 PDT
SHASTA County Communication Facility | TDS TELECOM | Tier 2 | 8/14/2021 17:54 PDT
SHASTA County Communication Facility | T-MOBILE WEST LLC | Tier 2, Tier 3 | 8/14/2021 21:11 PDT
SHASTA County Communication Facility | US DEPARTMENT OF AGRICULTURE | Tier 2 | 8/14/2021 17:54 PDT
SHASTA County Communication Facility | VERIZON WIRELESS | Tier 2 | 8/14/2021 17:54 PDT
SIERRA County Communication Facility | AT&T MOBILITY LLC | Tier 3 | 8/14/2021 17:54 PDT
SIERRA County Communication Facility | AT&T SERVICES INC | Tier 2, Tier 3 | 8/14/2021 17:54 PDT
SIERRA County Communication Facility | CALIFORNIA HIGHWAY PATROL | Tier 3 | 8/14/2021 17:54 PDT
SIERRA County Communication Facility | US DEPARTMENT OF AGRICULTURE | Tier 3 | 8/14/2021 17:54 PDT
SIERRA County Water and Waste Water Facility | DOWNIEVILLE PUBLIC UTILITIES DISTRICT | Tier 3 | 8/14/2021 17:54 PDT
SIERRA County Water and Waste Water Facility | HASKELL CREEK TRACT ASSOCIATION | Tier 1 | 8/14/2021 17:54 PDT
SOLANO County Communication Facility | AMERICAN TOWER CORP | Tier 2 | 8/14/2021 21:11 PDT
SOLANO County Communication Facility | AT&T MOBILITY LLC | N/A | 8/14/2021 21:11 PDT
SOLANO County Communication Facility | AT&T SERVICES INC | Tier 2 | 8/14/2021 17:54 PDT
SOLANO County Communication Facility | GTE MOBILNET OF CALIFORNIA LIMITED PARTNERSHIP | Tier 2 | 8/14/2021 21:11 PDT
SONOMA County Communication Facility | AT&T | Tier 3 | 8/14/2021 21:11 PDT
SONOMA County Communication Facility | AT&T MOBILITY LLC | Tier 2, Tier 3 | 8/14/2021 17:54 PDT
SONOMA County Communication Facility | AT&T SERVICES INC | Tier 2, Tier 3 | 8/14/2021 17:54 PDT
SONOMA County Communication Facility | CALIFORNIA HIGHWAY PATROL | Tier 2 | 8/14/2021 21:11 PDT
SONOMA County Communication Facility | FRONTIER COMMUNICATIONS CORPORATION DIP | Tier 3 | 8/14/2021 21:11 PDT
SONOMA County Communication Facility | GTE MOBILNET OF CALIFORNIA LIMITED PARTNERSHIP | N/A | 8/14/2021 21:11 PDT
SONOMA County Communication Facility | SPRINT CORPORATION | Tier 2, Tier 3 | 8/14/2021 17:54 PDT
SONOMA County Communication Facility | T-MOBILE WEST LLC | Tier 2 | 8/14/2021 21:11 PDT
TEHAMA County Communication Facility | AT&T MOBILITY | Tier 2 | 8/14/2021 21:11 PDT
TEHAMA County Communication Facility | AT&T MOBILITY LLC | Tier 2 | 8/14/2021 17:54 PDT
TEHAMA County Communication Facility | AT&T SERVICES INC | Tier 2 | 8/14/2021 17:54 PDT
TEHAMA County Communication Facility | CHARTER COMMUNICATIONS HOLDING COMPANY LLC | Tier 2 | 8/14/2021 21:11 PDT
TEHAMA County Communication Facility | FRONTIER COMMUNICATIONS CORPORATION DIP | Tier 2 | 8/14/2021 17:54 PDT
TEHAMA County Communication Facility | GTE MOBILNET OF CALIFORNIA LIMITED PARTNERSHIP | Tier 2 | 8/14/2021 21:11 PDT
TEHAMA County Communication Facility | GTE MOBILNET OF CALIFORNIA LP | Tier 2 | 8/14/2021 17:54 PDT
TEHAMA County Communication Facility | SPRINT CORPORATION | Tier 2 | 8/14/2021 21:11 PDT
TEHAMA County Communication Facility | SPRINT NEXTEL CORPORATION | Tier 2 | 8/14/2021 21:11 PDT
TEHAMA County Communication Facility | T-MOBILE WEST LLC | Tier 2 | 8/14/2021 21:11 PDT
TEHAMA County Communication Facility | VERIZON WIRELESS | Tier 2 | 8/14/2021 21:11 PDT
TEHAMA County Other Facility | AT&T SERVICES INC | N/A | 8/14/2021 21:11 PDT
TRINITY County Communication Facility | FRONTIER COMMUNICATIONS CORPORATION DIP | Tier 2 | 8/14/2021 17:54 PDT
TRINITY County Communication Facility | GTE MOBILNET OF CALIFORNIA LIMITED PARTNERSHIP | N/A | 8/14/2021 17:54 PDT
YOLO County Communication Facility | AT&T MOBILITY LLC | Tier 2 | 8/14/2021 17:54 PDT
YOLO County Communication Facility | AT&T SERVICES INC | N/A | 8/14/2021 17:54 PDT
YOLO County Communication Facility | GTE MOBILNET OF CALIFORNIA LP | Tier 2 | 8/14/2021 17:54 PDT
YOLO County Communication Facility | SPRINT CORPORATION | Tier 2 | 8/14/2021 17:54 PDT
YUBA County Communication Facility | AT&T SERVICES INC | Tier 3 | 8/14/2021 17:54 PDT
YUBA County Communication Facility | VERIZON | Tier 3 | 8/14/2021 17:54 PDT

## Appendix G
Post-Event Report Data: PG&E August 17 - 19, 2021 De-energization Event
Appendix G: Community Resource Centers Provided by PG&E
# | County | Site Name | Address | Hours of Operation (PDT) |  |  | Total Visitors | Site Type | Amenities Provided
|  |  |  | Day 1 | Day 2 | Day 3 |  | (Indoor, Micro)
|  |  |  | 2021-08-17 | 2021-08-18 | 2021-08-19
1 | Butte | Berry Creek Elementary | 286 Rockerfeller Rd, Berry Creek, CA 95916 | 17:00-22:00 | 08:00-22:00 | 08:00-13:00 | 3 | Micro | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging
2 | Butte | Magalia Pines Baptist Church | 14098 Skyway Rd, Magalia, CA 95954 | 17:00-22:00 | 08:00-22:00 | 08:00-13:00 | 216 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging, Cooling & Heating, Ice
3 | Butte | Southside Oroville Community Center | 2959 Lower Wyandotte Rd, Oroville, CA 95966 | 17:00-22:00 | 08:00-22:00 | 08:00-13:00 | 13 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging, Cooling & Heating, Ice
4 | Butte | Paradise Parks and Recreation Center (aka Terry Ashe Center) | 6626 Skyway, Paradise, CA 95969 | 17:00-22:00 | 08:00-22:00 | 08:00-13:00 | 50 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging, Cooling & Heating, Ice
5 | Colusa | Stonyford Community Center/Hall | 229 Market St, Stonyford, CA 95979 | 17:00-22:00 | 08:00-22:00 | 08:00-13:00 | 203 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging, Cooling & Heating, Ice
6 | Contra Costa | St. Bonaventure Catholic Church | 5562 Clayton Rd, Concord, CA 94521 | 17:00-22:00 | 08:00-13:00 | N/A | 3 | Mobile | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging
7 | Glenn | Elk Creek Junior Senior High School | 3430 Co Rd 309, Elk Creek, CA 95939 | 17:00-22:00 | 08:00-22:00 | 08:00-13:00 | 108 | Mobile | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging
8 | Lake | Clearlake Senior Community Center | 3245 Bowers Ave, Clearlake, CA 95422 | 17:00-22:00 | 08:00-22:00 | 08:00-13:00 | 84 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging, Cooling & Heating, Ice
9 | Lake | Live Oaks Senior Center | 12502 Foot hill Blvd, Clearlake Oaks, CA 95423 | 17:00-22:00 | 08:00-15:00 | N/A | 14 | Mobile | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging
10 | Lake | Mountain Lion’s Club (also known as Little Red Schoolhouse) | 15780 Bottlerock Rd, Cobb, CA 95426 | 17:00-22:00 | 08:00-22:00 | 08:00-13:00 | 149 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging, Cooling & Heating, Ice
11 | Lake | Scotts Valley Band of Pomo Indians Red Hills Property | 7130 Red Hills Rd, Kelseyville, CA 95451 | 19:00-22:00 | 08:00-22:00 | 08:00-13:00 | 18 | Mobile | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging
12 | Mendocino | Keith's Market IGA | 76201 Covelo Rd, Covelo, CA 95428 | 17:00-22:00 | 08:00-13:00 | N/A | 32 | Mobile | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging
13 | Mendocino | Harwood Hall | 44400 Willis Ave, Laytonville, CA 95454 | 17:00-22:00 | 08:00-13:00 | N/A | 35 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging, Cooling & Heating, Ice
14 | Mendocino | Ukiah Empty Lot | 1775 N State St, Ukiah, CA 95482 | 19:00-22:00 | 08:00-13:00 | N/A | 27 | Mobile | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging
15 | Napa | Pacific Union College | 35 La Jota Dr, Angwin, CA 94508 | 17:00-22:00 | 08:00-22:00 | N/A | 236 | Mobile | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging
16 | Napa | Highlands Christian Fellowship | 970 Petrified Forest Rd, Calistoga, CA 94515 | 17:00-22:00 | 08:00-22:00 | N/A | 492 | Mobile | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging
17 | Napa | Crosswalk Community Church | 2590 1st St, Napa, CA 94558 | 17:00-22:00 | 08:00-22:00 | N/A | 8 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging, Cooling & Heating, Ice
18 | Napa | Saint Helena Catholic School | 1255 Oak Ave, St. Helena, CA 94574 | 17:00-22:00 | 08:00-22:00 | N/A | 28 | Mobile | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging
19 | Plumas | Quincy Elks Lodge 1884 | 2004 E Main St, Quincy, CA 95971 | 17:00-22:00 | 08:00-22:00 | 08:00-13:00 | 82 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging, Cooling & Heating, Ice
20 | Shasta | Anderson (Frontier) Senior Center | 2081 Frontier Trail, Anderson, CA 96007 | 17:00-22:00 | 08:00-22:00 | 08:00-13:00 | 122 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging, Cooling & Heating, Ice
21 | Shasta | Happy Valley Community Center | 5400 Happy Valley Rd, Anderson, CA 96007 | 17:00-22:00 | 08:00-22:00 | 08:00-13:00 | 128 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging, Cooling & Heating, Ice
22 | Shasta | Lakehead Lions Hall | 20814 Mammoth Dr, Lakehead, CA 96051 | 17:00-22:00 | 08:00-22:00 | 08:00-13:00 | 6 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging, Cooling & Heating, Ice
23 | Shasta | Mercy Oaks | 100 Mercy Oaks Dr, Redding, CA 96003 | 17:00-22:00 | 08:00-22:00 | 08:00-13:00 | 61 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging, Cooling & Heating, Ice
24 | Shasta | Hill Country Health and Wellness Center | 29632 CA-299, Round Mountain, CA 96084 | 17:00-22:00 | 08:00-22:00 | 08:00-13:00 | 355 | Micro | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging
25 | Sierra | Lower Alleghany Volunteer Fire Dept | 514 Miners St, Alleghany, CA 95910 | 17:00-22:00 | 08:00-13:00 | N/A | 15 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging, Cooling & Heating, Ice
26 | Sierra | Downieville Community Hall | 327 Main St, Downieville, CA 95936 | 17:00-22:00 | 08:00-13:00 | N/A | 24 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging, Cooling & Heating, Ice
27 | Solano | Solano Community College - Vacaville | 2001 N Village Pkwy, Vacaville, CA 95688 | 17:00-22:00 | 08:00-22:00 | 08:00-13:00 | 42 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging, Cooling & Heating, Ice
28 | Sonoma | Cloverdale Citrus Fairgrounds | 1 Citrus Fair Dr, Cloverdale, CA 95425 | 17:00-22:00 | 08:00-22:00 | N/A | 8 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging, Cooling & Heating, Ice
29 | Sonoma | Presbyterian Church of the Roses | 2500 Patio Ct., Santa Rosa, CA 95409 | 19:00-22:00 | 08:00-22:00 | N/A | 10 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging, Cooling & Heating, Ice
30 | Sonoma | First Congregational Church of Sonoma | 252 W Spain St, Sonoma, CA 95476 | 19:00-22:00 | 08:00-22:00 | N/A | 65 | Mobile | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging
31 | Tehama | Noland Park | 19001 Bowman Rd, Cottonwood, CA 96022 | 17:00-22:00 | 08:00-22:00 | 08:00-13:00 | 214 | Micro | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging
32 | Tehama | Rancho Tehema Association | 17605 Park Terrace Rd, Rancho Tehama, CA 96021 | 17:00-22:00 | 08:00-22:00 | 08:00-13:00 | 472 | Micro | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging
33 | Yolo | United States Postal Service | 7575 CA-16, Guinda, CA 95637 | 17:00-22:00 | 08:00-22:00 | N/A | 40 | Mobile | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging
34 | Yuba | Alcouffe Center | 9185 Marysville Rd, Oregon House, CA 95962 | 17:00-22:00 | 08:00-13:00 | N/A | 13 | Indoor | Wi-Fi, Restrooms, Water and Snacks, Blankets, Device Charging, Medical Device Charging, Cooling & Heating, Ice