## Summary
Party Name | Count of Party Name | Count of Data Request | Sum of Subparts
GPI | 1 | 3 | 12
MGRA | 6 | 42 | 59
OEIS | 21 | 98 | 510
SPD | 15 | 183 | 696
TURN | 4 | 36 | 105
Grand Total | 47 | 362 | 1382

## 2026-2028 WMP Discovery
Week No. | Count | Party Name | Data Set | Data Request | Question No. | Supp/Rev | Question ID | Question Text | Responses | Requestor | Date Received | Final Due Date | Date Sent | Links | Number of Atchs | NDA Required | 2025 WMP Section | Category | Subcategory | 2025 WMP Section Name
15 | 1 | TURN | 002 | TURN_002 | 1 | No | TURN_002_Q1 | Section 5.2.1, page 57 states, “starting in January 2023, PG&E incorporated additional customers who could be impacted into the PSPS consequence model and classified them as Potentially-Impacted Customers (PIC).” a. How were the PIC selected? b. How were they initially identified? c. What types of consequences do they have that were not included in the 12-year customer lookback? d. Please explain the basis for PG&E’s belief that “not every customer who could experience a PSPS event is captured in the historical backcast.” e. Regarding the statement on page 57 that “this enables the calculation of roughly double the potentially-affected customers …”, please provide the specific data on which this statement is based. | Please note that, PG&E no longer accounts for Potentially Impacted Customers (PICs) in its PSPS consequence model due to the low incremental risk values associated with customers that were not included in our lookback. Thus, the statement on page 57 of the 2026-2028 WMP is historical in nature. a. The selection criteria for PICs were created by using our distribution planning models under the scenario of “what if” every distribution line in HFTD/HFRA is required to be de-energized. b. Potentially impacted customers (i.e. all customers who would impacted by the theoretical de-energization of every HFTD/HFRA distribution line) were identified through our distribution planning models. WMP-Discovery 2026-2028_DR_TURN_002-Q001 Page 2 c. The inclusion of PICs results in an increased risk associated with customers in locations where PSPS thresholds were not met in our historical lookback, but have exposure to PSPS risk based on HFTD/HFRA location and system configuration. This evaluation does not include the addition of new consequences. d. The meaning behind this statement is that this is a low probabilistic event, and the intent was to assign risk exposure to customers that are not accounted for in PG&E’s traditional lookback. This is because our lookback is based on historical weather conditions that have met PSPS thresholds to initiate a PSPS event. This is not to say that locations in HFTD that have never met PSPS thresholds could not see an event in the future. e. This statement is based on the idea that all customers that would be impacted by the theoretical de-energization of every HFTD/HFRA distribution line, minus the unique customers included in our lookback. | A Mireille Fall-Fry | 2025-04-07 | 2025-04-10 | 2025-04-10 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-TURN_002.zip | 0 | No | 5 | Risk Methodology & Assessment | 5.2.1 | Risk and Risk Component Identification
15 | 2 | TURN | 002 | TURN_002 | 2 | No | TURN_002_Q2 | Section 5.2.2.1 page 63 provides the formula for PSPS likelihood. Please explain why 5 years was selected as the denominator? | PG&E’s lookback is used to estimate PSPS consequence and includes 2018-2022 data (5 years). This is to align with the initiation and execution of PSPS events in 2018. PG&E’s enterprise risk model also includes an additional 2 years of data (2023- 2024) that was not included in the existing lookback due to meteorology polygons not being available at the time of the analysis. To address this data gap, PG&E used actual PSPS events but determined the customer impact by de-energizing the upstream device as would be specified using our most recent PSPS guidance and protocols. | A Mireille Fall-Fry | 2025-04-07 | 2025-04-10 | 2025-04-10 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-TURN_002.zip | 0 | No | 5 | Risk Methodology & Assessment | 5.2.2.1 | Likelihood of Risk Event
15 | 3 | TURN | 002 | TURN_002 | 3 | No | TURN_002_Q3 | Section 6.1.2, page 118 states that, instead of undergrounding, “in certain circumstances we may choose to overhead harden a circuit segment or portion of a circuit segment because of feasibility constraints.” Please identify and explain each and every criterion that PG&E would use to determine that feasibility constraints have reached the point that PG&E would choose overhead hardening over undergrounding and how PG&E would decide, based on those criteria, that overhead hardening is the best choice. | PG&E objects to this request as it is overbroad, vague, ambiguous, and unduly burdensome. It is not possible to identify every single criterion that PG&E could use in evaluating the feasibility of a project. Notwithstanding and without waiving this objection, PG&E responds as follows: The feasibility of installing underground infrastructure can vary significantly across PG&E's service area, and therefore, the specific circumstances and facts must be evaluated for each case. Certain conditions may necessitate overhead hardening instead of undergrounding due to feasibility constraints. These conditions may include, but are not limited to: • Culturally Restricted Areas: Locations where underground installation may not be permitted due to cultural or historical considerations. • Geographical Challenges: Situations such as large water crossings where bridge attachments are not possible or large canyon crossings where no reasonable underground path exists. • Legal and Land Use Constraints: Inability to acquire the necessary easements or rights to install underground infrastructure. WMP-Discovery 2026-2028_DR_TURN_002-Q003 Page 2 • Geological Conditions: Presence of hard rock or granite terrain, where excavation costs are prohibitively high. These feasibility constraints are reviewed during the scoping process, and the associated costs are included in mitigation scenario analyses, such as the Cost-Benefit Ratio (CBR). This evaluation may lead to choosing a hybrid solution in some cases. In other instances, feasibility constraints become apparent later in the project lifecycle. When this occurs, decisions regarding overhead hardening versus undergrounding are made based on financial implications, timing considerations, risk assessment, and constructability challenges. This ensures that the selected approach is the most feasible and effective given the circumstances. | A Mireille Fall-Fry | 2025-04-07 | 2025-04-10 | 2025-04-10 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-TURN_002.zip | 0 | No | 6 | Wildfire Mitigation Strategy Development | 6.1.2 | Risk-Informed Prioritization
15 | 4 | TURN | 002 | TURN_002 | 4 | No | TURN_002_Q4 | Section 6.1.3.1, page 129, states, “While undergrounding is PG&E’s preferred solution for mitigating ignition risk in the highest risk areas, we recognize that undergrounding takes longer to execute than overhead hardening and is a more costly investment in the short term[,]” and “Covered conductor can generally be installed more quickly and costs less than undergrounding, but it does not protect against tree strike risk or fully address the reliability risk[,]” and concludes that “undergrounding, where feasible, is the best alternative where tree strike risk is high.” This conclusion does not address the information provided in Table 6.1.3-1 on page 128. Please explain why the cost and timing of undergrounding, which the table provides has a 98-99% average effectiveness, is preferred to the combination of covered conductor, EPSS, and PSPS, which the table provides has a 97% average effectiveness. | We disagree that this conclusion is not addressed. On page 128, we noted that “[t]he combined use of covered conductor, EPSS, and PSPS introduces a high likelihood of system outage risk and is disruptive to our customers.” As further and more fully described in Section 6.1.3.2 (pg. 134-135) and in PG&E’s 2025 WMP Update, ACI 23- 05 (pp. 56-57), PG&E recognizes that overhead hardening can be installed more quickly than an undergrounding solution; however, the initial risk reduction achieved from quicker installation of an overhead mitigation does not compensate for the greater total, more permanent risk reduction achieved over the lifetime of an underground solution. Undergrounding is preferred to the combination of covered conductor, EPSS, and PSPS because it nearly eliminates wildfire risk. We expect undergrounding to also reduce reliability risk and the need to operate and maintain overhead equipment and clearing vegetation around the overhead facilities. PG&E’s intent is to significantly reduce reliability impacts of outage programs and to offer near permanent solutions to the highest risk areas. | A Mireille Fall-Fry | 2025-04-07 | 2025-04-10 | 2025-04-10 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-TURN_002.zip | 0 | No | 6 | Wildfire Mitigation Strategy Development | 6.1.3.1 | Identifying and Evaluating Activities
15 | 5 | TURN | 002 | TURN_002 | 5 | No | TURN_002_Q5 | Regarding Table PG&E-6.1.3-1 on page 128, please provide the supporting data on which the “Blended Average Effectiveness” values for Rows 4, 5, and 6 are based. | Please refer to “WMP-Discovery2026-2028_DR_TURN_002-Q005Atch01.xlsx” The table below is a summary of references for the supporting data for each of the Blended Average Effectiveness values from Table PG&E-6.1.3-1 in the attached Excel sheet. Line No. System Hardening Mitigations Blended Average Effectiveness (a) Notes 2015-2024 1 Undergrounding All (b) 99% See "Effectiveness Analysis" tab for supporting data 2 Undergrounding Primary Distribution Lines (c ) 98% See "Effectiveness Analysis" tab for supporting data 3 Line Removal with Remote Grid 98% See "Effectiveness Analysis" tab for supporting data 4 Covered Conductor + EPSS + PSPS (d) 97% Calculated value using formula outlined in footnote (d). See 4a. And 4b. for input data for the calculation and the associated data sources 4a. Covered Conductor + EPSS + DCD 79% See "Effectiveness Analysis" tab for supporting data WMP-Discovery 2026-2028_DR_TURN_002-Q005 Page 2 Line No. System Hardening Mitigations Blended Average Effectiveness (a) Notes 4b. PSPS Effectiveness 84% See "PSPS_effectiveness_calculation" tab for supporting data 5 Covered Conductor + EPSS + DCD 79% See "Effectiveness Analysis" tab for supporting data 6 Covered Conductor 67% See "Effectiveness Analysis" tab for supporting data (a) This effectiveness evaluation is based on an assessment of each mitigation’s prevention of an ignition from active faults of known cause on overhead assets. Company-initiated outages, including PSPS outages, outages of unknown cause, as well as outages on existing underground assets are not applicable to this study and are excluded from calculation results as “N/A.” (b) Includes distribution primary, secondary, and services line(s). (c) Includes distribution secondary and services parallel to targeted primary line(s). (d) The combined “Overhead with EPSS and PSPS” effectiveness differs from others in the table as it is the result of two independent studies. The first study yields PSPS effectiveness alone to be approximately 84% effective at mitigating wildfire risk. Subsequently, the combined effectiveness of approximately 79% for “Overhead with EPSS” is applied on top of the PSPS reduction, resulting in: Mitigation Effectiveness = 84% + (100% - 84%) * 79% = 97% Within “WMP-Discovery2026-2028_DR_TURN_002-Q005Atch01.xlsx”, the following Excel sheets are provided: 1. Effectiveness Analysis Summary: This is summary of the data and includes the formulas for how each value was derived. 2. Effectiveness Analysis Detail: Includes all supporting data for calculating Blended Average Effectiveness Values in Line No. 1, 2, 3, 4a., 5 and 6 of the table above. 3. PSPS_effectiveness_calculation: Includes the analysis to calculate the PSPS supporting data for the PSPS effectiveness values using the RiskScore_Attribute tab to support the value in Line No. 4b. of the table above. 4. RiskScore_Attribute: Includes additional supporting data and information on the Risk Score data for Baseline and Baseline_wPSPS based on WLDFR bowtie model to calculate the PSPS effectiveness value. 5. PSPS_effectiveness_validation: Includes analysis used to validate PSPS effectiveness values provided in Line 4b. of the table above. | A Mireille Fall-Fry | 2025-04-07 | 2025-04-10 | 2025-04-10 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-TURN_002.zip | 1 | No | 6 | Wildfire Mitigation Strategy Development | 6.1.3-1 | Activity Selection Process
15 | 6 | TURN | 002 | TURN_002 | 6 | No | TURN_002_Q6 | Section 6.1.3.2, page 134, states: “Overhead system hardening combined with operations mitigations EPSS and PSPS has a high-risk reduction benefit that is roughly comparable to that of undergrounding without these operational mitigations. PG&E continues to prefer undergrounding on high-risk circuits where feasible for several reasons. Undergrounding is permanent risk reduction that does not have the negative reliability impacts from PSPS and EPSS. Underground facilities are less likely to be damaged during winter storms by high winds and vegetation falling into lines damaging the facilities or other contact with the lines from third parties. Over time, undergrounding also has lower operations and maintenance expenses.” a. Please provide any studies or reports in PG&E’s possession that compare the long-term or life cycle costs of undergrounding with the costs of overhead hardening combined with EPSS and PSPS. b. Please provide any studies or reports in PG&E’s possession that compare the long-term or life cycle costs of undergrounding with the costs of overhead hardening combined with EPSS, PSPS, and remote grids to reduce the reliability impacts of EPSS and PSPS. c. Please provide any studies or reports in PG&E’s possession that compare the operations and maintenance expenses of undergrounding with overhead hardening. d. Please provide any studies or reports in PG&E’s possession that compare the operations and maintenance expenses of undergrounding with overhead hardening, combined with EPSS and PSPS. e. Please provide any studies or reports in PG&E’s possession that compare the reliability (e.g., SAIDI, SAIFI, CAIDI, etc.) of undergrounded vs. overhead hardened facilities. f. Please provide any studies or reports in PG&E’s possession that compare the reliability (e.g., SAIDI, SAIFI, CAIDI, etc.) of undergrounded vs. overhead hardened facilities – not including the reliability impacts of PSPS and EPSS. | Please see PG&E’s responses below. 1,2,3 PG&E has performed and will continue to perform a reasonably diligent search for any relevant studies or reports and will supplement this response if any are identified. a. As described in the 2023-2025 WMP (Revision Notice PG&E-23-05), PG&E is developing a tool that we anticipate using in future regulatory filings. The tool, referred to as the Wildfire Benefit Cost Analysis (WBCA) tool, will compare the long-term costs of undergrounding to the long-term costs for other mitigations including overhead hardening combined with EPSS and PSPS and line removal with remote grid. The tool will consider capital installation costs and several categories of O&M costs such as patrols and inspections, emergency response, and vegetation management. The output from the tool will be a comparison of the long-term costs and benefits for different mitigation alternatives. b. As described in the 2023-2025 WMP (Revision Notice PG&E-23-05), PG&E is developing a tool that we anticipate using in future regulatory filings. The tool, referred to as the Wildfire Benefit Cost Analysis (WBCA) tool, will compare the long-term costs of undergrounding to the long-term costs for other mitigations including overhead hardening combined with EPSS and PSPS and line removal with remote grid. The tool will consider capital installation costs and several categories of O&M costs such as patrols and inspections, emergency response, and vegetation management. The output from the tool will be a comparison of the long-term costs and benefits for different mitigation alternatives. 1 PG&E is aware of various studies produced by academic institutions and third-parties that compare the costs and benefits of undergrounding to other mitigations. See, for example, Dynamic Grid Management Technologies Reduce Wildfire Adaptation Costs in the Electric Power Sector. PG&E has not reviewed and does not necessarily support the information or conclusions in these third-party and academic studies. 2 Note, in the 2023 GRC PG&E prepared data response GRC-2023- PhI_DR_TURN_154_Q014Supp01 that included an analysis of long-term operations and maintenance costs associated with its 2023 GRC undergrounding proposal. The system hardening milage assumptions and cost assumptions used in this analysis were based on information from the 2023 GRC and in many cases are no longer relevant. PG&E is identifying this study in order to be responsive to this data request but notes that the information in the study is outdated and is not representative of mileage and cost assumptions currently considered as part of our system hardening program. 3 In response to Area for Continuing Improvement (ACI) PG&E-25U-03, PG&E, SCE and SDG&E prepared a Joint IOU Grid Hardening Working Group Report: Update for 2026-2028 Wildfire Mitigation Plan (3/19/25) that is included with PG&E’s 2026-2028 Base WMP. Certain sections of the ACI discuss system hardening costs though the report does not include a direct comparison of the life cycle costs of undergrounding to overhead hardening. WMP-Discovery 2026-2028_DR_TURN_002-Q006 Page 3 c. As described in the 2023-2025 WMP (Revision Notice PG&E-23-05), PG&E is developing a tool that we anticipate using in future regulatory filings. The tool, referred to as the Wildfire Benefit Cost Analysis (WBCA) tool, will compare the longterm costs of undergrounding to the long-term costs for other mitigations including overhead hardening combined with EPSS and PSPS and line removal with remote grid and several categories of O&M costs such as patrols and inspections, emergency response, and vegetation management. The output from the tool will be a comparison of the long-term costs and benefits for different mitigation alternatives. d. As described in the 2023-2025 WMP (Revision Notice PG&E-23-05), PG&E is developing a tool that we anticipate using in future regulatory filings. The tool, referred to as the Wildfire Benefit Cost Analysis (WBCA) tool, will compare the long-term costs of undergrounding to the long-term costs for other mitigations including overhead hardening combined with EPSS and PSPS and line removal with remote grid. The tool will consider capital installation costs and several categories of O&M costs such as patrols and inspections, emergency response, and vegetation management. The output from the tool will be a comparison of the long-term costs and benefits for different mitigation alternatives. e. Pursuant to agreement with TURN on April 10, 2025, we will supplement this response on or before Monday, April 14, 2025. f. Pursuant to agreement with TURN on April 10, 2025, we will supplement this response on or before Monday, April 14, 2025. | A Mireille Fall-Fry | 2025-04-07 | 2025-04-10 | 2025-04-10 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-TURN_002.zip | 0 | No | 6 | Wildfire Mitigation Strategy Development | 6.1.3.2 | Activity Prioritization
15 | 6 | TURN | 002 | TURN_002 | 6(s) | Yes | TURN_002_Q6(s) | Section 6.1.3.2, page 134, states: “Overhead system hardening combined with operations mitigations EPSS and PSPS has a high-risk reduction benefit that is roughly comparable to that of undergrounding without these operational mitigations. PG&E continues to prefer undergrounding on high-risk circuits where feasible for several reasons. Undergrounding is permanent risk reduction that does not have the negative reliability impacts from PSPS and EPSS. Underground facilities are less likely to be damaged during winter storms by high winds and vegetation falling into lines damaging the facilities or other contact with the lines from third parties. Over time, undergrounding also has lower operations and maintenance expenses.” a. Please provide any studies or reports in PG&E’s possession that compare the long-term or life cycle costs of undergrounding with the costs of overhead hardening combined with EPSS and PSPS. b. Please provide any studies or reports in PG&E’s possession that compare the long-term or life cycle costs of undergrounding with the costs of overhead hardening combined with EPSS, PSPS, and remote grids to reduce the reliability impacts of EPSS and PSPS. c. Please provide any studies or reports in PG&E’s possession that compare the operations and maintenance expenses of undergrounding with overhead hardening. d. Please provide any studies or reports in PG&E’s possession that compare the operations and maintenance expenses of undergrounding with overhead hardening, combined with EPSS and PSPS. e. Please provide any studies or reports in PG&E’s possession that compare the reliability (e.g., SAIDI, SAIFI, CAIDI, etc.) of undergrounded vs. overhead hardened facilities. f. Please provide any studies or reports in PG&E’s possession that compare the reliability (e.g., SAIDI, SAIFI, CAIDI, etc.) of undergrounded vs. overhead hardened facilities – not including the reliability impacts of PSPS and EPSS. | e. PG&E analyzed the reliability performance on sections of circuits where we performed undergrounding work in 2022 and 2023 to quantify overall improvements to service reliability and showed approximately a 90% reduction in faults that resulted in sustained outages after undergrounding work was completed. Please see Section 8.2.2 of our 2026-2028 WMP. Please note that this analysis did not compare undergrounding to overhead hardening. Please refer to Section 6.2.1.2 for PG&E’s explanation of risk impacts of mitigation activities including covered conductor and undergrounding. PG&E is not currently aware of any studies or reports in PG&E’s possession that compare the reliability of undergrounded and overhead hardened facilities. Ultimately, we expect undergrounded lines to be less susceptible to outage-causing conditions associated with exposed overhead lines such as damage and/or vegetation contact from severe winds, animal contact, line slap or wire down. f. PG&E analyzed the reliability performance on sections of circuits where we performed undergrounding work in 2022 and 2023 to quantify overall improvements to service reliability and showed approximately a 90% reduction in faults that resulted in sustained outages after undergrounding work was completed. Please see Section 8.2.2 of our 2026-2028 WMP. Please note that this analysis did not compare undergrounding to overhead hardening. We are not aware of any studies or reports that are in our possession that compare the reliability of undergrounded vs. overhead hardened facilities—not including the reliability impacts of PSPS and EPSS; however, we expect undergrounded lines to be less susceptible to outage-causing conditions associated with exposed overhead lines such as damage and/or vegetation contact from severe winds, animal contact, line slap or wire down. | A Mireille Fall-Fry | 2025-04-07 | 2025-04-14 | 2025-04-14 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-TURN_002.zip | 0 | No | 6 | Wildfire Mitigation Strategy Development | 6.1.3.2 | Activity Prioritization
15 | 7 | TURN | 002 | TURN_002 | 7 | No | TURN_002_Q7 | The microgrids discussed in 8.2.7 are said to not impact reliability because they are not dependent on upstream lines. Do they increase reliability in areas where they have been installed and can they be deployed in conjunction with other hardening mitigations to minimize reliability concerns? | Section 8.2.7 addresses three microgrid related initiatives. Remote Grids Remote grids are not connected to the distribution system, as they place generation assets right at the customer locations and the upstream distribution line to that location is removed. Therefore, any reliability concerns due to outages from the upstream distribution system are eliminated in the Remote Grid system architecture. Temporary Distribution Microgrids These microgrids are not set to ‘automatically’ energize upon an outage condition; they are manually operated to isolate and energize the microgrid footprint once the PSPS event has de-energized the area, in a pre-planned, pre-staged, pre-resourced manner due to its inherent design. While it is possible that they could be utilized during unplanned or planned outages, it would be highly dependent upon whether the temporary generators are pre-staged at the location, whether the location is safe to actually energize in that outage, and whether the actual process of energizing the microgrid (and subsequently restoring back to source), is actually beneficial from an outage duration standpoint versus simply patrolling, repairing, and restoring the outage condition. Since these temporary distribution microgrids utilize reciprocating engine generating assets, the ability to ‘automatically’ energize these locations is not available. Community Microgrid Enablement Program and Microgrid Incentive Program WMP-Discovery 2026-2028_DR_TURN_002-Q007 Page 2 These microgrids are community driven and could increase reliability in areas where they are installed, but are dependent upon the condition and nature of the outages and the grid design of the microgrid footprint that determine its conditions for safe operations. Each microgrid being requested to be designed by these communities through these funds are unique and therefore their impact on reliability is dependent upon their design, operational capabilities, and the communities desired objectives. | A Mireille Fall-Fry | 2025-04-07 | 2025-04-10 | 2025-04-10 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-TURN_002.zip | 0 | No | 8 | Grid Design, Operations, and Maintenance | 8.2.7 | Microgrids
15 | 8 | TURN | 002 | TURN_002 | 8 | No | TURN_002_Q8 | Section 7, page 170, states that “during the July 2, 2024[,] PSPS event, we were able to reduce the event duration for some customers by temporarily re-energizing a line that serves a portion of the impacted customers[,]” and “[w]e may offer temporary re-energization during future PSPS events where conditions allow.” What conditions are necessary to replicate partial or temporary re-energization during PSPS events? | As described Section 7, page 170 “PSPS Lessons Learned” and explained in PG&E’s post de-energization report for the July 2, 2024 PSPS event, two severe wind events were forecasted to come in separate back to back waves. The first wind event meeting PSPS criteria occurred during overnight period of July 1-2 with a brief lull in the winds that occurred during the day of July 2. The second forecasted wave of critical fire weather conditions meeting our PSPS criteria was forecasted to occur later in the evening which allowed us to patrol and temporarily re-energize the portion of the customers who were impacted by the first wave to allow customers to cool their homes and charge their devices. On the evening of July 2, weather conditions deteriorated rapidly meeting our PSPS criteria and requiring us to de-energize a second time as a result of the second wave of severe weather conditions. Please see the following link for our July 2, 2024 post de-energization report: https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-andsupport/PGE_PSPS_Post-Event_Report_20240702-amended.pdf Generally, conditions that allow PG&E to temporarily re-energize during PSPS events are the lull in critical weather conditions. The lull period would need to have sufficient time for our crews to patrol following the weather all-clear. Weather “All-Clears” are called based on pre-defined, geographic areas and mapping of each weather station in each zone to that area. WMP-Discovery 2026-2028_DR_TURN_002-Q008 Page 2 Please note that the specific conditions that arose during the July 2, 2024 event allowed PG&E to temporarily re-energize a portion of the affected customers, but that such temporary re-energization is condition and event-specific and not a programmatic mitigation strategy to reduce PSPS duration | A Mireille Fall-Fry | 2025-04-07 | 2025-04-10 | 2025-04-10 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-TURN_002.zip | 0 | No | 7 | Public Safety Power Shutoff | 7 | Public Safety Power Shutoff
15 | 9 | TURN | 002 | TURN_002 | 9 | No | TURN_002_Q9 | Please fill in the values in the following table (all units are miles): | Please see attachment “WMP-Discovery2026-2028_DR_TURN_002-Q009Atch01.xlsx”. The following considerations and assumptions are applied to this response: • If a subproject spans multiple High Fire-Threat District (HFTD) tiers, the subproject is attributed to the higher tier (e.g., if a subproject falls under both Tier 2 and Tier 3, its mileage is attributed to Tier 3). • For data on overhead miles replaced by undergrounding: a. For subprojects that are 100% undergrounding with available overhead removal data, the reported figures reflect the overhead miles removed. b. For hybrid subprojects (partially underground and a combination of overhead hardening and/or line removal) or cases where overhead removal data is unavailable, miles are calculated using a conversion factor: 1 mile of overhead equals 1.25 miles of undergrounding. WMP-Discovery 2026-2028_DR_TURN_002-Q009 Page 2 • Since the template does not request miles completed outside HFTDs, this response excludes system hardening work under the Community Rebuild program. • The original table requested both 2023 actuals and planned miles. We updated our response to include actuals through 2024 and planned work for 2025. | A Mireille Fall-Fry | 2025-04-07 | 2025-04-10 | 2025-04-10 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-TURN_002.zip | 1 | No | 8 | Grid Design, Operations, and Maintenance | 8.2.2 | Undergrounding of Electric Lines and/or Equipment
15 | 10 | TURN | 002 | TURN_002 | 10 | No | TURN_002_Q10 | Please provide a narrative explanation of the decision tree shown in figure 8.2.1-2, including any criteria that PG&E intends to use to determine if conditions in the decision tree are met. a. Figure 8.2.1-2 appears to indicate that UG is preferred when CBR > 1 and within 50% of the OH + EPSS CBR and UG NB > OH NB. Please explain the basis for the figure of 50%. b. It appears that the decision tree begins with UG as the default option and only moves to alternatives when certain criteria are not met. Why doesn’t PG&E begin with the more cost-effective hybrid approach and move to UG when absolutely necessary? c. Please explain the tree strike scores and how they are determined? Why is a score of 6+ significant? d. Please identify and explain and each and every criterion that is considered in determining “Are there Egress/Ingress concerns expressed by PSS team? Please provide a narrative explanation of the types of concerns and how they impact risk. e. Please provide a narrative explanation of the PSPS polygon and the effect on CPZ. f. At any point in the decision tree, are the hybrid project CBRs recalculated based on different permutations/combinations? | a. PG&E is incorporating the Cost-Benefit Ratio (CBR) into our decision-making framework in anticipation of this requirement as part of the 10-year Electrical Undergrounding Plan (EUP). The Commission has stated that “the utility is not bound to select its mitigation strategy based solely on the CBRs produced by the Cost-Benefit Approach,” supporting the concept that CBR does not need to be the sole determinant of risk mitigation strategies.1 This is because an over-emphasis on CBR devalues high cost / high benefit projects. CBR does not consider the absolute benefits and holistic value of permanent risk mitigations, and when used as the sole criteria, results in situations where risk is permanently left on the system, including on circuit segments where undergrounding’s benefits are greater than those of overhead hardening. In our decision tree, CBR is used as the primary criteria for selecting mitigation measures. However, for undergrounding (UG) projects where the benefits are morefavorable than OH hardening + EPSS, these projects will also be considered, provided their cost-benefit ratio falls within an acceptable range relative to the CBR of overhead hardening projects. The 50% threshold is a discretionary value intended to ensure that CBR remains a key consideration, while also allowing for the engineering team to weigh the full range of benefits, including mitigation of tree strike risks, reliability risks created by operational mitigations, and ingress/egress considerations, which are often not fully quantified in CBR or risk calculations. In these cases, the CBR must also be greater than 1, indicating the benefits of the mitigation outweigh its costs. b. PG&E’s approach to system hardening has been, and continues to be, to begin with the mitigation alternative that permanently reduces the greatest amount of risk, which is undergrounding and line removal with remote grid. If these mitigations do not meet our economic decision criteria, we consider overhead hardening where it may be considered more effective than undergrounding. c. PG&E describes what the tree strikes scores are and how they are calculated in our 2022 WMP (PG&E’s Revised 2022 WMP, July 26, 2022, pages 584-585). The scores represent the number of fall-in trees that can touch and break a hardened overhead line. Scores greater than or equal to 6 represent a moderate or greater tree fall-in risk. d. The PSS considers many factors when evaluating ingress and egress concerns, and it is not possible to identify each and every criterion and how that criterion particularly impacts risk in every situation. The specific facts and circumstances of each situation must be considered on a case by case basis. The specific facts and circumstances of a case, when taken together, form our understanding of the real time risk associated with a particular area. Some of the factors considered include, but are not limited to:: • Population density • Time of day (there are differences between evacuating communities at night when most people are at home compared to during the day when fewer people are at home) • Amount of time the public would need to evacuate or shelter in place • Notifications and information made available to the public • Road infrastructure (e.g., road size, number of lanes, type of surface, destination) 1 Decision (D.) 22-12-027, Appendix A, Row 26. • Fuel types along an evacuation corridor (e.g., grass vs. brush vs. timber) • Elevated Weather conditions (e.g., red flag days including high temperatures, high winds, low relative humidities) • Topography/terrain (do evacuation routes place evacuees in danger due to steep slopes, drainages, and chimneys along a corridor which are often associated with extreme fire behavior) • Human factors (e.g., elderly, special needs, evacuating large and small pets, knowledge or experience of citizens living in high fire hazard areas) • Location of overhead electrical assets (e.g., poles proximity to the road’s shoulder and conductor crossings over those ingress/egress thoroughfares should they become impacted by fire and fail onto the evacuation corridor) • Firefighting ingress (e.g., number, type, size of equipment, staging areas, etc. e. A PSPS Polygon is a geographical area identified for each PSPS event in the lookback period that identifies which of the overhead assets will have required deenergization. Sometimes the polygon will encompass the entire CPZ, other times just parts. For those instances where it encompasses the full zone, the underground option is considered the PSPS mitigation. For those instances where the underground option does not meet our decision criteria and it has events where only parts of the CPZ is impacted, a more targeted approach to PSPS mitigation is considered for underground inclusion. f. There are potentially three iterations of the hybrid scenario in which a new CBR may be calculated in the decision tree: 1. The first time is when all three risks are considered (PSPS, Ingress/Egress, Tree Fall-in). 2. If that does not meet the economic decision criteria, the underground required for PSPS mitigation is removed and a hybrid scenario considering two risks are considered (Ingress/Egress and Tree Fall-in). 3. If that does not meet the economic decision criteria, the final hybrid scenario considers only the tree fall-in risk. | A Mireille Fall-Fry | 2025-04-07 | 2025-04-10 | 2025-04-10 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-TURN_002.zip | 0 | No | 8 | Grid Design, Operations, and Maintenance | 8.2.1-2 | Covered Conductor Installation
15 | 11 | OEIS | 001 | OEIS_001 | 1 | No | OEIS_001_Q1 | Regarding Vegetation Management QA and QC Units On page 410 of its 2026-2028 WMP, PG&E lists “inspections” as the “Population size/Sample Unit” for VM-08D, VM-08T, VM-22D, and VM-22T. However, in the “Sample Size” column, PG&E uses a different unit, listing the number of miles (VM-08D, VM-08T, and VM-22T) and spans (VM-22D), that it will audit. a. Define what constitutes an “inspection” unit. b. Clarify whether PG&E is auditing all work performed and not performed along the length of the sample spans/miles, or discrete documented “inspections” within those spans/miles. c. If PG&E audits discrete inspections rather than the entire length of a span/mile, reproduce Table 9-6 “Vegetation Management QA and QC Activity” with: i. An estimated total number of inspections it could potentially audit under the 2026, 2027, and 2028 “Population Size” columns. ii. An estimated number of inspections PG&E plans to audit under the 2026, 2027, and 2028 “Sample Size” columns. d. For VM-22T units, PG&E lists “miles” in “Population Size” column, “spans” in “Sample Size,” and “Inspections” in the “Population/Sample Unit.” Clarify the unit used for VM-22T. | a. For VM-22 D&T, an inspection unit will be the location1 of overhead electric facilities inspected by Vegetation Management (VM) Operations. b. For VM-08 D&T, an inspection unit will consist of overhead line segments.QA/QC work will be performed along the length of the sample spans/miles/locations. Both, post VM inspection and/or post Tree work activities can be evaluated. c. N/A; please see response B. i. N/A ii. N/A d. The population provides the total estimated volume of overhead transmission facilities in HFTD. The sample size is the minimum volume of VM QC transmission inspected locations to verify. As noted above, for VM-22T, an inspection unit will be the location of overhead electric facilities inspected by Vegetation Management (VM) Operations. See the footnote above for more detail. | Nathan Poon | 2025-04-08 | 2025-04-11 | 2025-04-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_001.zip | 0 | No | 9 | Vegetation Management & Inspections | 9.11 | Changes to QA/QC
15 | 12 | OEIS | 001 | OEIS_001 | 2 | No | OEIS_001_Q2 | Regarding Vegetation Management QA and QC Outside the HFTD On page 410 of its 2026-2028 WMP, PG&E specifies that 100% of QA/QC samples are from locations within the HFTD. a. Does PG&E perform QA/QC in its HFRA? i. If yes, describe its QA/QC program in its HFRA. ii. If not, why does it not extend its QA/QC program to its HFRA? b. Does PG&E perform QA/QC in non-HFTD areas? i. If yes, describe its QA/QC program in non-HFTD areas. ii. If not, why does it not extend its QA/QC program to non-HFTD areas? | a. Yes. QC and QA will perform assessments in HFRA. i. PG&E’s QA/QC will be conducted the same in HFRA as elsewhere. ii. N/A b. Yes. QC and QA will perform assessments in both HFTD and non-HFTD areas. i. PG&E’s QA and QC will be conducted the same in Non-HFTD as elsewhere. ii. N/A | Nathan Poon | 2025-04-08 | 2025-04-11 | 2025-04-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_001.zip | 0 | No | 9 | Vegetation Management & Inspections | 9.11 | Changes to QA/QC
15 | 12 | OEIS | 001 | OEIS_001 | 2(a) | Yes | OEIS_001_Q2(a) | Regarding Vegetation Management QA and QC Outside the HFTD On page 410 of its 2026-2028 WMP, PG&E specifies that 100% of QA/QC samples are from locations within the HFTD. a. Does PG&E perform QA/QC in its HFRA? i. If yes, describe its QA/QC program in its HFRA. ii. If not, why does it not extend its QA/QC program to its HFRA? b. Does PG&E perform QA/QC in non-HFTD areas? i. If yes, describe its QA/QC program in non-HFTD areas. ii. If not, why does it not extend its QA/QC program to non-HFTD areas? | a. Yes. QC and QA will perform assessments in HFRA. i. PG&E’s QA/QC will be conducted the same in HFRA as elsewhere. ii. N/A b. Yes. QA will perform assessments systemwide, including HFTD, HFRA and nonHFTD/non-HFRA. However, QA will only count units in HFTD and HFRA areas towards WMP targets. QC will only perform assessments in HFTD and HFRA areas. i. PG&E’s QA and QC will be conducted the same in non-HFTD as elsewhere. ii. N/A | Nathan Poon | 2025-04-08 | 2025-04-16 | 2025-04-16 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_001.zip | 0 | No | 9 | Vegetation Management & Inspections | 9.11 | Changes to QA/QC
16 | 12 | SPD | 002 | SPD_002 | 4 | No | SPD_002_Q4 | Every Friday by noon, submit all of the materials requested in Questions 1-3 to Kiteworks. Each weekly response should be packaged in a single zip file and organized according to the following folder structure: a. Party Name (i.e. Energy Safety, Cal Advocates, etc.) b. DR Name (i.e. SPD-PGE-WMP2026-001) i. Place the data request responses in this folder. c. Attachments i. Place any attachments to the data request responses in this folder. | PG&E objects to this request on the grounds that continuing discovery obligations are not permitted under California law. Biles v. Exxon Mobil Corp., 124 Cal.App.4th 1315, 1328 (2004); Code Civ. Proc. § 2030.060(g). Notwithstanding and without waiving this objection, PG&E responds as follows. Discovery provided to Energy Safety and other requesting parties is publicly posted and available on PG&E’s website at Community Wildfire Safety Program. The native format version (Excel) of PG&E’s WMP DR Summary is updated on our website each Thursday. We will provide confidential versions of any confidential responses and/or attachments submitted to Energy Safety or any other party every Friday. We will do our best to provide such responses by noon each Friday, or as soon as is reasonably possible. | Eddie Schmitt | 2025-04-16 | 2025-04-18 | 2025-04-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_002.zip | 0 | No | N/A | N/A | N/A | N/A
15 | 13 | OEIS | 001 | OEIS_001 | 3 | No | OEIS_001_Q3 | Regarding Vegetation Management QA and QC Target Pass Rates On page 410 of its 2026-2028 WMP, PG&E sets a target pass rate for Vegetation Management Quality Assurance (VMQA) of 97%. On page 411, PG&E writes that VMQA has a “99% estimated level of compliance.” a. How does PG&E use the “estimated level of compliance” in its operations? b. Explain why the estimated level of compliance differs from the target pass rate. | a. The 99% estimated level of compliance is the predicted baseline score based on historic audit data. This estimated level of compliance is then entered into a sampling formula along with error rate and confidence level to derive an appropriate sample mileage. For 2025, we have been using between a 2.5% and 3.25% margin of error to account for variability in the audit sampling (since we aren’t looking at 100% of the line mileage in a given area). After the conclusion of the audit, we calculate the true margin of error since we’d have a collected grown-in tree population as a denominator at that point (this is because we use line mileage as a proxy for tree populations to get a minimum amount of mileage to review). At the conclusion of the audit, if the actual margin of error is less than the estimated margin of error used, the audit could be considered statistically valid. Basically, the margin of error would account for any outlier audits where the compliance score was well below 99%. b. Historical VMQA audit shows that system wide, scores average at or above 99% compliance. This is used strictly to derive audit mileage sample. The actual achieved pass rate is still a variable dependent on Operational Performance and independent of what VMQA expected to see. Using 99% as a baseline estimated level of compliance is consistent with the audit scores that QA has observed historically. | Nathan Poon | 2025-04-08 | 2025-04-11 | 2025-04-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_001.zip | 0 | No | 9 | Vegetation Management & Inspections | 9.11 | Changes to QA/QC
15 | 14 | OEIS | 001 | OEIS_001 | 4 | No | OEIS_001_Q4 | Regarding Vegetation Management Field Quality Control On page 415 of its 2026-2028 WMP, PG&E states that it discontinued its Field Quality Control (FQC) because it is redundant to “ongoing knowledge checks.” a. Describe the similarities and differences between FQC and “ongoing knowledge checks.” b. List the redundancies between FQC and “ongoing knowledge checks.” c. For non-redundant aspects: i. Explain whether and how PG&E accounts for these aspects in other ways (e.g., other QA/QC programs). ii. If PG&E does not account for these aspects in other ways, explain why PG&E discontinued | a. Vegetation Management (VM) Knowledge Checks i. VM operations new hire check-ins – required monthly ii. VM construction management development of a Vegetation Management Inspector (VMI) assessment yard with both field and desk review components iii. Periodic field visits of VMI from their PG&E leadership team or delegates Field Quality Control (FQC) Assessments i. Performs on-site knowledge assessments of VMI using a defined checklist applicable to specific VM work scopes ii. FQC scope required annual assessment of at least 90% of the eligible population WMP-Discovery 2026-2028_DR_OEIS_001-Q004 Page 2 iii. FQC scope included direct observation of VMI inspection work behaviors and adherence/non-adherence to applicable guidance documentation b. FQC performs on-site knowledge assessments of VMI using a standardized checklist. The VMI assessment yard will perform knowledge assessments of VMI using standardized testing methods. FQC performs on-site field observations of VMI. The existing Vegetation Operation Inspection (VOI) team and internal operations field leadership perform periodic field visits with VMI. c. For non-redundant aspects: i. FQC captures VMI adherence to applicable regulatory requirements and internal guidance documentation and publishes the results in a reporting space. QA/QC can be used as an analog for VMI performance by auditing the VMI work product. ii. N/A | Nathan Poon | 2025-04-08 | 2025-04-11 | 2025-04-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_001.zip | 0 | No | 9 | Vegetation Management & Inspections | 9.11 | Field Quality Control
15 | 15 | OEIS | 001 | OEIS_001 | 5 | No | OEIS_001_Q5 | Regarding Vegetation Management Field Reviews On page 411 of its 2026-2028 WMP, PG&E describes its Vegetation Management Quality Control (VMQC) program. PG&E states that it “performs field reviews after VM Operations has completed their inspections and/or tree work to verify the applicable procedural scope has been met.” a. Does PG&E’s record keeping system distinguish between field reviews of inspections and field reviews of tree work? i. If yes, list the sample size for distribution (VM-22D) and transmission (VM-22T) of: A. Inspection quality control field reviews; B. Tree work quality control field reviews. ii. Explain why PG&E aggregates quality control of two activities, inspections and tree work, into one target (e.g., VM-22D in Table 9-6, page 410). | a. No; PG&E’s VMQC program’s record keeping system does not distinguish between field reviews of inspections and field reviews of tree work. i. N/A ii. PG&E aggregates quality control of two activities, inspections, and tree work, into one target because the VMQC assessment criteria allows both VM inspection and tree work activities to be evaluated to ensure procedural and regulatory compliance is met for the annual routine cycle. | Nathan Poon | 2025-04-08 | 2025-04-11 | 2025-04-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_001.zip | 0 | No | 9 | Vegetation Management & Inspections | 9.11 | QA/QC Procedures
15 | 16 | OEIS | 001 | OEIS_001 | 6 | No | OEIS_001_Q6 | Regarding Vegetation Management Work Orders On page 417 of its 2026-2028 Base WMP, PG&E lists past-due work orders in Table 9-7 and 9-8 and notes that “constrained units are excluded” from both tables. a. Provide Tables 9-7 and 9-8 including constrained work orders. b. List the number of past due work orders constrained by the followed categories: i. Biological and Cultural ii. Customer iii. Encroachment Permit iv. Environmental Permit v. Operational c. For Encroachment and Environmental Permit constraints, list the number of past due work orders by the permit needed to remedy the constraint. | a. Please note, PG&E does not consider constrained units as past due. Please see table(s) below for a breakdown of constrained units by constrained category and HFTD Tier/Priority level. | Nathan Poon | 2025-04-08 | 2025-04-11 | 2025-04-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_001.zip | 0 | No | 9 | Vegetation Management & Inspections | 9.12 | Priority Assignment
15 | 17 | OEIS | 001 | OEIS_001 | 7 | No | OEIS_001_Q7 | Regarding Vegetation Management Training and Retention On pages 422-423 in its 2026-2028 Base WMP, PG&E describes “formal courses (instructor-led and web-based) and on-the-job training” in describing vegetation management personnel training. a. Describe how PG&E invests in the career advancement of its vegetation management personnel. b. Describe PG&E’s efforts to retain vegetation management personnel. | a. PG&E invests in the career advancement of its vegetation management (VM) personnel by covering both time and cost of certifications including basic Arborist Certification and advanced qualifications like Tree Risk Assessment Qualified (TRAQ). PG&E also helps to streamline the certification process and aid personnel in their Arborist certification test preparation, by hosting weekly International Society of Arboriculture (ISA) Arborist Certification study group calls. For current Arborists, PG&E collaborates with the Western Chapter ISA to schedule dedicated TRAQ qualification training days, ensuring easy access to the course. b. PG&E has unionized the Vegetation Management Inspector (VMI) and Vegetation Operations Inspector (VOI) positions to enhance retention of VM personnel. This initiative has resulted in increased wages and established clear career paths for advancement. | Nathan Poon | 2025-04-08 | 2025-04-11 | 2025-04-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_001.zip | 0 | No | 9 | Vegetation Management & Inspections | 9.13 | VM Training & Retention
15 | 18 | OEIS | 001 | OEIS_001 | 8 | No | OEIS_001_Q8 | Regarding PG&E-23B-18. Improving Vegetation Management Inspector Qualifications a. On page 590 of its 2026-2028 WMP, PG&E discusses how it will improve the qualifications and training of VM inspectors. PG&E writes that it has “implemented a process of profiling training courses within the VM organization based on personnel role and internal employee or contractor status.” i. Describe the “profiling” process. ii. Define "profiling" in the context of "profiling training courses.” | a. i. With the profiling process, Vegetation Management personnel are automatically assigned trainings based on their job titles. This process automatically adjusts training requirements when individuals are hired or change positions. ii. Profiling in the context of “Profiling Training Courses” is defined as linking specific trainings to job titles. | Nathan Poon | 2025-04-08 | 2025-04-11 | 2025-04-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_001.zip | 0 | No | 9 | Vegetation Management & Inspections | 9.13 | VM Inspector Qualifications
15 | 19 | OEIS | 001 | OEIS_001 | 9 | No | OEIS_001_Q9 | Regarding Distribution Routine Patrol Program On page 363, PG&E’s WMP states “PG&E is in the process of evaluating which component(s) of the [Focused Tree Inspection (FTI)] and [Tree Removal Inventory (TRI)] scope will be incorporated into the Distribution Routine Patrol Program. This analysis will be based on findings from efficacy studies planned to be performed in 2025. PG&E will incorporate VMOM into activities described in [Activities Based on Weather Conditions].” a. Does PG&E have specific, measurable, achievable, relevant, and time-bound (SMART) targets for evaluating which component(s) of the FTI and TRI scope will be incorporated into the Distribution Routine Patrol Program, the efficacy study, and incorporating VMOM into Activities Based on Weather Conditions? i. If so, provide those SMART targets. ii. If not, explain why PG&E does not have SMART targets for its plan to consolidate its vegetation inspection programs for distribution circuits in the HFTD. b. Provide the procedures for these efficacy studies. c. When does PG&E expect to determine which components of the FTI and TRI scope will be incorporated into the Distribution Routine Patrol Program? d. When does PG&E expect its new Distribution Routine Patrol Program procedure that | On page 363, PG&E’s WMP states “PG&E is in the process of evaluating which component(s) of the [Focused Tree Inspection (FTI)] and [Tree Removal Inventory (TRI)] scope will be incorporated into the Distribution Routine Patrol Program. This analysis will be based on findings from efficacy studies planned to be performed in 2025. PG&E will incorporate VMOM into activities described in [Activities Based on Weather Conditions].” a. Does PG&E have specific, measurable, achievable, relevant, and time-bound (SMART) targets for evaluating which component(s) of the FTI and TRI scope will be incorporated into the Distribution Routine Patrol Program, the efficacy study, and incorporating VMOM into Activities Based on Weather Conditions? i. If so, provide those SMART targets. ii. If not, explain why PG&E does not have SMART targets for its plan to consolidate its vegetation inspection programs for distribution circuits in the HFTD. b. Provide the procedures for these efficacy studies. c. When does PG&E expect to determine which components of the FTI and TRI scope will be incorporated into the Distribution Routine Patrol Program? d. When does PG&E expect its new Distribution Routine Patrol Program procedure that includes components of FTI and TRI will be effective (i.e., used by personnel in the field)? | Nathan Poon | 2025-04-08 | 2025-04-11 | 2025-04-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_001.zip | 0 | No | 9 | Vegetation Management & Inspections | 9.2.1 | Distribution Routine Patrol Program
15 | 20 | OEIS | 001 | OEIS_001 | 10 | No | OEIS_001_Q10 | Regarding Pruning and Removal On page 377, PG&E’s WMP states “PG&E is examining work prioritization categories beyond the P1, P2, and Routine designation.” For this examination: a. Provide examination criteria. b. Provide descriptions of work prioritization categories under examination. c. Provide a description of the parts of the service territory these new designations will apply to including the reason these parts of the service territory would benefit from additional prioritization categories. d. Provide a schedule for and anticipated completion date of this examination. e. Provide an anticipated effective date of the new prioritization category scheme (i.e., when the prioritization scheme will be used by personnel in the field). | a. The examination criteria are based on the completion timelines associated with P1, P2, and Routine designations. If appropriate, additional work prioritization categories would be introduced. b. The current Work Prioritization categories are defined in Priority Tag Procedure TD7102P-17. The current categories are under examination. Additional categories may be considered for creation. c. The consideration for a new work prioritization category could apply to any part of the service territory. A location of higher wildfire risk could have a higher work prioritization designation. d. This examination is a continuous improvement activity with no anticipated completion date at this time. We expect the examination through the end of 2025 to inform our 2026-2028 WMP activities. WMP-Discovery 2026-2028_DR_OEIS_001-Q010 Page 2 e. As the examination progresses, if PG&E determines to include any additional work prioritization categories, implementation of those additional categories will subsequently need to take into consideration the management of change to be utilized. We do not have an anticipated effective date at this time. | Nathan Poon | 2025-04-08 | 2025-04-11 | 2025-04-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_001.zip | 0 | No | 9 | Vegetation Management & Inspections | 9.3 | Pruning & Removal
15 | 21 | OEIS | 001 | OEIS_001 | 11 | No | OEIS_001_Q11 | Regarding Enterprise System Qualitative Targets On pages 535-536 of its WMP, PG&E provides qualitative target ES-01. a. Provide the current data quality, profiling, and monitoring practices used for VM data. b. Provide the data quality, profiling, and monitoring practices planned for use under ES-01. c. List the datasets that have been identified as critical for VM execution. | a. Our current data quality, profiling, and monitoring practices occur in three phases: • MANAGE o Define – develop dataset inventory o Own – identify owners for the critical dataset o Metadata – provide the information needed to use the data o Critical data elements – list the critical data elements to be managed. o Standards – define required data standards needed o Profile – analyze the critical data elements o Rules – define business rules to ensure the data meets quality requirements o Retain – determine retention timeline length for the dataset • MITIGATE o Test – build tests to measure quality data WMP-Discovery 2026-2028_DR_OEIS_001-Q011 Page 2 o Measure – identify data that fails quality standards o Control – identify control points in the process that need to be managed o Cleanse – conduct actions to remove or improve poor quality data o Monitor – ensure remediation actions complete and data maintains quality over time o Dispose – determine when and how to dispose of dataset records • MAINTAIN o Stability – ensure data maintains its quality over time o Maturity – update the process, the controls, and the data b. We will continue to apply the prior mentioned practices of MANAGE, MITIGATE, MAINTAIN against remaining unmanaged critical data sets. c. There are currently 28 critical datasets for VM execution. The number and specific datasets are subject to change as execution needs change. Please see list below: • Account • Asset • AssignedResource • Case • CaseComment • CaseTeamMember • Contact • Project_Pole • Project_VegPoint • ServiceAppointment • Task • User • VegPoint • VM_Alert__c • VM_CaseHistory • VM_Observation_Category__c • VM_Observed_Defects__C • VM_Pole_Parcel__C • VM_Prescription__c • VM_PrescriptionHistory • VM_Project__c • VM_Project_Span__c • VM_Span_Parcel__C • VM_Tree_Risk_Assessment__c • VM_Work_Code__c • VM_WorkOrderLineItemHistory • WorkOrder • WorkOrderLineItem | Nathan Poon | 2025-04-08 | 2025-04-11 | 2025-04-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_001.zip | 0 | No | 12 | Enterprise Systems | 12.2 | Summary of Enterprise Systems
15 | 22 | OEIS | 001 | OEIS_001 | 12 | No | OEIS_001_Q12 | Regarding PG&E-25U-08. Reinspection of Trees in Tree Removal Inventory On page 582 of its WMP, PG&E provides a response to PG&E-25U-08 indicating “In late 2024, PG&E began planning a pilot to re-evaluate trees listed for work within Shasta County.” a. Provide pilot study procedure(s). b. Provide pilot schedule. c. Provide any study results. | a. There is no formalized procedure specific to this pilot. PG&E followed TD-7102P01, Distribution Inspection Procedure and attachment 6 (Tree Removal Inventory program) process for a Level 2 inspection by a Tree Risk Assessment Qualified (TRAQ) -certified arborist. This process was followed for all Tree Assessment tool (TAT) Abate vegetation points with a record of “Yes” in the system of record within Shasta County. b. The field execution of the Pilot began in Quarter 4 of 2024 for Level 2 Inspections performed by a TRAQ-certified arborist and the subsequent Board-Certified Master Arborist review. • All Level 2 field inspections by TRAQ-certified arborists were completed in Q1 2025. • Any remaining Board-Certified Master Arborist reviews are expected to be completed in Q2 2025. Please note: Subsequent to the field collection of data, PG&E plans to analyze the results of the pilot and evaluate recommended next steps by Q4 2025. WMP-Discovery 2026-2028_DR_OEIS_001-Q012 Page 2 c. The study is pending completion and subsequent documentation. Documentation will be analyzed by Q4 2025 for recommendations. The recommendations resulting from the findings of the pilot are also dependent on continued feedback from internal or external stakeholders. | Nathan Poon | 2025-04-08 | 2025-04-11 | 2025-04-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_001.zip | 0 | No | 9 | Vegetation Management & Inspections | 9.2.1 | Reinspection of Trees
15 | 23 | OEIS | 001 | OEIS_001 | 13 | No | OEIS_001_Q13 | Regarding Wood and Slash Management Tracking Section 9.5.3 of PG&E's 2026-2028 WMP states that "Debris management is completed in coordination with tree work across PG&E's service area…Wood management that is conducted in response to a customer request is typically completed within 90 days of tree work project completion across PG&E's service area, unless affected by weather, field conditions, or other constraints" (p. 381). a. Does PG&E document and track the management of slash and woody debris that is a byproduct of VM work? i. If yes: A. Describe the documentation and record keeping methods used. B. List the data fields that are recorded as part of the wood and slash debris management tracking process. ii. If no, explain: A. How PG&E assures wood and slash management is completed in all VM treatment areas according to the Utility Standard, TD-7116S and Utility Procedure, TD-7116P-01. B. How PG&E plans to integrate wood and slash debris management tracking into internal procedures similar to tracking the completion of other VM orders. | a. No, PG&E does not track the management of slash and woody debris, vegetative material less than 4 inches in diameter. i. N/A WMP-Discovery 2026-2028_DR_OEIS_001-Q013 Page 2 ii. See below: A. There is no language in the Utility Standard, TD-7116S or the Utility Procedure, TD-7116P-01 requiring vegetation management (VM) crews to track the management of slash and woody debris. PG&E directs its VM crews to complete debris treatment in coordination with the tree work. This expectation is clearly defined in our contract specification, “Specific Conditions No. 5404 for Vegetation Management (VM) Tree Trimming and Brush Removal.” When tree work is logged as complete in the database by VM crews, it implies that the crews have also completed the associated debris treatment. For reference, here is a screenshot of the contract language from Exhibit J, Page 67 of the “Specific Conditions No. 5404 for Vegetation Management (VM) Tree Trimming and Brush Removal.”: B. PG&E has no plans to integrate wood and slash debris management tracking into internal procedures. | Nathan Poon | 2025-04-08 | 2025-04-11 | 2025-04-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_001.zip | 0 | No | 9 | Vegetation Management & Inspections | 9.5 | Wood & Slash Management Tracking
15 | 24 | OEIS | 001 | OEIS_001 | 14 | No | OEIS_001_Q14 | Regarding Wood and Slash Management Impacts on Wildfire Risk PG&E-23B-16, Updating Wood Management Procedure, requires an updated Wood Management Procedure that “[c]onsiders the wildfire risk related to accumulated fuels generated by PG&E’s vegetation management activities." On page 586 of its WMP, PG&E states that updates to Utility Standard, TD-7116S and Utility Procedure, TD-7116P-01 include “alignment to industry practices related to accumulated fuels generated by VM activities. a. Clarify what industry practices PG&E is referring to. b. Explain how wildfire risk related to accumulated fuels generated by PG&E’s vegetation management activities is considered in Utility Standard, TD-7116S and Utility Procedure, TD-7116P-01. | a. The utility vegetation management industry is increasingly concerned about wood remaining from line clearance activities. In response to these concerns, we are aligning with industry practices which includes expanding wood management offerings to all customers and land managers upon request, within a defined scope and across all vegetation management programs. This alignment with industry best practices is documented in our response to question 15 specifically referencing prior and futured scheduled benchmarking activities with SDG&E, SCE and Liberty Utilities. b. In addition to expanding wood management offerings as described above, our Wood Management Procedure aligns with defensible space requirements and expectations outlined in the State of California Public Resources Code (PRC) Section 4291 and California Code of Regulation (CCR) Title 14 Section 1299.03. Our scope includes wood management within the following zones: • 100 feet of a human inhabitable structure, structure footprint, or campsite. WMP-Discovery 2026-2028_DR_OEIS_001-Q014 Page 2 • Vegetative material located within 15 feet of the access road to a human inhabitable structure, structure footprint, or campsite. • Vegetative material is located within 15 feet of an outbuilding or propane tank. | Nathan Poon | 2025-04-08 | 2025-04-11 | 2025-04-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_001.zip | 0 | No | 9 | Vegetation Management & Inspections | 9.5 | Wood & Slash Management Tracking
15 | 25 | OEIS | 001 | OEIS_001 | 15 | No | OEIS_001_Q15 | Regarding Wood and Slash Management Benchmarking In response to PG&E-23B-16, Updating Wood Management Procedure, PG&E states that benchmarking meetings with SCE and SDG&E to discuss wood management began in 2023 (p. 586) and benchmarking is targeted to be complete by September 30, 2028 (p. 354). These discussions with SCE and SDG&E and a review of Liberty's procedure have "helped shape" the new Wood Management Standard and Procedure, though, "absent a consistent approach across utilities, [PG&E] aligned and updated our Standard and Procedure to reflect the common ground of PRC 4291" (p. 586). Future benchmarking meeting topics are expected to include consideration of whether each utility's respective wood management policy meet the required progress defined in the area for continued improvement (p. 587). a. Explain why PG&E plans for the benchmarking effort spans over five years. b. Describe common and uncommon practices between PG&E, SCE, and Liberty that have been identified during the benchmarking effort, explain how each uncommon practice was determined to be included or excluded from PG&E's updated Utility Standard, TD-7116S and Utility Procedure, TD-7116P-01. c. Describe specific outcomes from the benchmarking effort and clarify how these outcomes relate to specific updates in the Utility Standard, TD-7116S and Utility Procedure, TD-7116P-01. d. Compare PG&E's past wood management procedure (prior to benchmarking) to the updated wood management procedure and describe how the updates to the procedure meet the required progress of PG&E-23B-16. | a. The utility vegetation management industry is increasingly concerned about wood remaining from line clearance activities. In response to these concerns, we are aligning with industry practices which includes expanding wood management offerings to all customers and land managers upon request, within a defined scope and across all vegetation management programs. This alignment with industry best practices is documented in our response to question 15 specifically referencing prior and futured scheduled benchmarking activities with SDG&E, SCE and Liberty Utilities. b. In addition to expanding wood management offerings as described above, our Wood Management Procedure aligns with defensible space requirements and expectations outlined in the State of California Public Resources Code (PRC) Section 4291 and California Code of Regulation (CCR) Title 14 Section 1299.03. Our scope includes wood management within the following zones: • 100 feet of a human inhabitable structure, structure footprint, or campsite. • Vegetative material located within 15 feet of the access road to a human inhabitable structure, structure footprint, or campsite. • Vegetative material is located within 15 feet of an outbuilding or propane tank. | Nathan Poon | 2025-04-08 | 2025-04-11 | 2025-04-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_001.zip | 0 | No | 9 | Vegetation Management & Inspections | 9.5 | Wood & Slash Management Tracking
15 | 26 | OEIS | 001 | OEIS_001 | 16 | No | OEIS_001_Q16 | Regarding Integrated Vegetation Management Reassessment and Treatment Timing In Section 9.7.3 IVM Scheduling, PG&E states that, "For TIVM, previously worked ROWs are reassessed every 2-5 years" (p. 386). The 2026-2028 WMP does not described how the need for retreatment of Transmission ROWs is determined. In contrast, PG&E’s 2023-2025 WMP provided threshold triggers for retreatment of vegetation, including "incompatible vegetation exceeding 3 ft. in height and/or when incompatible vegetation is greater than 50 percent ground coverage within the ROW" (p. 695). a. Describe the rationale conducting reassessment inspection on a 2-5 year cycle and clarify what factors (e.g, species, growth rates, percent cover, height) were used to define this timeframe. b. Clarify the threshold triggers PG&E will use to determine the need for retreatment of vegetation in transmission ROWs during the 2026-2028 WMP cycle. | a. Historically, the rationale for a 2 to 5-year cycle of reassessment was due to it being known that incompatible vegetation will regrow within that timeframe. With the availability of LiDAR data, vegetation height and density conditions are analyzed each year. This data also allows for year-over-year growth analysis by span. The vegetation conditions are then used for work plan development using the inputs described below. As stated in the 2026-2028 WMP, PG&E schedules Transmission IVM (TIVM) ROW maintenance based on outputs of the work plan development described in the program overview (see 9.7.1 pp. 384). WMP-Discovery 2026-2028_DR_OEIS_001-Q016 Page 2 b. The quantity of TIVM work varies by year and is dependent on the resources available. PG&E considers the following inputs to determine the need for retreatment of vegetation in transmission ROWs during work plan development: • The year in which previous ROW expansion/ROW clearing project work was completed. Follow-up IVM maintenance is then typically targeted to occur within 1-5 years. • How many previous years of IVM maintenance have occurred on a line and when the last cycle of maintenance occurred. Follow-up IVM maintenance is then typically recommended to occur within 1-3, 3-5, or 5-7 years depending on other factors below. • Vegetation height and density (% cover of size classes at 6-12 feet, at 5-6 feet, and at 3-4 feet) • HFTD/HFRA Tiers and circuit mileage length • Agency and landowner commitments | Nathan Poon | 2025-04-08 | 2025-04-11 | 2025-04-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_001.zip | 0 | No | 9 | Vegetation Management & Inspections | 9.7.2 | Integrating VM Reassessment and Treatment Timing
15 | 27 | OEIS | 001 | OEIS_001 | 17 | No | OEIS_001_Q17 | Regarding Covered Conductor, Line Removal and Microgrids On page 180 of its 2026-2028 Base WMP, PG&E states “[PG&E’s System Hardening GH-12] initiative includes overhead hardening mitigations, specifically covered conductor installation and line removal, including remote grids.” a. Provide separate targets for the following initiatives in the same table format as Table 8-1. i. Covered Conductor ii. Line Removal iii. Microgrids | PG&E does not set separate targets for the initiatives that are included in GH-12. We have provided estimates based on the 2026-2028 workplan and these estimates may differ from the total miles completed each year. For clarity, microgrid information is not provided because those are not part of the Overhead and Line Removal – Distribution Initiative (GH-12) initiative. Instead, remote grid enables the removal of lines and is included in the line removal activity. See attachment “WMP-Discovery2026-2028_DR_OEIS_001-Q017Atch01.xlsx” with the estimates by initiative requested in Table 8-1 format. | Nathan Poon | 2025-04-08 | 2025-04-11 | 2025-04-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_001.zip | 1 | No | 8 | Grid Design, Operations, and Maintenance | 8.2.1/8.2.9/8.2.7 | Covered Conductor, Line Removal, Microgrids
15 | 28 | OEIS | 001 | OEIS_001 | 18 | No | OEIS_001_Q18 | Regarding idle transmission power lines a. How many circuit miles of idle transmission lines does PG&E have in the HFTD and HFRA? i. Do any of these idle transmission lines run parallel, and in close proximity to energized transmission lines? ii. Are any of these idle transmission lines planned for removal in 2026 to 2028? A. If yes, provide targets for 2026, 2027, and 2028. B. If no. explain: 1. Explain why removal is not planned. 2. Explain if any of these lines could become energized through induction. | a. PG&E has three idle transmission lines totaling 2.25 miles in HFTD and HFRA. i. One of these lines runs parallel and close to energized Distribution lines outside of HFTD and HFRA. ii. No A. N/A B. 1. PG&E plans to remove two of the three lines in 2025. The third line is not planned for removal at this time but is being evaluated for the optimal induction mitigation solution. 2. Only one of the three lines has sections that could become energized through induction. These sections are outside of HFTD and HFRA, and PG&E is evaluating induction mitigation WMP-Discovery 2026-2028_DR_OEIS_001-Q018 Page 2 options to reduce the risk of the line becoming energized through induction. | Nathan Poon | 2025-04-08 | 2025-04-16 | 2025-04-16 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_001.zip | 0 | No | 8 | Grid Design, Operations, and Maintenance | 8.2.9.1 | Line Removal (In the HFTD) - Transmission
15 | 29 | OEIS | 001 | OEIS_001 | 19 | No | OEIS_001_Q19 | Regarding CC and Undergrounding in Fire Rebuild Areas On page 186 of its WMP, PG&E states, “PG&E often refers to areas that have been impacted directly by wildfires within an HFTD as “Fire Rebuild” work. Work in areas impacted by wildfires outside of an HFTD area is referred to as “Community Rebuild” work.” Provide the targets for the “Overhead Hardening and Line Removal - Distribution (GH-12)” and “System Hardening - Undergrounding (GH-04)” activities for 2026 to 2028 which are designated as “Fire Rebuild” or “Community Rebuild.” Provide your response in the table below. | PG&E has not set separate targets for activities designated as “Fire Rebuild” or “Community Rebuild.” These workstreams are emergent and we rebuild, as needed, in response to fire incidents. Currently, 10 miles of Community Rebuild work are forecasted in 2026 in the System Hardening - Undergrounding Initiative GH-04. We do not have any additional forecasts for Fire or Community Rebuild. See the table below for the requested information: WMP-Discovery 2026-2028_DR_OEIS_001-Q019 Page 2 2026 2027 2028 “Fire Rebuild” “Community Rebuild” “Fire Rebuild” “Community Rebuild” “Fire Rebuild” “Community Rebuild” Overhead Hardening and Line Removal - Distribution (GH-12) Targets N/A N/A N/A N/A N/A N/A System Hardening - Undergrounding (GH-04) activity Targets N/A 10 miles N/A N/A N/A N/A | Nathan Poon | 2025-04-08 | 2025-04-11 | 2025-04-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_001.zip | 0 | No | 8 | Grid Design, Operations, and Maintenance | 8.2.1/8.2.2 | CC Installation/Undergrounding
15 | 30 | OEIS | 001 | OEIS_001 | 20 | No | OEIS_001_Q20 | Regarding the CBR Calculation in Area for Continued Improvement PG&E-25U-04 In response to Area for Continued Improvement PG&E-25U-04, PG&E discusses the methodology used for its CBR calculation on page 572. The discussion does not include how PG&E calculated the “eyes-on-risk” achieved by a detailed aerial inspection vs. and aerial scan inspection. a. Does PG&E assume that an aerial scan achieves the same eyes-on-risk as a detailed aerial inspection? i. If yes, discuss how PG&E determined an aerial scan achieves the same eyes-on-risk as a detailed aerial inspection. This discussion must include a description of differences in the process and execution of aerial scans vs. aerial detailed inspections (i.e. photograph locations, equipment required to be photographed, photograph quantity per inspection, photograph clarity requirements, reviewer inspection checklists, etc.) ii. If no, provide the following calculations: A. The eyes-on-risk of a detailed aerial inspection on an asset in an area of extreme consequence and extreme wildfire risk. 1. The eyes on risk of an aerial scan inspection on the same asset. B. The eyes-on-risk of a detailed aerial inspection on an asset in an area of severe consequence and severe wildfire risk. 1. The eyes on risk of an aerial scan inspection on the same asset. C. The eyes-on-risk of a detailed aerial inspection on an asset in an area of high consequence and high wildfire risk. 1. The eyes on risk of an aerial scan inspection on the same asset. | a. Yes, PG&E assumes that an aerial scan achieves the same eyes-on-risk as a detailed aerial inspection. i. The primary objective of inspections is to identify various conditions requiring corrective actions. Some of the corrective actions must be addressed in the short term while others have a longer time duration depending on the observed condition and location in the HFTD, in accordance to GO 95, Rule 18. PG&E’s eyes-on-risk metric associated with inspections is meant to capture the ability of an activity to detect conditions that could fail in the short-term. These are conditions that are associated with Level 1 findings and urgent Level 2 findings, which correspond to PG&E’s A, B, and X tags. These are the tag conditions that are addressed expeditiously: immediately for an A tag, within seven days for an X tag, and within a sixmonth time frame for a B tag. Since PG&E’s aerial scans will identify A, B, and X conditions, it achieves the same eyes-on-risk as a detailed ground or aerial inspection. b. Not applicable, please see the response to subpart (a) above. | Nathan Poon | 2025-04-08 | 2025-04-11 | 2025-04-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_001.zip | 0 | No | ACI PG&E-25U-04 | ACI PG&E-25U-04 | ACI PG&E-25U-04 | ACI PG&E-25U-04
15 | 31 | OEIS | 001 | OEIS_001 | 21 | No | OEIS_001_Q21 | Regarding Aerial Scan Inspections On page 236 of its 2026-2028 Base WMP, PG&E states that aerial scan inspections will be implemented to get additional eyes-on-risk in the riskiest areas. PG&E states that the inspection will consist of a review of a “streamlined set of photos…tailored to enable the identification of the conditions…that post the highest wildfire risk.” a. Provide a comprehensive list of the differences between aerial scan and aerial distribution detailed inspections (i.e. the number of photographs taken, the equipment photographed, the distance from camera to equipment being photographed, the number of photographs being reviewed, items on the reviewer’s inspection checklist, etc.). Provide documentation that supports this list of differences (job aids, inspection checklists, etc.) | The difference between the inspections is that, while the detailed inspection will identify all compelling abnormal conditions on the structure, the scan inspection will focus on emergency and urgent conditions, corresponding to A, B, and X tag priorities. PG&E is piloting the aerial scan inspection this year, utilizing different methodologies and shot sheets with the goal of selecting the best methodology with which to implement the inspection for 2026. Therefore, we cannot provide a fully detailed list of the differences between the two programs since the aerial scans have not yet been finalized. However, as described in PG&E’s 2026-2028 WMP, the scan inspection will consist of a review of a streamlined set of photos that have been tailored to enable identification of the conditions on the structure and equipment that pose the highest wildfire risk, including the mid-span conductor. While the aerial scans will be a more abbreviated assessment, they will have the ability to assess and identify the conditions that can lead to failure in the short-term. | Nathan Poon | 2025-04-08 | 2025-04-11 | 2025-04-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_001.zip | 0 | No | 8 | Grid Design, Operations, and Maintenance | 8.3.8/8.3.14 | Detailed Inspection Program/Aerial Inspection Program
15 | 32 | OEIS | 001 | OEIS_001 | 22 | No | OEIS_001_Q22 | Regarding Real Time Sensors On page 237 of its 2026-2028 Base WMP, PG&E states that it is piloting real time sensors that may collect data that in the future can be used in lieu of aerial scan inspections. a. Provide a list of sensors that are being/will be piloted from 2026-2028. b. For each sensor provide the following information i. Manufacturer ii. Model number/series iii. Data the sensor records/transmits (voltage, current, power quality, temperature, vibration, etc.) iv. Current phase of pilot (planning, execution, evaluation, scaling) v. Estimated completion date of pilot evaluation phase | PG&E is still early in exploring the relationship between grid sensors’ continuous monitoring capabilities and how they may be used to supplement electrical asset inspections. Information on our current distribution grid sensor technologies follows below. a. During the 2026-2028 period, we anticipate scaling deployment of Early Fault Detection (EFD) sensors, Distribution Fault Anticipator (DFA) sensors, and Gridscope sensors. b. Please see below for the requested information on sensor technology. As these sensors are beyond pilot phase, we are also providing the approximate number of sensors we have installed to date. WMP-Discovery 2026-2028_DR_OEIS_001-Q022 Page 2 Sensor EFD DFA Gridscope Manufacturer IND Technologies Power Solutions / Texas A&M University Gridware Approximate Number Installed 203 96 10,000 Model Number / Series EFD G4; EFD.Tap R5A1-0 Gridscope Data the sensor records/transmits (voltage, current, power quality, temperature, vibration, etc.) Radio frequency detections, temperature Voltage, current Vibration, acceleration, inclination, electric field voltage, infrared readings, temperature, barometric pressure, particulate matter, humidity, audio, images Current phase of pilot (planning, execution, evaluation, scaling) Scaling Scaling Scaling Estimated completion date of pilot evaluation phase The pilot evaluation phase is now complete. We plan to scale deployment of this technology in a manner that supports reliability improvements, optimization of inspection and maintenance work, and wildfire situational awareness. The pilot evaluation phase is now complete. We plan to scale deployment of this technology in a manner that supports reliability improvements, optimization of inspection and maintenance work, and wildfire situational awareness. The pilot evaluation phase is now complete. We plan to scale deployment of this technology in a manner that supports reliability improvements, optimization of inspection and maintenance work, and wildfire situational awareness. | Nathan Poon | 2025-04-08 | 2025-04-11 | 2025-04-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_001.zip | 0 | No | 10 | Situational Awareness and Forecasting | 10.4/10.31 | Real-Time Sensors
15 | 33 | OEIS | 001 | OEIS_001 | 23 | No | OEIS_001_Q23 | Regarding Projected Risk Reduction On page 147 of the 2026-2028 Base WMP, PG&E provides Figure 6-1: Projected Overall Service Territory Risk, showing the residual risk over time with resiliency mitigations and operational mitigations. a. Provide similar versions of this figure showing the associated projected risk reduction for wildfire risk, PSPS risk, and PEDS risk over time. b. From 2025 to 2028, PG&E shows a projected reduction in overall utility risk of approximately nine percent when only accounting for resiliency mitigations, but only a reduction of approximately one percent when accounting for operational mitigations and resiliency mitigations together. i. Provide the actual projected residual risk percentages broken out by year from 2025 to 2028 for both only resiliency mitigations as well as resiliency and operational mitigations. ii. Explain why there is nominal residual risk reduction when incorporating operational mitigations. | a. The following figures show the projected wildfire risk reduced 2023 – 2033 with and without operational mitigations, the projected PSPS risk reduced 2023 – 2033, and the projected EPSS risk reduced 2023 – 2033. | Nathan Poon | 2025-04-08 | 2025-04-16 | 2025-04-16 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_001.zip | 0 | No | 6 | Wildfire Mitigation Strategy Development | 6.2.1.1 | Projected Overall Risk reduction
15 | 34 | OEIS | 001 | OEIS_001 | 24 | No | OEIS_001_Q24 | Regarding Extreme Weather Conditions a. On page 87 of the 2026-2028 Base WMP, relating to vegetation, PG&E states that “For WFC, a set of worst weather days during historical fire seasons is used to develop fire simulations of potential ignitions given current fuel conditions.” i. What timeframe is used for evaluating historical fire seasons? ii. How does PG&E define “worst weather days”? iii. How many “worst weather days” are included within the set used for WFC? iv. Does PG&E use the same definition of “worst weather days” for weather and wind scenarios? If not, provide those definitions and the number of “worst weather days” within each set. b. On page 90 of the 2026-2028 Base WMP, PG&E states that it “seeks to incorporate the potential impacts of more extreme conditions in future models.” i. When does PG&E anticipate completing this evaluation? ii. Which future model is PG&E planning on- first incorporating these more extreme conditions? iii. When does PG&E anticipate operationalizing this model? iv. Is Figure PG&E-5.3.2-1 (p.90) exhaustive of the various extreme risks being studied? If not, provide a list of considerations currently being studied by PG&E. v. PG&E’s 2023-2025 WMP included Table 6-4: Example of Extreme Event Scenarios Under Consideration (p. 193), which was not included in PG&E’s 2026-2028 WMP. Provide a similar table showing the extreme event scenarios currently under consideration. c. On page 88 of the 2026-2028 Base WMP, Table-5-2: Summary of Design Scenarios, PG&E lists the scenarios used for its various models. Provide a detailed description of how the design scenarios Wind Load 3, Wind Load 4, and Vegetation 3 align and/or differ with extreme weather scenarios, as discussed in Section 5.3.2 Extreme-Event/High Uncertainty Scenarios. d. On page 46 of the 2026-2028 Base WMP, PG&E states that “in terms of risk modeling, this strategy entails paying special attention to tail risk—the low frequency, high consequence events” when discussing Cost-Benefit Analysis. Provide a detailed description of how the evaluation of these low frequency, high consequence events align and/or differ with extreme weather scenarios, as discussed in Section 5.3.2 Extreme-Event/High Uncertainty Scenarios. e. PG&E references fragility curves, shown in Figure PG&E-5.2.2.1-1, capturing Wind Load 1, 2, 3, and 4 conditions for its WTRM Planning Model. i. Provide a detailed description of how PG&E is evaluating the use of fragility curves to perform similar risk analysis for its distribution-level models. ii. If PG&E is not currently pursuing efforts to incorporate evaluations of impacts from conditions similar to Wind Loads 3 and 4 within its distribution-level models, explain why. | a. i. The months of June through November, inclusive, constitute the Fire season. ii. The Worst Weather Days are determined by the PG&E Meteorology team based on historical red flag warnings, PG&E’s Fire Potential Index, historical Diablo wind event days and historical catastrophic fires. The final list of days is reviewed and curated by the meteorology team. iii. PG&E includes 571 worst weather days from March 2003 to Dec 2020. iv. See response ii. b. i. The current suite of Wildfire Risk models (Wildfire Consequence, WDRM and WTRM) are used for long term planning wildfire mitigation strategies, which incorporate the full range of wildfire risk scenarios through the whole year. In parallel, PG&E is evaluating potential methodologies that can quantify the risk of urban conflagration type scenarios that are more likely to occur under extreme weather and fuel conditions. We anticipate completing the evaluation by Q2 2026. ii. If the methodologies to quantify urban conflagration type scenarios are found to be useful and approved for use, they will be incorporated in v5 of the wildfire consequence model. iii. The date of operationalization will depend on the model approval by PG&E’s internal Wildfire Risk Governance Steering Committee and consultations with the Asset Strategy teams. WMP-Discovery 2026-2028_DR_OEIS_001-Q024 Page 3 iv. PG&E is currently evaluating methodologies that quantify urban conflagration type scenarios that become more likely in extreme conditions. v. PG&E is currently evaluating methodologies that quantify urban conflagration type scenarios that become more likely in extreme conditions. The factors under consideration include structure density, terrain, wind speeds, distance from wildland urban interface and PG&E electrical assets. c. Please refer to pages 86 and 87 of 2026-2028 Base WMP that describes how the various risk models incorporate the weather, wind and vegetation scenarios as outlined in Section 5.3.1. d. PG&E’s enterprise risk model pays “special attention to tail risk” by employing the following modeling approaches: Fitting existing consequence data to Pareto/Power-Law probability distributions. These distributions have been established by extensive studies and considerable vetting in Phase 3 of the CPUC’s Risk-based OIR, R.20-07-013 to adequately capture the risk of extreme consequences1. Applying a market-based risk-scaling function to the distributions above2. This risk-adjustment step calibrates the loss distributions (obtained from historical data) with available prices from the insurance and catastrophic bond markets such that the resulting distribution of monetized losses is consistent with the magnitude of losses implied by the transacted prices and thereby represents a consensus view of future risk from wildfires. In its Evaluation Report on PG&Es RAMP, CPUC’s Safety Policy Division (SPD) found that PG&E’s risk-scaling approach to be valid3. As such, the enterprise model adopts a different approach to model tail risks than relying on the construction of explicit extreme weather scenarios as contemplated in Section 5.3.2 Extreme-Event/High Uncertainty Scenarios. e. i. PG&E is evaluating the use of fragility curves on the distribution system to help estimate the long-term impacts of climate change on distribution equipment. ii. The Distribution Event Probability Models are machine learning models trained to predict system failures and ignitions during wildfire season based on historical events. The machine learning models combine environmental conditions, seasonal weather patterns, and distribution system attributes to predict a likelihood of failure and ignition. The models do not require fragility curves to produce a failure probability for the wildfire season because localized, seasonal weather patterns are already an input to the model if the algorithm finds them important to predict historical events. | Nathan Poon | 2025-04-08 | 2025-04-16 | 2025-04-16 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_001.zip | 0 | No | 5 | Risk Methodology & Assessment | 5.3 | Weather Conditions
15 | 35 | OEIS | 001 | OEIS_001 | 25 | No | OEIS_001_Q25 | Regarding Suppression and Egress Impacts On page 56 of the 2026-2028 Base WMP, PG&E provides Figure PG&E-5.2.1-1: WFC v4 Components, which shows consequence value adjustment steps for suppression access and egress. a. Provide a detailed description of how the inclusion of suppression access impacts the overall WFC v4 base risk scores. Provide the percent change to the overall risk score when suppression access is incorporated, as well as a description of the impact to the ranking of highest risk circuits based on wildfire risk scores. b. Provide a detailed description of how the inclusion of egress impacts the overall WFC v4 base risk scores. Provide the percent change to the overall risk score when egress is incorporated, as well as a description of the impact to the ranking of highest risk circuits based on wildfire risk scores. c. PG&E shows TDI (terrain difficulty index) listed as the impacting value under suppression access. What other values, if any, are included to quantify the impact of suppression access? d. PG&E shows AFN (access/function needs) listed as the impacting value under egress. What other values, if any, are included to quantify the impact of egress? e. How has PG&E validated and verified the impact of including suppression access and egress into its WDRM? Provide any results of such validation, including a description | a. Egress and suppression were incorporated into the WF consequence model in response to the PG&E’s 2023-2025 WMP commitment. The current approach only generates the total WF consequence and WF risk values used by asset WMP-Discovery 2026-2028_DR_OEIS_001-Q025 Page 2 management teams. Suppression and egress consequence\risk values are not generated distinctly from the total consequence\risk values. b. See response (a) c. Please refer to the Wildfire Consequence model v4 documentation, Sections 4.1 and 4.3 for details on suppression modeling. d. Please refer to the Wildfire Consequence model v4 documentation, Sections 4.2 and 4.3 for details on egress modeling. e. The overall WF Consequence model v4 with egress and suppression incorporated was validated against historical fire outcomes. | Nathan Poon | 2025-04-08 | 2025-04-16 | 2025-04-16 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_001.zip | 0 | No | 5 | Risk Methodology & Assessment | 5.2.1 | Risk and Risk Component Identification
15 | 36 | OEIS | 001 | OEIS_001 | 26 | No | OEIS_001_Q26 | Regarding Community Vulnerability In its 2023-2025 Base WMP (R8), PG&E provides the following key milestone as part of its risk assessment improvement plan, in Table 6-7 on page 221: “By the end of 2023, evaluate an approach to incorporate community vulnerability attributes (AFN, Economic disadvantaged zones, Critical Facilities) into the WFC Model.” a. What were PG&E’s results of this evaluation? b. PG&E discusses inclusion of vulnerable customer populations as part of its PSPS risk components (page 57 of the 2026-2028 Base WMP) and through the critical customer weightings (Table PG&E-5.2.2.2-2, page 69 of the 2026-2028 Base WMP). Describe how these relate to the evaluation discussed in the key milestone identified in the 2023-2025 Base WMP. c. PG&E states that public egress impact considers vulnerability on page 67 of the 2026-2028 Base WMP. Describe how this relates to the evaluation discussed in the key milestone identified in the 2023-2025 Base WMP. d. Provide a description of how PG&E integrated community vulnerability considerations into its wildfire and PSPS consequence models? e. If PG&E is still undergoing this evaluation, what is PG&E’s timeline for integration into future models? | a. As a result of this evaluation, PG&E incorporated census data of age as a proxy for AFN as one measure of community vulnerability in the egress component of the WF consequence model v4. b. The same evaluation from the 2023-2025 Base WMP for critical customer weighting is applied to 2026-2026 Base WMP. PG&E uses customer weightings in its PSPS valuation to acknowledge certain customers are more vulnerable and are at elevated WMP-Discovery 2026-2028_DR_OEIS_001-Q026 Page 2 risks to sustained outages. A customer type system was selected to support riskprioritization of work for those critical customers and circuits that can be impacted by PSPS events. c. Please refer to section 2.4.3 on Public Egress Impact Model in the Wildfire consequence v4 model documentation how AFN was incorporated as one measure of community vulnerability. d. Please refer to section 2.4.3 on Public Egress Impact Model in the Wildfire consequence v4 model documentation for how AFN was incorporated as one measure of community vulnerability in the wildfire consequence model. For PSPS Consequence model, please refer to response b. e. PG&E has incorporated AFN as one measure of community vulnerability in the wildfire consequence model. Research and collaboration with other IOUs is ongoing to identify other areas where community vulnerability can be quantified and incorporated into the wildfire risk models. | Nathan Poon | 2025-04-08 | 2025-04-16 | 2025-04-16 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_001.zip | 0 | No | 11 | Emergency Preparedness, Collaboration, and Public Awareness | 11.3.2/11.3.3 | Collaboration on Local/Regional Wildfire Mitigation Planning
15 | 37 | OEIS | 001 | OEIS_001 | 27 | No | OEIS_001_Q27 | Regarding Independent Review a. Provide a copy of the E3 Review of PG&E’s Wildfire Risk Model Version 4, as referenced on page 105 of the 2026-2028 Base WMP. b. Provide PG&E’s plan and timeline to address the two areas for improvement listed on page 105 from that report. | a. Please see “WMP-Discovery2026-2028_DR_OEIS_001-Q027Atch01.pdf” for the E3 review of PG&E’s Wildfire Risk Model Version 4. b. PG&E is currently evaluating methods to incorporate temporal inputs into the vegetation Event Probability Models. PG&E has also initiated discussions on how to improve the probability of ignition model. PG&E plans to release the enhancements with the WDRM v5 model anticipated for release with the next WMP submission. | Nathan Poon | 2025-04-08 | 2025-04-16 | 2025-04-16 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_001.zip | 1 | No | 5 | Risk Methodology & Assessment | 5.6.1/5.6.2 | Independent Review
15 | 38 | OEIS | 001 | OEIS_001 | 28 | No | OEIS_001_Q28 | Regarding PG&E’s Wildfire Transmission Risk Model (WTRM) a. In Table 5-1: Risk Modeling Assumptions and Limitations, page 79 of the 2026-2028 Base WMP, PG&E states that it identified 47 components divided into nine asset groups. i. Provide a list of these 47 components and associated asset groupings for each component. ii. Figure PG&E-5.2-3: Wildfire Transmission Risk Analysis Framework only shows eight probability models relating to assets. How do these eight models relate to the nine asset groups? iii. What asset types, if any, are not captured through this analysis and grouping? How is PG&E working to evaluate the risk associated with these other asset types? | a. i. The table below lists the 47 components and associated asset group. “Component” refers to the individual component whose failure could result in an ignition, and “Group” is the component grouping for the TCM. There are 9 component groupings: (1) conductors, (2) insulators, (3) non-steel structures (NSS), (4) steel structures (SS), (5) foundations, (6) switches, (7) above grade hardware (AGH), (8) below grade hardware (BGH), and (9) splices. ii. The ninth asset group that is missing from Figure 5.2-3 is the switches. A deterministic approach was chosen for the transmission switch asset group rather than predictive modeling through the WTRM. The deterministic model utilizes asset data (age, manufacturer, type, location, etc.), manufacturers’ recommendations, industry best practices and inspection results to prioritize controls and mitigations. This approach is typically considered for components with small populations or limited deployment, which applies to transmission switches (approximately 2,000 installed in the system). iii. Individual components whose failure could result in an ignition are captured in this analysis and grouping. Risk associated with switches are evaluated as described in the previous answer (ii). | Nathan Poon | 2025-04-08 | 2025-04-16 | 2025-04-16 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_001.zip | 0 | No | 5 | Risk Methodology & Assessment | 5.2/5.5 | Risk Analysis Framework/Risk Analysis Results
15 | 39 | MGRA | 002 | MGRA_002 | 1 | No | MGRA_002_Q1 | Weather station metadata valid as of Q4 of 2024. | In response to this request, PG&E is providing the Weather Station Feature Class as delivered in the 4Q 2024 OEIS GIS Data Standard Submission. Please see the file “WMP-Discovery2026-2028_DR_MGRA_002-Q001Atch01.xlsx.” | Joseph Mitchell | 2025-04-11 | 2025-04-16 | 2025-04-16 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-MGRA_002.zip | 1 | No | N/A | GIS | N/A | N/A
15 | 39 | MGRA | 002 | MGRA_002 | 1(s) | Yes | MGRA_002_Q1(s) | Weather station metadata valid as of Q4 of 2024. | Please see “WMP-Discovery2026-2028_DR_MGRA_002-Q001Supp01Atch01.xlsx” in which PG&E has included requested lat/long information. | Joseph Mitchell | 2025-04-11 | 2025-04-18 | 2025-04-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-MGRA_002.zip | 1 | No | N/A | GIS | N/A | N/A
15 | 40 | MGRA | 002 | MGRA_002 | 2 | No | MGRA_002_Q2 | PSPS event damage event reports obtained from post-event patrols, including cause for all quarters of 2024. | In response to this request, PG&E is providing non-confidential data for the PSPS Event Damage Feature Classes, as delivered in 2024. Please note that PG&E did not have PSPS events during each quarter nor is every table applicable for relevant damages. For example, there were no support structure or other asset damages, so there are no data to report in the PspsEventSuppportStructureDamageDetail or PspsEventOtherAssetDamageDetail to report. Attached, please see the responsive files and associated explanations for when PG&E had relevant data to report each quarter for 2024: • “WMP-Discovery2026-2028_DR_MGRA_002-Q002Atch01.xlsx” o PG&E only provided data in this Feature Class for 4Q 2024. • “WMP-Discovery2026-2028_DR_MGRA_002-Q002Atch02.xlsx” o PG&E only provided data in this Feature Class for 4Q 2024. | Joseph Mitchell | 2025-04-11 | 2025-04-16 | 2025-04-16 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-MGRA_002.zip | 2 | No | N/A | GIS | N/A | N/A
15 | 40 | MGRA | 002 | MGRA_002 | 2(s) | Yes | MGRA_002_Q2(s) | PSPS event damage event reports obtained from post-event patrols, including cause for all quarters of 2024. | Please see the attachments listed below in which PG&E has included the requested lat/long information. Please note that a third file responsive to this question was inadvertently omitted from our initial response and is included here. • “WMP-Discovery2026-2028_DR_MGRA_002-Q002Supp01Atch01.xlsx” • “WMP-Discovery2026-2028_DR_MGRA_002-Q002Supp01Atch02.xlsx” • “WMP-Discovery2026-2028_DR_MGRA_002-Q002Supp01Atch03.xlsx” | Joseph Mitchell | 2025-04-11 | 2025-04-18 | 2025-04-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-MGRA_002.zip | 3 | No | N/A | GIS | N/A | N/A
15 | 41 | MGRA | 002 | MGRA_002 | 3 | No | MGRA_002_Q3 | Unplanned outage data, including cause for all four quarters of 2023 and 2024. a. If possible should include whether the outage occurred on a covered conductor segment | In response to this request, PG&E is providing non-confidential data for the Unplanned Outage Feature Class for all 8 quarters requested from 2023 and 2024, as delivered in the OEIS GIS Data Standard Submissions for each quarter. Please see “WMPDiscovery2026-2028_DR_MGRA_002-Q003Atch01.xlsx.” a. The provided Feature Classes are not structured to include data on covered conductor segmentation, and thus PG&E is presently unable to provide this requested data. When the non-confidential GDBs are created, as requested by MGRA in MGRA-PGE-WMP26_DataRequest1, MGRA will be able to identify line classifications and make spatial inferences through the Primary Distribution Line feature class. | Joseph Mitchell | 2025-04-11 | 2025-04-16 | 2025-04-16 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-MGRA_002.zip | 1 | No | N/A | GIS | N/A | N/A
15 | 41 | MGRA | 002 | MGRA_002 | 3(s) | Yes | MGRA_002_Q3(s) | Unplanned outage data, including cause for all four quarters of 2023 and 2024. a. If possible should include whether the outage occurred on a covered conductor segment | Please see “WMP-Discovery2026-2028_DR_MGRA_002-Q003Supp01Atch01.xlsx”, in which PG&E has included the requested lat/long information. | Joseph Mitchell | 2025-04-11 | 2025-04-18 | 2025-04-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-MGRA_002.zip | 1 | No | N/A | GIS | N/A | N/A
15 | 42 | MGRA | 002 | MGRA_002 | 4 | No | MGRA_002_Q4 | Wire down data for all four quarters of 2023 and 2024. Include cause and any associated outage identifier. a. If possible should include whether the outage occurred on a covered conductor segment | In response to this request, PG&E is providing non-confidential data for the Wire Down Feature Class, as delivered in the 8 quarters requested in 2023 and 2024. Please see the file “WMP-Discovery2026-2028_DR_MGRA_002-Q004Atch01.xlsx”. a. The provided Feature Classes are not structured to include data on covered conductor segmentation, and thus PG&E is presently unable to provide this requested data. When the non-confidential GDBs are created, as requested by MGRA in MGRA-PGE-WMP26_DataRequest1, MGRA will be able to identify line classifications and make spatial inferences through the Primary Distribution Line feature class. | Joseph Mitchell | 2025-04-11 | 2025-04-16 | 2025-04-16 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-MGRA_002.zip | 1 | No | N/A | GIS | N/A | N/A
15 | 42 | MGRA | 002 | MGRA_002 | 4(s) | Yes | MGRA_002_Q4(s) | Wire down data for all four quarters of 2023 and 2024. Include cause and any associated outage identifier. a. If possible should include whether the outage occurred on a covered conductor segment | Please see “WMP-Discovery2026-2028_DR_MGRA_002-Q004Supp01Atch01.xlsx”, in which PG&E has included the requested lat/long information. | Joseph Mitchell | 2025-04-11 | 2025-04-18 | 2025-04-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-MGRA_002.zip | 1 | No | N/A | GIS | N/A | N/A
15 | 43 | MGRA | 002 | MGRA_002 | 5 | No | MGRA_002_Q5 | Ignition data for all four quarters of 2023 and 2024. a. Should include cause and any associated outage identifier. b. If possible should include whether the ignition occurred on a covered conductor segment | In response to this request, PG&E is providing non-confidential data for the Ignition Feature Class, as delivered in the 8 quarters requested in 2023 and 2024. Please see “WMP-Discovery2026-2028_DR_MGRA_002-Q005Atch01.xlsx”. a. The provided Feature Classes include the columns SuspectedInitiatedCause and OutageID which are responsive to this question. b. The provided Feature Classes are not structured to include data on covered conductor segmentation, and thus PG&E is presently unable to provide this requested data. When the non-confidential GDBs are created, as requested by MGRA in MGRA-PGE-WMP26_DataRequest1, MGRA will be able to identify line classifications and make spatial inferences through the Primary Distribution Line feature class. | Joseph Mitchell | 2025-04-11 | 2025-04-16 | 2025-04-16 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-MGRA_002.zip | 1 | No | N/A | GIS | N/A | N/A
15 | 43 | MGRA | 002 | MGRA_002 | 5(s) | Yes | MGRA_002_Q5(s) | Ignition data for all four quarters of 2023 and 2024. a. Should include cause and any associated outage identifier. b. If possible should include whether the ignition occurred on a covered conductor segment | Please see “WMP-Discovery2026-2028_DR_MGRA_002-Q005Supp01Atch01.xlsx”, in which PG&E has included the requested lat/long information. | Joseph Mitchell | 2025-04-11 | 2025-04-18 | 2025-04-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-MGRA_002.zip | 1 | No | N/A | GIS | N/A | N/A
15 | 44 | MGRA | 003 | MGRA_003 | 1 | No | MGRA_003_Q1 | Please provide an excel spreadsheet table that provides for 2021, 2022, 2023, and 2024: a. Number of miles of fully covered conductor circuit segments in the HFTD+HFRA; b. Number of miles of fully “bare wire” conductor circuit segments in the HFTD+HFRA; c. Number of wires down for associated with a covered conductor circuit segment in the HFTD+HFRA; d. Number of wires down associated with a “bare wire” conductor circuit segments in the HFTD+HFRA; e. Number reportable ignitions for fully covered conductor circuit segments in the HFTD+HFRA. f. Number reportable ignitions for fully “bare wire” conductor circuit segments in the HFTD+HFRA; g. For ignitions on partially covered circuit segments in the HFTD+HFRA, or ignitions with uncertain origin, sum these into the “fully covered” or “bare wire” groups based on the most prevalent circuit configuration in the area of ignition. h. Number of outages attributable to infrastructure on fully “bare wire” conductor circuit segments in the HFTD+HFRA; i. Number of outages attributable to infrastructure on fully covered conductor circuit segments in the HFRA. j. For outages on partially covered circuit segments in the HFTD+HFRA, or outages with uncertain locations, sum these into the “fully covered” or “bare wire” groups based on the most prevalent circuit configuration in the area of the outage. | a. Please see “WMP-Discovery2026-2028_DR_MGRA_003-Q001Atch01.xlsx.” Please note that the data provided reflects asset status as included in our Q4 spatial data deliveries to the Office of Energy Safety for each of 2021-2024. Please note that PG&E has applied HFTD and HFRA filters based on current, not historical, definitions of HFTD and HFRA. b. Please see “WMP-Discovery2026-2028_DR_MGRA_003-Q001Atch01.xlsx.” Please note that the data provided reflects asset status as included in our Q4 spatial data deliveries to the Office of Energy Safety for each of 2021-2024. Please note that PG&E has applied HFTD and HFRA filters based on current, not historical, definitions of HFTD and HFRA. c. Please note that the data provided is drawn from PG&E’s Integrated Logging Information System (“ILIS”). The reporting structure for ILIS does not give single outage details for specific events, and wire down metrics may be over-reported as a result. ILIS records do not capture the type of wire, so PG&E is not able to differentiate between covered or bare conductor. In addition, ILIS does not capture HFRA locations, so the volume reported is limited to HFTD only. As a result of these limitations, PG&E is providing the total volume of wire down events in HFTDs in Part D for 2021, 2022, 2023 and 2024. d. Please see “WMP-Discovery2026-2028_DR_MGRA_003-Q001Atch01.xlsx.” Please note that the data provided is drawn from PG&E’s Integrated Logging Information System (“ILIS”). The reporting structure for ILIS does not give single outage details for specific events, and wire down metrics may be over-reported as a result. ILIS records do not capture the type of wire, so PG&E is not able to differentiate between covered or bare conductor. In addition, ILIS does not capture HFRA locations, so the volume reported is limited to HFTD only. As a result of these limitations, PG&E is providing the total volume of wire down events in HFTDs in Part D for 2021, 2022, 2023 and 2024. e. Please see “WMP-Discovery2026-2028_DR_MGRA_003-Q001Atch01.xlsx.” f. Please see “WMP-Discovery2026-2028_DR_MGRA_003-Q001Atch01.xlsx.” g. PG&E’s ignition tracking does not allow it to identify “partially covered circuit segments,” and all ignitions have a designated origin. No ignitions were summed into “fully covered” or “bare wire” for the purposes of this subpart. h. Please see “WMP-Discovery2026-2028_DR_MGRA_003-Q001Atch01.xlsx.” Please note that ILIS records do not capture the type of wire, so PG&E is not able to differentiate between covered or bare conductor. In addition, ILIS does not capture HFRA locations, so the volume reported is limited to HFTD only. As a result of these limitations, PG&E is providing the total volume of outages in HFTDs in Part H for 2021, 2022, 2023 and 2024. i. Please note that ILIS records do not capture the type of wire, so PG&E is not able to differentiate between covered or bare conductor. In addition, ILIS does not capture HFRA locations, so the volume reported is limited to HFTD only. As a result of these WMP-Discovery 2026-2028_DR_MGRA_003-Q001 Page 3 limitations, PG&E is providing the total volume of outages in HFTDs in Part H for 2021, 2022, 2023 and 2024. j. ILIS does not allow PG&E to identify “partially covered circuit segments,” and all ignitions have a designated origin. No outages were summed into “fully covered” or “bare wire” for the purposes of this subpart. | Joseph Mitchell | 2025-04-11 | 2025-04-16 | 2025-04-16 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-MGRA_003.zip | 1 | No | 8 | Grid Design, Operations, and Maintenance | 8.4.4/8.2.10 | Conductor, Including Covered Conductor Other Grid Topology Improvements to Minimize Risk of Ignitions
15 | 44 | MGRA | 003 | MGRA_003 | 1(a) | Yes | MGRA_003_Q1(a) | Please provide an excel spreadsheet table that provides for 2021, 2022, 2023, and 2024: a. Number of miles of fully covered conductor circuit segments in the HFTD+HFRA; b. Number of miles of fully “bare wire” conductor circuit segments in the HFTD+HFRA; c. Number of wires down for associated with a covered conductor circuit segment in the HFTD+HFRA; d. Number of wires down associated with a “bare wire” conductor circuit segments in the HFTD+HFRA; e. Number reportable ignitions for fully covered conductor circuit segments in the HFTD+HFRA. f. Number reportable ignitions for fully “bare wire” conductor circuit segments in the HFTD+HFRA; g. For ignitions on partially covered circuit segments in the HFTD+HFRA, or ignitions with uncertain origin, sum these into the “fully covered” or “bare wire” groups based on the most prevalent circuit configuration in the area of ignition. h. Number of outages attributable to infrastructure on fully “bare wire” conductor circuit segments in the HFTD+HFRA; i. Number of outages attributable to infrastructure on fully covered conductor circuit segments in the HFRA. j. For outages on partially covered circuit segments in the HFTD+HFRA, or outages with uncertain locations, sum these into the “fully covered” or “bare wire” groups based on the most prevalent circuit configuration in the area of the outage. | a. Please see “WMP-Discovery2026-2028_DR_MGRA_003-Q001Atch01.xlsx” for the requested information. Please note that the data provided reflects asset status as included in our Q4 spatial data deliveries to the Office of Energy Safety for each year from 2021-2024. Please note that PG&E has applied HFTD and HFRA filters based on current, not historical, definitions of HFTD and HFRA. b. Please see “WMP-Discovery2026-2028_DR_MGRA_003-Q001Atch01.xlsx” for the requested information. Please note that the data provided reflects asset status as included in our Q4 spatial data deliveries to the Office of Energy Infrastructure Safety for each year from 2021-2024. Please note that PG&E has applied HFTD and HFRA filters based on current, not historical, definitions of HFTD and HFRA. c. Please note that the data provided is drawn from PG&E’s Integrated Logging Information System (“ILIS”). The reporting structure for ILIS does not give single outage details for specific events, and wire down metrics may be over-reported as a result. ILIS records do not capture the type of wire, so PG&E is not able to differentiate between covered or bare conductor. In addition, ILIS does not capture HFRA locations, so the volume reported is limited to HFTD only. As a result of these limitations, PG&E is providing the total volume of wire down events in HFTDs in Part D for 2021, 2022, 2023 and 2024. d. Please see “WMP-Discovery2026-2028_DR_MGRA_003-Q001Atch01.xlsx” for the requested information. Please note that the data provided is drawn from PG&E’s Integrated Logging Information System (“ILIS”). The reporting structure for ILIS does not give single outage details for specific events, and wire down metrics may be over-reported as a result. ILIS records do not capture the type of wire, so PG&E is not able to differentiate between covered or bare conductor. In addition, ILIS does not capture HFRA locations, so the volume reported is limited to HFTD only. As a result of these limitations, PG&E is providing the total volume of wire down events in HFTDs in Part D for 2021, 2022, 2023 and 2024. e. Please see “WMP-Discovery2026-2028_DR_MGRA_003-Q001Rev01Atch01.xlsx” for the requested information. f. Please see “WMP-Discovery2026-2028_DR_MGRA_003-Q001Rev01Atch01.xlsx” for the requested information. g. PG&E’s ignition tracking does not identify “partially covered circuit segments” and all ignitions have a designated origin. No ignitions were summed into “fully covered” or “bare wire” for the purposes of this subpart. h. Please see “WMP-Discovery2026-2028_DR_MGRA_003-Q001Rev01Atch01.xlsx” for the requested information. Please note that ILIS records do not capture the type of wire, so PG&E is not able to differentiate between covered or bare conductor. In addition, ILIS does not capture HFRA locations, so the volume reported is limited to HFTD only. As a result of these limitations, PG&E is providing the total volume of outages in HFTDs in Part H for 2021, 2022, 2023 and 2024. i. Please note that ILIS records do not capture the type of wire, so PG&E is not able to differentiate between covered or bare conductor. In addition, ILIS does not capture HFRA locations, so the volume reported is limited to HFTD only. As a result of these limitations, PG&E is providing the total volume of outages in HFTDs in Part H for 2021, 2022, 2023 and 2024. j. ILIS does not allow PG&E to identify “partially covered circuit segments,” and all ignitions have a designated origin. No outages were summed into “fully covered” or “bare wire” for the purposes of this subpart. | Joseph Mitchell | 2025-04-11 | 2025-04-23 | 2025-04-23 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-MGRA_003.zip | 1 | No | 8 | Grid Design, Operations, and Maintenance | 8.4.4/8.2.10 | Conductor, Including Covered Conductor Other Grid Topology Improvements to Minimize Risk of Ignitions
15 | 45 | MGRA | 003 | MGRA_003 | 2 | No | MGRA_003_Q2 | Some of the risk drivers in Table 3-1 (pp. 20-21) show wind as a Climatological risk factor. Please provide a technical explanation as to why wind is a factor for the following Risk Sub-Drivers. Also provide data supporting this association: a. Capacitor Bank b. Fuse c. Lightning Arrestor d. Transformer e. Balloon f. Contamination | Wind increases the failure risk of overhead electrical utility equipment through both direct mechanical loading and indirect environmental effects. High wind speeds exert dynamic lateral forces on pole-mounted components such as capacitor banks, fuses, lightning arrestors, and transformers, especially those with large surface areas. Winddriven lateral forces can induce structural oscillations, accelerate fatigue, or cause displacement at the pole top – conditions that can accelerate structural degradation over time. Wind loading on conductors can also introduce tension imbalances and galloping, which can increase mechanical stress at connection points, bushings, and supporting structures. ASCE Manual No. 74 provides guidance for evaluating wind load impacts on transmission and distribution infrastructure. Wind also indirectly increases failure risk by driving foreign objects and vegetation into energized equipment. Vegetation clearance and line routing standards address the fact that high winds can cause branches or debris to contact components like fuses or WMP-Discovery 2026-2028_DR_MGRA_003-Q002 Page 2 arrestors, initiating phase-to-ground faults or electrical arcing. Mylar (metalized) balloons, which are highly conductive, can cause short circuits or flashovers (faults) when blown into energized overhead electrical equipment. Additionally, because devices like capacitor banks and transformers may have exposed energized-terminals and bushings, they can be vulnerable to mylar balloon-induced faults. Furthermore, wind contributes to the accumulation and activation of surface contamination – a known driver of insulation failure in overhead systems. Contamination refers to the buildup of debris or pollutants such as dust, salt, or industrial particulates on equipment and insulators. Under dry conditions, these materials typically cause no electrical or mechanical issues; however, wind combined with moisture (ex. fog or mist) can convert these deposits into conductive films. This can result in surface tracking or flashovers (faults), especially across insulators and bushings connected to transformers, capacitor banks, and lightning arrestors. IEEE Std 1313.2 and IEC 60815 provide methodologies to identify contamination and creepage distances to mitigate such failures. While the technical explanation (above) describes well-established engineering mechanisms, PG&E does not currently have asset-specific failure data that directly correlates wind conditions with elevated equipment failure rates or ignition rates for capacitor banks, fuses, lightning arrestors, transformers, or balloons. However, wind is a key component of PG&E’s Fire Potential Index (FPI), which is used extensively to inform the execution of key mitigations like PSPS and EPSS. | Joseph Mitchell | 2025-04-11 | 2025-04-16 | 2025-04-16 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-MGRA_003.zip | 0 | No | 3 | Overview of WMP | 3.4 | Prioritized List of Wildfire Risks and Risk Drivers
15 | 46 | MGRA | 003 | MGRA_003 | 3 | No | MGRA_003_Q3 | On p. 24, PG&E states that “These exceptional temperatures, in turn, impact the relative humidity of the atmosphere, increasing the occurrence of vapor pressure deficit that is also linked to more severe fires. These conditions also pose a health risk to vegetation, increasing the potential for branch or tree failures impacting our assets and creating potential sources of wildfire ignition.” a. What evidence does PG&E have that demonstrates how drought conditions relate to branch and tree failures? b. Has PG&E analyzed the relationship between drought variables and vegetation outage rates? If so please provide the results. c. If it has not done so, is it planning to do so and what would be the timeline? If it is not planning to do so what is the justification? | a. PG&E’s statement on page 24 of its WMP references a peer-reviewed article that offers strong scientific support for the mechanism of drought impact on tree aridity and stress. Specifically, it details how rising temperatures and increased vapor pressure deficit reduce vegetation moisture content and increase plant stress and flammability. The scientific rationale for linking drought conditions to tree mortality and failures is well established in the literature. For example, the article “Lesson from California’s 2012-2016 Drought”1 confirms this link stating: 1 Lessons from California’s 2012–2016 Drought. Jay Lund, Josue Medellin-Azuara, John Durand and Kathleen Stone. J. Water Resour. Plann. Manage., 2018 WMP-Discovery 2026-2028_DR_MGRA_003-Q003 Page 2 “Perhaps the greatest impact of California’s drought was the death of 1020 million forest trees, which depend on soil moisture accumulated in the wet season for growth during the spring and summer.” Though not PG&E-specific evidence, these peer-reviewed articles underscore how drought conditions severely compromise tree health. b. PG&E evaluated variables related to drought as inputs to the vegetation models released with WDRM v4, which are machine learning (ML) models trained on historical failure & outage events. Specifically, the SPEI (Standard Precipitation Evapotranspiration Index) and CWD (Climatic Water Deficit) were evaluated. The inputs needed to be summarized over multiple years to fit the Maximum Entropy ML algorithm configuration requirements, which is a spatial model. The multi-year aggregation and correlation to other weather variables caused the drought-related variables to have little influence in the model. These features are described in more detail in Section 3.5.2.3 in the Distribution Event Probability Models, Version 4 documentation available at Community Wildfire Safety Program. c. PG&E is continuing to evaluate whether inputs related to vegetation health, like soil moisture, can be incorporated into the vegetation models. If successful, the enhanced vegetation models would be released with Wildfire Distribution Risk Model (WDRM) v5. | Joseph Mitchell | 2025-04-11 | 2025-04-22 | 2025-04-22 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-MGRA_003.zip | 0 | No | 9 | Vegetation Management & Inspections | 9.9 | Activities Based on Weather Conditions
15 | 47 | MGRA | 003 | MGRA_003 | 4 | No | MGRA_003_Q4 | Provide technical description and available documentation for the Suppression Access model used in the WFC v4 Consequence model, along with data and analysis used to support the Suppression Access model. | Please refer to sections 2.4.2 and 4.1 in the Wildfire Consequence model version 4 documentation for details on the Suppression model, available at Community Wildfire Safety Program | Joseph Mitchell | 2025-04-11 | 2025-04-22 | 2025-04-22 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-MGRA_003.zip | 0 | No | 5 | Risk Methodology & Assessment | 5.4 | Summary of Risk Models
15 | 48 | MGRA | 003 | MGRA_003 | 5 | No | MGRA_003_Q5 | Provide technical description and available documentation for the Public Egress model used in the WFC v4 Consequence model, along with data and analysis used to support the Public Egress model. | Please refer to sections 2.4.3 and 4.2 in the Wildfire Consequence model version 4 documentation for details on the Public Egress model, available at Community Wildfire Safety Program | Joseph Mitchell | 2025-04-11 | 2025-04-22 | 2025-04-22 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-MGRA_003.zip | 0 | No | 5 | Risk Methodology & Assessment | 5.4 | Summary of Risk Models
15 | 49 | MGRA | 003 | MGRA_003 | 6 | No | MGRA_003_Q6 | Regarding the WDRM v4 ignition probability model: a. Are the covariates calculated for each geographic location in the machine learning models such as Random Forest calculated as one value per geographic location? Or are they calculated per year? b. Please provide tabular data supporting each of the “Feature Importance” figures in the Distribution Event Probability Models v4 documentation. c. If there is a single value for feature/attributes at each location, or if these are calculated on a coarse time scale (annually), then please provide GIS data for the following feature/attributes for the HFTD+HFRA areas of the PG&E service area: a) Average wildfire season daily max windspeed b) Percent difference from average wildfire season daily max windspeed c) Average wildfire season relative humidity d) Average wildfire season vapor pressure deficit e) Percent gusty summer day | c. The requested geospatial data is provided in the following formats. Each dataset was exported using EPSG:4326. • A shapefile is provided in the “WMP-Discovery2026-2028_DR_MGRA_003- Q006Supp01Atch01.zip” for the following data inputs. Each row represents a distribution support structure related to WDRM v4 and the associated multiyear average values. WMP-Discovery 2026-2028_DR_MGRA_003-Q006Supp01 Page 2 i. Average wildfire season daily max windspeed ii. Average wildfire season relative humidity iii. Average wildfire season vapor pressure deficit • A shapefile is provided in the Attachment “WMP-Discovery2026- 2028_DR_MGRA_003-Q006Supp01Atch02.zip” for the following data input. Each row represents a year of input data for a distribution support structure related to WDRM v4. i. Percent difference from average wildfire season daily max windspeed • A geotiff raster file in the Attachment “WMP-Discovery2026- 2028_DR_MGRA_003-Q006Supp01Atch03.tif” for the following data input. The raster file contains one band of data and is clipped to PG&E’s service territory. i. Percent gusty summer day | Joseph Mitchell | 2025-04-11 | 2025-05-05 | 2025-05-05 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-MGRA_003.zip | 1 | No | 5 | Risk Methodology & Assessment | 5.4 | Summary of Risk Models
15 | 49 | MGRA | 003 | MGRA_003 | 6(s) | Yes | MGRA_003_Q6(s) | Regarding the WDRM v4 ignition probability model: a. Are the covariates calculated for each geographic location in the machine learning models such as Random Forest calculated as one value per geographic location? Or are they calculated per year? b. Please provide tabular data supporting each of the “Feature Importance” figures in the Distribution Event Probability Models v4 documentation. c. If there is a single value for feature/attributes at each location, or if these are calculated on a coarse time scale (annually), then please provide GIS data for the following feature/attributes for the HFTD+HFRA areas of the PG&E service area: a) Average wildfire season daily max windspeed b) Percent difference from average wildfire season daily max windspeed c) Average wildfire season relative humidity d) Average wildfire season vapor pressure deficit e) Percent gusty summer day | c. The requested geospatial data is provided in the following formats. Each dataset was exported using EPSG:4326. • A shapefile is provided in the “WMP-Discovery2026-2028_DR_MGRA_003- Q006Supp01Atch01.zip” for the following data inputs. Each row represents a distribution support structure related to WDRM v4 and the associated multiyear average values. WMP-Discovery 2026-2028_DR_MGRA_003-Q006Supp01 Page 2 i. Average wildfire season daily max windspeed ii. Average wildfire season relative humidity iii. Average wildfire season vapor pressure deficit • A shapefile is provided in the Attachment “WMP-Discovery2026- 2028_DR_MGRA_003-Q006Supp01Atch02.zip” for the following data input. Each row represents a year of input data for a distribution support structure related to WDRM v4. i. Percent difference from average wildfire season daily max windspeed • A geotiff raster file in the Attachment “WMP-Discovery2026- 2028_DR_MGRA_003-Q006Supp01Atch03.tif” for the following data input. The raster file contains one band of data and is clipped to PG&E’s service territory. i. Percent gusty summer day | Joseph Mitchell | 2025-04-11 | 2025-05-06 | 2025-05-06 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-MGRA_003.zip | 3 | No | 5 | Risk Methodology & Assessment | 5.4 | Summary of Risk Models
15 | 50 | MGRA | 003 | MGRA_003 | 7 | No | MGRA_003_Q7 | Regarding Figure PG&E-6.1.3.2-1 (2026 Year Baseline) representing system-wide wildfire risk, do the values shown in the figure include PG&E’s risk scaling function? a. If the answer is ‘yes’, please provide a figure showing the same values without the scaling function (a neutral risk attitude). | Yes, the values shown in Figure PG&E-6.1.3.2-1 (2026 Year Baseline) includes PG&E’s risk scaling function. Please see the figure below which shows the same values without the scaling function (a neutral risk attitude). | Joseph Mitchell | 2025-04-11 | 2025-04-22 | 2025-04-22 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-MGRA_003.zip | 0 | No | 6 | Wildfire Mitigation Strategy Development | 6.1.3.2 | Activity Prioritization
15 | 51 | MGRA | 003 | MGRA_003 | 8 | No | MGRA_003_Q8 | Figure 6-1 (p. 149) shows PG&E’s fractional risk reduction on a yearly basis from 2023 to 2033. Using available data and methodology, please provide an equivalent risk reduction curve showing the fractional change of PG&E’s overall service territory wildfire risk between 2017 and 2024. | PG&E did not start estimating wildfire risk reduction until 2023 with the 2023-2025 WMP cycle. The risk reduction calculations require temporal and spatial alignment across a model version, circuit segments, and work plans. Currently, historical circuit segment datasets have only been prepared with a WDRM model release (earliest full-territory dataset is with WDRM v3). The earliest year that we have a WDRM model, respective circuit segment data, and associated work plans is in 2023. | Joseph Mitchell | 2025-04-11 | 2025-04-22 | 2025-04-22 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-MGRA_003.zip | 0 | No | 6 | Wildfire Mitigation Strategy Development | 6.1.3.2 | Activity Prioritization
15 | 52 | MGRA | 003 | MGRA_003 | 9 | No | MGRA_003_Q9 | Advanced Technologies PG&E states that “In 2023, there were observed ignitions that occurred during EPSS protection that were lower than the detectable thresholds of DCD. It was identified that a lower SGF pickup could have interrupted the events sooner, potentially preventing the ignition (DCD not present). In 2024, we revised SGF trip floor settings criteria and device reprogramming planned for increased detection of high-impedance faults to 5 amperage faults within 5 seconds.” a. Assuming that these ignitions are listed in the GIS and tabular data provided to MGRA by PG&E, indicate which of these ignitions were the high impedance faults that could potentially be detected by lower trip settings. b. What is the estimated increase in outage rate that would be caused by lowering the SGF trip floor setting to 5 amperes within 5 seconds? | a. Ignitions 20230693, 20230823, 20230912, 20231073, and 20231074 were the highimpedance faults that could potentially be interrupted sooner by lower SGF trip settings from 2023. b. As PG&E has just started to deploy the revised settings thresholds at the end of 2024 EPSS season, it is not possible to accurately estimate any negative reliability impact. While these changes are not expected to significantly contribute to negative reliability, there is not sufficient data to provide outage rate impacts at this time. PG&E will continue to monitor reliability system performance with SGF as settings are enabled in the 2025 EPSS season. | Joseph Mitchell | 2025-04-11 | 2025-04-16 | 2025-04-16 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-MGRA_003.zip | 0 | No | ACI PG&E-25U-06 | Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI PG&E-25U-06 | Evaluation and Reporting of Safety Impacts Relating to EPSS
15 | 53 | MGRA | 003 | MGRA_003 | 10 | No | MGRA_003_Q10 | On p. 458 PG&E writes that: “a paper on chaos and weather prediction from the European Centre for Medium-Range Weather states that: A requirement for skillful predictions is that numerical models can accurately simulate the dominant atmospheric phenomena. The fact that the description of some physical processes has only a certain degree of accuracy, and the fact that numerical models simulate only processes with certain spatial and temporal, is the second source of forecast errors. Computer resources contribute to limit the complexity and the resolution of numerical models and assimilation—since, to be useful, numerical predictions must be produced in a reasonable amount of time. These two sources of forecast errors cause weather forecasts to deteriorate with forecast time.” a. Provide a citation for this paper. | Please see “WMP-Discovery2026-2028_DR_MGRA_003-Q010Atch01.pdf,” and citation below: Buizza, Roberto. "Chaos and weather prediction January 2000." European Centre for medium-range weather meteorological training course lecture series ECMWF (2002). | Joseph Mitchell | 2025-04-11 | 2025-04-16 | 2025-04-16 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-MGRA_003.zip | 1 | No | 10 | Situational Awareness and Forecasting | 10.5 | Weather Forecasting
15 | 54 | MGRA | 003 | MGRA_003 | 11 | No | MGRA_003_Q11 | Please provide tabular data in Excel spreadsheet format containing the data in the following tables: a. TABLE 4-3: FREQUENTLY DE-ENERGIZED CIRCUITS (CONTINUED) b. TABLE 5-5: SUMMARY OF TOP-RISK CIRCUITS, SEGMENTS, OR SPANS c. TABLE 6-1: PG&E PRIORITIZED AREAS BASED ON OVERALL UTILITY RISK d. Table 6-4 - TABLE 6-4: SUMMARY OF RISK REDUCTION FOR TOP RISK | Please see “WMP-Discovery2026-2028_DR_MGRA_003-Q011Atch01.xlsx” for all tables in PG&E’s 2026-2028 WMP in Excel spreadsheet format. | Joseph Mitchell | 2025-04-11 | 2025-04-16 | 2025-04-16 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-MGRA_003.zip | 1 | No | 7 | Public Safety Power Shutoff | 7.7/6.2.1 | Public Safety Power Shutoff
15 | 55 | OEIS | 002 | OEIS_002 | 1 | No | OEIS_002_Q1 | PG&E states on page 168 of its 2026-2028 Base WMP that “The number of PSPS events is driven by weather, in particular wind speed and fuel conditions, both of which are difficult to reduce. However, PG&E is continuously improving our risk model sensitivity to weather, vegetation, and fuel conditions through the adoption of changes in our FPI, Ignition Probability Weather, and Operability Assessment models.” PG&E shows in Table 10.6.1-1 FPI Class Breakpoints on page 476 of the 2026-2028 Base WMP, that there are 4 tiers of FPI Breakpoints categorized as “Small, Large, Critical, and Catastrophic” based on potential fire acreage size. In the PSPS State Executive Briefings Slide Deck utilized on the December 9, 2024, PSPS briefing (slide 2), PG&E shows the Fire Potential Index as “R3”. a. Provide the following information regarding the Fire Potential Index Breakpoints and how they are used in the initiation of PSPS events: i. Clarification of the Fire Potential Index naming conventions used between the WMP submission and those utilized on the State Executive Briefings. Describe how “Small, Large, Critical, and Catastrophic” designations relate to the R1, R2, R3, etc. designations. ii. A detailed description of what weather conditions are associated with each level of the FPI Breakpoints (i.e. Small, Large, Critical, Catastrophic). iii. The initiation criteria for PSPS events for each of the FPI Breakpoints (i.e. Small, Large, Critical, Catastrophic). | a. i. The FPI model is based on a multi-classification balanced random forest framework, a state-of-the-art open-source machine learning model based on decision trees. FPI is trained on the novel fire occurrence dataset developed by Sonoma Technology (McClure et. al., 2023) that combines agency fire information with satellite fire detections. Fire detections are derived from satellite infrared data and provide information on the location, intensity and time of fires. FPI was trained on this historical dataset using defined classes that separate small, moderate, critical, and catastrophic defined fires. These classes are determined by both fire spread and intensity. For example, a slow moving, low intensity fire would be defined as small, while a fast moving, intense fire would be defined as catastrophic. These small to catastrophic definitions described here only apply to the FPI. The FPI model was trained using historical weather, fuels and topography data to be able to forecast the probability of small to catastrophic fires in both space and time. The actual FPI model outputs the conditional probability from 0 – 100% fire growth or intensity will align to the small, moderate, critical or catastrophic classes described in the WMP. The probability of the critical and catastrophic classes combined is translated into a fire danger rating scale from R1 (low) to R5 (extreme) based on climatological breakpoints and calibration with historical incidents. This method mirrors industry standards; for example, how unitless, relativistic numeric outputs of Energy Release Component or Burning Index from the Federal National Fire Danger Rating System (NFDRS) are translated to fire danger ratings from low, medium, high, very high and extreme (https://www.nwcg.gov/publications/pms437/fire-danger/nfdrs-system-inputsand-outputs). The NFDRS fire danger rating scale versus FPI is shown below; moving up the scale from R1 to R5 increases the forecasted conditional probability of critical or catastrophic growth or intensity according to the FPI classifications described above. We use the R (Rating) scale and not the NFDRS scale based on a historical request from agencies. Table 1. Fire potential index scale versus NFDRS rating and color scale WMP-Discovery 2026-2028_DR_OEIS_002-Q001 Page 3 ii. 32 model features were selected in the final FPI model for operations, which are summarized below. These model features are combined in both space and time to output the probability of fires across the classes described above. In general, the drier the fuel conditions, the windier the weather, lower the RH and more rugged the terrain, the FPI will increase probabilities in the critical class. The FPI 5.0 model features include: • weather features of wind speed, turbulence, temperature, and vapor pressure deficit, • new NDVI herbaceous fuel moisture model and enhanced existing dead, herbaceous and woody fuel moisture models, • topography features including terrain ruggedness and slope, • new soil moisture and solar radiation features, • improved fuel categories, • new fuel properties features including fuel bed depth and fuel complexity. • The fuel categories, fuel properties and topography features are aggregated to the 0.7km2 hexagons from the underlying 30m resolution. iii. The minimum criterion for FPI is >0.22 probability in the catastrophic fire class; however, PSPS could be initiated at lower values based on other factors considered like federal forecasts and external forecasts. This value was established from a historical review of past fires near ignition time and location (see figure below). | Nathan Poon | 2025-04-11 | 2025-04-16 | 2025-04-16 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_002.zip | 0 | No | 7 | Public Safety Power Shutoff | 7 | Public Safety Power Shutoff
15 | 56 | OEIS | 002 | OEIS_002 | 2 | No | OEIS_002_Q2 | Regarding improvements to accuracy of asset inventory data On page 536 of its 2026-2028 Base WMP, PG&E describes its objective to “evaluate and create new method(s) to improve the accuracy of asset inventory data (ES-02)” as an effort that “involves the design, development, and evaluation of methods to validate the accuracy of asset inventory data,” and Table 12-1 (page 538) states that the objective completion date is December 31, 2028. Additionally, Table 13-2 (page 553) identifies that the “Filling Asset Inventory Data Gaps (AI-11)” initiative from the 2023-2025 Base WMP “will continue under ES-02.” a. Describe the status of PG&E’s efforts to populate missing age data in the asset registry. b. Explain the relationship between ES-02 and the Asset Registry Data Quality (ARDQ) program described in its response to PG&E-22-33 – Progress on Filling Asset Inventory Data Gaps (PG&E 2023-2025 Base WMP R8, pages 1133-1135). c. Describe the milestones PG&E will use to measure progress toward this objective. | a. PG&E understands this sub-question to be related to the 2023-2025 AI-11 objective to populate missing age data in the asset registry to a 90% weighted average across risk prioritized distribution and transmission equipment types. PG&E has other data remediation projects and programmatic efforts like its map correction program that will not be covered in this response. Below are the milestones PG&E has achieved under the AI-11 objective: • In 2023, PG&E completed proof-of-concept projects to test the feasibility of manual and automated methods for locating missing age data, including field data collection, electronic records review, paper record scanning and review, and identification of PG&E age proxy data for the targeted equipment types. WMP-Discovery 2026-2028_DR_OEIS_002-Q002 Page 2 • In 2024, PG&E piloted both automated and manual methods of identifying age data to determine the scalability of each method. From these activities, PG&E determined that the cost and time required to manually remediate installation date data warranted a shift in approach to generating Estimated Asset Age using available age proxy data. • In Q4 of 2024, PG&E presented to the OEIS the plan to shift the focus of the AI-11 commitment toward generating Estimated Asset Ages. • In Q1 of 2025, PG&E deployed its Estimated Asset Age model that generates data-derived installation years for the 11 targeted, risk-prioritized transmission and distribution types. • In Q1 of 2025, PG&E also finalized its extended piloting to identify ways to optimize the scanning and review of paper records to identify installation dates. • By end of Q4 2025, PG&E expects the quantification of the Estimated Asset Age model results to be available. b. The Asset Registry Data Quality (ARDQ) program is designed to measure asset registry data quality dimensions using data quality rules. However, assessing the data quality dimension of Accuracy requires real-world validation. As such, the ARDQ program is not currently equipped with a means to establish a baseline of data accuracy and measure improvements. The objective of the ES-02 project is to identify and evaluate various methods for validating the accuracy of targeted asset registry data (e.g., leveraging field-based inspections, leveraging AI computer vision applied to asset photographs). To the extent possible, the ARDQ program will measure the validation of accurate data, and the correction of inaccurate data generated through ES-02 methods from a baseline. c. PG&E has not yet developed the milestones associated with the ES-02 objective but expects to have milestones developed by the end of Q3 2025. | Nathan Poon | 2025-04-11 | 2025-04-16 | 2025-04-16 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_002.zip | 0 | No | ES-02/AI-11 | ES-02/AI-11 | ES-02/AI-11 | ES-02/AI-11
15 | 57 | OEIS | 002 | OEIS_002 | 3 | No | OEIS_002_Q3 | Regarding PG&E’s Q4 quarterly data report for 2022, 2023, and 2024 PG&E’s 2026-2028 Base WMP defines “Fire Rebuild” work as undergrounding installations in areas impacted by wildfires within High Fire Threat District (HFTD); and defines “Community Rebuild” work as undergrounding installations in areas impacted by wildfires outside of the HFTD. Additionally, PG&E states that its undergrounding work includes activities under System Hardening, Butte County Rebuild, Community Rebuild programs, and other efforts in HFTD, High Fire Risk Area (HFRA), buffer zones, and fire rebuild areas. a. For 2024: PG&E reported 348.3 circuit miles total completed under 10K Undergrounding (GH-04). Provide a breakdown of the total miles completed in 2024 by the following categories: i. Undergrounding as part of System Hardening (GH-01) activity. ii. Undergrounding as part of its Fire Rebuild program iii. Undergrounding as part of its Community Rebuild program iv. Any other undergrounding work performed in HFTD, HFRA and Buffer Zone A. For each other type of undergrounding work specified here, explain why this work was not reported under the System Hardening (GH-01) activity. b. For 2023: PG&E reported 363.9 circuit miles total completed under 10K Undergrounding (GH-04). Provide a breakdown of the total miles completed in 2023 by the following categories: i. Undergrounding completed as part of System Hardening (GH-01); ii. Undergrounding completed as part of the Fire Rebuild program; iii. Undergrounding completed as part of the Community Rebuild program; iv. Any other undergrounding completed in HFTDs, HFRAs, or buffer zones. A. For each other type of undergrounding work specified here, explain why this work was not reported under the System Hardening (GH-01) activity. | Please see the table below for the requested information in subparts a. and b. The data provided is updated as of January 14, 2025, in alignment with the Q4 2024 WMP Quarterly Data Report (QDR). Note, the data provided is slightly adjusted from the values reported in the Q4 2023 QDR due to the completion of project as-built construction packages. For clarity, in 2024, PG&E completed 257.8 miles under WMP initiative GH-04, not 348.3 miles referenced in the question, which are the miles completed in WMP initiative GH-01, instead. Based on the detail included in the question, we assume the intention was to include the total completed GH-04 mileage and associated sub-programs, which is reflected in our response. Year i. Undergrounding as part of System Hardening activity1 ii. Undergrounding as part of the Fire Rebuild program2 iii. Undergrounding as part of the Community Rebuild program3 iv. Any other undergrounding work performed in HFTD, HFRA and Buffer Zone4 Total (i+iii+iv) a. 2024 213.8 27.5 42.0 2.0 257.8 b. 2023 284.4 57.6 75.7 4.1 364.2 1 System Hardening Undergrounding miles are included in both 2023 Base WMP Initiatives: GH-01 System Hardening and GH-04 Undergrounding. 2 Fire Rebuild Undergrounding miles are included in the GH-01 System Hardening activity and these miles are included for reference, not in addition to the miles under sub-part i. These miles are also included in GH-04. 3 The Community Rebuild Program includes Butte and other Community Rebuild. These Undergrounding miles are only included in GH-04, and not in GH-01. 4 Undergrounding work in this Other category includes projects that were initiated under other programs outside of the System Hardening program which is funded by MAT codes 08W and 3UG, such as Work Requested by Others (WRO), capacity, and Rule 20 B and C programs. These Undergrounding miles are included in both GH-01 and GH-04. In the table below, PG&E reiterates the sub-program activities that contribute to the GH01 and GH-04 Initiatives in the 2023 WMP, as well as the updated 2026 WMP Initiative GH-12. In the 2023 WMP, the System Hardening Undergrounding is included in both GH-04 and GH-01 initiatives. In the 2026-2028 Base WMP, the GH-01 initiative was retired due to the overlap with GH-04. The covered conductor target is now GH-12 and no longer includes undergrounding. GH-12 includes work associated with overhead distribution hardening (covered conductor installation) and line removal with remote grid for base system hardening work, fire rebuild work, and other work in the HFTD. GH-04 will continue as is from the 2023 WMP to the 2026 WMP. | Nathan Poon | 2025-04-11 | 2025-04-16 | 2025-04-16 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_002.zip | 0 | No | 8 | Grid Design, Operations, and Maintenance | 8.2.2 | Undergrounding of Electric Lines and/or Equipment
15 | 58 | OEIS | 002 | OEIS_002 | 4 | No | OEIS_002_Q4 | Regarding Distribution Infrared Inspections On page 247 of its 2026-2028 WMP, PG&E states that it shifted its distribution IR inspection program from inspecting all the HFTD/HFRA in 2020-2022, to focusing on specific areas with known issues expected to be detectable by IR in 2023-2025 (mostly outside of the HFTD/HFRA). In 2026-2028, PG&E plans to “target IR to areas of emerging concern as needed.” a. Provide the following distribution IR inspection data: i. The number of inspections performed in 2021, 2022, 2023, and 2024. ii. The number of inspections performed in the HFRA/HFTD in 2021, 2022, 2023, and 2024. iii. The number of level 1 conditions identified by distribution IR inspections in 2021, 2022, 2023, and 2024. iv. The number of level 1 conditions identified by distribution IR inspections in the HFRA/HFTD in 2021, 2022, 2023, and 2024 v. The number of level 2 conditions identified by distribution IR inspections in 2021, 2022, 2023, and 2024. vi. The number of level 2 conditions identified by distribution IR inspections in the HFRA/HFTD in 2021, 2022, 2023, and 2024 b. Provide the estimated number of level 1 and 2 conditions that would have been identified by distribution detailed inspections, aerial scan inspections, or sensor readings, had an inspection or sensor reading been used in place of the IR inspection. i. For each IR condition that PG&E anticipates would have been identified by a sensor reading, provide the sensor manufacturer and model/series number that could have identified the issue, and the percentage of PG&E's assets in the HFTD/HFRA that are currently actively monitored by the sensor. ii. For each IR condition that PG&E anticipates would have been identified by a detailed or scan inspection, provide a description of the visible indicators expected to be present and the corresponding inspection guidance on job aid TD-2305M-JA02 rev 14. c. Provide the criteria PG&E will use to determine areas of emerging concern that warrant IR inspections. | a. Table 1: Q4(a)(i)-(vi) Infrared Inspections and Findings Metric Number Metric Name 2021 2022 2023 2024 Q4(a)(i) Total Inspections Performed1 12948 10080 3686 2224 Q4(a)(ii) HFTD-HFRA Inspections Performed1 10094 9560 3618 2152 Q4(a)(iii) Total Level 1 Conditions Identified 0 0 0 0 Q4(a)(iv) HFTD-HFRA Level 1 Conditions Identified 0 0 0 0 Q4(a)(v) Total Level 2 Conditions Identified 108 72 35 21 Q4(a)(vi) HFTD-HFRA Level 2 Conditions Identified 61 62 26 12 1. Infrared (IR) inspections are conducted by circuit-mile. Inspection counts represent miles of conductor inspected by IR. b. i. Sensors can detect some of the excessive heat conditions that would be detected by IR, but this ability would be highly dependent on the specific type and placement of the sensor. The proportion of IR conditions that may have been caught by visual or sensor means is not quantifiable since new technologies such as Early Fault Detection and pole monitoring sensors are currently in pilot phases and have limited deployment. ii. IR inspections detect excessive heat conditions that are not readily detected by visual means, including ground and aerial inspections. To a limited extent, overheating equipment may leave charring or arcing marks that may in some WMP-Discovery 2026-2028_DR_OEIS_002-Q004 Page 3 more severe cases be detectable visually, and faulting transformers may have some electrical anomalies that may be caught with sensors or visual fault indicators. c. At this time, PG&E does not apply a fixed or predefined set of criteria to identify areas of emerging concern that require an IR inspection. IR locations are informed by a combination of operational experience, risk assessments, failure assessments, asset data, time since last IR inspection and field observations. For example, based on IR’s ability to detect connector failures, PG&E may focus IR inspections on circuit segments with known historical failures and high concentrations of connectors. | Nathan Poon | 2025-04-11 | 2025-04-16 | 2025-04-16 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_002.zip | 0 | No | 8 | Grid Design, Operations, and Maintenance | 8.3.10 | Distribution - Infrared Inspections
15 | 59 | OEIS | 002 | OEIS_002 | 5 | No | OEIS_002_Q5 | Regarding distribution detailed aerial and ground inspections On page 226 of it WMP, PG&E sets a target of 218,000 distribution detailed inspections per year for 2026-2028. The target states the inspections can be either ground or aerial; separate targets are not provided for detailed aerial or detailed ground inspections. a. Provide the following information related to scheduling detailed aerial and ground inspections: i. Does PG&E have controls in place to avoid an asset being only subject to one variety of detailed inspection for extended periods of time? (i.e. an asset in an area of extreme consequence and extreme wildfire risk only receiving detailed aerial inspections for 10 years). Provide PG&E’s reasoning for its chosen approach. b. Some hazardous conditions may be less likely identified via ground inspections while others may be less likely identified via aerial inspections. ii. Provide a list of conditions that PG&E has recognized as being more likely identified via aerial inspections and less likely identified via ground inspections. Provide a brief explanation for each condition. A. If PG&E has not recognized any such conditions, briefly discuss its reasoning. iii. Provide a list of conditions that PG&E has recognized as being more likely identified via ground inspections and less likely identified via aerial inspections. Provide a brief explanation for each condition. A. If PG&E has not recognized any such conditions, briefly discuss its reasoning. | a. PG&E anticipates that the vast majority of detailed inspections completed in HFTD/HFRA in the 2026-2028 time frame will be completed via aerial means. PG&E is working towards having the aerial inspection meet PG&E’s GO 165 detailed inspection requirements beginning in 2026. Ground inspections may continue to be used where aerial inspections cannot access the structure due to various issues such as customer or vegetation. Changes in HFTD/HFRA inspection frequency are reviewed and approved through PG&E’s Wildfire Risk Governance Committee to ensure changes mitigate wildfire risk. As described in response to part b below, PG&E expects that the detailed aerial inspection will detect all conditions that the ground inspection detects. b. PG&E has been improving and maturing its aerial inspections as aerial has evolved from pilot stages to an inspection deployed at scale. In 2023, the pilot aerial inspection focused on only pole top conditions. In 2024, as PG&E deployed the inspection at scale for the first time, we expanded the aerial inspection to include the full structure. The aerial inspection performed by PG&E in 2024 and 2025 is a risk-based inspection, focusing on identifying Level 1 and 2 conditions. It was not a detailed GO 165 inspection for all abnormal compelling conditions. This risk-based aerial inspection demonstrated improved ability to detect most Level 1 and 2 conditions on the assets that are most likely to fail: pole, crossarm/insulator, equipment, and conductor conditions. However, since aerial inspection was limited to Level 1 and 2 conditions, it would not report Level 3 conditions such as high voltage sign, visibility strip, and guy issues that the ground inspection detects. For 2025, PG&E already updated the aerial shot sheet to enable better capture of exposed grounds and issues that require particular angles to detect such as leaning poles and slack guys. There was also a need to create a handheld shot sheet in order to capture photos where drone flights were not able to be completed due to safety concerns or tree obstructions. This shot profile will allow the desktop inspector to do a full inspection using a combination of drone imagery and images captured from the handheld device. Currently, PG&E is identifying additional requirements to make the aerial inspection a GO-165 detailed inspection beginning in 2026. These include adding the requirement for aerial to report Level 3 conditions as well as the handful of conditions that are currently reported by ground inspections but not part of the aerial inspection. These include idle facilities, third party notifications, and vegetation notifications. Once these changes are implemented, PG&E expects the detailed aerial inspection to detect all conditions the detailed ground inspection detects. | Nathan Poon | 2025-04-11 | 2025-04-16 | 2025-04-16 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_002.zip | 0 | No | 8 | Grid Design, Operations, and Maintenance | 8.3.8 | Distribution - Detailed Ground Inspection
15 | 60 | OEIS | 002 | OEIS_002 | 6 | No | OEIS_002_Q6 | Regarding transmission detailed aerial and ground inspections On page 226 of it WMP, PG&E sets a target of 22,000 transmission detailed inspections per year. The target states the inspections can be either ground or aerial; separate targets are not provided for detailed aerial or detailed ground inspections. a. Provide supporting documentation for transmission detailed inspections, including any job aids, procedural documentation, or inspector checklists. Specify any documents that are unique to aerial or ground inspections. b. Provide the following information related to scheduling detailed aerial and ground inspections: i. Does PG&E have controls in place to avoid an asset being only subject to one variety of detailed inspection for extended periods of time? (i.e. an asset only receiving detailed aerial inspections for 10 years). Provide PG&E’s reasoning for its chosen approach. c. Some hazardous conditions may be less likely identified via ground inspections while others may be less likely identified via aerial inspections. i. Provide a list of conditions that PG&E has recognized as being more likely identified via aerial inspections and less likely identified via ground inspections. Provide a brief explanation for each condition. A. If PG&E has not recognized any such conditions, briefly discuss its reasoning. ii. Provide a list of conditions that PG&E has recognized as being more likely identified via ground inspections and less likely identified via aerial inspections. Provide a brief explanation for each condition. A. If PG&E has not recognized any such conditions, briefly discuss its reasoning. | a. See attachment “WMP-Discovery2026-2028_DR_OEIS_002- Q006Atch01CONF.zip” for 2025 job aids, inspection form, and inspection procedures. b. i. Currently both Ground and Aerial inspections are required for HFTD/HFRA structures but the frequency or population scope of either inspection method may evolve in the future to best address wildfire risk based on inspection finding trends and emerging technology. Changes in HFTD/HFRA inspection frequency are reviewed and approved through PG&E’s Wildfire Risk Governance Committee to ensure changes mitigate wildfire risk. c. i. PG&E has identified conditions located at the top of structures are more likely to be identified by Aerial in comparison to Ground inspections due to the higher vantage point of the aerial method. This includes conditions related to: • Conductor • Jumper • Insulator • Switch • Pole top • Tower peak ii. PG&E has identified conditions located at the bottom of structures are more likely to be identified by Ground in comparison to Aerial inspections due to the ground level vantage point of the inspectors. This includes conditions related to: • Foundations • Guys • Anchors | Nathan Poon | 2025-04-11 | 2025-04-16 | 2025-04-16 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_002.zip | 1 | No | 8 | Grid Design, Operations, and Maintenance | 8.3.1 | Transmission - Detailed Inpsection Program
15 | 61 | OEIS | 002 | OEIS_002 | 7 | No | OEIS_002_Q7 | Regarding transmission switch function testing PG&E does not provide a target for its transmission switch function testing inspection program in its 2026-2028 Base WMP. However, of the ten inspection initiatives with find rates provided, transmission switch function testing demonstrates the highest find rate of level 1 conditions and the fourth highest find rate of level 2 conditions. a. Briefly discuss PG&E’s reasoning for not including a compliance target for transmission switch testing. b. Provide the following data for transmission switch function testing: i. The total number of transmission switches in the HFTD/HFRA in 2022, 2023, and 2024. ii. The number of transmission switch function tests performed in the HFRA/HFTD in 2022, 2023, and 2024. iii. The number of level 1 conditions identified in 2022, 2023 and 2024. iv. The number of level 1 conditions with associated wildfire risk identified in 2022, 2023, and 2024. v. The number of level 2 conditions identified in 2022, 2023 and 2024. vi. The number of level 2 conditions with associated wildfire risk identified in 2022, 2023, and 2024. | a. The Switch Function Test program is in the process of maturation and is reliant on opportunistic clearance timing. The process of scheduling and executing these inspections has been steadily improving as shown by the growth in completed inspections year over year. PG&E tentatively expects to revisit the decision on whether to include this program as a WMP target in 2029. WMP-Discovery 2026-2028_DR_OEIS_002-Q007 Page 2 b. NOTE: Due to the small sample size of the Switch Function Test program the find rate reported in PG&E’s submitted WMP includes both HFTD and Non-HFTD. | Nathan Poon | 2025-04-11 | 2025-04-16 | 2025-04-16 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_002.zip | 0 | No | 8 | Grid Design, Operations, and Maintenance | 8.3.5 | Transmission - Switch Function Testing
15 | 62 | OEIS | 002 | OEIS_002 | 8 | No | OEIS_002_Q8 | Regarding vegetation inspections and pole clearing targets On WMP page 356, PG&E provides quantitative targets for its vegetation inspection and vegetation management programs. For the column “% HFTD Covered in 2026” it appears PG&E provided the percentage of the 2026 target that is performed within the HFTD. The WMP Guidelines (page 104) defines this column as “the percentage of total overhead circuit miles in the HFTD covered by the [Year 1] target (e.g., 100 circuit miles of patrol inspections in [Year 1] divided by 300 overhead circuit miles in the HFTD equals 33 percent coverage)” a. Provide the equation PG&E used to calculate the “% HFTD Covered in 2026” column. b. If PG&E used a different equation other than the one defined in the Guidelines, provide “% HFTD in 2026” figures for each of PG&E’s targets in Table 9-2 using the calculation defined in the WMP Guidelines. For targets that do not use overhead circuit miles as a unit, the denominator should be the total number of the unit present the HFTD. | a. The equation used to calculate the “% HFTD Covered in 2026” is as follows: For VM-02: The quantity of VM-02 inspected poles in HFTD divided by the total inventory of VM-02 inspected poles for 2026. For VM-05, VM-06, VM-07: The quantity of sub stations/power generation facilities in HFTD divided by the total inventory of inspected substations for 2026. For VM-13, VM-14, VM-16, and VM-17: The total 2026 program miles in HFTD is divided by the total 2026 program miles target. WMP-Discovery 2026-2028_DR_OEIS_002-Q008 Page 2 b. The %HFTD as defined in the WMP guidelines are as follows: VM-02: 8% of Distribution Poles in HFTD for 2026 VM-05: 100% of Distribution substations in HFTD for 2026 VM-06: 100% of Transmission substations in HFTD for 2026 VM-07: 100% of power generation substations in HFTD for 2026 VM-13: 100% of Routine Transmission-Ground miles in HFTD for 2026 VM-14: 100% of Transmission Hazard Patrol in HFTD for 2026 VM-16: 100% of HFTD distribution circuit miles in 2026 VM-17: 39% of HFTD distribution circuit miles in 2026 | Nathan Poon | 2025-04-11 | 2025-04-16 | 2025-04-16 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_002.zip | 0 | No | 9 | Vegetation Management & Inspections | 9.4 | Pole Clearing
15 | 63 | OEIS | 002 | OEIS_002 | 9 | No | OEIS_002_Q9 | Regarding Distribution Routine Patrol quantitative targets (VM-16) On WMP page 356, PG&E sets cumulative quarterly targets for Q4 in 2026, 2027, and 2028 of 78,200, 77,800, and 77,500 circuit miles respectively. These are annual decreases of 400 miles from 2026 to 2027, and 300 miles from 2027 to 2028. a. Do the incrementally decreasing targets reflect miles of distribution lines projected to be undergrounded? i. If so, explain how PG&E calculated each annual decrease in Distribution Routine Patrol target circuit miles. ii. If not provide the justification for each annual decrease in Distribution Routine Patrol target circuit miles. | a. Yes, the incremental decrease is based on mileage reduction due to undergrounding for the respective year. i. PG&E utilized the total mileage from prior year’s total distribution mileage less the total underground mileage workplan for the current year to end of year. For example, the tentative 2026 underground mileage plan is 400 miles, therefore the inspection targets were reduced by 400 miles for 2027. ii. N/A | Nathan Poon | 2025-04-11 | 2025-04-16 | 2025-04-16 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_002.zip | 0 | No | 9 | Vegetation Management & Inspections | 9.1.2 | Quantitative Targets
15 | 64 | OEIS | 002 | OEIS_002 | 10 | No | OEIS_002_Q10 | Regarding PG&E’s Pole Clearing Program target (VM-02) On page 356 of its 2026-2028 Base WMP, PG&E sets cumulative quarterly targets for Q4 in 2026, 2027, and 2028 of 70,000 distribution poles. a. Clarify whether PG&E’s target is to clear vegetation around 70,000 distribution poles or inspect 70,000 distribution poles and clear vegetation at those poles only as needed. b. Of the 70,000 poles targeted for pole clearing specify how many of those poles: i. Are required to be cleared under Public Resources Code (PRC) 4292. ii. Are not required to be cleared under PRC 4292. | a. PG&E’s target is to inspect 871,000 distribution/transmission poles and a target to clear vegetation at 70,000 of those poles if necessary. Please note, the VM-02 Pole Clearing target will be adjusted as determined by inspections in the previous year and may additionally be impacted by changes to facilities or based on other utility risk mitigation reasons. b. Based on the 2025 analysis: i. Approximately 66% of the Poles are required to be cleared under PRC 4292. ii. Approximately 34% of these Poles are not required to be cleared under PRC 4292. See WMP Section 9.4.1 for further information regarding PG&E’s risk reduction pole clearing work. | Nathan Poon | 2025-04-11 | 2025-04-16 | 2025-04-16 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_002.zip | 0 | No | 9 | Vegetation Management & Inspections | 9.4 | Pole Clearing
15 | 65 | OEIS | 002 | OEIS_002 | 11 | No | OEIS_002_Q11 | Regarding PG&E-23B-21 Identification of High-Risk Species for Focused Tree Inspections On page 591 of its 2026-2028 WMP, PG&E defines “criteria for determining which [tree] species warrant increased scrutiny during Focused Tree Inspections and other inspections.” PG&E states that it provides Vegetation Management Inspectors (VMIs) historical outage data and developed a “dashboard [that] allows the user to drill down to the circuit or CPZ level to see historical outage and ignition causes by species, diameter, and failure.” a. Is PG&E able to calculate outage and ignition probabilities by tree species at the CPZ level? i. If it is able to calculate outage and ignition probabilities by tree species, how does PG&E plan to use this information to inform its vegetation management program? ii. If it is unable to calculate outage and ignition probabilities by tree species, list the information PG&E would require to perform this calculation. A. Describe when PG&E expects to obtain the information it requires to calculate outage and ignition probabilities by tree species. | a. PG&E has calculated outage probability by tree species at the eco-region level. There is not enough data at the CPZ level to confidently estimate the outage or ignition probability of tree species at such a granular level. PG&E plans to evaluate ignition probability of tree species at the eco-region level in 2025. i. At present, we do not plan to use this information to inform our vegetation management program. ii. N/A | Nathan Poon | 2025-04-11 | 2025-04-16 | 2025-04-16 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_002.zip | 0 | No | ACI PG&E-23B-15 | ACI PG&E-23B-15 | ACI PG&E-23B-15 | ACI PG&E-23B-15
15 | 67 | OEIS | 002 | OEIS_002 | 12 | No | OEIS_002_Q12 | Regarding Integrated Vegetation Management (VM-15) On page 384 of its 2026-2028 WMP, PG&E states that “TIVM [transmission integrated vegetation management] LiDAR data…assesses vegetation conditions by electric transmission lines (ETL).” On page 356, PG&E targets 17,500 miles annually for its Routine Transmission Patrol (VM-13), and 5,625 circuit miles annually for its Transmission Hazard Patrol (VM-14). a. Do the Routine Transmission Patrol (VM-13) and the Transmission Hazard Patrol (VM-14) also capture the LiDAR data used for TIVM? b. List the number of circuit miles PG&E inspects annually using LiDAR to assess transmission rights-of-way for IVM. c. Clarify how the Transmission Hazard ortho-imagery is captured (e.g., satellite, helicopter, drone, etc.). d. What other remote sensing data does PG&E collect besides ortho-imagery during the Transmission Hazard Patrol (VM-14)? (e.g., LiDAR, infrared, etc.). | a. Yes; TIVM utilizes the same LiDAR collection as Routine Transmission Patrol (VM13) and Transmission Hazard Patrol (VM-14). b. The circuit mileage used to assess transmission rights-of-way for IVM (VM-15) are the same as the circuit mileage assessed for Routine Transmission Patrol (VM-13), which is approximately 17,500 circuit miles systemwide. c. Fixed wing aircraft are utilized to capture imagery for the Transmission Hazard Patrol program. d. PG&E does not collect any other remote sensing data besides ortho-imagery during Transmission Hazard Patrol (VM-14). | Nathan Poon | 2025-04-11 | 2025-04-16 | 2025-04-16 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_002.zip | 0 | No | 9 | Vegetation Management & Inspections | 9.7 | Integrated Vegetation Management
15 | 68 | OEIS | 002 | OEIS_002 | 13 | No | OEIS_002_Q13 | Regarding risk model documentation a. Page 6 of PG&E’s Distribution Event Probability Models Version 4 (DEPM v4) Documentation includes “RaDA Algorithms and Methodologies” under its list of documents as part of the documentation suite for the Wildfire Distribution Risk Model (WDRM) v4. Provide a copy of this document. b. Figure 24: RaDA Product Plan – WDRM on page 25 of PG&E’s Wildfire Distribution Risk Model Version 4 (WDRM v4) Documentation shows that the following components are not included in the WDRM plan: Insulator Contamination Update, Public Safety Risk Model v2, Reliability Risk Model v1, Public Safety Consequence v2, and Reliability Consequence V1. i. Why are these components not included in WDRM plans? ii. Provide documentation that captures and discusses these components, similar to the documentations provided for the DEPM v4, WDRM v4, and WFC v4. | a. “See “WMP-Discovery2026-2028_DR_OEIS_002-Q013Atch01.pdf”. b. i. The Insulator Contamination model is under development for the WTRM but is not yet completed. It will be documented with the other transmission models, which are separate from the WDRM. Models for Reliability and Public Safety risk are separate from the WDRM planning models. They are developed to help inform internal investment planning primarily outside of HFTD. ii. Reliability and Public Safety risk models are not considered components of the WDRM and are not currently used for wildfire mitigation planning. | Nathan Poon | 2025-04-11 | 2025-04-21 | 2025-04-21 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_002.zip | 1 | No | Appendix B | Supporting Documentation for Risk Methodology | Appendix B | Supporting Documentation for Risk Methodology
15 | 69 | OEIS | 002 | OEIS_002 | 14 | No | OEIS_002_Q14 | Regarding suppression and egress impacts On page 32 of PG&E’s Wildfire Consequence Model Version 4 (WFC v4) Documentation, PG&E states that “This was not the original expectation for adding the wildfire Suppression and public Egress impacts, resulting in additional efforts to validate the results and confirm the model development” when discussing the adjusted consequence curve and associated work to mitigate 60% of the wildfire risk. a. How did PG&E calculate the mileages associated with mitigating 60% of the wildfire risk? b. What “additional efforts” were completed for model development as a result of this finding? c. How did any efforts resulting in response to this validation impact the consequence curve? Provide copies of the curve before and after. d. Provide a step-by-step process showing how PG&E calculated the associated mileage of work needed to mitigate 60% of the wildfire risk before and after. | a. The plots were generated by creating risk rankings for all circuit segments with overhead conductor assets within the PG&E territory using approximated risk values. Approximated risk values were calculated using release candidate asset probability data that was converted into spatial values for simplified compositing and aggregation multiplied times the base and adjusted consequence values. Processing the circuit segments in order of their risk rank, each circuit segment’s summed risk value, as a percentage of summed risk in the service territory, was sequentially subtracted from 100% to form the data series for the y-axis values for the buydown curves. The x-axis data series was formed by creating a running total of miles for each ordered circuit segment. WMP-Discovery 2026-2028_DR_OEIS_002-Q014 Page 2 b. The sentence highlighted from the Wildfire Consequence Model v4 documentation indicates that incorporating the egress and suppression impacts into wildfire consequence resulted in risk buydown curve that showed that the number of miles that needed to be undergrounded to mitigate 60% of the wildfire risk was higher than anticipated. As a result of this finding, the team dedicated extra validation to confirm the results by evaluating against historical fire outcomes. The additional validation resulted in the removal of several lightning fires from the consequence training data set as described in Section 3.2.4 on page 12 of the consequence documentation. In the end, the team concluded that the general flattening of the risk buydown curve when adjusting consequence for egress and suppression was a correct outcome. c. As stated above in (b.), lightning fires were taken out of the historical fire data set used to calibrate the wildfire consequence model as they skewed results for fires initiated on non-predicted destructive weather days, which resulted in slightly steeper buydown curves for both base and adjusted consequence. No changes were made that altered the Egress or Suppression impacts for the adjusted consequence. The relative differences between the base and adjusted consequence curves remained as depicted in Figure 20. d. The calculation process was described in the response for (a.). | Nathan Poon | 2025-04-11 | 2025-04-21 | 2025-04-21 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_002.zip | 0 | No | 5 | Risk Methodology & Assessment | 5.4 | Summary of Risk Models
15 | 70 | OEIS | 002 | OEIS_002 | 15 | No | OEIS_002_Q15 | Q15. Regarding PG&E’s Ignition Investigation Process Figure PG&E-6.1.3.1-2: Summary of Ignition Investigation Process, on page 123 of PG&E’s 2026-2028 Base WMP includes a step for “Corrective Actions Generated and Assigned.” a. Provide a list of corrective actions generated by the ignition investigation team that have led to changes in PG&E’s wildfire mitigation efforts since PG&E’s 2023-2025 Base WMP. b. Provide a list of ignitions, including causes and locations, associated with the changes discussed in part (a). | Many of the corrective actions generated by single incidents are focused on the single incidents and do not directly lead to changes in PG&E’s wildfire mitigation efforts. However, PG&E conducts trend analyses to identify possible corrective actions, including corrective actions associated with some of PG&E’s wildfire mitigation programs. The corrective actions listed below, which did lead to changes in our wildfire mitigation efforts, are based on trend analyses across many incidents along with input from subject matter experts who contribute to the investigation. The table below includes the mitigation efforts that have resulted from analyzing trends generated from the ignition investigation team along with various example ignitions associated with those corrective actions and causes thereof. Corrective Action Example Associated Indexes Cause Location Improvements to HighImpedance Fault Protection (including implementing lower sensitive ground fault thresholds and high20230530, 20230692, 20230693, 20230782N, 20230792, 20230823, 20230912, 20230981, Various Various WMP-Discovery 2026-2028_DR_OEIS_002-Q015 Page 2 Corrective Action Example Associated Indexes Cause Location impedance fault detection on four-wire circuits) 20231073, 20231074, 20231083 Expanded Ground Vegetation Clearing around Poles 20230966, 20231053, 20240583, 20240887, 20241105N Various Various Mitigations for SMU-20 Fuses (including proactive pole clearing around fuses and replacement of SMU-20 fuses) 20230440, 20230875, 20240309N Various Various Expedited Completion of Infrared Notifications 20230836, 20240583 Various Various Expedited Completion of Bird Nest Removal Notifications 20240909N, 20241105N Various Various | Nathan Poon | 2025-04-11 | 2025-04-16 | 2025-04-16 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_002.zip | 0 | No | ACI PG&E-25U-01 | Outage-to-Ignition Risk Analyses | ACI PG&E-25U-01 | Outage-to-Ignition Risk Analyses
15 | 71 | OEIS | 002 | OEIS_002 | 16 | No | OEIS_002_Q16 | Regarding Table 5-5: Summary of Top Risk Circuit Segments a. Provide a copy of Table 5-5: Summary of Top Risk Circuit Segments from the 2026-2028 Base WMP via Excel that includes additional columns for: i. WFC v4 Consequence Values ii. PSPS Risk Score iii. PEDS Risk score iv. HFTD Designation, including percentage by circuit mileage that falls in each designation (HFTD Tier II, HFTD Tier III, non-HFTD/HFRA, and non-HFTD/non-HFRA) | a. Expanded Table 5-5 with requested data is provided in “WMP-Discovery2026- 2028_DR_OEIS_002-Q016Atch01.xlsx”. | Nathan Poon | 2025-04-11 | 2025-04-21 | 2025-04-21 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_002.zip | 1 | No | 5 | Risk Methodology & Assessment | 5.5.2 | Top Risk-Contributing Circuits/Segments/Spans
15 | 72 | OEIS | 002 | OEIS_002 | 17 | No | OEIS_002_Q17 | Regarding Table 6-4: Summary of Risk Reduction for Top Risk Circuits Provide a copy of Table 6-4: Summary of Risk Reduction for Top Risk Circuits from the 2026-2028 Base WMP via Excel with the following additions: a. The associated circuit mileage for each of the hardening activities (covered conductor installation, undergrounding, and line removal) planned for each circuit segment for each year of the Base WMP (2026-2028). b. The percentage (by circuit mileage) in which each circuit segment has already been planned for hardening as part of a previous Wildfire Mitigation Plan up to 2025, broken out by type of hardening. | Please see “WMP-Discovery2026-2028_DR_OEIS_002-Q017Atch01.xlsx” for the requested information. a. In response to subpart a: Please reference columns I-K, N-P, and S-U for miles planned in 2026, 2027, and 2028, respectively. Miles provided by circuit segment are estimates and subject to change as the 2026- 2028 workplan continues to move through planning and execution phases. Circuit segment names can vary across different Wildfire Distribution Risk Model (WDRM) versions. Circuit segments in the 2026-2028 WMP are from WDRM v4. As a result, forecast work might not be reflected in the reported mileages if the circuit segment name has changed. b. In response to subpart b: Please reference columns D-F. WMP-Discovery 2026-2028_DR_OEIS_002-Q017 Page 2 For reference, as adopted by 2023 GRC Decision (Conclusion of Law 80, pg. 862), the undergrounding to overhead conversion factor is 1 mile of overhead to 1.25 miles of undergrounding. We have adjusted the % of Circuit Segment that is Undergrounded through 2025 (Column D) to reflect this ratio. Total circuit segment mileage used in this analysis represents miles associated with WDRM v4. Circuit segment mileage varies in each WDRM update. Mileage completed/planned on a circuit segment may exceed the total circuit segment mileage due to changes across risk model updates. As noted in subpart a, circuit segment names also change across different WDRM versions, and there may be completed or forecast work not reflected in these mileages if the circuit segment name changed. For subprojects spanning multiple circuit segments, the total mileage is attributed to the primary circuit segment. This results in the primary circuit segment having more mileage than was executed on that circuit segment. | Nathan Poon | 2025-04-11 | 2025-04-16 | 2025-04-16 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_002.zip | 1 | No | 5 | Risk Methodology & Assessment | 5.5.2 | Top Risk-Contributing Circuits/Segments/Spans
15 | 72 | OEIS | 002 | OEIS_002 | 17(a) | Yes | OEIS_002_Q17(a) | Regarding Table 6-4: Summary of Risk Reduction for Top Risk Circuits Provide a copy of Table 6-4: Summary of Risk Reduction for Top Risk Circuits from the 2026-2028 Base WMP via Excel with the following additions: a. The associated circuit mileage for each of the hardening activities (covered conductor installation, undergrounding, and line removal) planned for each circuit segment for each year of the Base WMP (2026-2028). b. The percentage (by circuit mileage) in which each circuit segment has already been planned for hardening as part of a previous Wildfire Mitigation Plan up to 2025, broken out by type of hardening. | Please see attachment “WMP-Discovery2026-2028_DR_OEIS_002- Q017Rev01Atch01.xlsx” for the requested information. a. Please reference columns I-K, N-P, and S-U for miles planned in 2026, 2027, and 2028, respectively. Miles provided by circuit segment are estimates and subject to change as the 2026- 2028 workplan continues to move through planning and execution phases. Circuit segment names can vary across different Wildfire Distribution Risk Model (WDRM) versions. Circuit segments in the 2026-2028 WMP are from WDRM v4. As a result, forecast work might not be reflected in the reported mileages if the circuit segment name has changed. b. Please reference columns D-F. For reference, as adopted by 2023 GRC Decision (Conclusion of Law 80, pg. 862), the undergrounding to overhead conversion factor is 1 mile of overhead to 1.25 WMP-Discovery 2026-2028_DR_OEIS_002-Q017Rev01 Page 2 miles of undergrounding. We have adjusted the % of Circuit Segment that is Undergrounded through 2025 (Column D) to reflect this ratio. Total circuit segment mileage used in this analysis represents miles associated with WDRM v4. Circuit segment mileage varies in each WDRM update. Mileage completed/planned on a circuit segment may exceed the total circuit segment mileage due to changes across risk model updates. As noted in subpart a, circuit segment names also change across different WDRM versions, and there may be completed or forecast work not reflected in these mileages if the circuit segment name changed. For subprojects spanning multiple circuit segments, the total mileage is attributed to the primary circuit segment. This results in the primary circuit segment having more mileage than was executed on that circuit segment. | Nathan Poon | 2025-04-11 | 2025-04-29 | 2025-04-29 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_002.zip | 1 | No | 5 | Risk Methodology & Assessment | 5.5.2 | Top Risk-Contributing Circuits/Segments/Spans
15 | 73 | OEIS | 002 | OEIS_002 | 18 | No | OEIS_002_Q18 | Regarding Independent Review of PG&E’s Wildfire Risk Model For each of the following recommendations made in the E3 Review of PG&E’s Wildfire Risk Model Version 4, provide a description of 1) the progress/improvements made, 2) the current status, 3) the timeline/completion date for addressing the recommendation, and 4) the model(s) and associated version impacted by implementing the recommendation. a. Right-size development efforts based on importance and impact (pp. 11, 36, 50, 59) b. Justify and seek improvements for model approaches that dilute valuable upstream detail: consequence binning and conservative age logic (pp. 11, 49, 55, 59) c. Report risk + uncertainty in outputs and develop a process to understand how individual modeling updates impact results (pp. 12, 33, 60) d. Incorporate air quality and health impacts (pp. 13, 57, 60) e. Increase collaboration between modeling efforts (p. 37) f. Develop robust validation procedures (p. 49) g. Improve transparency and assessment of proprietary wildfire spread modeling and the wildfire consequence model at large (p. 56) h. Consider the differences in mitigation lifetimes (p. 58) | a. Right-size development efforts PG&E continuously manages and adjusts the resources dedicated to the development of the WDRM and WTRM models based on regulatory requirements and PG&E user needs. As managing resources is an ongoing effort to respond to changing internal and external needs, there are no committed resource targets and timelines to be tracked. b. Consequence binning and conservative age logic i. Conservative age logic: Initial improvements to the conservative age logic have already been released with the latest WTRM model release. The improvements are ongoing and will continue to improve with each new model release. ii. Consequence binning: PG&E is investigating methods to create a Wildfire Consequence output with a continuous distribution, aiming to replace the eight Consequence regimes from version 4. If any of these methods demonstrate predictive accuracy during validation and review, they will be incorporated into version 5 of the Wildfire Consequence model. c. Report risk + uncertainty in outputs and develop a process to understand how individual modeling updates impact results This E3 recommendation proposes that a different methodology be adopted for mitigation project selection, which would in turn require specific risk model functionality development. PG&E does not plan to commit any resources for this recommendation until the proposed methodology has been thoroughly discussed and a decision has been made to change from the current risk ranking process. d. Incorporate air quality and health impacts This E3 recommendation is targeted at all IOUs and the State of CA. While this is an area of interest for PG&E research, there are currently no committed development objectives for these impacts. e. Increase collaboration between modeling efforts PG&E has already implemented E3’s recommendation to improve the collaboration of modeling efforts. The PG&E Risk and Data Analytics (RaDA) team that produces the WDRM and WTRM models was reorganized in late 2023. The data scientists that produce the event probability models for distribution and transmission assets now belong to a common data science team. For several event types, the same data scientist produces both the distribution and transmission event models. 1. Progress: Complete 2. Status: Complete 3. Timeline: Complete f. Develop robust validation procedures PG&E has developed a validation procedure for the TCM. Data validation is done by comparing model outputs with outage and tag data. SME validation includes evaluation of failure modes and field studies with respect to model outputs. Both steps must be completed before the Wildfire Governance Steering Committee reviews the validation results and either accepts the findings, or requests additional validation work to be done. This process is already in place for new TCM releases. g. Improve transparency and assessment of proprietary wildfire spread modeling and the wildfire consequence model at large This E3 recommendation is largely targeted at the State of CA and CalFire concerning validation of Technosylva products. This item also reiterates their recommendation regarding the consequence binning already addressed in item b). h. Consider the differences in mitigation lifetimes This E3 recommendation concerns PG&E’s use of cost benefit analyses methodologies used to drive mitigation option selection for mitigation program projects. This recommendation impacts decisions made by downstream users of the WDRM/WTRM risk results and proposes no changes to the risk models | Nathan Poon | 2025-04-11 | 2025-04-21 | 2025-04-21 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_002.zip | 0 | No | 5 | Risk Methodology & Assessment | 5.4 | Summary of Risk Models
16 | 74 | SPD | 001 | SPD_001 | 1 | No | SPD_001_Q1 | Provide the confidential versions of PG&E’s 2026-2028 Wildfire Mitigation Plan (WMP) and any confidential associated documents or attachments submitted to the Office of Energy Infrastructure and Safety not currently on PG&E’s Community Wildfire Safety Program Website (Community Wildfire Safety Program). | PG&E did not submit a confidential version of its 2026-2028 Wildfire Mitigation Plan or any confidential associated documents or attachments. | Eddie Schmitt | 2025-04-15 | 2025-04-18 | 2025-04-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_001.zip | 0 | No | N/A | N/A | N/A | N/A
16 | 75 | SPD | 001 | SPD_001 | 2 | No | SPD_001_Q2 | The PG&E’s 2023-2025 WMP contained attachments PGE_2023_WMP_R0_Appendix D ACI PG&E-22-16_Atch01_Redacted.xlsx and PGE_2023_WMP_R0_Section_642_Atch01.xlsx. Submit equivalent documents for the 2026-2028 WMP. Schedule a meeting with SPD if equivalent documents do not exist. | With regard to the 2023-2025 WMP attachment titled “PGE_2023_WMP_R0_Appendix D ACI PG&E-22-16_Atch01_Redacted.xlsx,” PG&E does not have this information readily available in the format requested. We are compiling it and will supplement the response by Friday, April 25. With regard to the 2023-2025 WMP attachment titled PGE_2023_WMP_R0_Section_642_Atch01.xlsx, please refer to Table 6-4 included in Appendix F of PG&E’s 2026-2028 WMP. | Eddie Schmitt | 2025-04-15 | 2025-04-18 | 2025-04-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_001.zip | 0 | No | 6 | Wildfire Mitigation Strategy Development | 6 | Wildfire Mitigation Strategy
16 | 75 | SPD | 001 | SPD_001 | 2(s) | Yes | SPD_001_Q2(s) | The PG&E’s 2023-2025 WMP contained attachments PGE_2023_WMP_R0_Appendix D ACI PG&E-22-16_Atch01_Redacted.xlsx and PGE_2023_WMP_R0_Section_642_Atch01.xlsx. Submit equivalent documents for the 2026-2028 WMP. Schedule a meeting with SPD if equivalent documents do not exist. | Please see attachment “WMP-Discovery2026-2028_DR_SPD_001- Q002Supp01Atch01CONF.xlsx” and for documentation equivalent to "PGE_2023_WMP_R0_Appendix D ACI PG&E-22-16_Atch01_Redacted.xlsx." | Eddie Schmitt | 2025-04-15 | 2025-04-29 | 2025-04-29 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_001.zip | 1 | No | 6 | Wildfire Mitigation Strategy Development | 6 | Wildfire Mitigation Strategy
16 | 76 | SPD | 001 | SPD_001 | 3 | No | SPD_001_Q3 | For FIGURE PG&E-8.3.8.3-1, FIGURE PG&E-8.3.8.3-2, and FIGURE PG&E-8.3.8.3-3, provide the work orders for each condition, a. Describe why each condition met the designated priority of the work order. | With regard to Figure 8.3.8.3-1, a damaged conductor with more than 30% broken strands requires a priority A or priority X tag, depending on exposure. Please see “WMP-Discovery2026-2028_DR_SPD_001-Q003Atch01CONF.pdf.” With regard to Figure 8.3.8.3-2, a secondary floater making contact with a cross arm requires a priority X notification. Please see “WMP-Discovery2026- 2028_DR_SPD_001-Q003Atch02CONF.pdf.” With regard to Figure 8.3.8.3-3, a heavily decayed pole top with hardware sinking into the pole requires a minimum priority E notification. However, this was created as a priority B notification due to the severity of the decay and exposure. Please see “WMPDiscovery2026-2028_DR_SPD_001-Q003Atch03CONF.pdf.” | Eddie Schmitt | 2025-04-15 | 2025-04-18 | 2025-04-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_001.zip | 3 | No | 8 | Grid Design, Operations, and Maintenance | 8.3.8 | Distribution - Detailed Ground Inspection
16 | 77 | SPD | 001 | SPD_001 | 4 | No | SPD_001_Q4 | Provide all research or engineering reports which contributed to distribution inspection job aid changes in 2024 and 2025. | Please see the attachments listed below for the research and engineering reports that contributed to distribution inspection job aid changes in 2024 and 2025: • WMP-Discovery2026-2028_DR_SPD_001-Q004Atch01CONF.pdf • WMP-Discovery2026-2028_DR_SPD_001-Q004Atch02CONF.pdf • WMP-Discovery2026-2028_DR_SPD_001-Q004Atch03CONF.pdf • WMP-Discovery2026-2028_DR_SPD_001-Q004Atch04CONF.pdf • WMP-Discovery2026-2028_DR_SPD_001-Q004Atch05CONF.pdf • WMP-Discovery2026-2028_DR_SPD_001-Q004Atch06CONF.pdf • WMP-Discovery2026-2028_DR_SPD_001-Q004Atch07CONF.pdf • WMP-Discovery2026-2028_DR_SPD_001-Q004Atch08CONF.pdf • WMP-Discovery2026-2028_DR_SPD_001-Q004Atch09CONF.pdf | Eddie Schmitt | 2025-04-15 | 2025-04-18 | 2025-04-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_001.zip | 9 | No | 8 | Grid Design, Operations, and Maintenance | 8.3.8 | Distribution - Detailed Ground Inspection
16 | 78 | SPD | 001 | SPD_001 | 5 | No | SPD_001_Q5 | Provide the full year inspection 2024 inspection find rates in a format matching “WMP-Discovery2023-2025_DR_SPD_014-Q005Rev02Supp01”. | Table Q-005 Inspection Find Rates 20241 1. Find rate is calculated as number of new notifications created divided by number of inspections. Counts for Priority E notifications include Priority H notifications as well. 2. Includes Priority A and X conditions from Aerial Inspection which were processed manually and not flagged as created by aerial in our system of record. 3. PTT find rates reflect the routine PTT program described in the WMP. | Eddie Schmitt | 2025-04-15 | 2025-04-18 | 2025-04-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_001.zip | 0 | No | 8 | Grid Design, Operations, and Maintenance | 8.3.8 | Distribution - Detailed Ground Inspection
16 | 79 | SPD | 001 | SPD_001 | 6 | No | SPD_001_Q6 | Update the ignition data from 2014-2024 in the same format as the response to WMP-Discovery2023_DR_SPD_004-Q001, which must include values to be filled in for “FPI,” “HFTD” information, and “Acreage”, along with some additional columns described below. Additionally, verify and update the ignition dataset with any new information (for instance if PG&E has determined an ignition occurred which it was not aware of at the time of the original template). The columns required in this data set should be as follows:. a. “FPI” – State the Fire Potential Index (FPI) for each ignition using FPI 5.0 on a scale of R1 to R5. The FPI should be specified at the most granular level (circuit segment). b. “FPI Natural Units” - State the FPI for each ignition using FPI 5.0’s numerical output. c. “HFTD”: Classify each ignition based on its location as “Zone 1,” “Tier 2,” or “Tier 3,” “HFRA” or “Non-HFTD” d. “Acreage” – Provide the acres burned of each ignition where known. e. “Failure_driver” – Update each ignition from 2014 through 2024 with the same method for categorization as column G in worksheet “ign_enriched_edited_v12-22-2023” of the 2024 Risk Assessment and Mitigation Phase (RAMP) workpaper “EO-WLDFR-6_PG&E Ignitions 2015-2022.xlsx” f. “Failure_sub_driver” – Update each ignition from 2014 through 2024 with the same method for categorization as column H in worksheet “ign_enriched_edited_v12-22-2023” of the 2024 RAMP workpaper “EO-WLDFR-6_PG&E Ignitions 2015-2022.xlsx” g. “wsd_driver” – Update each ignition from 2014 through 2024 with the same method for categorization as column I in worksheet “ign_enriched_edited_v12-22-2023” of the 2024 RAMP workpaper “EO-WLDFR-6_PG&E Ignitions 2015-2022.xlsx” h. “event model wildfire risk classification” – Update each ignition from 2014 through 2024 indicating which submodel would use each ignition as defined in columns S-AO from “WMP-Discovery2023-2025_DR_CalAdvocates_041-Q005Atch01.xlsx.” If an ignition is used in multiple submodels, provide them as a list in one column separated by a comma. i. “wdrm v4 subdriver” - Update each ignition from 2014 through 2024 with the same method for categorization as the WDRM v4 subdriver definition in Column A of worksheet “Effectiveness Analysis Detail” in the file “WMP-Discovery2026-2028_DR_TURN_002-Q005Atch01.xslx” | Please see “WMP-Discovery2026-2028_DR_SPD_001-Q006Atch01CONF.xlsx” for the requested information for subparts (a) through (g). Additionally, please see the explanatory notes below. • With regard to subparts (a) and (b), please note that circuit identifiers can change over time which can lead to an incomplete or incorrect match of historical ignition circuit identifiers with current asset circuit identifiers. Further, circuit geometries can also change over time, for example when circuits are moved, re-configured, or removed as has been the case in some catastrophic fires. FPI 5.0 circuit ratings cannot be generated if the circuit geometries no longer exist in EDGIS and ETGIS. A 2024 snapshot of EDGIS primary overhead and ETGIS overhead line geometries were intersected with HFRA/HFTD to generate the FPI 5.0 circuit climatology. Two key ignitions, the Dixie fire and Camp fire, were added from a 2020 snapshot of EDGIS and ETGIS respectively to produce FPI 5.0 circuit ratings as these lines are no longer in the 2024 EDGIS & ETGIS snapshots. • PG&E is providing the column “fpi_5_0_circuit_rating” in response to part (a) and two columns—"fpi_5_0_circuit_prob_catastrophic” and “fpi_5_0_circuit_prob_critical_or_catastrophic”—in response to subpart (b). These columns represent, respectively, the circuit level aggregations of FPI probability of catastrophic wildfire and circuit probability of critical or catastrophic wildfire. FPI 5.0 circuit ratings and probabilities are not produced or provided outside of the HFRA/HFTD. We will supplement this response by April 30, 2024 with responses to parts (h) and (i). | Eddie Schmitt | 2025-04-15 | 2025-04-25 | 2025-04-25 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_001.zip | 1 | No | Appendix D: Areas of Continued Improvement | Areas of Continued Improvement | ACI PG&E-25U-01 | ACI PG&E-25U-01 - Outage-to-Ignition Risk Analysis
16 | 79 | SPD | 001 | SPD_001 | 6(s) | Yes | SPD_001_Q6(s) | Update the ignition data from 2014-2024 in the same format as the response to WMP-Discovery2023_DR_SPD_004-Q001, which must include values to be filled in for “FPI,” “HFTD” information, and “Acreage”, along with some additional columns described below. Additionally, verify and update the ignition dataset with any new information (for instance if PG&E has determined an ignition occurred which it was not aware of at the time of the original template). The columns required in this data set should be as follows:. a. “FPI” – State the Fire Potential Index (FPI) for each ignition using FPI 5.0 on a scale of R1 to R5. The FPI should be specified at the most granular level (circuit segment). b. “FPI Natural Units” - State the FPI for each ignition using FPI 5.0’s numerical output. c. “HFTD”: Classify each ignition based on its location as “Zone 1,” “Tier 2,” or “Tier 3,” “HFRA” or “Non-HFTD” d. “Acreage” – Provide the acres burned of each ignition where known. e. “Failure_driver” – Update each ignition from 2014 through 2024 with the same method for categorization as column G in worksheet “ign_enriched_edited_v12-22-2023” of the 2024 Risk Assessment and Mitigation Phase (RAMP) workpaper “EO-WLDFR-6_PG&E Ignitions 2015-2022.xlsx” f. “Failure_sub_driver” – Update each ignition from 2014 through 2024 with the same method for categorization as column H in worksheet “ign_enriched_edited_v12-22-2023” of the 2024 RAMP workpaper “EO-WLDFR-6_PG&E Ignitions 2015-2022.xlsx” g. “wsd_driver” – Update each ignition from 2014 through 2024 with the same method for categorization as column I in worksheet “ign_enriched_edited_v12-22-2023” of the 2024 RAMP workpaper “EO-WLDFR-6_PG&E Ignitions 2015-2022.xlsx” h. “event model wildfire risk classification” – Update each ignition from 2014 through 2024 indicating which submodel would use each ignition as defined in columns S-AO from “WMP-Discovery2023-2025_DR_CalAdvocates_041-Q005Atch01.xlsx.” If an ignition is used in multiple submodels, provide them as a list in one column separated by a comma. i. “wdrm v4 subdriver” - Update each ignition from 2014 through 2024 with the same method for categorization as the WDRM v4 subdriver definition in Column A of worksheet “Effectiveness Analysis Detail” in the file “WMP-Discovery2026-2028_DR_TURN_002-Q005Atch01.xslx” | h. WDRM v4 model classification for historical ignitions is included as column AH (WDRM v4 event model wildfire risk classification) of the attachment. Please note that the WDRM v4 submodels were modeled using the following filters. Ignitions outside of the filter criteria were not included in the modeling dataset and are not linked to an ignition in the attached spreadsheet. • Years: 2015 – 2022. • Months: June – November. • Valid location: Latitude and longitude within service territory bounds. • Equipment: Distribution-only. i. The assignment of outage failure combinations to WDRM subdrivers in EOWLDFR-6_PG&E Ignitions 2015-2022.xlsx is based on four key components of each outage: basic cause, supplemental cause, equipment, and equipment condition. These same fields are not available, nor applicable in every case, in PG&E’s ignitions dataset, therefore, the requested analysis cannot be completed. | Eddie Schmitt | 2025-04-15 | 2025-04-30 | 2025-04-30 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_001.zip | 1 | No | Appendix D: Areas of Continued Improvement | Areas of Continued Improvement | ACI PG&E-25U-01 | ACI PG&E-25U-01 - Outage-to-Ignition Risk Analysis
16 | 80 | SPD | 001 | SPD_001 | 7 | No | SPD_001_Q7 | Q11 asks for data related to various classifications PG&E used in risk modeling of ignitions in parts e through i. Explain where each classification is used, and how the classifications relate. a. Describe why the WDRM v4 subdrivers in in Column A of worksheet “Effectiveness Analysis Detail” in the file “WMP-Discovery2026-2028_DR_TURN_002-Q005Atch01.xslx” do not seem to match one to one with the WDRMv4 submodels in columns S-AO from “WMP-Discovery2023-2025_DR_CalAdvocates_041-Q005Atch01.xlsx.” | On April 17, 2025, SPD clarified that this question is seeking Q06 data. a. The mapping between WDRM v4 subdrivers in worksheet Effectiveness Analysis Detail map to the WDRM v4 submodels in columns S-AO as shown in the table below. These items do not map one-to-one because the “Support Structure: Electrical” and “Transformer: Leaking” submodels are not included in the System Hardening composite used by the Undergrounding program (Column AQ in “WMPDiscovery2023-2025_DR_CalAdvocates_041-Q005Atch01.xlsx”). Notes: 1 The WDRM does not model planned outages. 2 The “Support Structure: Electrical” and “Transformer: Leaking” submodels are not included in the System Hardening composite. | Eddie Schmitt | 2025-04-15 | 2025-04-30 | 2025-04-30 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_001.zip | 0 | No | 5 | Risk Methodology & Assessment | 5.4 | Summary of Risk Models
16 | 81 | SPD | 001 | SPD_001 | 8 | No | SPD_001_Q8 | Provide the outage data set used in WDRM v4. Include a unique outage ID that matches the data in the Spatial Quarterly Data Reports (QDR) data set in excel format. Each row should correspond to an outage, and each column should correspond to a feature related to the outage used in the model. a. Describe how the outage location was used in WDRM v4 to determine risk at an asset location. i. If the GPS-based outage location was not used, explain why? ii. Was the classification of HFTD/non-HFTD (or other similar HFRA/non-HFRA) used as a factor in the model? If so, explain how. | The modeling dataset used for the Distribution Event Probability Models in WDRM v4 with the primary key for the outage is included in Attachment “WMP-Discovery2026- 2028_DR_SPD_001-Q008Atch01.xlsx”. Please note that not all failure events result in an outage so the outage id is blank for some events. a. i. Assignment of outage/failure to assets or pixels varied by model type. • For asset models: For WDRM v4, outages/failure events were assigned using the unique equipment id. If a unique equipment ID for the asset or pole could not be extracted from historical records, then the latitude and longitude were used to identify the nearest asset if the values were GPSbased. If no equipment ID or GPS-based location data were identified, then the event was excluded from the model training dataset. WMP-Discovery 2026-2028_DR_SPD_001-Q008 Page 2 • For pixel models: Reliable locations for failure/outage data were prioritized first (such as GPS-based outage locations). Non-GPS locations were used as a last resort. Locations that were outside of a “grid” pixel (i.e. events more than ~100m from the distribution system) were excluded from the model training dataset. ii. HFTD classification was used as an input to some of the Distribution Event Probability Models (DEPM). The feature importance of model inputs is documented in the DEPM, version 4 model documentation. HFTD was not majorly influential in any of the DEPM models. | Eddie Schmitt | 2025-04-15 | 2025-04-30 | 2025-04-30 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_001.zip | 1 | No | 5 | Risk Methodology & Assessment | 5.4 | Summary of Risk Models
16 | 82 | SPD | 001 | SPD_001 | 9 | No | SPD_001_Q9 | Provide the ignition data set used in WDRM v4 in excel format. Each row should correspond to an ignition, and each column should correspond to a feature related to the ignition used in the model. | Ignitions used for the p(ignition ¦ outage) model are included in attachment “WMPDiscovery2026-2028_DR_SPD_001-Q008Atch01.xlsx”. Please note that the input data for the p(ignition ¦ outage) model are based on failure/outage events and whether the event resulted in an ignition. Thus, the majority of rows in the model training dataset are not associated with an ignition. The ignitions can be identified by filtering the spreadsheet to where the ignition_primary_key column is not Null. | Eddie Schmitt | 2025-04-15 | 2025-04-30 | 2025-04-30 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_001.zip | 0 | No | 5 | Risk Methodology & Assessment | 5.4 | Summary of Risk Models
16 | 83 | SPD | 001 | SPD_001 | 10 | No | SPD_001_Q10 | The current data set in “WMP-Discovery2026-2028_DR_TURN_002-Q005Atch01.xlsx” appears to be missing columns and spreadsheets necessary to generate important data and analysis. Many of the columns in the “Effective Analysis Detail” seem to indicate the same subdriver/drivers. a. Provide an updated version which clarifies the difference between each row. b. “WMP-Discovery2023-2025_DR_SPD_016-Q007Atch01.xlsx.” include more data and spreadsheets than “WMP-Discovery2026-2028_DR_TURN_002-Q005Atch01.xlsx”, such as columns for basic_cause, supplemental_cause, equipinvolved, equipcondition and the counts of incidents in each year as well as worksheets like Grid Hardening SME Input, Outages_HFTD and Mapping. Provide these columns and worksheets in an update to “WMP-Discovery2026-2028_DR_TURN_002-Q005Atch01.xlsx”. SPD expects that this new outage data set should be a more complete dataset than was used to generate PG&E’s Effectiveness Analysis in WMP-Discovery2026-2028_DR_TURN_002-Q005Atch01.xlsx. The data should match the columns within Outages_HFTD found in WMP-Discovery2023-2025_DR_SPD_016-Q007Atch01.xlsx but also should include the unique outage IDs and GPS location. The unique outage IDs should be the same as the unique outage IDs found in the Spatial QDR data set. i. SPD expects to be able to aggregate this data into “WMP-Discovery2026-2028_DR_TURN_002-Q005Atch01.xlsx” | a. On The Effectiveness Analysis Detail worksheet, columns D, E, F and G have been added to “WMP-Discovery2026-2028_DR_SPD_001-Q010Atch01.xlsx” with Basic Cause, Supplemental Cause, Equipment Involved, and Equipment Condition fields for additional clarity. WMP-Discovery 2026-2028_DR_SPD_001-Q010 Page 2 b. The following updates have been made to the “WMP-Discovery2026- 2028_DR_SPD_001-Q010Atch02.xlsx”: i. Basic Cause, Supplemental Cause, Equipment Involved, and Equipment Condition fields have been added to the Effectiveness Analysis Detail tab for counts of incidents by year. Additional worksheets have been added: (1) Grid Hardening SME Input, (2) Outages_HFTD and (2) Mapping. QDR is not the original source for the outages used in the mitigation effectiveness analysis; however, columns P (“Latitude”), Q ("Longitude”), and R (“OutageID”) have been added to the Outages_HFTD worksheet on attachment “WMPDiscovery2026-2028_DR_SPD_001-Q010Atch02.xlsx”, to align outages as possible to the unique outage ID’s found in the Spatial QDR data set. Note that the Lat./Log. of outages may be based on the operating device and not necessarily at the damage location. For outages that did not align with the QDR data set, locations were sourced from a repository of ILIS outages. | Eddie Schmitt | 2025-04-15 | 2025-04-25 | 2025-04-25 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_001.zip | 2 | No | 6 | Wildfire Mitigation Strategy Development | 6.1.3-1 | Activity Selection Process
16 | 84 | SPD | 001 | SPD_001 | 11 | No | SPD_001_Q11 | Describe how the data set associated with Question 10 was created. a. Was the dataset associated with Question 10 created from a PG&E dataset of all outages? b. Was the dataset associated with Question 10 created from a subset of a PG&E dataset of all outages? If so, describe that subset. | a. No, the dataset is comprised of snapshots of only outages in the HFTD from PG&E’s ILIS database, which were taken at different points in time. The initial iteration of the analysis included a snapshot of HFTD outages between 2015-2022, then snapshots of 2023 and 2024 HFTD outages were added in early 2024 and early 2025, respectively. b. Yes, the dataset was created from a subset of outages recorded in ILIS, specifically HFTD outages between 2015-2024. | Eddie Schmitt | 2025-04-15 | 2025-04-25 | 2025-04-25 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_001.zip | 0 | No | 6 | Wildfire Mitigation Strategy Development | 6.1.3-1 | Activity Selection Process
16 | 85 | SPD | 001 | SPD_001 | 12 | No | SPD_001_Q12 | Provide the number of overhead circuit mile-days for each FPI rating per year starting in 2014 through 2024. The response should mirror the format of PG&E’s response “WMP-Discovery2023_DR_SPD_004-Q003.pdf”. However, the circuit mile-day data is to be calculated based on FPI 5.0 at the circuit segment level. a. Provide the FPI circuit mile day breakdown for the HFTD miles. b. Provide the FPI circuit mile day breakdown for HFRA miles. | The FPI 5.0 climatology from 2014 to 2024 was utilized for this analysis. Each grid cell along each distribution and transmission circuit using a 4/17/2025 GIS snapshot was intersected with daily aggregated FPI ratings and then intersected with the HFTD and HFRA to produce the results below. Units are in circuit-mile. a. Year R1 R2 R3 R4 R5 2014 6,204,052 875,330 1,996,733 1,078,358 937,058 2015 6,416,277 776,182 1,986,206 1,065,202 847,665 2016 7,052,437 527,748 1,601,247 1,063,928 876,560 2017 6,568,671 586,534 1,868,555 1,162,468 905,304 2018 6,307,438 559,128 1,992,872 1,222,168 1,009,924 2019 6,327,327 659,921 2,363,061 1,154,387 586,836 2020 6,089,637 690,180 1,932,752 1,312,260 1,097,092 2021 6,310,138 595,646 1,817,545 1,145,826 1,222,376 2022 6,590,773 683,700 2,030,006 987,614 799,438 WMP-Discovery 2026-2028_DR_SPD_001-Q012 Page 2 Year R1 R2 R3 R4 R5 2023 7,238,427 789,799 1,816,725 734,199 512,382 2024 6,282,480 615,916 2,219,990 1,293,915 709,618 b. Year R1 R2 R3 R4 R5 2014 6,302,847 900,503 2,094,010 1,109,103 942,836 2015 6,525,569 798,562 2,082,916 1,091,025 851,230 2016 7,182,680 543,334 1,683,989 1,090,317 880,075 2017 6,687,063 605,022 1,958,763 1,189,024 909,428 2018 6,416,804 578,971 2,091,430 1,247,382 1,014,713 2019 6,445,704 679,117 2,463,307 1,173,062 588,111 2020 6,196,071 709,146 2,029,859 1,341,945 1,103,373 2021 6,422,137 608,323 1,910,688 1,179,194 1,228,960 2022 6,709,675 701,874 2,120,979 1,014,161 802,611 2023 7,367,041 811,508 1,905,571 750,791 514,389 2024 6,397,133 634,225 2,326,397 1,310,176 712,465 | Eddie Schmitt | 2025-04-15 | 2025-04-18 | 2025-04-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_001.zip | 0 | No | 5 | Risk Methodology & Assessment | 5.5.2 | Top Risk-Contributing Circuits/Segments/Spans
16 | 86 | SPD | 001 | SPD_001 | 13 | No | SPD_001_Q13 | Identify any ignitions in 2024 associated with assets where PG&E had an existing corrective notification at the time of the ignition. Provide a spreadsheet listing each such ignition (as rows) in the same format as that provided to the CPUC in the annual CPUC Fire Ignition Data (see this website for the publicly available version: Wildfire and Wildfire Safety). a. Include one additional column that includes the corrective notification (i.e., work order or tag). | a. PG&E observed 166 CPUC-reportable ignition events in 2024 associated with equipment failure. We were able to identify 20 CPUC-reportable ignitions where the suspected cause was equipment failure, and the support structure associated with the location of the fire had an open EC or LC notification at the time of the ignition event. Please see “WMP-Discovery2026-2028_DR_SPD_001-Q013Atch01.xlsx” for the information associated with those 20 fires. | Eddie Schmitt | 2025-04-15 | 2025-04-25 | 2025-04-25 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_001.zip | 1 | No | Appendix D: Areas of Continued Improvement | Areas of Continued Improvement | ACI PG&E-25U-01 | ACI PG&E-25U-01 - Outage-to-Ignition Risk Analysis
16 | 87 | SPD | 001 | SPD_001 | 14 | No | SPD_001_Q14 | Identify any ignitions in 2024 associated with assets where PG&E had an existing corrective notification at the time of the ignition which PG&E attributes as causally connected to the ignition. Provide a spreadsheet listing each such ignition (as rows) in the same format as that provided to the CPUC in the annual CPUC Fire Ignition Data (see this website for the publicly available version: Wildfire and Wildfire Safety). a. Include one additional column that includes the existing corrective notification number (i.e., work order or tag number). b. Provide the existing corrective notification for each identified ignition (i.e., the work order). | a. PG&E observed 166 CPUC-reportable ignition events in 2024 associated with equipment failure. We were able to identify 7 CPUC-reportable ignitions that have completed our ignition analysis process where the suspected cause is equipment failure and the failure mode associated with the fire was specifically captured in the scope of a EC or LC corrective notification created prior to, and still open at, the ignition event. Please see “WMP-Discovery2026-2028_DR_SPD_001- Q014Atch01.xlsx” for information associated with those 7 fires. Please note that PG&E has determined that the conditions identified by the provided corrective notifications are likely related to the failure mode of an ignition event but cannot definitively determine causality. b. Please see the attachments listed below for the requested information: • WMP-Discovery2026-2028_DR_SPD_001-Q014Atch02CONF.pdf • WMP-Discovery2026-2028_DR_SPD_001-Q014Atch03CONF.pdf • WMP-Discovery2026-2028_DR_SPD_001-Q014Atch04CONF.pdf WMP-Discovery 2026-2028_DR_SPD_001-Q014 Page 2 • WMP-Discovery2026-2028_DR_SPD_001-Q014Atch05CONF.pdf • WMP-Discovery2026-2028_DR_SPD_001-Q014Atch06CONF.pdf • WMP-Discovery2026-2028_DR_SPD_001-Q014Atch07CONF.pdf • WMP-Discovery2026-2028_DR_SPD_001-Q014Atch08CONF.pdf | Eddie Schmitt | 2025-04-15 | 2025-04-25 | 2025-04-25 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_001.zip | 8 | No | Appendix D: Areas of Continued Improvement | Areas of Continued Improvement | ACI PG&E-25U-01 | ACI PG&E-25U-01 - Outage-to-Ignition Risk Analysis
16 | 88 | SPD | 001 | SPD_001 | 15 | No | SPD_001_Q15 | Identify any outages in 2024 associated with assets where PG&E had an existing corrective notification at the time of the outage which PG&E attributes as causally connected to the outage. Provide a list with unique IDs of each outage which can be cross-referenced with the data provided as part of the 2024 QDR spatial data and the corrective notification number. | Distribution: Please see “WMP-Discovery2026-2028_DR_SPD_001-Q015Atch01.xlsx” for distribution outages associated with overhead assets where PG&E had an existing corrective notification at the time of the outage. Due to the volume of data, the method used to derive this data defines “causally connected” as having a Level 1 (emergency) tag, linked to an unplanned outage, attributed to an equipment failure associated with the primary indicator on the same electric facility as the open maintenance tag. As this is a data pull and each event has not been desktop reviewed, there may be cases where the associated notification was not causal—for example, an instance in which a pole with two crossarms and an open tag on crossarm 1 experiences an outage caused by a failure of crossarm 2. Similarly, there may be cases where causally connected notifications are excluded—for example, an instance in which a pole fails due to a broken/damaged guy which had an existing notification. Details on the filtering procedure are included in “WMP-Discovery2026-2028_DR_SPD_001- Q015Atch01.xlsx.” Transmission: Please see “WMP-Discovery2026-2028_DR_SPD_001- Q015Atch02.xlsx” for transmission outages associated with assets where PG&E had an existing corrective notification at the time of the outage. Most outages are linked to an asset through manual review, which allows lookup of notifications on that asset; however, the outage dataset still contains some entries where the location is WMP-Discovery 2026-2028_DR_SPD_001-Q015 Page 2 approximate, and these locations were not considered in the analysis. Determining which open notifications have a causal connection was performed by a combination of methods: this data already is collected for a subset of outages through previous manual review, some outages are associated with Level 1 findings that were reviewed as part of Question 016, and the remaining outages were analyzed by attempting to match the Facility/Damage/Action (FDA) of all open notifications on the asset to the outage cause and asset type information. The last of these approaches is not expected to be completely accurate due to the level of granularity and imperfect alignment between notification FDAs and outage cause and asset type information. An outage may have more than one open notification with a causal connection; a separate list pivoted by the outage ID is provided to group multiple open notifications for the same outage. | Eddie Schmitt | 2025-04-15 | 2025-04-25 | 2025-04-25 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_001.zip | 2 | No | Appendix D: Areas of Continued Improvement | Areas of Continued Improvement | ACI PG&E-25U-01 | ACI PG&E-25U-01 - Outage-to-Ignition Risk Analysis
16 | 89 | SPD | 001 | SPD_001 | 16 | No | SPD_001_Q16 | Identify any level 1 corrective actions in 2024 associated with assets where PG&E had an existing corrective notification at the time of the level 1 corrective action which PG&E attributes as causally connected to the level 1 corrective action (one example would be if a level one corrective action was created on a pole with a priority E tag failure). For each instance, provide a list of the electric corrective notification numbers for both the existing corrective notification and the new level one corrective action, the priority level of the existing notification, as well as the date of the occurrence, and the unique ID of each outage (if available) which can be cross-referenced with the data provided as part of the 2024 QDR spatial data. | Distribution: Please see “WMP-Discovery2026-2028_DR_SPD_001-Q016Atch01.xlsx” for Level 1 corrective notifications associated with overhead distribution assets where PG&E had an existing corrective notification at the time of failure. Due to the volume of data, the method used to derive this data defines “causally connected” as having a Level 1 (emergency) tag, attributed to an equipment failure associated with the primary indicator on the same electric facility as the open maintenance tag. As this is a data pull and each event has not been desktop reviewed, there may be cases where the associated notification was not causal—for example, an instance in which a pole with two crossarms and an open tag on crossarm 1 experiences a failure of crossarm 2. Similarly, there may be cases where causally connected notifications are excluded—for example, an instance in which a pole fails due to a broken/damaged guy which had an existing notification. Details on the filtering procedure are included in “WMPDiscovery2026-2028_DR_SPD_001-Q016Atch01.xlsx”. | Eddie Schmitt | 2025-04-15 | 2025-04-25 | 2025-04-25 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_001.zip | 2 | No | Appendix D: Areas of Continued Improvement | Areas of Continued Improvement | ACI PG&E-25U-01 | ACI PG&E-25U-01 - Outage-to-Ignition Risk Analysis
16 | 90 | SPD | 001 | SPD_001 | 17 | No | SPD_001_Q17 | Provide all Preliminary Ignition Investigation Reports (PIIRs) associated with Underground Ignitions. | Please see the records below for PG&E’s PIIRs associated with underground ignitions. • WMP-Discovery2026-2028_DR_SPD_001-Q017Atch01_Redacted.pdf • WMP-Discovery2026-2028_DR_SPD_001-Q017Atch02_Redacted.pdf Please note, we have provided redacted copies of the requested PIIRs in an effort to provide them expeditiously. | Eddie Schmitt | 2025-04-15 | 2025-04-18 | 2025-04-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_001.zip | 2 | No | Appendix D: Areas of Continued Improvement | Areas of Continued Improvement | ACI PG&E-25U-01 | ACI PG&E-25U-01 - Outage-to-Ignition Risk Analysis
16 | 91 | SPD | 001 | SPD_001 | 18 | No | SPD_001_Q18 | Provide all PIIRs for ignitions in the HFTD in 2024. | Please see PG&E’s PIIRs for ignitions in the HFTD in 2024 at “WMP-Discovery2026- 2028_DR_SPD_001-Q018Atch01.zip.” | Eddie Schmitt | 2025-04-15 | 2025-04-18 | 2025-04-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_001.zip | 1 | No | Appendix D: Areas of Continued Improvement | Areas of Continued Improvement | ACI PG&E-25U-01 | ACI PG&E-25U-01 - Outage-to-Ignition Risk Analysis
16 | 92 | SPD | 001 | SPD_001 | 19 | No | SPD_001_Q19 | Provide all Priority A work orders PG&E created between 2020 and 2024 in the same format as “WMP-Discovery2023-2025_DR_SPD_019-Q002Atch01CONF,” with the exception that column T and U need not be filled out. Include Priority As for both distribution and transmission. a. For the purposes of this response to the data request, use column J (“Completion Data (if applicable)” for the date the work order was closed and column R (“Last Maintenance Date”) as the date the field work was finished. b. Correct Column P so the values are either Y (for yes, a wire down occurred) or N (for no, a wire down did not occur), unless there is a unique identifier for the wires down that does not match the Outage ID. Add a new column with the Outage Event ID that matches the unique outage ID identifier for the QDR data set. For instance, in the current data set, the column Q outage ID 1910360 appears to refer to an event in 2023, but in the QDR spatial data set, outage ID 1910360 appears to refer to an event in 2024. Continue to use the same methodology for creating outage event IDs for column Q. i. Explain why the QDR spatial data appears to have a different outage event IDs than those specified in column Q. | Please see attachment “WMP-Discovery2026-2028_DR_SPD_001-Q019Atch01.xlsx” for Priority A distribution work orders, and attachment “WMP-Discovery2026- 2028_DR_SPD_001-Q019Atch02.xlsx” for Priority A transmission work orders. With regard to “WMP-Discovery2026-2028_DR_SPD_001-Q019Atch01.xlsx,” please note that PG&E has refreshed the data provided using its Quarterly Data Reports (QDR). PG&E amended its Priority A tag reporting in its past QDRs to more accurately reflect Priority A tag metrics, and this submission reflects that amendment. WMP-Discovery 2026-2028_DR_SPD_001-Q019 Page 2 a. Distribution: Column J has been changed to reflect the SAP closure date. Column T “Last maintenance date (if applicable)” and Column I “Completed On Date” contain the date the notification was completed in the field. Transmission: Column J has been changed to reflect the SAP closure date. Note that if a notification is re-opened for administrative reasons, when it is re-closed the SAP closure date will change. Column R now contains the date the notification was completed in the field. The remaining logic is identical to that used to generate the previously provided data in “WMP-Discovery2023-2025_DR_SPD_019- Q002Atch01CONF.xlsx,” in which outages are matched to A-priority notifications on the same day and circuit. b. Distribution: Column R “OutageID QDR” has been added. Please note that there are multiple unique outage identifiers in PG&Es systems of record, Integrated Logging and Information System (ILIS). The OutageID in the QDR represents the outage_log_id, which is the primary identifier of an outage in ILIS where this data was pulled from. The outage event IDs specified in column Q are the Outage Information System (OIS) number, which is the primary identifier of the same outage in the Distribution Management System (DMS). Please note that PG&E has populated “Outage event ID” using the OIS number associated with each respective Priority A tag. There may be instances in which an OIS identifier is not associated with an outage (e.g. a troubleshooter dispatched to an emergency that does not result in an outage), and therefore where the “Outage event ID” column is populated but the “OutageID QDR” column is not. Please note PG&E has endeavored to match the provided Priority A tags to outages associated with the condition to the best of its ability. However, certain circumstances such as data entry by troubleshooters may prevent all Priority A tags from being matched to an associated outage. Transmission: Column P has been changed so that it is ‘Y’ if a wire down outage was matched to the notification date and circuit, or ‘N’ otherwise. The TOTL number is the only unique identifier for transmission outages; it is used as the outage ID in Column Q and in the spatial QDR. | Eddie Schmitt | 2025-04-15 | 2025-04-25 | 2025-04-25 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_001.zip | 2 | No | 8 | Grid Design, Operations, and Maintenance | 8.6 | Work Orders
16 | 93 | SPD | 001 | SPD_001 | 20 | No | SPD_001_Q20 | Provide an update version of “WMP-Discovery2023-2025_DR_CalAdvocates_041-Q005Atch01.xlsx” if the risk model has been updated since this spreadsheet was generated. a. Additionally, update the narrative and table provided in the response “WMP-Discovery2023-2025_DR_CalAdvocates_041-Q001.pdf” | The risk model, WDRMv4, has not been updated since the generation of this spreadsheet. | Eddie Schmitt | 2025-04-15 | 2025-04-18 | 2025-04-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_001.zip | 0 | No | 5 | Risk Methodology & Assessment | 5.4 | Summary of Risk Models
16 | 94 | SPD | 001 | SPD_001 | 21 | No | SPD_001_Q21 | SPD is attempting to compute the cost per unit for many of the WMP initiatives tracked in the WMP Implementation Dashboard (WMP Implementation Dashboard). Review and confirm the cost per unit is correct for the initiatives. See the attached workbook titled PGE WMP Implementation Dashboard.xlsx. a. Follow all of the instructions within the cells and notes included in PGE WMP Implementation Dashboard.xlsx. b. SPD is attempting to do a similar exercise for the 2026-2028 WMP but the QDR tabular data was not submitted. SPD saw some of the data in the WMP, but was unable to determine if this data was inclusive of all initiatives. Where should SPD look for equivalent data? | a. Please see attachment “WMP-Discovery2026-2028_DR_SPD_001- Q021Atch01.xlsx” for the requested information. The values provided in the Excel file section titled “PGE Response” represent PG&E’s response to this data request using the formulas and data sources provided by SPD, except to the extent amended as described below, and do not reflect PG&E’s official or final calculation of the unit costs associated with the listed WMP Initiatives. Please note, the values in the “PG&E RESPONSE” worksheet are based on SPD’s instructions, data, and formulas but with the following amendments, adjustments, and corrections: • PG&E has updated values in the “Total Cost” column for the year 2024 to reflect final, actual (as opposed to forecasted) costs as reported in our 2024 Annual Report on Compliance (ARC). • PG&E has updated “Units Planned/Completed” for the year 2024 to reflect final units as reported in our 2023 and 2024 ARCs. • Initiatives GH-01 (System Hardening) and GH-04 (Undergrounding) do not calculate unit costs using the method proposed by SPD. The following are clarifications about how unit costs are calculated for these projects. These corrections have been incorporated into worksheet “GH-01 & GH-04 Unit Cost” in attachment WMP-Discovery2026-2028_DR_SPD_001- Q021Atch01.xlsx. The 2023 and 2024 unit costs are from historically completed projects. The 2025 unit costs are predominately based on forecasts with a current workplan that contains more miles than targets. (1) WMP Reporting Clarifications: As approved in the 2023 WMP, the GH01 initiative includes the System Hardening Undergrounding miles, as well as the overhead hardening and line removal work. In Table 11 of the WMP QDR, the undergrounding costs, however, are not reported for GH-01 in order to not double-count those costs reported in GH-04. The System Hardening Undergrounding miles, however, are reported in Table 1 of the QDR and ARC. Therefore, the approach to divide cost spent per year by the miles is not appropriate.1 Additionally, for WMP reporting, PG&E includes hardening miles from nonSystem Hardening programs like Work Requested by Others (WRO), Capacity, and Rule 20A. Costs for those projects are not included in the unit cost calculation since they are outside of the base System Hardening program captured in MAT Codes 08W and 3UG. (2) Unit Cost Calculation Method: Unit cost is calculated using total costssince-inception (multi-year) and total miles completed (which can be multiyear) of the subprojects that are 100% complete in the associated year. Unit cost is not calculated by dividing the total program cost spent by the total miles completed in a given year because it would: (i) Inaccurately include both the readiness/pre-construction costs for future subprojects that are not yet complete and the postconstruction/closeout costs for previously completed subprojects, and (ii) Inaccurately include subprojects with partially completed miles at year-end. • Note, the miles reported in the WMP QDRs and ARCs include the miles that have been energized and completed the final Fire Risk Safety Audit in a particular year, even if the subproject completes work across multiple years (i.e. there could be a portion of the subproject energized work in year 1 – which is reported in the WMP mileage completed – and the project is 100% completed in year 2. The unit cost will be calculated only in year 2, but the energized miles based on the portion of the project completed will be reported in the relevant year). • Note, the approach we take for calculating unit cost is consistent with PG&E’s response to data request TURN_003-Q004, which was specific to the System Hardening Undergrounding unit cost. The following two additions are captured in worksheet “GH-01 & GH-04 Unit Cost” in attachment “WMP-Discovery2026-2028_DR_SPD_001- Q021Atch01.xlsx” based on the scope of this request being at the WMP initiative-level: o GH-01: This response includes unit costs separated by the three mitigation types included within GH-01: (1) System Hardening Undergrounding, (2) Overhead hardening, and (3) Line removal. One combined unit cost for the GH-01 initiative is not useful to capture, since it includes multiple hardening mitigation types that are not comparable for unit cost calculations. o GH-04: This response includes unit cost separated by two sub programs, and PG&E has a combined GH-04 Undergrounding Unit cost included, as well:  System Hardening Undergrounding;  Community Rebuild Undergrounding. • Mitigation SA-02 includes both capital and operational expenditures. PG&E has split SA-02 to reflect separate calculations for each of capital and operational expenditures. • Costs for GM-02 are not separated but included in the Activity level “Vegetation Inspections – Transmission.” • Costs for GM-03 are not separated but included in the Activity level “Vegetation Inspections – Distribution.” • PG&E has determined that a formula error occurred in SPD’s calculations for Mitigations VM-03 and VM-04 and provides corrected values in the “PGE_RESPONSE” worksheet. • Upon consultation with mitigation owners, PG&E has made corrections to the “Total Cost” and, accordingly, “updated Average Cost per Unit” columns for the following mitigations for 2023: AI-02, AI-04, AI-05, AI-06, AI-07, VM-04. • Upon consultation with mitigation owners, PG&E has made corrections to the “Total Cost” and, accordingly, “updated Average Cost per Unit” columns for the following mitigations for 2023: AI-02, AI-04, AI-05, AI-06, AI-07. • Upon consultation with mitigation owners, PG&E has made corrections to the “Units Completed” and, accordingly, “Updated Average Cost per Unit” columns for 2023 and 2024 for GM-06. • With regard to values for 2025, PG&E notes that the values used by SPD reflect forecasts first made in 2022. PG&E has provided updated values reflecting more current forecasts. b. PG&E’s QDR tabular data will be provided with the Q1 2025 QDR in May 2025 | Eddie Schmitt | 2025-04-15 | 2025-05-07 | 2025-05-07 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_001.zip | 1 | No | 3 | Overview of WMP | 3.6 | Projected Expenditures
16 | 94 | SPD | 001 | SPD_001 | 21(a) | Yes | SPD_001_Q21(a) | SPD is attempting to compute the cost per unit for many of the WMP initiatives tracked in the WMP Implementation Dashboard (WMP Implementation Dashboard). Review and confirm the cost per unit is correct for the initiatives. See the attached workbook titled PGE WMP Implementation Dashboard.xlsx. a. Follow all of the instructions within the cells and notes included in PGE WMP Implementation Dashboard.xlsx. b. SPD is attempting to do a similar exercise for the 2026-2028 WMP but the QDR tabular data was not submitted. SPD saw some of the data in the WMP, but was unable to determine if this data was inclusive of all initiatives. Where should SPD look for equivalent data? | a. Please see attachment “WMP-Discovery2026-2028_DR_SPD_001- Q021Rev01Atch01.xlsx” for the requested information. The values provided in the Excel file section titled “PGE Response” represent PG&E’s response to this data request using the formulas and data sources provided by SPD, except to the extent amended as described below, and do not reflect PG&E’s official or final calculation of the unit costs associated with the listed WMP initiatives. Please note, the values in the “PG&E RESPONSE” worksheet are based on SPD’s instructions, data, and formulas but with the following amendments, adjustments, and corrections: WMP-Discovery 2026-2028_DR_SPD_001-Q021Rev01 Page 2 • PG&E has updated values in the “Total Cost” column for the year 2024 to reflect final, actual (as opposed to forecasted) costs as reported in our 2024 Annual Report on Compliance (ARC). • PG&E has updated “Units Planned/Completed” for the year 2024 to reflect final units as reported in our 2023 and 2024 ARCs. • Initiatives GH-01 (System Hardening) and GH-04 (Undergrounding) do not calculate unit costs using the method proposed by SPD. The following are clarifications about how unit costs are calculated for these projects. These corrections have been incorporated into worksheet “GH-01 & GH-04 Unit Cost” in attachment “WMP-Discovery2026-2028_DR_SPD_001- Q021Rev01Atch01.xlsx”. The 2023 and 2024 unit costs are from historically completed projects. The 2025 unit costs are predominately based on forecasts with a current workplan that contains more miles than targets. (1) WMP Reporting Clarifications: As approved in the 2023 WMP, the GH- 01 initiative includes the System Hardening Undergrounding miles, as well as the overhead hardening and line removal work. In Table 11 of the WMP QDR, the undergrounding costs, however, are not reported for GH-01 in order to not double-count those costs reported in GH-04. The System Hardening Undergrounding miles, however, are reported in Table 1 of the QDR and ARC. Therefore, the approach to divide cost spent per year by the miles is not appropriate.1 Additionally, for WMP reporting, PG&E includes hardening miles from non- System Hardening programs like Work Requested by Others (WRO), Capacity, and Rule 20A. Costs for those projects are not included in the unit cost calculation since they are outside of the base System Hardening program captured in MAT Codes 08W and 3UG. (2) Unit Cost Calculation Method: Unit cost is calculated using total costssince- inception (multi-year) and total miles completed (which can be multiyear) of the subprojects that are 100% complete in the associated year. Unit cost is not calculated by dividing the total program cost spent by the total miles completed in a given year because it would: (i) Inaccurately include both the readiness/pre-construction costs for future subprojects that are not yet complete and the postconstruction/ closeout costs for previously completed subprojects, and (ii) Inaccurately include subprojects with partially completed miles at year-end. • Note, the miles reported in the WMP QDRs and ARCs include the miles that have been energized and completed the final Fire Risk Safety Audit in a particular year, even if the subproject completes work across multiple years (i.e. there could be a portion of the subproject energized work in year 1 – which is reported in the WMP mileage completed – and the project is 100% completed in year 2. The unit cost 1 Note, in the 2026 WMP, we have removed the system hardening undergrounding miles from GH-01 initiative and renamed to GH-12 to only include overhead hardening and line removal. WMP-Discovery 2026-2028_DR_SPD_001-Q021Rev01 Page 3 will be calculated only in year 2, but the energized miles based on the portion of the project completed will be reported in the relevant year). • Note, the approach we take for calculating unit cost is consistent with PG&E’s response to data request TURN_003-Q004, which was specific to the System Hardening Undergrounding unit cost. The following two additions are captured in worksheet “GH-01 & GH-04 Unit Cost” in attachment “WMP-Discovery2026-2028_DR_SPD_001- Q021Rev01Atch01.xlsx” based on the scope of this request being at the WMP initiative-level: o GH-01: This response includes unit costs separated by the three mitigation types included within GH-01: (1) System Hardening Undergrounding, (2) Overhead hardening, and (3) Line removal. One combined unit cost for the GH-01 initiative is not useful to capture, since it includes multiple hardening mitigation types that are not comparable for unit cost calculations. o GH-04: This response includes unit cost separated by two sub programs, and PG&E has a combined GH-04 Undergrounding Unit cost included, as well: ▪ System Hardening Undergrounding; ▪ Community Rebuild Undergrounding. • Mitigation SA-02 includes both capital and operational expenditures. PG&E has split SA-02 to reflect separate calculations for each of capital and operational expenditures. • Costs for GM-02 are not separated but included in the Activity level “Vegetation Inspections – Transmission.” • Costs for GM-03 are not separated but included in the Activity level “Vegetation Inspections – Distribution.” • PG&E has determined that a formula error occurred in SPD’s calculations for Mitigations VM-03 and VM-04 and provides corrected values in the “PGE_RESPONSE” worksheet. • Upon consultation with mitigation owners, PG&E has made corrections to the “Total Cost” and, accordingly, “updated Average Cost per Unit” columns for the following mitigations for 2023: AI-02, AI-04, AI-05, AI-06, AI-07, VM-04. • Upon consultation with mitigation owners, PG&E has made corrections to the “Total Cost” and, accordingly, “updated Average Cost per Unit” columns for the following mitigations for 2023: AI-02, AI-04, AI-05, AI-06, AI-07. • Upon consultation with mitigation owners, PG&E has made corrections to the “Units Completed” and, accordingly, “Updated Average Cost per Unit” columns for 2023 and 2024 for GM-06. • With regard to values for 2025, PG&E notes that the values used by SPD reflect forecasts first made in 2022. PG&E has provided updated values reflecting more current forecasts. b. PG&E’s QDR tabular data will be provided with the Q1 2025 QDR in May 2025. | Eddie Schmitt | 2025-04-15 | 2025-05-22 | 2025-05-22 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_001.zip | 1 |  | 3 | Overview of WMP | 3.6 | Projected Expenditures
16 | 95 | SPD | 001 | SPD_001 | 22 | No | SPD_001_Q22 | The 2026-2028 WMP states on page 182 that the System Hardening Project Scoping Decision Tree and Process is shown in Figures PG&E-8.2.1-1, PG&E-8.2.1-2, and PG&E-8.2.1-3 will begin to inform the selection of projects in 2027. What methodology is being used for 2026? | The system hardening decision tree presented in PG&E’s 2023-2025 Base WMP (Figures SRN-PG&E-23-05-06A, SRN-PG&E-23-05-06B, SRN-PG&E-23-05-06C) is the decision tree used as the starting point for selecting system hardening mitigations for 2026. | Eddie Schmitt | 2025-04-15 | 2025-04-18 | 2025-04-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_001.zip | 0 | No | 8 | Grid Design, Operations, and Maintenance | 8.2.1 | Covered Conductor Installation
16 | 96 | SPD | 001 | SPD_001 | 23 | No | SPD_001_Q23 | Provide a narrative explanation regarding how the decision tree on pg. 125 of PG&E’s 2026-2028 WMP (Figure PG&E-6.1.3.1-4) and the decision tree on pg. 183-185 (Figures PG&E-8.2.1-1, PG&E-8.2.1-2, and PG&E-8.2.1-3) are related. a. Provide examples of how the four decision trees were used to determine some form of system hardening as the selected mitigation at a given circuit segment. The examples should exhaust all of the system hardening results made possible by these four decision trees. | The Mitigation Selection, Planning and Execution process referenced in Figure PG&E6.1.3.1-4 describes the general process by which PG&E’s Investment Planning Organization considers budgets for mitigation programs. Figures PG&E-8.2.1-1, PG&E-8.2.1-2, and PG&E-8.2.1-3 is the decision tree used by the System Hardening Program for choosing system hardening mitigation alternatives for projects starting in 2027. We use the budgets developed by Investment Planning shown in Figure PG&E-6.1.3.1-4 to fund the system hardening mitigations. a. Figures PG&E-8.2.1-1, PG&E-8.2.1-2, and PG&E-8.2.1-3 is one single decision tree that we use to choose system hardening mitigation alternatives for projects starting in 2027. It is shown in the WMP as three individual figures so that it is more legible. To be clear, there are not four decision trees used to determine some form of system hardening as the selected mitigation at a given circuit segment―there is only one decision tree (Figures PG&E-8.2.1-1, PG&E-8.2.1-2, and PG&E-8.2.1-3). The system hardening results made possible by the decision tree are: (1) do not implement system hardening; (2) implement a 100% overhead hardening solution; (3) implement a 100% undergrounding solution; (4) implement a hybrid hardening WMP-Discovery 2026-2028_DR_SPD_001-Q023 Page 2 solution where portions of a line are undergrounded and other portions are overhead hardened; and (5) implement a line removal with remote grid solution. Figure PG&E-6.1.3.1-4 is a high-level illustration showing a life-cycle view of how we consider risk drivers to develop mitigation initiatives, develop an investment plan to fund the mitigations and then execute them. This decision tree is not used to select system hardening mitigation alternatives. | Eddie Schmitt | 2025-04-15 | 2025-04-18 | 2025-04-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_001.zip | 0 | No | 6 | Wildfire Mitigation Strategy Development | 6.1.3 | Activity Selection Process
16 | 97 | SPD | 001 | SPD_001 | 24 | No | SPD_001_Q24 | In response to WMP-Discovery2026-2028_DR_TURN_002-Q006, PG&E references the Wildfire Benefit Cost Analysis (WBCA) Tool. Provide a description of the WBCA Tool as referenced in PG&E’s 5th Revision to its 2023-2025 WMP on pg. 425 and on page 187 of the 2026-2028 WMP that includes the following: a. An explanation of how Cost-Benefit Ratios are utilized within the Tool. b. An explanation of how the Tool complies with the requirements of D.22-12-027. c. An explanation of how the Tool complies with the requirements of D.24-05-064. d. A definition for each of the following terms presented in TABLE RN-PG&E-23-05-3 of PG&E’s 5th Revision to its 2023-2025 WMP on pg. 427: i. PVRR Cap. Invest. ii. Lifetime O&M Costs iii. Wildfire iv. Public Safety v. Normal Reliability vi. PSPS vii. EPSS viii. Total Risk ix. Risk Avoidance over Lifetime Benefit x. Residual Risk over Lifetime xi. Lifetime – Benefit-Cost e. Provide a step by step explanation of how each of the terms in Question 24d. are calculated. | a. PG&E uses its Wildfire Benefit Cost Analysis (WBCA) tool to estimate project costs, wildfire risk reduction, and reliability improvements that are applicable to system hardening mitigations (undergrounding, overhead hardening + Enhanced Powerline Safety Setting + Downed Conductor Detection, and hybrid mitigations). The WBCA considers: the approximate capital costs to construct a system hardening project; the expected capital and expense operation and maintenance (O&M) costs for the life of the asset; financing costs; ignition risk reduction and outage program reliability; the benefits period/asset life; rebuild costs for overhead assets; and the effectiveness of different mitigations. The WBCA output for each circuit segment is an estimated cost to build and maintain system hardening alternatives, a Cost Benefit Ratio (CBR), and net benefit analysis. PG&E uses the CBR and net benefit results to inform mitigation selection at the circuit-segment level. b. D.22-12-027 replaced the Multi-Attribute Value Framework (MAVF) with a CostBenefit Approach that includes standardized dollar valuations of Safety, Electric Reliability and Gas Reliability Consequences from risk events. Investor-Owned Utilities (IOUs) are required to use the Cost-Benefit Approach to assess and rank risks and mitigations. PG&E’s WBCA complies with the requirements in D.22-12- 027 by using standardized dollar valuations for safety and electric reliability consequence to calculate a CBR. CBRs are calculated within the WBCA for various mitigation alternatives on each circuit segment. PG&E evaluates the CBR results as part of our mitigation selection process. We will use the outputs from the WBCA as one factor for informing our mitigation alternative selection. D.22-12-027 allows a utility to consider other factors when selecting a mitigation alternative if we explain how other factors influenced our mitigation selection.1 c. D.24-05-064 modified the Risk-Based Decision-Making Framework (RDF) included in Appendix A to D.22-12-027 and includes four salient requirements: (1) require the IOUs to present cost-benefit ratios (CBR) for each general rate case post-test year rather than an aggregate CBR for the entire post-test year period;2 (2) should require the IOUs to determine reporting tranches in the RDF by using combinations of quantities of LoRE and CoRE where portions of a risk with the highest 20 percent of LoRE would be grouped within a tranche and the highest 20 percent of CoRE would be grouped in another tranche or, where data is available, require IOUs to also submit more granular data regarding tranches;3 (3) when a utility chooses to address Risk-Adjusted Levels by relying on a convex scaling function, require IOUs to also present Risk-Adjusted Attribute Levels by relying on a linear scaling function;4 and (4) require IOUs to provide three discount rate scenarios for the Cost-Benefit Ratio including the Societal Discount Rate Scenario, the Weighted Average Cost of Capital, and the Hybrid Discount Scenario.5 (1) PG&E’s WBCA generates CBRs at the circuit segment level. Circuit-segment level CBRs can be aggregated outside of the WBCA to generate an annual post-test year CBR. (2) PG&E’s WBCA complies with D.24-05-064 in that we can use it to calculate CBRs by circuit segment, a much more granular level of detail, than calculating CBRs at the tranche level. (3) PG&E relies on a convex scaling function in its analysis, as detailed in its 2024 RAMP application6. PG&E will also be able to provide supplemental RiskAdjusted Attribute Levels based on using a linear scaling function with the WBCA; however, linearly scaled values are not used to calculate CBRs in the tool. (4) PG&E will use its WBCA to calculate and present Cost-Benefit Ratios using the three discount rate scenarios set forth in D.24-05-064; however, PG&E intends to use only one discount rate scenario (Weighted Average Cost of Capital) to inform mitigation selection. d. A definition for each of the following terms presented in TABLE RN-PG&E-23-05-3 of PG&E’s 5th Revision to its 2023-2025 WMP on pg. 427: i. PVRR Cap. Invest. – Estimated initial cost of installing the mitigation multiplied by the present value of revenue requirement to accurately account for the cost of capital ii. Lifetime O&M Costs – Present value of lifetime expenses incurred for operating and maintaining the asset. iii. Wildfire – Present value of the wildfire risk exposure over the lifetime of the asset. iv. Public Safety – Present value of the public safety risk posed by bare overhead assets based on incidents such as contact with energized conductors over the lifetime of the asset. v. Normal Reliability - Present value of risk from non-wildfire related outages over the lifetime of the asset. vi. PSPS – Present value of risk from PSPS outages over the lifetime of the asset. vii. EPSS – Present value of risk from EPSS outages over the lifetime of the asset. viii. Total Risk – Sum of Wildfire, Public Safety, Normal Reliability, PSPS and EPSS Risks. ix. Risk Avoidance over Lifetime Benefit – Present value of all risks reduced by the mitigation. x. Residual Risk over Lifetime – Present value of remaining risk after mitigation. xi. Lifetime – Benefit-Cost – Present value of all risks reduced less costs of the mitigation. e. The following is a high-level, step-by-step explanation of how each of the terms in Question 24d. are calculated. i. PVRR Cap. Invest. = Initial Capital Investment * PVRR (set value of ~1.39) ii. Lifetime O&M Costs = Sum of all O&M Costs over lifetime of the asset. iii. Wildfire = Wildfire Risk as represented in PG&E’s WLDFR Risk Bowtie is allocated across all WDRM risk points. The Wildfire risk for an individual circuit segment is based on the total risk points therein. iv. Public Safety – Public Safety Risk is based on PG&E’s PCEEE Bowtie for distribution overhead assets. This total risk is allocated across primary overhead line miles and distributed to each circuit segment based on the primary overhead line miles therein. v. Normal Reliability – Calculated based on historic non-wildfire customer minutes interrupted (CMI) for each circuit segment monetized in accordance with the Interruption Cost Estimate (ICE) Calculator. vi. PSPS – Calculated based on PSPS Lookback CMI for each circuit segment monetized in accordance with the ICE Calculator vii. EPSS = Calculated based on EPSS Lookback CMI for each circuit segment monetized in accordance with the ICE Calculator viii. Total Risk = Wildfire + Public Safety + Normal Reliability + PSPS + EPSS ix. Risk Avoidance over Lifetime Benefit = Wildfire*Mitigation Effectiveness + Public Safety*Mitigation Effectiveness + Normal Reliability*Mitigation Effectiveness + PSPS*Mitigation Effectiveness + EPSS*Mitigation Effectiveness x. Residual Risk over Lifetime = Total Risk - Risk Avoidance over Lifetime Benefit xi. Lifetime – Benefit-Cost = Risk Avoidance over Lifetime Benefit – (PVRR Cap. Investment + Lifetime O&M Costs) | Eddie Schmitt | 2025-04-15 | 2025-04-25 | 2025-04-25 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_001.zip | 0 | No | 5 | Risk Methodology & Assessment | 5.4 | Summary of Risk Models
16 | 98 | SPD | 001 | SPD_001 | 25 | No | SPD_001_Q25 | State the filings where PG&E has used the Wildfire Benefit Cost Analysis Tool (i.e. RAMP, GRC, WMP, other proceedings or filings) a. Does PG&E intend to apply the Wildfire Benefit Cost Analysis Tool in its 2027 Test Year GRC Application? i. If no, explain why not. ii. If yes, explain how this tool will be applied in the 2027 Test Year GRC Application. a) Which mitigations presented in the 2024 RAMP Application will be impacted by PG&E’s use of the Wildfire Benefit Cost Analysis Tool when PG&E files its 2027 Test Year GRC Application? | a. Yes, PG&E intends to use the WBCA, in addition to other analysis, to select mitigations for our 2027 GRC system hardening program. i. N/A ii. We will use the WBCA to: (1) aggregate risk analysis for circuit segments and (2) generate CBRs and Net Benefits for mitigation alternatives (undergrounding, overhead hardening + Enhanced Powerline Safety Setting + Downed Conductor Detection, and hybrid mitigations) for each circuit segment. PG&E will further evaluate the circuit segment risk ranking, CBRs and Net Benefits from the WBCA, along with other considerations such as tree-strike risk and ingress/egress, to ultimately select the mitigation for each circuit segment. WMP-Discovery 2026-2028_DR_SPD_001-Q025 Page 2 a) In the 2024 RAMP PG&E planned three system hardening mitigations for 2027-2030: 1. System hardening undergrounding (WLDFR-M022), 2. System hardening overhead hardening (WLDFR-M002) and 3. Line removal with remote grid (WLDFR-M011). The three system hardening mitigations planned in the 2024 RAMP will be considered in the WBCA for PG&E’s test year 2027 GRC. | Eddie Schmitt | 2025-04-15 | 2025-04-18 | 2025-04-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_001.zip | 0 | No | 5 | Risk Methodology & Assessment | 5.4 | Summary of Risk Models
16 | 99 | SPD | 001 | SPD_001 | 26 | No | SPD_001_Q26 | The 2026-2028 WMP references the WBCA Tool, but SPD has reviewed other filings like PG&E’s 2024 RAMP Application (R.24-05-008) where this tool is not referenced. a. The WBCA was not referenced in PG&E’s 2024 RAMP Application. During the preparation of PG&E’s 2024 RAMP, were any aspects of the WBCA used to determine mitigation effectiveness values and/or mitigation selection and, if so, explain in detail how. If not, explain why not. i. When did PG&E begin developing the WBCA Tool? b. List the differences between the way mitigation effectiveness values were calculated when preparing PG&E’s 2024 RAMP Application and when preparing the 2026-2028 WMP submission. i. Provide an explanation for each difference listed. c. List the differences between the way mitigations were selected for a given asset when preparing PG&E’s 2024 RAMP Application and when preparing the 2026-2028 WMP submission. i. Provide an explanation for each difference listed. d. In WMP-Discovery2026-2028_DR_TURN_002-Q006, PG&E stated the WBCA tool is still in development in its response to TURN’s questions, but pages 187 through 192 of the 2026-2028 WMP appear to present the tool as complete. What portions of the WBCA Tool are still under development? e. SPD understands that PG&E has two risk models for its wildfire risk, (1) the EORM and (2) the WDRM/WTRM. How does the WBCA Tool incorporate information from both of these risk models? | a. The WBCA was not used for any analysis in the 2024 RAMP Application as the WBCA tool was not developed at the time of the 2024 RAMP Application. i. PG&E conceptualized the WBCA in 2023 and began developing the WBCA tool in earnest in 2024 based upon OEIS’ Revised EUP Guidelines and described it in the 2023 WMP Revision Notice 23-05. Starting this year, the inputs of PG&E’s WBCA are being used to inform the cost-benefit analysis for scoping using the System Hardening Project Scoping Decision Tree and Process (shown in Figures PG&E-8.2.1-1, PG&E-8.2.1-2, and PG&E-8.2.1- 3) for work that will be completed in 2027, and included in our Test Year 2027 GRC and our EUP. b. The mitigation effectiveness values in the 2026-2028 Base WMP submission are calculated at the circuit segment-level (see Section 8.2.1, p. 187). When analyzing a potential project, the WBCA uses specific effectiveness values for those circuit segments based on the unique risk sub-drivers (outage combinations) for that location, as identified by the WDRM. The 2024 RAMP Application mitigation effectiveness values were calculated using the system averages for undergrounding work, and sub-driver mitigation effectiveness values for covered conductor. The mitigation effectiveness values in the 2024 RAMP Application are aggregated at the tranche level rather than the circuit segment-level. This was based on analysis available at the time of filing. i. The 2026-2028 Base WMP submission uses the most recent mitigation effectiveness analysis that uses a preliminary version of the WBCA tool that was not available at the time of the 2024 RAMP application. In addition, the 2024 RAMP analysis focuses on tranche-level analysis rather than circuit segment analysis. c. For the 2024 RAMP Filing, the mitigation selected was based on a filtering of the circuit segments from 1-N based on wildfire risk rank. There was no cost-benefit analysis conducted for the RAMP filing. It was assumed that projects selected for undergrounding had a hybrid split between overhead hardening and undergrounding (90% of a circuit segment was assumed to be undergrounding and 10% of the circuit segment assumed to be overhead hardening). The focus for mitigation selection at the time of the 2024 RAMP filing was risk reduction. For work planned in 2026, we used the system hardening decision tree presented in PG&E’s 2023-2025 Base WMP (Figures SRN-PG&E-23-05-06A, SRN-PG&E-23- 05-06B, SRN-PG&E-23-05-06C). It was the starting point for selecting system hardening mitigations for 2026. Additional considerations included the presence of tree strike risk and ingress/egress concerns. For work planned for completion in 2027, we are using the decision tree (Figures PG&E-8.2.1-1, PG&E-8.2.1-2, and PG&E-8.2.1-3) in the 2026-2028 Base WMP. This updated decision tree includes the Cost Benefit Ratio (CBR) and Net Benefit (NB) criteria as we revise our strategies to meet the requirements of the Electrical Undergrounding Plan (EUP). PG&E anticipates transitioning the undergrounding program to the EUP for 2028 and may need to adapt the project selection approach described in the decision tree outlined above to align with the final EUP guidelines and approval conditions after the EUP is approved and goes into effect. WMP-Discovery 2026-2028_DR_SPD_001-Q026 Page 3 d. On pages 187 through 192 of the 2026-2028 WMP PG&E describes how we use the WBCA to calculate wildfire mitigation effectiveness at the circuit segment level. PG&E used a preliminary version of the WBCA to analyze the allocation of mitigation effectiveness to specific circuit segments, which was used for the 2026- 2028 Base WMP submission. The final WBCA tool that will be used for the purpose of calculating cost-benefit ratios and that will meet the EUP requirements is not complete. The methodology, tool development and input values are being finalized, before quality assurance can be completed. The final version of the WBCA tool will be used for project selection for the 2027 GRC and the upcoming EUP. e. The WBCA tool incorporates risk information from both the EORM model and the WDRM model. The EORM model is used to quantify the absolute value of the risk on the circuit segment. The WDRM model portrays the relative risk of a circuit segment across the system and provides a risk ranking for the circuit segments. These models provide key inputs for calculating the risk reduction benefit and costbenefit ratio calculations of the mitigation alternatives. | Eddie Schmitt | 2025-04-15 | 2025-04-18 | 2025-04-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_001.zip | 0 | No | 5 | Risk Methodology & Assessment | 5.4 | Summary of Risk Models
16 | 100 | SPD | 001 | SPD_001 | 27 | No | SPD_001_Q27 | Provide SPD with any follow up responses PG&E provides in response to WMP-Discovery2026-2028_DR_TURN_002-Q006e-f. | Please see “WMP-Discovery2026-2028_DR_TURN_002-Q006Supp01.pdf,” which is also available on our website at Community Wildfire Safety Program. | Eddie Schmitt | 2025-04-15 | 2025-04-18 | 2025-04-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_001.zip | 0 | No | N/A | N/A | N/A | N/A
16 | 101 | SPD | 001 | SPD_001 | 28 | No | SPD_001_Q28 | Building on PG&E’s response in WMP-Discovery2026-2028_DR_TURN_002-Q009Atch01.xlsx, fill out the Table provided below. The rows labeled “HFTD Tier 2 with Spans Outside HFTD” and “HFTD Tier 3 with Spans Outside HFTD” refers to miles that meet the requirements found on pg. 16 of Energy Safety’s 10-Year Electrical Undergrounding Plan Guidelines. | Building on PG&E’s response in WMP-Discovery2026-2028_DR_TURN_002- Q009Atch01.xlsx, fill out the Table provided below. The rows labeled “HFTD Tier 2 with Spans Outside HFTD” and “HFTD Tier 3 with Spans Outside HFTD” refers to miles that meet the requirements found on pg.16 of Energy Safety’s 10-Year Electrical Undergrounding Plan Guidelines. Total Miles OH Hardening Miles Year X OH replaced by UG Miles Year X Total HFTD HFTD Tier 2 HFTD Tier 2 with Spans Outside HFTD HFTD Tier 3 HFTD Tier 3 with Spans Outside HFTD Additional HFRA Answer 028 PG&E does not have the requested information and does not maintain the data required to compile such information. PG&E would need to expend significant time, effort, and cost to perform the evaluations necessary to create the information. Please let us know if you would like to have a call to discuss this further. | Eddie Schmitt | 2025-04-15 | 2025-04-18 | 2025-04-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_001.zip | 0 | No | 8 | Grid Design, Operations, and Maintenance | 8.2.2 | Undergrounding of Electric Lines and/or Equipment
16 | 102 | OEIS | 003 | OEIS_003 | 1 | No | OEIS_003_Q1 | Regarding Tree Removal Inventory (TRI) PG&E does not list TRI as a vegetation management program in its 2026-2028 Base WMP. On page 363, PG&E’s WMP states “PG&E is in the process of evaluating which component(s) of the ... [Tree Removal Inventory (TRI)] scope will be incorporated into the Distribution Routine Patrol Program.” a. How many trees are currently listed for work under TRI? b. How many trees does PG&E expect to remain in the TRI list on January 1, 2026? c. How will PG&E mitigate trees listed for work under TRI during the 2026-2028 cycle? d. When does PG&E expect to mitigate all the trees listed for work under TRI? | a. As of April 16, 2025, there are currently 45,604 trees listed for tree work under TRI. Of those trees, 32,100 are constrained. b. We estimate there will be approximately 291,792 trees still to be reviewed in the TRI inventory as of January 1, 2026. This includes 223,963 trees that have not been released for review in the TRI work plans yet, plus an estimated 67,829 trees that may be remaining from the current year’s work plan, which may include trees where work is scheduled, trees that are listed for work but are constrained, and trees that have not yet been reviewed. c. We are planning to mitigate TRI trees through the Distribution Routine program. See the 2023-2025 WMP page 622 for more information regarding methods of mitigation. d. PG&E expects to mitigate all the trees listed in the TRI inventory by 2030. | Nathan Poon | 2025-04-15 | 2025-04-18 | 2025-04-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_003.zip | 0 | No | Appendix D: Areas of Continued Improvement | Areas of Continued Improvement | ACI PG&E-25U-08 | ACI PG&E-25U-08 - Reinspection of Trees in the Tree Removal Inventory
16 | 103 | OEIS | 003 | OEIS_003 | 2 | No | OEIS_003_Q2 | Regarding Constrained Vegetation Management Work Orders In response to data request OEIS-P-WMP_2025-PGE-001, Questions 6, PG&E lists 7,084 Priority 2 constrained work orders. a. In the table below, categorize all 7,084 constrained work orders by age (days since inspection) and HFTD tier. | Please see table below for the 7,084 constrained work orders by age (days since inspection) and HFTD tier. a. Please note, the data set utilized to generate the table below was pulled on 12/31/2024 and aligns with the data that was used to populate the response in the prior OEIS-001 Question 6 response. 1 1 As of 4/18/2025 5,226 of the 7,084 constrained work orders pulled 12/31/2024 remain constrained. WMP-Discovery 2026-2028_DR_OEIS_003-Q002 Page 2 HFTD Area 0-30 Days 31-90 Days 91-180 Days 181-270 Days 270-365 Days 366+ Days Non-HFTD 6 938 723 260 188 101 HFTD Tier 2 7 963 904 283 139 176 HFTD Tier 3 8 814 1074 247 156 97 | Nathan Poon | 2025-04-15 | 2025-04-18 | 2025-04-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_003.zip | 0 | No | 9 | Vegetation Management & Inspections | 9.12 | Priority Assignment
16 | 104 | OEIS | 003 | OEIS_003 | 3 | No | OEIS_003_Q3 | Regarding System Hardening Decision-Making Regarding Figure PG&E-8.2.1-2: PG&E’s System Hardening Project Scoping Decision Tree and Process (PG&E’s 2026-2028 Base WMP, pp. 183-185): a. Define “NB” as seen for “UG NB > OH NB.” i. How does PG&E calculate UG NB and OH NB for the purpose of determining these criteria? ii. How does NB differ from the CBR in terms of how benefit is calculated? iii. Does PG&E calculate benefit (for NB and CBR) based on overall effectiveness for mitigations (as seen in Table PG&E-6.1.3-1, PG&E’s 2026-2028 Base WMP, p. 128), or based on location-specific effectiveness accounting for local risk drivers? Provide a brief explanation of this calculation in the response. b. Provide the spatial data (via KML or KMZ) for the tree strike potential throughout PG&E’s service territory, showing a heat map across circuit segments for areas with no/low (0-5) versus high (6+) strike potential. c. How are areas of egress/ingress concern identified by the Public Safety Specialist (PSS) team (i.e. annually produce a list of areas of concern, review specific projects through this process to evaluate concerns once triggered)? i. Provide a list of areas that have been identified by the PSS team for ingress/egress concerns. This should include the circuit protection zone. d. What criteria and threshold does PG&E use when determining whether a circuit protection zone (CPZ) is affected by PSPS? e. Provide a list of projects scheduled for 2026 to 2028 that have been triggered to be a hybrid solution (from strike tree potential, ingress/egress concerns, or PSPS impacts), as depicted by one of the three criteria listed in the decision tree. Provide the information via Excel following the table below for each project. f. Provide a list of projects scheduled for 2026 to 2028 that are undergrounding projects where the UG CBR is greater than the OH+EPSS CBR, but due to the UG CBR being within 50% of the OH+EPSS CBR, the project is scoped to be undergrounded. This must also include hybrid projects that were triggered from the criteria discussed in Q03(e). Provide the information via Excel following the table below for each project. | a. NB is defined as Net Benefit. i. Net Benefit is calculated as: Net Benefit = Benefits – Costs ii. Net benefit is the difference between total present value of benefits and total present value of costs (costs are subtracted from benefits) whereas a cost benefit ratio compares the total present value of benefits expected from a project to the total present value of its costs (the total project benefits are divided by the total project costs). The cost and benefit inputs used in both the CBR and net benefit calculations are the same. PG&E considers multiple factors in selecting alternatives because an overemphasis on CBR devalues high cost / high benefit projects. CBR does not consider the absolute benefits and holistic value of permanent risk mitigations, and when used as the sole criteria, results in situations where risk is permanently left on the system, including on circuit segments where undergrounding’s benefits are greater than those of overhead hardening. iii. The CBR calculation in the WBCA starts with the overall effectiveness values as seen in Table PG&E-6.1.3-1 and then calculates a location-specific mitigation effectiveness value for each circuit-segment. This location-specific effectiveness value is then multiplied by the same location’s initial risk value to calculate the risk reduction benefit of the mitigation. Effectiveness calculation details can be found in PG&E’s response to WMP-Discovery2026-2028_DR_TURN_002-Q005, with follow-up information to be provided in WMP-Discovery 2026- 2028_DR_SPD_001-Q010. b. PG&E does not have a single KMZ file that represents tree strike potential throughout PG&E’s service territory. Instead, each circuit is associated with its own set of KMZ files based on the following conductor types: • Not Hardened • #2Cu TW • 1/0ASR TW • 397AAC TW • 715AAC TW For reference, please see the attachment folder “WMP-Discovery2026- 2028_DR_OEIS_003-Q003Atch01.zip,” which contains example KMZ files for circuits Alto 1124 and Dobbins 1101. c. As part of scoping, the Public Safety Specialist (PSS) team evaluates specific projects to identify ingress/egress concerns and shares with the scoping team while discussing all identified dependencies and constraints. This evaluation also considers previous fire history, types of customers, fuel/weather/topography impact, and other relevant factors. For reference, please see “WMP-Discovery2026-2028_DR_OEIS_003- Q003Atch02.kmz,” “WMP-Discovery2026-2028_DR_OEIS_003-Q003Atch03.kmz,” and “WMP-Discovery2026-2028_DR_OEIS_003-Q003Atch04CONF.pdf,” which provide examples for circuit protection zones Alleghany 1101804 and ALLEGHANY 1101SC 1101/2. This includes details on ingress/egress considerations within the circuit protection zone. d. During the scoping process, PG&E leverages a PSPS weather polygon that illustrates the impact of PSPS on our service territory, based on a five-year lookback starting in 2018. The criteria for determining whether a circuit protection zone is affected by PSPS is binary and PG&E considers the distinction of whether there is PSPS impact or not. e. The 2027 workplan is in the process of being scoped using the Decision Tree and 2028 has not yet started. Please reference “WMP-Discovery2026- 2028_DR_OEIS_003-Q003Atch05.xlsx” for examples of hybrid projects scheduled between 2026 and 2027 that align with the three criteria (tree strike potential, ingress/egress concerns, and PSPS impacts) listed in the decision tree. There is also an example of how hybrid projects can be created post scoping due to infeasible undergrounding locations. Project ID was not provided for projects currently in scoping that do not yet have subprojects. For 2026 and 2027 projects that have been scoped or are in scoping, we can provide which projects are hybrid, however, there is not an existing database with associated drivers for each project. Instead, this information is in each project’s scoping package, which would require a manual review. f. PG&E is providing those 2027 planned projects currently progressing through scoping where the UG/Hybrid CBR is less than the OH+EPSS CBR, but within the 50% threshold and PG&E is progressing with the UG/Hybrid solution. See Attachment “WMP-Discovery2026-2028_DR_OEIS_003-Q003Atch06.xlsx.” The project ID’s included are the first order only and will have additional sub-project ID’s once the projects proceed through scoping, and they are included in the workplan. The associated triggers include tree strike potential, PSPS, and Ingress/Egress risk. It also includes triggers driven by feasibility, identified removals and making connections between already OH hardened facilities. | Nathan Poon | 2025-04-15 | 2025-04-18 | 2025-04-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_003.zip | 6 | No | 8 | Grid Design, Operations, and Maintenance | 8.2.1 | Covered Conductor Installation
16 | 105 | OEIS | 003 | OEIS_003 | 4 | No | OEIS_003_Q4 | Regarding Effectiveness Analysis Regarding PG&E’s response to TURN’s Data Request 2 Question 5, Attachment 1: a. In its response to the data request, PG&E states that “Company-initiated outages, including PSPS outages, outages of unknown cause, as well as outages on existing underground assets are not applicable to this study.” i. Why does PG&E not include outages on existing underground assets? ii. 561 events are shown as “N/A” that are not under the GRC drivers of “Unknown” or “Utility Work / Operation.” A. Are these 561 events limited to existing underground assets or PSPS outages? B. If not, why are these listed as “N/A” for determining effectiveness? b. PG&E’s response included a spreadsheet with a tab accounting for risk scores and associated wildfire intensity and outcome when calculating for PSPS effectiveness. Provide a detailed description of how PG&E accounts for wildfire intensity and outcome when determining the effectiveness of reducing wildfire risk for mitigations. | a. i. The purpose of the study is to analyze the effectiveness of an array of mitigations in comparison to existing bare overhead conductors within the HFTD. Replacement of existing underground assets, which are mostly located in urban settings, are not the focus of system hardening mitigations. ii. PG&E notes 581 outage combinations (not 561) with effectiveness values of “N/A” that are not explicitly listed as “Unknown” or “Utility Work / Operation” drivers. WMP-Discovery 2026-2028_DR_OEIS_003-Q004 Page 2 A. These 581 outage combinations are categorized as follows: (i) 221 were underground outages (ii) 121 have insufficient information to assess mitigation effectiveness (iii) 100 were caused by environmental/external forces of either wildfires or ice/snow storms and outage cause could not be properly associated with any specific equipment failure (iv) 65 were substation outages (v) 74 were caused by 3rd party/metering equipment B. PG&E excluded these outage events from consideration in the analysis as they are not directly applicable to system hardening mitigations. b. In determining the effectiveness of reducing wildfire risk for mitigation, PG&E accounts for wildfire intensity and outcomes by differentiating (a) the type of fire – categorized as destructive, large, or small – and (b) whether the fire would occur during Red Flag Warning (RFW) conditions. This distinction is important because both the environmental conditions and the potential severity of a fire influence the overall risk. The likelihood of a destructive fire is significantly higher under RFW conditions compared to non-RFW conditions, and the fire type further informs the expected impact. When assessing the effectiveness of wildfire risk mitigations, especially Public Safety Power Shutoffs (PSPS), PG&E factors in this elevated risk by specifying effectiveness in reducing likelihood of ignition by different outcomes (which is combination of fire severity and RFW flag) if applicable. This allows PG&E to also account for the fact that the PSPS is not likely to be activated in non-RFW conditions by assuming zero effectiveness for those non-RFW outcomes. Also, it can account for the fact that not all RFW conditions result in a PSPS activation. The table in “WMP-Discovery2026-2028_DR_TURN_002-Q005Atch01.xlsx”, tab “RiskScore_Attribute”, shows the assumptions used for the PSPS effectiveness by RFW condition and fire outcome (destructive, large, and small). When determining overall effectiveness of the program, the outcome-level effectiveness is multiplied with the outcome-level risk scores over all outcomes to derive risk reduction and then the risk reduction is divided by the total risk score to derive the overall effectiveness. | Nathan Poon | 2025-04-15 | 2025-04-23 | 2025-04-23 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_003.zip | 0 | No | 6 | Wildfire Mitigation Strategy Development | 6.1.3-1 | Activity Selection Process
16 | 106 | OEIS | 003 | OEIS_003 | 5 | No | OEIS_003_Q5 | Regarding Risk Reduction a. Provide a copy of Table 6-4: Summary of Risk Reduction for Top Risk Circuits (PG&E’s 2026-2028 Base WMP, p. 163) that has the overall utility risk scores for all top risk circuits broken out by year without including the expected risk reduction from EPSS. | Please see “WMP-Discovery2026-2028_DR_OEIS_003-Q005Atch01.xlsx” for the Summary of Risk Reduction without the expected risk reduction from EPSS. | Nathan Poon | 2025-04-15 | 2025-04-23 | 2025-04-23 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_003.zip | 1 | No | 6 | Wildfire Mitigation Strategy Development | 6.2.1 | Projected Risk Reduction on Highest-Risk Circuits Over the Three-Year WMP Cycle
16 | 107 | OEIS | 003 | OEIS_003 | 6 | No | OEIS_003_Q6 | Regarding Pole Clearing Table 9-2 shows an Activity Timeline Target of 365 days for Pole Clearing Program (VM-02). a. Explain how this timeline target allows PG&E to maintain compliance with PRC 4292. b. Provide documentation of an example of past conditions that required PG&E to use a substantial portion of the 365-day Activity Timeline Target to complete pole clearing work. | a. To maintain compliance with PRC 4292, PG&E performs year-round pole clearing activities. Per TD-7112S Section 7.1 “Annual Planning”, pole clearing personnel must perform inspection and work at each designated location to ensure compliance with PRC § 4292. Pole clearing activities occur during four phases which are conducted annually: • Inspection: October of the Prior Year – March • Initial Clear: January – April • Maintenance 1 (M1) Except for “lnspect No Work” locations, all documented Subject Poles are targeted for clearance: May – August • Maintenance 2 (M2) Except for “lnspect No Work” locations, all documented Subject Poles are targeted for clearance: September – December WMP-Discovery 2026-2028_DR_OEIS_003-Q006 Page 2 b. Please refer to response in ‘A’ for the four phases established and utilized annually by the Pole Clearing program that covers the 365-day timeline needed to ensure we remain compliant with the PRC 4292 guidelines for our VM-02 initiative. These phases allow us to address constraints, regrowth and accumulation of debris that may impact pole clearance. | Nathan Poon | 2025-04-15 | 2025-04-18 | 2025-04-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_003.zip | 0 | No | 9 | Vegetation Management & Inspections | 9.4 | Pole Clearing
16 | 108 | OEIS | 003 | OEIS_003 | 7 | No | OEIS_003_Q7 | Regarding Substation Inspection Timelines Table 9-2 shows an Activity Timeline Target of 274 days for Substation Inspections - Distribution (VM-05), Substation Inspections - Transmission (VM-06), and Substation Inspections - Power Generation (VM-07). a. Explain how this timeline target allows PG&E to maintain compliance with PRC 4291. b. Provide documentation of an example of past conditions that required PG&E to use a substantial portion of the 274-day Activity Timeline Target to complete pole clearing work. | a. PG&E targets completion of inspections under VM-05, VM-06, and VM-07 no later than the end of Q3 so that any related mitigation work required to maintain compliance with PRC 4291 can be completed by the end of the year. b. PG&E understands this request to refer to VM-05, VM-06, and VM-07, which perform defensible space inspections for substations and powerhouses, not pole clearing work. Please see “WMP-Discovery2026-2028_DR_OEIS_003- Q007Atch01.jpg” for an example of an external factor which may temporarily delay our ability to perform defensible space inspections at substations and powerhouses. In general, those factors may include, but are not limited to, physical conditions, weather conditions, active wildfire, and other safety considerations. This example is a road access issue with a snowed-in road that temporarily delayed access to the substation. | Nathan Poon | 2025-04-15 | 2025-04-18 | 2025-04-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_003.zip | 1 | No | 8 | Grid Design, Operations, and Maintenance | 8.3.15 | Substation Inspections
16 | 109 | SPD | 002 | SPD_002 | 1 | No | SPD_002_Q1 | Every Friday by noon, provide SPD with copies of any data requests PG&E received from the Office of Energy Infrastructure Safety (Energy Safety) or any other party within the previous seven days. Include any attachments, appendices or datasets in the native format that were submitted to PG&E with the data requests. | PG&E objects to this request on the grounds that continuing discovery obligations are not permitted under California law. Biles v. Exxon Mobil Corp., 124 Cal.App.4th 1315, 1328 (2004); Code Civ. Proc. § 2030.060(g). Notwithstanding and without waiving this objection, PG&E responds as follows. Discovery provided to Energy Safety and other requesting parties is publicly posted and available on PG&E’s website at Community Wildfire Safety Program. The native format version (Excel) of PG&E’s WMP DR Summary is updated on our website each Thursday. We will provide confidential versions of any confidential responses and/or attachments submitted to Energy Safety or any other party every Friday. We will do our best to provide such responses by noon each Friday, or as soon as is reasonably possible. | Eddie Schmitt | 2025-04-16 | 2025-04-18 | 2025-04-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_002.zip | 0 | No | N/A | N/A | N/A | N/A
16 | 110 | SPD | 002 | SPD_002 | 2 | No | SPD_002_Q2 | Every Friday by noon, provide SPD with any responses to data requests that PG&E sent to Energy Safety or any other party within the previous seven days. Include any attachments, appendices or datasets in the native format that were sent to Energy Safety or any other party with the data requests. | PG&E objects to this request on the grounds that continuing discovery obligations are not permitted under California law. Biles v. Exxon Mobil Corp., 124 Cal.App.4th 1315, 1328 (2004); Code Civ. Proc. § 2030.060(g). Notwithstanding and without waiving this objection, PG&E responds as follows. Discovery provided to Energy Safety and other requesting parties is publicly posted and available on PG&E’s website at Community Wildfire Safety Program. The native format version (Excel) of PG&E’s WMP DR Summary is updated on our website each Thursday. We will provide confidential versions of any confidential responses and/or attachments submitted to Energy Safety or any other party every Friday. We will do our best to provide such responses by noon each Friday, or as soon as is reasonably possible. | Eddie Schmitt | 2025-04-16 | 2025-04-18 | 2025-04-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_002.zip | 0 | No | N/A | N/A | N/A | N/A
16 | 111 | SPD | 002 | SPD_002 | 3 | No | SPD_002_Q3 | Every Friday by noon, provide SPD with the updated native format version (i.e. Excel) of the PG&E WMP DR Summary1 that is submitted weekly to the Energy Safety docket. | PG&E objects to this request on the grounds that continuing discovery obligations are not permitted under California law. Biles v. Exxon Mobil Corp., 124 Cal.App.4th 1315, 1328 (2004); Code Civ. Proc. § 2030.060(g). Notwithstanding and without waiving this objection, PG&E responds as follows. Discovery provided to Energy Safety and other requesting parties is publicly posted and available on PG&E’s website at Community Wildfire Safety Program. The native format version (Excel) of PG&E’s WMP DR Summary is updated on our website each Thursday. We will provide confidential versions of any confidential responses and/or attachments submitted to Energy Safety or any other party every Friday. We will do our best to provide such responses by noon each Friday, or as soon as is reasonably possible. | Eddie Schmitt | 2025-04-16 | 2025-04-18 | 2025-04-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_002.zip | 0 | No | N/A | N/A | N/A | N/A
16 | 112 | TURN | 003 | TURN_003 | 1 | No | TURN_003_Q1 | Please provide PG&E’s wildfire risk model (WDRM v4) assumptions and results in Excel. Please provide all outputs and assumptions available. At minimum, this should include Circuit Protection Zone (CPZ) name, likelihood, consequence, total risk score, and number of overhead miles of each CPZ in separate columns. In addition, please include the following: a. Indicate which CPZs are prioritized for undergrounding from 2026-2028 (please indicate the year work will start and finish). b. Indicate which CPZs are prioritized for overhead hardening from 2026-2028 (please indicate the year work will start and finish). c. For each CPZ prioritized for undergrounding or overhead hardening from 2026-2028, please provide the CBR for both overhead hardening and undergrounding, regardless of which mitigation was selected. i. Please provide all calculations and assumptions for the CBRs in Excel. ii. Please explain whether project-specific unit costs are used for this calculation. iii. Please explain whether project-specific mitigation effectiveness is used for this calculation. | Please see attachment “WMP-Discovery2026-2028_DR_TURN_003-Q001Atch01.xlsx,” which is PG&E’s wildfire risk model (WDRM v4) output. Please refer to sections 3, 4, and 5 in the Wildfire Distribution Risk Model v4 documentation for the requested assumptions, available at https://www.pge.com/en/outages-andsafety/safety/community-wildfire-safetyprogram.html?WT.mc_id=Vanity_wildfiremitigationplan#accordion-99016a73ab-item4366b98ea7. a. Please see attachment “WMP-Discovery2026-2028_DR_TURN_003- Q001Atch02CONF.xlsx,” which is the 2026-2028 workplan for GH-04 Undergrounding, which includes system hardening undergrounding and community rebuild work. A few notes about the data provided: • The projects planned to be completed in 2026 have been scoped and are broken out into subprojects (i.e. jobs by order). • The projects planned to be completed in 2027 and 2028 have been identified starting with the highest ignition risk ranked circuit segments that have not yet been scoped and divided into subprojects. • Project plans for 2027 and 2028 are subject to change once scoping takes place. • For the year that the work will start and end, we have indicated the construction start year, recognizing planning and scoping takes place in advance of construction start. • If a subproject is included but 0.0 miles are captured in the workplan, this is due to rounding. • For the risk score, we have replaced the previously provided mean risk score with the estimated wildfire risk reduction. Mean risk was a data point at the circuit segment level, and estimated wildfire risk provides the total estimated risk reduction for each subproject including all mitigation types across all years on the subproject. • While PG&E is providing the estimated v4 risk score, this data is based on the assumption that circuit segment names and configurations stay consistent from one model to the next, which is not always the case. Circuit segment names and configurations can change over time. • Approximately six miles are listed as TBD and represent miles from 2025 that we expect to be carried over into the 2026 workplan, pending construction schedules in the final months of the year. b. Please see attachment “WMP-Discovery2026-2028_DR_TURN_003- Q001Atch03CONF.xlsx,” which is the 2026-2028 workplan for GH-12 Covered Conductor, which includes overhead hardening and line removal work. A few notes about the data provided: • The projects planned to be completed in 2026 have been scoped and are broken into subprojects (i.e. jobs by order). • The projects planned to be completed in 2027 and 2028 have been identified starting with the highest ignition risk ranked circuit segments that have not yet been scoped and divided into subprojects. Some fields for these projects include “N/A” in a given cell if that information is not available yet. • Project plans for 2027 and 2028 are subject to change once scoping takes place. • For the year that the work will start and end, we have indicated the construction start year, recognizing planning and scoping takes place in advance of construction start. • For the risk score, we have replaced the previously provided mean risk score with the estimated wildfire risk reduction. Mean risk was a data point at the circuit segment level, and estimated wildfire risk provides the total estimated risk reduction for each subproject including all mitigation types across all years on the subproject. • While PG&E is providing the estimated v4 risk score, this data is based on the assumption that circuit segment names and configurations stay consistent from one model to the next, which is not always the case. Circuit segment names and configurations can change over time. c. CBRs are not available for circuit segments prioritized for undergrounding or overhead hardening from 2026-2028. PG&E did not calculate CBRs for projects planned to be completed in 2026 in alignment with the Risk-Based Decision-Making Framework Phase 2 Decision that did not require project-level CBR calculations.1 PG&E will use elements of the WBCA to perform a cost-benefit analysis during scoping for 2027 and 2028, however that analysis had not been initiated at the time of our 2026-2028 WMP submission. Preliminary CBRs have been estimated, as seen in previous DR response (OEIS-P-WMP_2025-PG&E-003, Q03f) which included some of the analysis conducted to-date. The CBR data presented in PG&E’s 2026-2028 WMP are presented at the programmatic level. Those CBR calculations are consistent with those that will be proposed in the GRC and are generated using the Enterprise Risk Models. Additionally, these cost-benefit-ratios account for the entire benefit life of the projects and present value of revenue requirements (PVRR). For more detail, please see section 6.2.1.2 Cost Benefit Scores of PG&E WMP Plan R0 2026-2028. i. Not applicable. ii. Not applicable. iii. Not applicable. | Reina Yanagiba | 2025-04-17 | 2025-04-29 | 2025-04-29 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-TURN_003.zip | 3 | No | 5 | Risk Methodology & Assessment | 5.4 | Summary of Risk Models
16 | 113 | TURN | 003 | TURN_003 | 2 | No | TURN_003_Q2 | Please provide an estimate, by activity, of total annual cost and risk reduction, for all wildfire mitigation activities from 2019-2024 (recorded). Please explain whether this risk reduction has been incorporated into PG&E’s baseline risk. Please provide all supporting calculations and data in Excel. | PG&E did not start estimating wildfire risk reduction until 2023 with the 2023-2025 WMP cycle. The risk reduction calculations require temporal and spatial alignment across a model version, circuit segments, and work plans. Currently, historical circuit segment datasets have only been prepared with a WDRM model release (earliest full-territory dataset is with WDRM v3). The earliest year that we have a WDRM model, respective circuit segment data, and associated work plans is in 2023. Risk reduction results for 2023 and 2024 can be found in each year’s respective Annual Report on Compliance (ARC), and total annual recorded costs can be found in PG&E’s Non-Spatial Quarterly Data Report (QDR) Table 11. Both are published either on PG&E’s Community Wildfire Safety Program website1 or on the Office of Energy Infrastructure Safety’s (Energy Safety) e-filing system. Please note that PG&E is unable to provide the supporting calculations and data regarding annual risk reduction without substantial time and effort. PG&E would be happy to meet with TURN to discuss this issue further. Additionally, please note that PG&E’s QDR financial data is entered from our financial records and there are no supporting calculations or data to provide. Please find the referenced public filings at the links below: 2019-2022: Financial data for the 2019-2022 period is located in Table 11 of our 2022 Q4 QDR, which is available at the following link: d in Table 11 of our 2022 Q4 QDR, which is available at the following link: 1 See https://www.pge.com/en/outages-and-safety/safety/community-wildfire-safetyprogram.html#accordion-99016a73ab-item-c788794778. WMP-Discovery 2026-2028_DR_TURN_003-Q002 Page 2 • https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparednessand-support/PGE-2022-Q4-QDR-r1-20230301.zip. 2023: Financial data for 2023 is located in Table 11 of our 2023 Q4 QDR, and risk reduction data is located in our 2023 ARC. These documents are available at the following links: • https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparednessand-support/q4-2023-qdr.xlsx (see Table 11). • https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparednessand-support/04-02-2024-pge-2023-arc-attachments.zip (see attachments, Table 3). 2024: Financial data for 2024 is located in Table 11 of our 2024 Q4 QDR, and risk reduction data is located in our 2024 ARC. These documents are available at the following links: • https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparednessand-support/q4-2024-qdr.xlsx (see Table 11). • https://efiling.energysafety.ca.gov/Search.aspx?docket=2024-EC_ARC (see PGE_2024-ARC_Table_3-Targets).2 | Reina Yanagiba | 2025-04-17 | 2025-04-25 | 2025-04-25 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-TURN_003.zip | 0 | No | 5 | Risk Methodology & Assessment | 5.4 | Summary of Risk Models
16 | 114 | TURN | 003 | TURN_003 | 3 | No | TURN_003_Q3 | In Excel, please provide the outputs of the PSPS and EPSS risk models, respectively, with the same circuit/CPZ identifiers as provided in the previous questions. At minimum, this should include Circuit Protection Zone (CPZ) name, likelihood, consequence, total risk score, and number of overhead miles of each CPZ in separate columns. In addition, please indicate which CPZs are targeted for PSPS and EPSS mitigations from 2026-2028. Please indicate what the mitigation is. | Please see attachment “WMP-Discovery2026-2028_DR_TURN_003-Q003Atch01.xlsx” for the outputs of the PSPS and EPSS risk models. This data was created as of April 24, 2025. There are currently six circuit segments planned for construction in 2026-2027 with the purpose of reducing PSPS risk: 1. TEJON 1102732836; 2. DUNBAR 1103534; 3. PLACERVILLE 21067522; 4. EL DORADO PH 2101CB; 5. CORNING 110253184; and 6. PIT NO 3 21011482. The above projects were selected based on a historic lookback of PSPS data, not the outputs of the PSPS risk model provided, as these projects were selected prior to the development of the PSPS risk model. Please note that scoping for 2027 and 2028 jobs is still in progress and additional PSPS mitigation work may be added to the workplan once scoping is complete. All planned system hardening and undergrounding work will support reliability mitigations for EPSS. | Reina Yanagiba | 2025-04-17 | 2025-04-25 | 2025-04-25 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-TURN_003.zip | 1 | No | 5 | Risk Methodology & Assessment | 5.4 | Summary of Risk Models
16 | 115 | TURN | 003 | TURN_003 | 4 | No | TURN_003_Q4 | Section 6.1.3.1, Page 129, states “PG&E estimates that the average cost for primary distribution undergrounding is approximately $3.0 million per mile and the average cost to install covered conductor is approximately $1.0 million per mile.” a. Please provide support for these estimates, including any calculations in Excel. b. Are both estimates in dollars per overhead mile? If not, please provide PG&E’s estimates in dollars per overhead mile and provide the underlying assumptions/calculations to show how the estimates were formed. c. For all undergrounding projects completed from 2018 to 2024, please provide, on a project-level basis, the following information in Excel with supporting data and calculations: i. the dates of the project (start and finish), ii. total cost, iii. number of overhead miles removed, iv. purpose of the project, including whether it was related to wildfire risk or in an urban setting, v. overhead miles removed, vi. overhead miles undergrounded, and vii. cost per overhead mile. d. For all overhead hardening projects completed from 2018 to 2024, please provide, on a project-level basis, the following information in Excel with supporting data and calculations: i. the dates of the project (start and finish), ii. total cost, iii. number of overhead miles covered/hardened, iv. purpose of the project, including whether it was related to wildfire risk, and v. cost per overhead mile. e. Please provide assumed unit costs ($/overhead mile) for covered conductor and undergrounding, separately, in 2026, 2027, and 2028, respectively. Please provide all supporting data and calculations for these estimates. | a. Please see worksheet Subparts A and B in attachment “WMP-Discovery2026- 2028_DR_TURN_003-Q004Atch01.xlsx,” which shows the calculations for PG&E’s estimated average unit costs for undergrounding and overhead hardening, which is based on the historical performance. Unit cost is calculated based on the total costs-since-inception (multi-year) of the subprojects that are 100% complete each year. For Undergrounding, we have included the unit costs for system hardening undergrounding (excluding Community Rebuild undergrounding). Note, unit cost is not calculated by dividing the total program cost spent in one year by the total miles completed in one year because this would inaccurately include the readiness costs for future work that is not yet complete and post-construction costs for previously completed projects. b. Please see column F in worksheet Subparts A and B in attachment “WMPDiscovery2026-2028_DR_TURN_003-Q004Atch01.xlsx.” The undergrounding unit cost at approximately $3.0 million per mile is the cost for undergrounding installed, not per overhead mile removed. The overhead miles removed and replaced by UG reflect actual overhead miles removed on undergrounding subprojects, where data is available; otherwise, where data is not yet available, we used the adopted1 overhead to undergrounding conversion factor of 1 mile of overhead to 1.25 miles of undergrounding. c. Please see worksheet Subpart C in attachment “WMP-Discovery2026- 2028_DR_TURN_003-Q004Atch01.xlsx.” • Note, the question asks for “iii. number of overhead miles removed” and “v. overhead miles removed”. We are assuming those are the same request and have included one column for overhead miles removed. Additionally, because the unit cost is associated with undergrounding miles installed, we have included the undergrounding miles installed as an additional column in this dataset. • Note, the start date reflects when the project was first identified for scoping; the end date reflects when the project was fully constructed. • Year complete signifies the year a subproject completes the final Fire Risk Safety Audit, which may differ from the end date year, which reflects when the project was fully constructed. • Some subprojects have a negative total cost. This can be due to credits from joint trenching with a PG&E gas project or cost corrections related to spoils management or other project construction costs. . Please see worksheet Subpart D in attachment “WMP-Discovery2026- 2028_DR_TURN_003-Q004Atch01.xlsx.” • Note, the start date reflects when the project was first identified for scoping; the end date reflects when the project was fully constructed. • Year complete signifies the year a subproject completes the final Fire Risk Safety Audit, which may differ from the end date year, which reflects when the project was fully constructed. • Some subprojects have a negative total cost. This can be due to credits from joint trenching with a PG&E gas project or cost corrections related to spoils management or other project construction costs. e. The below table includes the undergrounded estimated unit costs (million $ per mile) expressed both as undergrounding miles installed and as cost per overhead mile for overhead and undergrounding in 2026-2028, and includes overhead estimated unit costs (million $ per mile). Mitigation 2026 2027 2028 Undergrounding Installed Per Mile $2.8M/mi $3.0M/mi $3.0M/mi Undergrounding Expressed as Overhead Removed Per Mile $3.5M/mi. $3.8M/mi. $3.8M/mi. Overhead $1.1M/mi $1.0M/mi $1.0M/mi • The 2026 undergrounding unit cost assumes the unit cost as presented in the 2023 GRC (Conclusion of Law 79) of approximately $2.8M per mile. The underground unit cost forecast in 2027-2028 assumes the four-year average unit cost in the 2023-2026 GRC period of $2.97M/mi (as adopted by Conclusion of Law 79) plus $55k per mile for transformers. The 2027-2028 unit cost forecast assumes that escalation is absorbed. Our project-level cost forecasts for 2026-2028 are still being developed to incorporate our latest efficiency actions. • For underground unit cost targets from 2026 to 2028, undergrounding expressed as Overhead removed per mile is calculated using the overhead to undergrounding conversion rate of 1 to 1.25 miles, respectively. • For Overhead Hardening unit cost, we leveraged historical unit cost data2, and included assumptions for declining unit costs based on program efficiencies from 2026 to 2027. From 2027 to 2028 the increase in unit cost is due to escalation (using 2027 GRC standard rates) plus $20,000 per mile for transformers. • From 2027 onwards, the unit cost for Overhead Hardening and Undergrounding includes the cost for transformers. The costs for transformers are currently centralized across PG&E, but they will be allocated to individual programs starting in 2027. The transformer allocation costs are calculated using historic data to determine an average cost for the number of transformers used per mile and the types of transformers used. See attachment WMP-Discovery2026-2028_DR_TURN_003-Q004Atch01, Subpart E tab, which outlines the transformer costs. | Reina Yanagiba | 2025-04-17 | 2025-04-25 | 2025-04-25 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-TURN_003.zip | 1 | No | 6 | Wildfire Mitigation Strategy Development | 6.1.3.1 | Identifying and Evaluating Activities
16 | 116 | TURN | 003 | TURN_003 | 5 | No | TURN_003_Q5 | Section 6.1.3.1, page 129, states “Covered conductor can generally be installed more quickly and costs less than undergrounding, but it does not protect against tree strike risk or fully address the reliability risk. Given increasing instances of extreme weather and volatility, the stress on vegetation around our assets is only expected to get worse. Therefore, undergrounding, where feasible, is the best alternative where tree strike risk is high.” In Excel, please provide the time (days) from project initiation to project completion for all covered conductor and undergrounding projects, separately from 2018. Please include all supporting data/calculations. a. Please explain and quantify whether the fact that covered conductor can be installed more quickly than undergrounding has been incorporated into PG&E’s risk modeling and cost-benefit ratios. If yes, please explain and provide an illustrative calculation. If no, please explain why not. | Please see worksheets, “Summary” and “Duration Analysis” in attachment “WMPDiscovery2026-2028_DR_TURN_003-Q005Atch01.xlsx”. The attachment includes the days the subproject was initiated (i.e., start of project scoping) to the end of the project (i.e., construction complete) for both undergrounding and overhead subprojects between 2018 and 2024, split between base system hardening and fire rebuild work. A few notes about the subproject data provided in the “Duration Analysis”: • Construction End Date represents the date construction was complete. If that date was not available, we provided the date the project was energized. • As identified in Column I, projects were removed from the analysis if there were data anomalies based on: o Negative duration (i.e., construction end date showed prior to the project start) o Missing dates (i.e., data was not captured at the time) o Data discrepancies (i.e., where we know that construction end date is inaccurate based on when the project was energized and passed the Fire Risk Safety Audit) • Projects with less than 14-day durations were removed from the average calculation in the “summary” worksheet based on subject matter expertise of project durations of fire rebuild work. a. Please see the discussion of cumulative risk in PG&E’s 2025 WMP Update (PG&E's 2025 Wildfire Mitigation Plan Update R2, p. 57-58). While speed of initiative construction has not explicitly been incorporated into PG&E’s risk modeling and cost-benefit ratios, PG&E manages its suite of wildfire mitigation initiatives to minimize cumulative risk exposure and does account for the time value of risk based on the useful life of the asset. Specifically, PG&E uses an integrated mitigation strategy to manage wildfire risk across our system while we implement more permanent risk reduction strategies like undergrounding and other system hardening work. PG&E’s objective when scheduling mitigation initiatives is to ensure that we have built sufficient risk mitigation into the system to minimize risk exposure as we develop our long-term system hardening programs. PG&E achieves this through a suite of Comprehensive Monitoring and Data Collection programs designed to provide insight into the changing environmental hazards around our assets and the condition of our equipment (e.g., the Hazard Awareness and Warning Center and wildfire cameras) and Operational Mitigations (e.g., EPSS and vegetation management) that provide on-going risk reduction and influence how we manage the environment around the electric grid. As we contemplate the alternative solutions for permanent risk reduction, PG&E considers the time value of risk and cumulative risk reduction. In addition, by factoring in the lifetime benefits and costs of various possible mitigations, the WBCA tool will account for the cumulative risk exposure of PG&E’s mitigation initiative portfolio. PG&E recognizes that overhead hardening can be installed more quickly than an undergrounding solution. However, as depicted in Figure ACI-PG&E-23-05-1 below, the initial, permanent risk reduction achieved from quicker installation of an overhead mitigation does not compensate for the greater total, more permanent risk reduction achieved over the lifetime of an underground solution. This figure shows an illustrative comparison of the cumulative wildfire risk reduction for overhead hardening and undergrounding over the life of the assets. This demonstrates that, for the possible portfolio miles in our 10 Year Plan workplan, the risk exposure (i.e., residual risk) is greater if the miles were overhead hardened rather than if those miles were undergrounded. Thus, while overhead hardening can scale quickly and thus reduce some wildfire risk sooner than undergrounding, it is a less effective solution in the long term because of the higher residual risk left by overhead assets. As depicted, overhead hardening can be completed at a rate of approximately three times that of undergrounding but while those miles may be mitigated quicker in the overhead hardening scenario, doing so would achieve approximately 21% less risk reduction, which is then compounded as cumulative exposure every year for the life of the asset. | Reina Yanagiba | 2025-04-17 | 2025-04-29 | 2025-04-29 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-TURN_003.zip | 1 | No | 6 | Wildfire Mitigation Strategy Development | 6.1.3.1 | Identifying and Evaluating Activities
16 | 117 | TURN | 003 | TURN_003 | 6 | No | TURN_003_Q6 | Please provide recorded and forecast red flag warning circuit mile days from 2020-2028 on an annual basis in PG&E’s HFTD. Please define “forecast” as the assumption for PG&E’s risk modeling, if available. | Please see “WMP-Discovery2026-2028_DR_TURN_003-Q006Atch01.xlsx” for recorded red flag warning circuit mile days from 2013 – 4/15/2025 broken out by year. PG&E does not include "forecasts" for red flag warning circuit mile days in its risk modeling. | Reina Yanagiba | 2025-04-17 | 2025-04-22 | 2025-04-22 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-TURN_003.zip | 1 | No | 5 | Risk Methodology & Assessment | 5.3 | Risk Scenarios
16 | 118 | TURN | 003 | TURN_003 | 7 | No | TURN_003_Q7 | In one Excel workbook, please provide the annual number of ignitions started by PG&E equipment from 2018-2024 in PG&E’s HFTD (or indicating which are in the HFTD) with supporting data and calculations. Please also include: a. The date of each ignition. b. Driver of the ignition (cause). c. Structures destroyed. d. Fatalities and/or injuries. e. Whether there was red flag warning at the time of the ignition. f. Any other information readily available and used by PG&E in its risk modeling. | Please see “WMP-Discovery2026-2028_DR_TURN_003-Q007Atch01.xlsx” for the requested information. | Reina Yanagiba | 2025-04-17 | 2025-04-22 | 2025-04-22 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-TURN_003.zip | 1 | No | 5 | Risk Methodology & Assessment | 5.2.2.1 | Likelihood of Risk Event
16 | 119 | TURN | 003 | TURN_003 | 8 | No | TURN_003_Q8 | Regarding the mitigation effectiveness of covered conductor: a. Please provide all studies known to PG&E that calculate the mitigation effectiveness of covered conductor using data rather than SME estimates. b. From 2020-2024 on an annual basis, please provide the number of faults per mile on lines with covered conductor versus lines without covered conductor in PG&E’s HFTD. c. From 2020-2024 on an annual basis, please provide the number of ignitions per mile on lines with covered conductor versus lines without covered conductor in PG&E’s HFTD. | a. Please see PG&E’s response titled "RAMP-2024_DR_TURN_006-Q004," provided to TURN on September 10, 2024, for further details regarding an example analysis of observed covered conductor mitigation effectiveness and details around why PG&E does not support application of this analysis. These reasons include: • Much of PG&E’s covered conductor installation has been in wildfire rebuild areas in the absence of significant vegetation growth • Limited degradation of assets due to recent installation • Targeted installation in areas areas of low tree strike risk in alignment with PG&E’s decision tree Please note that this analysis was based on only two known reportable ignitions on covered conductor. PG&E has subsequently identified an additional ignition related to covered conductor which occurred in 2023. PG&E is also partnering with UCLA on an observed effectiveness study for covered conductor but has not yet operationalized this methodology due to the limited data availability in addition to the key points reflected above. b. Please see the table below for the volume of faults per mile of PG&E’s overhead conductor in HFTDs. Please note that PG&E interprets “faults” as outages, which are drawn from the Integrated Logging Information System (“ILIS”). ILIS records do not capture the type of wire, so PG&E is not able to differentiate between covered or bare conductor. As a result, PG&E is providing the outages per HFTD miles of conductor c. Please see the table below for the volume of ignitions per mile of PG&E’s overhead covered vs non-covered conductor in the HFTD/HFRA. Please note that we do not track ignitions by covered conductor line mile. However, we estimate the following values for ignitions per line mile of overhead covered conductor in the HFTD, based on the number of such ignitions in each year and the line miles of overhead covered conductor in the HFTD/HFRA at the close of each year. As such, the values may not be fully representative, as covered conductor line milage may have changed throughout the year. | Reina Yanagiba | 2025-04-17 | 2025-04-22 | 2025-04-22 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-TURN_003.zip | 0 | No | 8 | Grid Design, Operations, and Maintenance | 8.2.1 | Covered Conductor Installation
16 | 120 | TURN | 003 | TURN_003 | 9 | No | TURN_003_Q9 | For each project proposed from 2026-2028 for UG and CC, please provide the following in Excel with all supporting data, calculations, and assumptions: a. Cost-benefit ratio of UG and CC for each project, indicating which mitigation was chosen (UG or CC). i. This should include unit costs assumed for each mitigation. ii. This should include number of overhead miles of each project. iii. This should include total risk and risk reduction from the project. | a. As discussed in response to TURN-003, Q01, PG&E did not calculate CBRs for projects planned to be completed in 2026 and analysis was in line with the RiskBased Decision-Making Framework, Phase 2 Decision,1 that did not require project level CBR calculations. PG&E will use elements of the WBCA to perform a cost-benefit analysis during scoping for work to be completed in 2027 and 2028; however, that analysis had not been initiated at the time of our 2026-2028 WMP submission. Preliminary CBRs have been estimated, as seen in previous DR response (OEIS-003, Q03f), which included some of the analysis conducted to date. The CBR data presented in PG&E’s 2026-2028 WMP are presented at the programmatic level. Those CBR calculations are consistent with those that will be proposed in the GRC and are generated using the Enterprise Risk Models. These models include our wildfire and reliability bowties and evaluate the risk reduction benefits based on location of work and program effectiveness. Additionally, these cost-benefit-ratios account for the entire benefit life of the projects and present value 1 D.22-12-017 WMP-Discovery 2026-2028_DR_TURN_003-Q009 Page 2 of revenue requirements (PVRR). For more detail, please see section 6.2.1.2 Cost Benefit Scores of PG&E WMP Plan R0 2026-2028. i. N/A ii. N/A iii. N/A | Reina Yanagiba | 2025-04-17 | 2025-04-22 | 2025-04-22 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-TURN_003.zip | 0 | No | 8 | Grid Design, Operations, and Maintenance | 8.2.1 | Covered Conductor Installation
16 | 121 | TURN | 003 | TURN_003 | 10 | No | TURN_003_Q10 | Section 8.2.1, Page 195 states “In any given location, overhead hardening does not reduce the impact from PSPS events, but is expected to reduce EPSS-caused outages.” Please explain why PG&E has not instituted higher wind thresholds for overhead hardened circuits, which reduce the probability of PSPS, as Southern California Edison has done. Please support the response with all analyses and data regarding purported differences between SCE’s and PG&E’s service territory or overhead hardening programs. | PG&E does not use verbatim yes/no wind speed thresholds for PSPS execution. Please see the Section 5 of the WMP. Instead, PG&E uses a risk-informed methodology that combines the probability of an ignition (Ignition Probability Weather model [IPW]) with the probability of rapid and intense fire (Fire Potential Index Model [FPI]). The IPW model is informed by a machine learning outage model called OPW, that is trained on if outages were observed or not, hourly, across our entire network combined with meteorological, topographic and asset information. Thus, any benefits from covered conductor, vegetation management, or any other program that would reduce the probability of an outage is reflected in the actual grid performance in localized areas which the model is trained on. Thus, we do not apply wind speed threshold modifiers for grid hardening, vegetation management or any other program that could reduce outage or ignition risk outside the OPW model, nor do we have to make any assumptions or estimates about the effectiveness of each program to then apply across all circuits. To ensure our model is reflective of the latest grid performance, we annually update the model with the last year of performance versus weather data and utilize an exponential function (which was calibrated to provide the best performance), that weights the most current years most heavily in final model predictions. | Reina Yanagiba | 2025-04-17 | 2025-04-22 | 2025-04-22 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-TURN_003.zip | 0 | No | 8 | Grid Design, Operations, and Maintenance | 8.2.1 | Covered Conductor Installation
16 | 122 | OEIS | 004 | OEIS_004 | 1 | No | OEIS_004_Q1 | Regarding Third-Party Model Review a. Page 12 of the E3 review states that "the main driver for consequence is the FPI score which further reduces the impacts of the in-depth simulations coming from the Technosylva analysis." On page 15 of the Wildfire Consequence Model V4 document, two criteria are mentioned for the predictive destructive criteria, one for FPI-R and one for the Technosylva simulations. i. Out of the simulated weather history, how many days from 2012 through 2022 have met each criterion in the highest risk circuits? ii. Provide a detailed description of how FPI-R compared to predictive destructive criteria influence the consequence score. | a. i. The criteria for “predicted destructive” are computed for every 100x100m raster pixel containing grid infrastructure. We confirmed that this request is for the tabulation of days where at least one grid pixel containing part of each high risk circuit segment meets each of the “predicted destructive” criteria. There are 90 high risk circuit segments in Tables 5-5 and 6-1 of the 2026 WMP, so those were used for the analysis, the results of which are tabulated in “WMP-Discovery2026-2028_DR_OEIS_004-Q001Atch01.xlsx” in the worksheet titled “Predicted destructive days.” ii. The predicted destructive criteria draw on two different sources of information: • The predictions of the FPI model, an empirical model trained on historical fire outcomes conditional on weather and environmental covariates, via its 1-5 R-score (4+ are classified as predicted destructive conditions). The Rscore expresses how likely a destructive fire is, given the input conditions, based on model fit using outcomes of historical fires. These values are available and adopted by the v4 wildfire consequence model for all 183 WMP-Discovery 2026-2028_DR_TURN_001-Q001 Page 2 days of the June-November wildfire season annually from 2012 through 2022. • The flame length and rate of spread produced by wildfire simulations run by Technosylva across all grid locations. These metrics describe how intense and fast-moving simulated fires were, with thresholds for predicted destructive set to include all the values output by simulations of historically destructive fires. For the v4 model, and in keeping with past practice, the simulations were performed across the set of worst wildfire conditions days identified by PG&E’s meteorology team from the weather data for each year. There are approximately 30 such days with simulation data available each year, with data spanning 2012 through 2020 available at the time of v4 model finalization. Either source of data is sufficient to label conditions as “predicted destructive”. The FPI model is probabilistic and tuned to past outcomes, while the flame length and rate of spread come from deterministic physicsbased simulations. The simulations tend to respond to finer scale fuel and topographical information. | Nathan Poon | 2025-04-18 | 2025-04-29 | 2025-04-29 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_004.zip | 1 | No | 5 | Risk Methodology & Assessment | 5.4 | Summary of Risk Models
16 | 123 | OEIS | 004 | OEIS_004 | 2 | No | OEIS_004_Q2 | Regarding the Wildfire Transmission Risk Model a. On page 32 of PG&E’s Wildfire Transmission Risk Model Documentation v4, PG&E references the "T-Line Asset Data Quality Improvement - Critical Components, Guide to Conservative Assumptions," dated January 14, 2020. Provide a copy of this document. | Please see “WMP-Discovery2026-2028_DR_OEIS_004-Q002Atch01.pdf” for the requested information. | Nathan Poon | 2025-04-18 | 2025-04-23 | 2025-04-23 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_004.zip | 1 | No | 5 | Risk Methodology & Assessment | 5.4 | Summary of Risk Models
16 | 124 | OEIS | 004 | OEIS_004 | 3 | No | OEIS_004_Q3 | Regarding the Wildfire Consequence Model a. On pages 18-22 of PG&E’s Wildfire Consequence Model V4 document, PG&E provides an example of the suppression model applied to the Dixie Fire. i. Provide an expanded version of the example to show the calculation of the number of structures in Table 11 (p. 22). This includes providing the data on Existing Structures, live fuel moisture (LFM), and wind speed (WS), as noted on page 20, which are not reported in the example. ii. How did PG&E select the 300 m height for wind speed (p. 20)? What impact does that have on the statistical performance of the model? iii. On page 14 of the Wildfire Consequence Model V4 document, Table 4 lists the dry wind conditions criteria. Are these sampled at a weather station height, at 300 m above surface (like the consequence model wind speeds), or some other reference height? b. On page 26 of PG&E’s Wildfire Consequence Model V4 document, PG&E presents the equation for calculating the fractional fatalities based on AFN and WS fatalities. i. What are the units of the AFN value? ii. How does this correspond to the AFN deciles shown in Figure 13 and Table 13 (p. 26)? c. On page 36 of the Wildfire Consequence Model V4 document, Table 20 provides example consequence training data. Provide this table as an Excel spreadsheet with one row per historical fire used in consequence training. Provide the following columns in addition to the columns shown in Table 20: (1) TDI level (2) AFN decile level (3) Wind speed in mph at 300 m (4) Live fuel moisture (5) Daily average wind speed for Dry Wind Conditions (if this is different from wind speed in mph at 300 m) (6) 10-hr dry fuel moisture (7) Relative humidity (8) FPI-R (9) Flame Length (10) Rate of Spread (11) Whether the fire is within the HFRA (12) Whether the fire was used for training or validation d. In PG&E’s response to Energy Safety’s Data Request 1 Question 25, PG&E states that “the overall WF Consequence model v4 with egress and suppression incorporated was validated against historical fire outcomes.” i. Provide a list of all fires used to validate WFC v4. ii. Provide a detailed description of the validation PG&E performed, and include the results of the validation for each historical fire outcome evaluated. | a. i. The calculations in the 4.1.3.2 and 4.1.3.3 sections of documentation were included as an illustrative example not drawn from the modeling performed for the v4 release. A worksheet named “Dixie example” in “WMP-Discovery2026- 2028_DR_OEIS_004-Q003Atch01.xlsx” reproduces the calculations for the equivalent of Table 11, starting with model coefficients and covariate values for the Dixie Fire, but based on coefficients aligned with the released v4 model. The model only requires the known count of structures burned under actual conditions, not existing structures, because other values are computed as a ratio relative to the actual values. ii. Modeling wind in weather models, like the one used to create the historical gridded weather data available at PG&E, requires accounting for air flows in 3 dimensions. Wind is particularly impacted by the boundary layer at ground level and various obstructions like topographical features, buildings, trees, etc. In PG&E’s weather model (which is a standard model in the meteorological community), wind is modeled at various heights above the ground, with values at 10m influenced by surface roughness and topographic obstructions and values at 300m typically capturing more “free flow” conditions. In other words, there is much more spatial/local variability in the data closer to the surface due to surface characteristics. The higher altitude winds are also (very generally speaking) the drivers of wind gusts at the ground level. When considering the conditions that would correlate with the expected outcome of a hypothetical wildfire, we opted to use speeds at 300m to avoid overly local influences at the point of origin that may not be representative of the prevailing conditions in the surrounding area. We did not perform a formal sensitivity analysis on other potential covariates in the same role. WMP-Discovery 2026-2028_DR_OEIS_004-Q003 Page 3 iii. The Dry Wind criteria are based on 10m wind speed. Dry Wind is predictive of outcomes due to its role in drying fuels (as well as propelling fires) and humidity is modeled at 2m above the ground, so the 10m wind speed is closer to the fuels and the humidity values. b. i. AFN is the fraction of the population (from 0.0 to 1.0) with “access and functional needs.” ii. The table below summarizes the relationship between AFN fractions and the decile cuts. Please see “WMP-Discovery2026-2028_DR_OEIS_004- Q003Atch01.xlsx” at the sheet titled “AFN Deciles.” c. i. The requested data is provided in the “Fire data” sheet of “WMPDiscovery2026-2028_DR_OEIS_004-Q003Atch01.xlsx”. Note that requested columns for 10-hr dry fuel moisture and relative humidity were not available in the source data used in the consequence modeling (as they are not direct inputs into the modeling based on that data). The acreage field uses CAL FIRE data when available and VIIRS estimates otherwise. Also, all fires were used for modeling and validation, so no label is needed for those. d. i. The validation was performed on the full set of consequence predictions drawing on all fires found in the “Fire data” sheet of “WMP-Discovery2026- 2028_DR_OEIS_004-Q003Atch01.xlsx”. ii. The validation started with checks that intended calculations were correct, that data sets did not contain duplicates of fires or erroneous data, that VIIRS fire detections from space were properly matched with CAL FIRE tracked outcome data, that the VIIRS ignition locations (estimated from space) were close to known points of origin. WMP-Discovery 2026-2028_DR_OEIS_004-Q003 Page 4 The primary test of fidelity with historical outcomes was the ROC-like figures presented in Figure 5 of the v4 consequence model documentation, which provides the results of historical fire validation. Those figures rank order historical fires by the consequence at their point of origin (consequence values are not specific to the days those fire occurred on) and then calculate and plot the cumulative sum of relevant fire outcomes, including the cumulative counts of fires that burned greater than 300 acres, destroyed structures, and caused fatalities. Those figures and related discussion are based on all fires in the data set with non-zero CAL FIRE values for each of those tabulated consequence metrics. The steepness of the curves confirms that the model is discriminating between locations with low and high historical fire outcomes well. The validation of the egress and suppression modeling was done by mapping, looking at rank order shifts, and looking at rank-ordered consequence buy-down curves, all of which are provided and discussed in section 4.4 of the v4 consequence document | Nathan Poon | 2025-04-18 | 2025-04-29 | 2025-04-29 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_004.zip | 1 | No | 5 | Risk Methodology & Assessment | 5.4 | Summary of Risk Models
16 | 125 | OEIS | 004 | OEIS_004 | 4 | No | OEIS_004_Q4 | Regarding Table 6-4: Summary of Risk Reduction for Top Risk Circuits In response to Energy Safety’s Data Request 2, Question 17, PG&E provided an updated version of Table 6-4 including the associated mileage for various hardening planned and percentage that has already been hardened. a. Compared to the targets provided in Table 8-1 (PG&E’s 2026-2028 Base WMP, p. 175) and estimates in PG&E’s response to Energy Safety’s Data Request 1 Question 17 (labeled “WMP” in the table), to the summation of the mileages provided in Attachment 1 (labeled “DR” in the table), Energy Safety found the following: 2026 2027 2028 Hardening Type WMP DR Δ WMP DR Δ WMP DR Δ Undergrounding 370 16.94 353 307 203.68 103 400 278.10 122 Covered Conductor 294 78.23 216 190 91.23 99 190 115.70 74 Line Removal 24 3.04 21 10 4.5 5.5 10 8.70 1.3 Provide the following mileages associated for each hardening mitigation type missing from the mileages provided in the updated Table 6-4 (labeled “Δ” in the table): i. Work prescribed in lower 80% of risk due to prioritization based on WDRM v3 ii. Work prescribed in lower 80% of risk due to other qualifying threshold, broken out by threshold (i.e. ingress/egress issue, tree strike potential, PSPS risk) iii. Work not yet planned for specific circuit segments iv. Other not listed above, including associated reasoning b. Provide the following risk score values, similar to those provided within Table 6-4 for the top 20% riskiest circuit segments: i. The total initial overall utility risk for PG&E’s service territory ii. The total overall utility risk for each year (2026-2028) for PG&E’s service territory including EPSS iii. The total overall utility risk for each year (2026-2028) for PG&E’s service territory excluding EPSS c. The following circuit segments listed within Table 6-4 do not have any type of hardening planned from 2026 to 2028 and have undergone either no hardening or minimal hardening (less than one percent). For each circuit, explain why no hardening is planned currently, and whether hardening is planned past 2028: 1) MIDDLETOWN 1101644756 2) CALPINE 1144CB 3) MARIPOSA 210237282 4) BIG BEND 1101CB 5) CALAVERAS CEMENT 1101502 6) CORNING 110185152 7) CURTIS 17048140 8) COLUMBIA HILL 1101CB 9) TEMPLETON 2113A12 10) PINE GROVE 11026080 11) MARTELL 110191216 12) MOLINO 1102318 13) HIGHLANDS 1103520 14) COARSEGOLD 210410110 15) MARIPOSA 210237288 16) FROGTOWN 170113412 17) CORNING 11021622 18) DIAMOND SPRINGS 110676088 19) BRUNSWICK 11021010 20) APPLE HILL 110413512 21) DIAMOND SPRINGS 11057722 22) APPLE HILL 2102836878 23) APPLE HILL 21028372 24) LOS OSITOS 21037014 25) MARIPOSA 2101439030 26) HOPLAND 11014626 27) PINE GROVE 1102269286 28) ORO FINO 110239154 29) WEST POINT 110234416 30) CEDAR CREEK 1101CB 31) SISQUOC 1102M52 32) TEMPLETON 2113641367 33) FORESTHILL 1102359542 34) BRUNSWICK 110651486 35) SHINGLE SPRINGS 210913322 36) PINE GROVE 11013170 37) APPLE HILL 21021532 38) WILDWOOD 1101384582 39) PERRY 110179696 | a. Please see attachment “WMP-Discovery2026-2028_DR_OEIS_004- Q004Atch01.xlsx” for missing from the mileages provided in the updated Table 6-4 (labeled “Δ” in the table). A few notes about this data: • In answering this question, we identified a calculation error in our response to OEIS_002_Question 17 regarding the miles pulled in for each circuit segment. That response under counted the miles planned on circuit segments in Table 6-4 based on the formula that was used to pull in the data (i.e., the miles originally included only captured the miles for one subproject associated with the circuit segment, not all subprojects planned on that circuit segment). We have corrected the miles in the table and provided as a supplemental response to this data request as attachment “CORRECTED_WMP-Discovery2026- 2028_DR_OEIS_002-Q017Atch01.xlsx”. • The 2027-2028 portfolio is currently planned at the circuit segment-level based on the top 20% risk ranked circuit segments of the WDRM v4 model. The work is not yet scoped and broken into subprojects. Columns ii-iv cannot be filled out. • i. The values in Table 6-4 were generated using WDRM v4. We assume the intent of this subpart was to provide work prescribed in lower 80% of total overall utility risk due to prioritization based on WDRM v4, not v3, and have responded accordingly. PG&E welcomes clarification if there was different intent about scope of this request. • ii. Work in this category represents projects that are Fire Rebuild, PSPS, or “Other”, which includes projects that were initiated under other programs outside of the System Hardening program which is funded by MAT codes 08W and 3UG, such as Work Requested by Others (WRO), capacity, and Rule 20 B and C programs. • iv. Work in this category represents Community Rebuild miles. This work occurs in HFTD and non-HFTD areas following fire incidents. b. Table 6-4 of the WMP includes the top 20% of total overall utility risk for circuit segments within the HFTD/HFRA. These tables are generated from WDRM v4. The responses included in subparts i-iii are for the entire service territory. Additionally, subparts i and ii will be included in the same attachment as Overall Utility Risk is comprised of Wildfire Risk + EPSS and PSPS risk. As described in subpart (a) above, the portfolio was selected based on the top 20% wildfire risk ranked circuit segments, not accounting for the outage program risk as included in Overall Utility Risk. i. Please see attachment “WMP-Discovery2026-2028_DR_OEIS_004- Q004Atch02.xlsx” for total overall utility risk by year. ii. Please see attachment “WMP-Discovery2026-2028_DR_OEIS_004- Q004Atch02.xlsx” for total overall utility risk by year. iii. Please see attachment “WMP-Discovery2026-2028_DR_OEIS_004- Q004Atch03.xlsx” for total overall utility risk by year, excluding EPSS risk. c. Projects in previous year’s workplans, including up to 2026, were prioritized by earlier wildfire distribution risk models and drivers (e.g., WDRM V2 or V3, PSPS lookback, etc.) and were not targeted based on WDRM V4 or total Overall Utility Risk. For work in 2027 and 2028, the primary driver for targeting circuit protection zones (CPZs) for a hardening mitigation is based on the WDRM v4 risk ranked circuit segments based on density of risk per mile (not total risk on the circuit segment). There are various reasons why these CPZs are not in our current hardening workplans, including the below reason codes: A. They are Privately Owned Lines (POL). PG&E does not harden privately owned lines. B. High total overall utility risk. The program does not select and prioritize CPZs for system hardening work based on total risk or overall utility risk. C. Work was completed or planned under a previous model’s CPZ name. Our workplan will continue to evolve as we scope work and validate more granular data associated with the CPZs, such as Privately Owned Lines. For example, we recently initiated scoping on MIDDLETOWN 1101644756 and BIG BEND 1101CB, which were originally identified as Privately Owned Lines, but through the scoping process we validated these are not Privately Owned Lines. These two CPZs are tagged with an asterisk (*). | Nathan Poon | 2025-04-18 | 2025-04-29 | 2025-04-29 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_004.zip | 3 | No | 6 | Wildfire Mitigation Strategy Development | 6.2.1.3 | Projected Risk Reduction on Highest-Risk Circuits Over the Three-Year WMP Cycle
17 | 126 | MGRA | 004 | MGRA_004 | 1 | No | MGRA_004_Q1 | PSPS event damage event reports obtained from post-event patrols, including cause and estimated time of damage for all quarters of 2024. Cause was not included in the provided data. a. Also please extend the request to cover four quarters or 2023 as well. | In the PSPS Event Damage Feature Class schema previously provided in “WMP-Discovery2026-2028_DR_MGRA_002-Q002Supp01Atch02.xlsx”, there is a field titled DamageDateTime. This field should be used to relate records in the Feature Class to the PSPS Event Conductor Damage and PSPS Event Support Structure Damage Detail tables, which are provided in “WMP-Discovery2026-2028_DR_MGRA_002-Q002Supp01Atch01.xlsx” and “WMP-Discovery2026-2028_DR_MGRA_002-Q002Supp01Atch03.xlsx”, respectively. Please note that DamageDateTime is not a native field within the detail table schemas as defined by Energy Safety; rather, it is a linking field that exists in the Feature Class and must be used to establish the relationship with the associated detail tables. Regarding the Cause field, PG&E considers this information to be confidential and applies a consistent policy of nondisclosure, regardless of the feature class. Data submitted in quarterly reports to the Office of Energy Infrastructure Safety may be part of ongoing investigations and analyses and is protected under applicable legal privileges, including the attorney-client privilege (e.g., Evid. Code § 954; Code Civ. Proc. § 2018.010, et seq.). These reports capture a snapshot in time and are not subsequently updated to reflect findings from later investigations. Moreover, PG&E exercises caution in disclosing information that could be exploited by malicious actors to replicate adverse events. Cause data may include sensitive details about physical infrastructure, cybersecurity systems, or critical energy assets, all of which are protected under federal and state laws (see 18 C.F.R. § 388.113; Gov. Code § 6254(k), (ab); 6 U.S.C. § 131; 6 C.F.R. § 29.2). For example, if a specific piece of equipment was identified as causing a large-scale outage, that knowledge could potentially be used to target similar equipment elsewhere. WMP-Discovery 2026-2028_DR_MRGA_001-Q001 Page 2 PG&E is resharing data provided to MGRA from last year’s MGRA request where MGRA requested PSPS Event Damages. As noted last year, there were two PSPS events during the year and both took place during Q3 2023. Please see “WMP-Discovery2026-2028_DR_MGRA_004-Q001Atch01.xlsx”. Data is extracted from our quarterly GDB files, which contain a high volume of records in each submission (anywhere between 10-16 million records). The feature classes and related tables included in the submission are not static and change each quarter. Similarly, the Office of Energy Infrastructure Safety (Energy Safety) often revises their Data Guidelines introducing and removing various data points, consolidating feature classes, changing field names, updating definitions, and renaming fields. Such revisions make it difficult to create a consistent, non-confidential GDB version. Energy Safety does not have a non-confidential GDB submission. The submission they receive is confidential. To create a non-confidential file for MGRA, PG&E attempts to apply logic to the feature classes to strike known confidential fields, data types, or entire datasets across the entire GDB. However, confidential data could still have been provided inadvertently. PG&E respectfully requests that MGRA use this data for internal purposes only and restrict access to a need-to-know basis. Additionally, the interconnected aspect of feature classes data and geospatial representation of the data creates complexities in identifying the confidentiality of individual records and introduces additional risk for error. As such, PG&E may designate additional data points confidential at a later point in time should more confidentiality considerations become known. PG&E would be happy to provide the requested confidential information under the terms of a non-disclosure agreement to protect the confidentiality of the information. | Joseph Mitchell | 2025-04-21 | 2025-04-23 | 2025-04-23 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-MGRA_004.zip | 1 | No | N/A | GIS | N/A | N/A
17 | 127 | MGRA | 004 | MGRA_004 | 2 | No | MGRA_004_Q2 | Unplanned outage data, including cause. Cause was not provided in the initial response | PG&E considers the BasicCause field information to be confidential. Data submitted in quarterly reports to the Office of Energy Infrastructure and Safety may be part of ongoing investigations and analyses and is protected under applicable legal privileges, including the attorney-client privilege (e.g., Evid. Code § 954; Code Civ. Proc. § 2018.010, et seq.). These reports capture a snapshot in time and are not subsequently updated to reflect findings from later investigations. Moreover, PG&E exercises caution in disclosing information that could be exploited by malicious actors to replicate adverse events. Cause data may include sensitive details about physical infrastructure, cybersecurity systems, or critical energy assets, all of which are protected under federal and state laws (see 18 C.F.R. § 388.113; Gov. Code § 6254(k), (ab); 6 U.S.C. § 131; 6 C.F.R. § 29.2). For example, if a specific piece of equipment were identified as causing a large-scale outage, that knowledge could potentially be used to target similar equipment elsewhere. Data is extracted from our quarterly GDB files, which contain a high volume of records in each submission (anywhere between 10-16 million records). The feature classes and related tables included in the submission are not static and change each quarter. Similarly, the Office of Energy Infrastructure Safety (Energy Safety) often revises their Data Guidelines introducing and removing various data points, consolidating feature classes, changing field names, updating definitions, and renaming fields. Such revisions make it difficult to create a consistent, non-confidential GDB version. Energy Safety does not have a non-confidential GDB submission. The submission they receive is confidential. To create a non-confidential file for MGRA, PG&E attempts to apply logic to the feature classes to strike known confidential fields, data types, or entire datasets across the entire GDB. However, confidential data could still have been provided inadvertently. PG&E respectfully requests that MGRA use this data for internal purposes only and restrict access to a need-to-know basis. WMP-Discovery 2026-2028_DR_MRGA_001-Q002 Page 2 Additionally, the interconnected aspect of feature classes data and geospatial representation of the data creates complexities in identifying the confidentiality of individual records and introduces additional risk for error. As such, PG&E may designate additional data points confidential at a later point in time should more confidentiality considerations become known. PG&E would be happy to provide the requested confidential information under the terms of a non-disclosure agreement to protect the confidentiality of the information. | Joseph Mitchell | 2025-04-21 | 2025-04-23 | 2025-04-23 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-MGRA_004.zip | 0 | No | N/A | GIS | N/A | N/A
17 | 128 | MGRA | 004 | MGRA_004 | 3 | No | MGRA_004_Q3 | Wire down data for all four quarters of 2023 and 2024. This was missing cause and event time. | PG&E considers the Cause fields to be confidential. While this field was inadvertently shared with MGRA in the past, PG&E maintains that such information is protected. Data included in quarterly reports submitted to the Office of Energy Infrastructure and Safety may be part of ongoing investigations and analyses and is protected under applicable legal privileges, including the attorney-client privilege (e.g., Evid. Code § 954; Code Civ. Proc. § 2018.010, et seq.). These reports capture a snapshot in time and are not subsequently updated to reflect findings from later investigations. Moreover, PG&E exercises caution in disclosing information that could be exploited by malicious actors to replicate adverse events. Cause data may include sensitive details about physical infrastructure, cybersecurity systems, or critical energy assets, all of which are protected under federal and state laws (see 18 C.F.R. § 388.113; Gov. Code § 6254(k), (ab); 6 U.S.C. § 131; 6 C.F.R. § 29.2). For example, if a specific piece of equipment were identified as causing a large-scale outage, that knowledge could potentially be used to target similar equipment elsewhere. Data is extracted from our quarterly GDB files, which contain a high volume of records in each submission (anywhere between 10-16 million records). The feature classes and related tables included in the submission are not static and change each quarter. Similarly, the Office of Energy Infrastructure Safety (Energy Safety) often revises their Data Guidelines introducing and removing various data points, consolidating feature classes, changing field names, updating definitions, and renaming fields. Such revisions make it difficult to create a consistent, non-confidential GDB version. Energy Safety does not have a non-confidential GDB submission. The submission they receive is confidential. To create a non-confidential file for MGRA, PG&E attempts to apply logic to the feature classes to strike known confidential fields, data types, or entire datasets across the entire GDB. However, confidential data could still have been provided inadvertently. WMP-Discovery 2026-2028_DR_MRGA_001-Q003 Page 2 PG&E respectfully requests that MGRA use this data for internal purposes only and restrict access to a need-to-know basis. Additionally, the interconnected aspect of feature classes data and geospatial representation of the data creates complexities in identifying the confidentiality of individual records and introduces additional risk for error. As such, PG&E may designate additional data points confidential at a later point in time should more confidentiality considerations become known. PG&E would be happy to provide the additional confidential information under the terms of a non-disclosure agreement to protect the confidentiality of the information. Lastly, please note that Event Time is not a field included in the schema template provided by the Office of Energy Infrastructure and Safety. | Joseph Mitchell | 2025-04-21 | 2025-04-23 | 2025-04-23 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-MGRA_004.zip | 0 | No | N/A | GIS | N/A | N/A
17 | 129 | OEIS | 005 | OEIS_005 | 1 | No | OEIS_005_Q1 | Regarding distribution detailed inspections and findings a. Provide the following data related to detailed distribution inspections: i. The number of detailed distribution inspections performed in the HFRA/HFTD 2020, 2021, 2022, 2023 and 2024. ii. The number of level 1 work orders that resulted from distribution detailed inspections in the HFRA/HFTD in 2020, 2021, 2022, 2023 and 2024. iii. The number of level 1 work orders originating from distribution detailed inspections closed in the HFRA/HFTD 2020, 2021, 2022, 2023, and 2024. iv. The number of level 2 work orders that resulted from distribution detailed inspections in the HFRA/HFTD in 2020, 2021, 2022, 2023 and 2024. v. The number of level 2 work orders originating from distribution detailed inspections closed in the HFRA/HFTD in 2020, 2021, 2022, 2023 and 2024. | Please see the table below for the requested information. Notes 1 and 2 below help explain the data in the table. Metric Number Metric Name 2020 2021 2022 2023 2024 Q01(a)(i) Total Inspections Performed in HFTD-HFRA 352,057 449,645 395,968 235,265 10,197 Q01(a)(ii) HFTD-HFRA Level 1 Work Orders 1,200 855 896 1,138 23 WMP-Discovery 2026-2028_DR_TURN_005-Q001 Page 2 Metric Number Metric Name 2020 2021 2022 2023 2024 resulting from inspection Q01(a)(iii) Level 1 Work orders closed 1,015 999 894 1,324 69 Q01(a)(iv) HFTD-HFRA Level 2 Work Orders resulting from inspection 56,596 64,275 80,654 72,294 1,240 Q01(a)(v) Level 2 Work orders closed 12,478 35,722 35,135 41,231 52,633 1. PG&E understands “detailed distribution inspections” to mean “detailed overhead inspections” conducted by ground inspectors in accordance with General Order (GO) 165. Therefore, Wildfire Safety Inspection Program (WSIP) and aerial inspections or notifications are not included in these tables. Please note that PG&E also conducted 216,796 aerial inspections in HFTD/HFRA in 2024. These aerial inspections were not conducted in accordance with GO 165 and therefore are not included in the table above. 2. Level 1 closure dates reflect the date at which an A priority notification was completely repaired. Please note that the date of complete repair may be different than the date of temporary repair. | Nathan Poon | 2025-04-22 | 2025-04-25 | 2025-04-25 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_005.zip | 0 | No | 8 | Grid Design, Operations, and Maintenance | 8.3.8.1 | Distribution - Detailed Inspection Program - Overview
17 | 130 | OEIS | 005 | OEIS_005 | 2 | No | OEIS_005_Q2 | Regarding Distribution Hazard Patrol Page 364 of PG&E’s 2026-2028 Base WMP states Distribution Hazard Patrol inspections are “conducted in high-risk areas based on a risk-prioritized approach.” Figure PG&E-9.2.2.1-1, reproduced below, shows the Consequence and Severity ratings by mile for HFTD and HRFA locations in the scope of the Distribution Hazard Patrol. a. The sum of miles shaded as Routine/Hazard/Remote Sensing (red) and Routine/Hazard (yellow) is 10,994 miles. The target for Distribution Hazard Patrol listed on Table 9-2 is 10,000 miles. i. If Distribution Hazard Patrol will cover all miles with Consequence or Wildfire Risk ratings at or above “Medium,” explain the discrepancy between Figure PG&E-9.2.2.1-1 and Table 9-2. ii. If Distribution Hazard Patrol will not cover all miles with Consequence or Wildfire Risk ratings at or above “Medium”: 1. Provide the criteria used to select the subset of “Medium” or higher rated miles for inspection. 2. Explain how wildfire risk is managed for “Medium” or higher rated miles that are not targeted for Distribution Hazard Patrol inspection. | a. i. The Distribution Hazard Patrol target of 10,000 miles in Table 9-2 reflects our original target mileage. The final target mileage will change as we continue to assess and develop our plans for the Hazard Patrol program for 2026. We expect the final mileage inspected to cover the miles with Consequence or Wildfire Risk at or above “Medium” shown in Figure PG&E9.2.2.1-1 barring any external factors. ii. N/A, Distribution plans to cover all miles with Consequence or Wildfire Risk Rating at or above "Medium. | Nathan Poon | 2025-04-22 | 2025-04-25 | 2025-04-25 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_005.zip | 0 | No | 9 | Vegetation Management & Inspections | 9.2.2 | Hazard Patrol - Distribution
17 | 131 | OEIS | 005 | OEIS_005 | 3 | No | OEIS_005_Q3 | Regarding Distribution Routine Patrol Page 363 of PG&E’s 2026-2028 Base WMP states “In 2025, PG&E will use data gathered from proven remote sensing technologies to analyze how distribution inspections could be further evolved to incorporate remote sensing techniques.” Further, page 363 states “PG&E may consider utilizing remote sensing in lieu of ground-based inspections on electrical spans that typically have no trees around the lines, to provide customers with a more cost-effective solution.” a. Does the target for Distribution Routine Patrol listed on Table 9-2 (VM-16) include circuit miles that will be inspected using only remote sensing? i. If yes, A. Provide the number of circuit miles in each quarterly target that will be inspected using only remote sensing. B. Provide any procedures governing remote sensing inspections of vegetation along distribution lines. | a. No, the target for Distribution Routine Patrol listed in Table 9-2 does not currently include circuit miles to be inspected using remote sensing. PG&E is analyzing remote sensing detection and identification data in 2025 to determine whether some number of miles may be inspected using only remote sensing in the future. The use of remote sensing is expected to be applied where there are typically no trees in proximity to the line. i. N/A | Nathan Poon | 2025-04-22 | 2025-04-25 | 2025-04-25 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_005.zip | 0 | No | 9 | Vegetation Management and Inspections | 9.2.1 | Routine Patrol - Distribution
17 | 132 | OEIS | 005 | OEIS_005 | 4 | No | OEIS_005_Q4 | Regarding Quality Assurance and Quality Control Unit Equivalents On page 410 of its 2026-2028 Base WMP, PG&E lists “Inspections” as the “Population/Sample Unit” for VM-08D&T, and VM-22D&T. In the “Population Size” and “Sample Size” columns, PG&E then indicates the unit is either “miles” or “spans.” This makes it unclear whether the “Population/Sample Unit” is “inspections” or another factor. a. Clarify what the sample unit is for quality control and quality assurance audits by describing: i. The randomization software PG&E uses to draw samples randomly. ii. The unit that the randomization software draws from the population to create a sample (i.e., describe if PG&E selects from a population of inspections, miles, spans, or another population). iii. Any procedural differences when auditing randomly sampled areas for VM-08D, VM-08T, VM-22D, and VM-22T. For example, procedural differences might include selecting an inspection location randomly and then auditing an entire mile in a specific direction or selecting an inspection location randomly and then auditing the span where the inspection occurred. A. In the table below, for VM-08D&T and VM-22D&T, convert all values in “Population Size” and “Sample Size” columns from “miles” to actual or estimated numbers of inspections by completing the “2026, 2027, or 2028 Inspection Population Size” and “2026, 2027, and 2028 Inspection Sample Size” columns. Initiative/ Activity Being Audited Population/ Sample Unit Mile or Span Population Size 2026, 2027, or 2028 Inspection Population Size Mile or Span Sample Size 2026, 2027, or 2028 Inspection Sample Size Vegetation Management Quality Assurance Distribution Routine (VM-08D) Inspections 25,748 miles ______ inspections 500 miles ______ inspections Vegetation Management Quality Assurance Transmission Routine (VM-08T) Inspections 5,624 miles ______ inspections 200 miles ______ inspections Vegetation Management Quality Control Distribution Routine (VM-22D) Inspections 551,643 spans ______ inspections 80,000 spans ______ inspections Vegetation Management Quality Control Transmission Routine (VM-22T) Inspections 5,624 miles ______ inspections 13,500 spans ______ inspections | a. i. QC (VM-22D, -22P and -22T): Excel will be used as our randomization tool in 2026-28 for both distribution and transmission. QA (VM-08D): Distribution uses ArcGIS Pro to randomize sample locations with Python scripts. QA (VM-08T): Transmission is randomized by excel. ii. QC (VM-22D): The randomization software selects from a population of Work Packets consisting of spans inspected. QC (VM-22T): The randomization software selects from a population of Work Packets consisting of a group of individual inspected locations. Transmission locations may consist of individual spans, portions of spans or multiple spans inspected, depending on the system of record, as described in greater detail in OEIS_001, Q001. QC (VM-22P): The randomization software selects from a population of poles inspected and/or cleared. QA (VM-08D): The randomization software selects from a population of Distribution units calculated based off overhead circuit mileage. QA (VM-08T): The randomization software selects from a population of Transmission units calculated based on transmission structures. iii. QC (VM-22D and VM-22T): QC verifies Distribution and Transmission span/locations inspected to affirm procedural scope met. QA (VM-08D and VM-08T): QA uses randomized starting locations of overhead (OH) line segments for distribution and structures for transmission, independent of whether there is an existing inspection record. Distribution target mileage for each audit segment is 0.5-line mile segments. Transmission designates 1-mile line segments for transmission audits that originate from the transmission structure sample selected. QA WMP-Discovery 2026-2028_DR_TURN_005-Q004 Page 3 then assesses whether VM Operations is compliant with applicable regulatory requirements. A. QC (VM-22D): The estimated ‘inspection’ unit is determined by a span (pole to pole) inspected by the VMI in One VM. QC (VM-22T): The QC Transmission Routine inspection record may not be a full span (pole to pole). We estimated 5.5 inspection records per mile for the Inspection Population, and 1 inspection record per span for the Inspection Sample Size. Please see the table below. QA (VM-08D and VM-08T): The estimated ‘inspection’ unit is measured in miles. Distribution Routine, there are two inspection audit segments for each mile; and for transmission routine, it is one inspection audit segment per mile that originates from the transmission structure selected in the audit sample. Initiative/ Activity Being Audited Population/ Sample Unit Mile or Span Population Size 2026, 2027, or 2028 Inspection Population Size Mile or Span Sample Size 2026, 2027, or 2028 Inspection Sample Size Vegetation Management Quality Assurance Distribution Routine (VM-08D) Inspections 25,748 miles 51,496 inspections 500 miles 1,000 inspections Vegetation Management Quality Assurance Transmission Routine (VM-08T) Inspections 5,624 miles 5,624 inspections 200 miles 200 inspections Vegetation Management Quality Control Distribution Routine (VM-22D) Inspections 551,643 spans 551,643 inspections 80,000 spans 80,000 inspections Vegetation Management Quality Control Transmission Routine (VM-22T) Inspections 5,624 miles 30,932 inspections 13,500 spans 13,500 inspections | Nathan Poon | 2025-04-22 | 2025-04-25 | 2025-04-25 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_005.zip | 0 | No | 9 | Vegetation Management and Inspections | 9.11 | Quality Assurance and Quality Control
17 | 133 | OEIS | 005 | OEIS_005 | 5 | No | OEIS_005_Q5 | Regarding Quality Control – Pole Clearing (VM-22P) Target On page 7 of its 2026-2028 Base WMP Substantive Errata, PG&E lists 99,933 poles as the population size for its annual Quality Control of Pole Clearing activity. On page 356 of its 2026-2028 Base WMP, PG&E targets 70,000 poles annually for its Pole Clearing (VM-02) activity. a. Explain why PG&E’s audit population for quality control is 29,933 more poles than it targets for its pole clearing activity each year. | We apologize; the discrepancy is due to an inadvertent error. The correct population number of Quality Control Pole Clearing poles in HFRA and HFTD to be sampled from is 70,000 annually, not 99,933 poles. | Nathan Poon | 2025-04-22 | 2025-04-25 | 2025-04-25 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_005.zip | 0 | No | 9 | Vegetation Management and Inspections | 9.4 | Pole Clearing
17 | 134 | OEIS | 005 | OEIS_005 | 6 | No | OEIS_005_Q6 | Regarding Risk Model Validation a. In PG&E's response to data request OEIS-P-WMP_2025-PG&E-002, Question 14, PG&E states that "the team dedicated extra validation to confirm the results by evaluating against historical fire outcomes" and that the validation "resulted in the removal of several lightning fires from the consequence training data set". i. Provide the date this validation was completed, including, at minimum the month(s) and year. ii. Provide the date the model was updated as a result of this validation, including, at minimum the month(s) and year. b. On p. 29 of E3’s Review of PG&E’s Wildfire Risk Model Version 4, E3 includes a recommendation on “establishing an expanded model roadmap for model direction.” i. Has PG&E established this roadmap for its planned risk model changes? A. If so, provide this roadmap. B. If not, provide a timeline for establishing this roadmap. C. If PG&E does not intend to establish this roadmap, explain why it does not intend to do so. c. Provide completion dates and/or expected completion dates (at a minimum, quarter and year) for each of the elements discussed in PG&E’s response to data request OEIS-P-WMP_2025-PG&E-002, Question 18. | a. i. The validation task was executed during the months of August to December 2023 as part of the Wildfire Consequence v4 model development and validation. WMP-Discovery 2026-2028_DR_TURN_005-Q006 Page 2 ii. The model update became the official Wildfire Consequence v4 release after WRGSC approval in Jan 2024. There was no release other than the official release in Jan 2024. b. The table on page 31 of the E3 review provides more context on this recommendation’s history, which originated in a review of WDRM v3 and includes an update from July 2023. The original line item calls for the RaDA team to “continue to provide a schedule of data and model updates”. The current published version of the RaDA roadmap is included on page 25 of the “Wildfire Distribution Risk Model Version 4 Documentation”, which has been previously provided as an attachment with the 2026-2028 WMP. The roadmap, Figure 24, was produced in August 2024. Note that WDRM/WTRM development scope and delivery is synchronized to the WMP delivery cycle. The WDRM/WTRM roadmap will be refined as new needs for the next versions are identified and approved for development. | Nathan Poon | 2025-04-22 | 2025-05-01 | 2025-05-01 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_005.zip | 0 | No | 5 | Risk Methodology & Assessment | 5.4 | Summary of Risk Models
17 | 135 | OEIS | 005 | OEIS_005 | 7 | No | OEIS_005_Q7 | Regarding Reliability and Public Safety Risk Models In response to data request OEIS-P-WMP_2025-PG&E-002, Question 13 regarding Reliability and Public Safety risk models, PG&E states that the components — Insulator Contamination Update, Public Safety Risk Model v2, Reliability Risk Model v1, Public Safety Consequence v2, and Reliability Consequence V1 — "are not currently used for wildfire mitigation planning" and are "developed to help inform internal investment planning primarily outside of HFTD." a. Provide documentation that captures and discusses these components, as previously requested in data request OEIS-P-WMP_2025-PG&E-002, Question 13. If such documentation does not exist, explain how these models are documented. b. Describe why these components are separate for wildfire mitigation planning, and what models do capture reliability and public safety components for the sake of wildfire mitigation planning. c. Provide a list of projects informed by these models within the HFTD, if applicable. | a. • Insulator contamination: This model is still in development for WTRM. There is no formal documentation yet. • Public Safety ▪ Public Safety Consequence v2: Public safety consequence estimates the presence of people near PG&E equipment. For example, if there were a wire down event, this would estimate the number of people who would be present in the area, on average. The focus of the model is on urban areas with larger populations. Documentation is in progress and not finalized. ▪ Public Safety Risk Model v2: No official model has been released. The proposed model would combine likelihood of failure values with the Public Safety Consequence v2 values. • Reliability Risk ▪ Reliability Consequence V1: The Reliability consequence model estimates customer reliability impacts from an unplanned outage. ▪ Reliability Risk Model v1: No official model has been released. The proposed model would combine the likelihood of unplanned outage values with the Reliability Consequence v1 values. This model is independent of the EPSS Risk and PSPS Risk models described in the WMP. The models listed are in support of internal analysis and prioritization programs for specific PG&E business needs only. The model outputs were not used for the mitigation plans and prioritizations for the 2026-2028 WMP. b. • Public Safety: The proposed Public Safety Risk model is intended to capture public safety risks in urban, more populated areas outside of HFTD. Wildfire safety risks in HFTD are captured by the WDRM and WTRM. • Reliability Risk: Reliability risks from unplanned outages are quantified for Integrated Grid Planning purposes, which compares asset management investment scenarios. The tooling is still in development. Wildfire related reliability risks are captured by the EPSS risk and PSPS risk models described in the WMP. c. The Public Safety and Reliability Models described in subparts (a) and (b) are for PG&E internal business purposes only and have not been used to plan WMPrelated projects in HFTD. | Nathan Poon | 2025-04-22 | 2025-05-06 | 2025-05-06 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_005.zip | 0 | No | 5 | Risk Methodology & Assessment | 5.4 | Summary of Risk Models
17 | 136 | OEIS | 005 | OEIS_005 | 8 | No | OEIS_005_Q8 | Regarding Climate-Driven Extreme Risk Figure PG&E-5.3.2-1 (p. 90, PG&E's 2026-2028 Base WMP) shows scenarios involving climate-driven risk as part of extreme event evaluation. However, in PG&E's response to data request OEIS-P-WMP_2025-PG&E-001, Question 24, PG&E discusses conflagration risk as part of its extreme scenarios. a. Provide a description of what PG&E is planning on implementing changes related to climate-driven risk as it relates to the research paper in Figure PG&E-5.3.2-1. b. Provide a timeline, with dates (at a minimum, quarter and year) for when PG&E is planning on implementing changes related to climate-driven risk as it relates to the findings from the research paper referenced in Figure PG&E-5.3.2-1. c. If no such changes are planned relating to the figure, describe why no such changes are planned. | a. Physics-based models: PG&E's physics-based models provide a risk-based framework for evaluating the condition of transmission line assets subject to various hazards, which could be used to assess changes in failure likelihood during extreme events. These models use a variety of data to evaluate the current condition of an asset relative to the condition of a new pristine asset. These data are used to adjust the median condition of an asset, resulting in an estimate of the probability of failure at a given wind speed, for example, in the form of an asset-specific fragility curve. Machine Learning (ML) models: PG&E’s incorporation of extreme scenario handling within its ML models is more challenging. For the WDRM models, each model update incorporates the recent ignitions and historical fires that have occurred since the last update. As more extreme scenarios are experienced, it would be expected that with each fire season either the number of ignitions will increase, the frequency of ignitions will increase, or fire outcomes will be more severe. These deviations from what was expected via the prior model will be incorporated into the new training data sets for the new model, and hence the locations of highest relative risk will change to account for the extreme scenarios that have occurred, driven by changes to both the probability of ignition and the consequence models. Additionally, RaDA is evaluating methodologies to estimate climate impacts as a post-processing step rather than developed as an integral part of the models. The discussion about conflagration risk in the prior answer is our most current work where we are looking at how some types of extreme scenarios might be accounted for directly within the consequence model. b. PG&E is planning to evaluate methodologies to incorporate future climate impacts into ML models. If successful, the enhancements would be incorporated into WDRM v5 or with WDRM v5 if the methodology is a post-processing step. The WDRM v5 release is tied to the WMP submission cycle. The next Base WMP is expected to be submitted in April 2028 and, if the evaluation determines it is appropriate, this would coincide with the release of a new version of the WDRM. c. Not applicable. | Nathan Poon | 2025-04-22 | 2025-05-01 | 2025-05-01 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_005.zip | 0 | No | 5 | Risk Methodology & Assessment | 5.3.2 | Extreme-Event/High Uncertainty Scenarios
17 | 137 | OEIS | 005 | OEIS_005 | 9 | No | OEIS_005_Q9 | Regarding Top-Risk Transmission Circuits Table 5-5 (p. 103 and pp. 770-773, PG&E’s 2026-2028 Base WMP) shows only distribution-level circuits. a. Provide similar tables to Table 5-5, Table 6-1, and Table 6-4 for the top-risk transmission-level circuit segments based on WTRM v2 output. b. Provide the total overall utility risk score for transmission-level circuits. | a. Transmission does not have circuit segments. However, we can provide circuits/line level risks. Please note that prioritization of transmission controls and mitigations may use additional factors in addition to wildfire risk. Note that PG&E currently does not evaluate transmission related EPSS risk (Outage Program Risk score) Note that PG&E currently does not evaluate transmission related EPSS risk (Outage Program Risk score) Note that post mitigation wildfire risk scores for transmission are limited to WMP hardening targets and are listed as part of GH-06 and GH-11 in the 2026-2028 WMP Table 8-1. Additional activities may be included in 2027 and 2028, pending development in 2026. PG&E inspects the highest wildfire risk structures on an annual basis. Wildfire risk is calculated annually to reflect completed and newly identified work. b. Based on the 2026-2028 WMP Bowtie Risk Models, the overall transmission utility risk is estimated at $2,806M. Currently, PG&E does not evaluate transmission related EPSS risk. | Nathan Poon | 2025-04-22 | 2025-05-06 | 2025-05-06 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_005.zip | 0 | No | 5 | Risk Methodology & Assessment | 5.5.2 | Top Risk-Contributing Circuits/Segments/Spans
17 | 138 | SPD | 003 | SPD_003 | 1 | No | SPD_003_Q1 | On page 186 of PG&E’s 2026-2208 WMP, PG&E mentions the Line Elimination Incentive Plan. a. Describe the plan, including when it would be used. b. Page 183 shows the decision tree with the LEIP screening process – describe the screening process and provide the criteria for evaluation of LEIP, including an example of when the LEIP mitigation would be chosen versus when it would not be chosen. c. What is the average cost of LEIP per customer and what is the expected future cost per customer? i. What is the average cost per circuit mile? d. Why is this not included as a WMP initiative considering it is in the decision tree? e. How many customers are PG&E targeting for this plan over the course of the 2026-2028 Wildfire Mitigation Plan? f. How many customers did the LEIP (or a similar customer buyout programs) remove from the PG&E’s system in each year from 2017 through 2024, and is expected to remove in 2025? g. List out options available to customers that do not wish to participate in LEIP. i. If there are no options, explain why? h. How does LEIP relate to line removal as defined GH-12? i. What is the cost-benefit ratio of the LEIP program? Provide a workpaper that demonstrates how the ratio was calculated. | This response contains confidential material provided pursuan to the accompanying confidential information. | Henry Sweat | 2025-04-23 | 2025-04-29 | 2025-04-29 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_003.zip | 1 | No | 8 | Grid Design, Operations, and Maintenance | 8.2.1 | Covered Conductor Installation
17 | 139 | SPD | 003 | SPD_003 | 2 | No | SPD_003_Q2 | PG&E’s Figure-6.1.3.2-1 states EPSS combined with PSPS removes 81.7% (16,012/19,578=81.7%) wildfire risk. Separately, PG&E’s response in the first figure in part a of “WMP-Discovery2026-2028_DR_OEIS_001-Q023" implies that PSPS/EPSS is closer to 90% effective at mitigating wildfire risk. Table PG&E-6.1.3-1 also states PSPS reduces 84% of the wildfire risk. Why is there an apparently discrepancy between the response of Part a of “WMP-Discovery2026-2028_DR_OEIS_001-Q023" and Table PG&E-6.1.3-1 compared to PG&E’s Figure-6.1.3.2-1? | The wildfire risk reduction values in WMP-Discovery2026- 2028_DR_OEIS_001-Q023 are based on applying effectiveness values for EPSS and PSPS to the circuit segments where those mitigations are implemented in the WDRM v4. The table below shows values from the enterprise WLDFR risk bowtie and shows how the 81.7% and 84% numbers are calculated. Please note that the case and the tranche are different for the 81.7% and 84% effectiveness values. PG&E moved from using the enterprise model in the WMP to the WDRM tool because it was better suited to address granularity and location of work. The two methodologies are not 100% aligned, but it explains the differences in results. | Henry Sweat | 2025-04-23 | 2025-05-07 | 2025-05-07 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_003.zip | 0 | No | 6 | Wildfire Mitigation Strategy Development | 6.1.3.2 | Activity Prioritization
17 | 140 | SPD | 003 | SPD_003 | 3 | No | SPD_003_Q3 | In Figure 6-1, what are the projected mileages for each resiliency mitigation for each year through 2033? a. How were the projected mileages, especially those beyond 2028, for the resiliency mitigations established? | Figure 6-1 includes projected mileage beyond 2028 for two mitigation programs only: Overhead Hardening and Undergrounding. Projected miles include 190 miles of Overhead Hardening and 400 Miles of Undergrounding. a. The projected mileage estimates beyond 2028 were established by looking at historical performance as well as 2026-2028 planned mileage for those resiliency mitigations and assuming a relatively flat unit execution across future years. The high-level workplans are not based on scoped projects, but rather a 1-n WDRM v4 wildfire risk ranked list of circuit segments. Mileage values as well as targeted locations will be subject to change in future years due to concurrent and ongoing regulatory filings such as the GRC and the Electric Undergrounding Plan (EUP). Further detail surrounding mitigation selection criteria are described within section 8 of the WMP. | Henry Sweat | 2025-04-23 | 2025-05-02 | 2025-05-02 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_003.zip | 0 | No | 6 | Wildfire Mitigation Strategy Development | 6.2.1 | Anticipated Risk Reduction
17 | 141 | SPD | 003 | SPD_003 | 4 | No | SPD_003_Q4 | For Figure 6-1 and the figures in Part a of “WMP-Discovery2026-2028_DR_OEIS_001-Q023," what are the actual percentage values for each year? a. What are the baseline 2023 values for Wildfire Risk, PSPS Risk and EPSS Risk? b. Provide the three figures in Part a of “WMP-Discovery2026-2028_DR_OEIS_001-Q023," using absolute values of monetized risk in dollar values. c. What is the assumed risk reduction from operational mitigations for each year for wildfire risk (the first figure in the response to part (a) of “WMP-Discovery2026-2028_DR_OEIS_001-Q023,")? | The actual percentages of each risk and mitigation from Figure 6-1 has been extracted in to the following table. a. The baseline risk values, in dollarized figures are listed in the below table. b. Figure 6-1 is regenerated based on dollars in the following 3 figures c. The following figure assumes that the operational mitigations and their effects on wildfire risk without operational mitigations are to be presented in dollarized risk, similar to the answers in part b. | Henry Sweat | 2025-04-23 | 2025-05-02 | 2025-05-02 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_003.zip | 0 | No | 6 | Wildfire Mitigation Strategy Development | 6.2.1 | Anticipated Risk Reduction
17 | 142 | SPD | 003 | SPD_003 | 5 | No | SPD_003_Q5 | Compute the as-built conversion factor for projects in 2023 and 2024 between overhead lines to underground lines. Provide an explanation of the computation. See the computation provided in PG&E’s response to “WMP-Discovery2023_DR_SPD_005-Q006” for an example. | Please see attachment “WMP-Discovery2026-2028_DR_SPD_003-Q005Atch01.xlsx”. This includes undergrounding subprojects 100% completed in 2023 and 2024. Note, this is the same subset of data provided in response to “WMP-Discovery2026- 2028_DR_TURN_003-Q004Atch01.xlsx”, and with the conversion factor appended. The primary overhead miles removed and replaced by undergrounding reflect actual overhead miles removed on undergrounding subprojects, where data is available; otherwise, where data is not yet available, we used the adopted1 overhead to undergrounding conversion factor of 1 mile of overhead to 1.25 miles of undergrounding. | Henry Sweat | 2025-04-23 | 2025-04-29 | 2025-04-29 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_003.zip | 1 | No | 8 | Grid Design, Operations, and Maintenance | 8.2.2 | Undergrounding of Electric Lines and/or Equipment
17 | 143 | SPD | 003 | SPD_003 | 6 | No | SPD_003_Q6 | For GH-04, provide a definition of the miles target and compare the definition to the target in the 2026-2028 WMP. For instance, is the target some combination of: “the miles of primary overhead line to be replaced by undergrounding,” “the miles of overhead (primary, secondary and service) line to be replaced by undergrounding,” “the miles of undergrounded primary lines to be installed” or “the miles of undergrounded (primary, secondary and service) lines to be installed.” a. PG&E proposes two forms of undergrounding (underground primary, and underground all). Provide the number of miles for each undergrounding type planned for 2026, 2027, and 2028. b. Page 181 of the PGE’s 2026-2028 WMP states: “While PG&E will choose either overhead hardening or undergrounding as the primary mitigation, PG&E often implements a hybrid mitigation solution that consists of both overhead hardening and undergrounding on portions of the same circuit segment.” i. If a hybrid solution is implemented, how will the mileage be recorded in GH-04 and GH-12? ii. If undergrounding is the primary mitigation, but some covered conductor is installed on the project because undergrounding is infeasible for a small section of the line – how will the mileage be recorded in GH-04 and GH-12? iii. Provide the number of miles where PG&E expects a hybrid solution will be implemented and recorded in GH-04 and/or GH-12. | a. While PG&E’s WMP references the effectiveness of Underground All (primary, secondary and service lines) and of Underground Primary, the undergrounding mileage commitments for GH-04 listed in table 8.1.1 for this WMP period are specifically for the undergrounding of primary distribution lines. WMP-Discovery 2026-2028_DR_SPD_003-Q006 Page 2 b. i. For any project with a combination of undergrounding and overhead hardening and/or line removal, undergrounding mileage will be recorded in GH-04 and overhead hardening and line removal mileage will be recorded in GH-12. ii. For any project with a combination of undergrounding and overhead hardening and/or line removal, undergrounding mileage will be recorded in GH-04 and overhead hardening and line removal mileage will be recorded in GH-12. iii. Please reference “WMP-Discovery2026-2028_DR_SPD_003-Q006Atch01.xlsx” for a list of all circuit segments that have been identified for undergrounding and overhead hardening and/or line removal. For 2026 work, subprojects have been scoped and the miles associated the multiple mitigation types have been included at the subproject-level. For 2027 and 2028 work, the miles associated with hybrid solutions will be determined once they are fully scoped. A summary of the miles is included in the “Summary” tab and below for reference. | Henry Sweat | 2025-04-23 | 2025-04-29 | 2025-04-29 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_003.zip | 1 | No | GH-04 | GH-04 | GH-04 | GH-04
17 | 144 | SPD | 003 | SPD_003 | 7 | No | SPD_003_Q7 | Explain how PG&E calculates the risk reduced when there is a combination of undergrounding and covered conductor on a particular circuit segment. Clarify if there is a difference in how the risk reduction is calculated if a primary covered conductor project, primary undergrounding project or a hybrid project is chosen. | Risk reduction is based on the unique effectiveness values of each mitigation applied against the proportion of a circuit segment addressed by the corresponding mitigation. For example, for a segment with a wildfire mitigation effectiveness value of 67% for OH and 98% for UG, the risk reduction for that circuit segment containing 10 risk points prior to mitigation would be: 1. For OH: Risk Reduction = 10 risk points x 67% = 6.7 risk points 2. For UG: Risk Reduction = 10 risk points x 98% = 9.8 risk points 3. For a Hybrid Project (half of the segment mileage mitigated by OH and half mitigated by UG): Risk Reduction = (5 risk points x 67%) + (5 risk points x 98%) = 8.25 risk points This is a simplified example of the calculation detailed in PG&E’s Advice Letter 7150-E-A. | Henry Sweat | 2025-04-23 | 2025-04-29 | 2025-04-29 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_003.zip | 0 | No | 8 | Grid Design, Operations, and Maintenance | 8.2.2 | Undergrounding of Electric Lines and/or Equipment
17 | 145 | SPD | 003 | SPD_003 | 8 | No | SPD_003_Q8 | Provide additional explanation on the discussion in section 8.2.2 under the heading, “Impacts on Likelihood and Consequence of Program Events.” The questions below are posed under the assumption that the lines would not be subject to PSPS/EPSS conditions due to overhead lines upstream or downstream. a. For circuit segments where there are covered conductor miles interspersed among undergrounded miles, explain how PG&E will plan to use PSPS and EPSS for these circuit segments. i. Is there a threshold for the amount of covered conductor? (i.e. if there is a 5-mile undergrounded circuit segment that has only 100 feet of covered conductor and that circuit segment is subjected to PSPS conditions, would a PSPS event be triggered?) b. For undergrounded segments from the 2023-2025 WMP where only the primary conductor was undergrounded, explain how PG&E will use of PSPS and EPSS. | Regarding PSPS, see “Impacts on Likelihood and Consequence of Program Events” in section 8.2.1 of the 2026-2028 WMP which further explains overhead and underground inclusion for PSPS events at a high level. There is no threshold for the amount of covered conductor to be exempt from PSPS. In the event primary conductor segments have been undergrounded, replacing all overhead primary exposure in High Fire Risk Areas (HFRA) and EPSS buffer areas, a circuit may be removed from EPSS program scope. If only a portion of a circuit is undergrounded, the portions of the overhead primary remaining in HFRA or EPSS buffer areas will continue to be protected by EPSS capable devices when criteria are met. | Henry Sweat | 2025-04-23 | 2025-04-29 | 2025-04-29 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_003.zip | 0 | No | 8 | Grid Design, Operations, and Maintenance | 8.2.2 | Undergrounding of Electric Lines and/or Equipment
17 | 146 | SPD | 003 | SPD_003 | 9 | No | SPD_003_Q9 | The system target for GH-04 is 370 miles for 2026 whereas PG&E previously forecasted a target of 440 miles. a. Provide the breakdown for miles related to Butte County Rebuild in 2026. b. The WMP states the reduction is because the PG&E forecasts being able to achieve the risk reduction in the GRC with less miles than previously forecasted. Provide a high-level justification for this number. The justification should be desegregated by the amount of risk reduced per year by mitigation and by the risk model. c. Provide the risk reduced in part (b) but calculate the risk reduced based on the risk calculated in WDRM v4. d. In Advice Letter 7312-E submitted on July 1, 2024, PG&E presented its System Hardening Accountability Report. In the Baseline_Risk_Miles spreadsheet of Attachment B, PG&E forecasted 53.5 WDRM v2 miles and 575.1 WDRM v3 miles of hardening to be completed in 2026. Do these numbers account for the changed forecast in GH-04? i. If so, please provide how many WDRM v2 miles of undergrounding and how many WDRM v3 miles of undergrounding PG&E now forecasts as being completed in 2026 in order to satisfy the risk reduction target adopted in OP 22 of D.23-11-069. ii. If not, provide the new forecast of WDRM v2 miles and WDRM v3 miles of hardening to be completed in 2026. Also provide how much of the updated forecast of WDRM v2 miles and WDRM v3 miles of hardening that PG&E forecasts would be undergrounding to be completed in 2026. | a. As described in response to WMP-Discovery2026-2028_DR_OEIS_001-Q019, the GH-04 Undergrounding target of 370 reflects PG&E’s forecast to complete approximately 10 miles of undergrounding as part of the Butte Community Rebuild effort in 2026. b. PG&E reduced the planned GH-04 mileage for 2026 based on the risk reduction achieved in 2023-2024 and forecasted for completion in 2025 in order to stay in compliance with the 2023 GRC risk reduction requirements. Please see Table 1 below with the 2023-2026 risk reduction achieved and forecasted (as of February 24, 2025) in accordance with PG&E Advice 7130 E-A, approved by the CPUC on May 30, 2024. Table 2 shows that the miles planned each year by mitigation type, which exceeds the four-year (2023-2026) 18% cumulative risk reduction target of the 2023 GRC. Note, the risk and miles included in the tables below exclude Community Rebuild work given it is not part of the 2023-2026 GRC System Hardening program. c. The estimated WDRM v4 risk values provided in this response represent the risk metrics for circuit segments sharing the same name as the legacy circuit segments on which each project was planned. The risk values from WDRM v4 may be different than risk values from legacy models. Actual circuit segmentation varies over time and there is no guarantee that a project originally targeted on a circuit segment will still lie within the bounds of that same circuit segment’s namesake in the updated risk model. It is also possible the name of the circuit segment stays the same, even though the parameters of the circuit segment changes (e.g. segment splits into two upon installation of new protective devices, replacement of a protective device changes the name of the segment, customer load transfers take place). In some cases, the circuit segment’s namesake may be entirely absent from the updated risk model. Acknowledging the aforementioned limitations of this analysis, please see a summary of estimated risk reduced by year and by mitigation type in the Table 3 below: d. The GRC Advice Letter 7312-E (SHAR) did not consider PG&E’s 2026 undergrounding WMP mileage forecast being reduced from 440 miles to 370 miles in one year. PG&E is managing the System Hardening work portfolio to meet the annual cumulative risk reduction targets as required by the 2023 GRC: 2% by 12/31/2023, by a total of 5% by 12/31/2024, by a total of 10% by 12/31/2025, and by at least a total of 18% by 12/31/2026 of the 2023 baseline risk amount (OP 23). While PG&E does manage to the WMP mileage targets, the 2026 miles included in the 2023 WMP was an estimate, and not a target (2023 WMP, R8, Table 8.1.2-2, pg. 408). The 2023 WMP requires annual targets for 2023-2025. For clarity, the 2026 miles referenced in the question (53.5 WDRM v2 miles and 575.1 WDRM v3) include three system hardening mitigations: overhead hardening, undergrounding and line removal.1 In the SHAR, the 2025 forecasted undergrounding work (438 miles) exceeded the WMP target for 2025 (310 miles, excluding Butte Community rebuild forecasts) because the 2025 work was oversubscribed in the SHAR and PG&E anticipated a portion of the portfolio to shift to 2026 or later in order to achieve the risk reduction targets. i. Not applicable. 1 Undergrounding was approximately 305 miles of the 628 miles forecasted in 2026. ii. Please see Table 2 above for the requested information. Please note that an additional estimated 6 miles in 2026 are reserved for potential dependencies or carryover from 2025 and are not designated as v2 or v3 applicable in this response as those specific projects cannot be specified in advance. The 10 Butte County Rebuild miles, which apply toward PG&E’s GH-04 target, but not the GRC/SHAR, were not selected based on a risk model and are also excluded from the v2/v3 totals in this response. | Henry Sweat | 2025-04-23 | 2025-04-29 | 2025-04-29 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_003.zip | 0 | No | GH-04 | GH-04 | GH-04 | GH-04
17 | 147 | SPD | 003 | SPD_003 | 10 | No | SPD_003_Q10 | In the 2024 QDR spatial data set, the polylines GH-01 and GH-04 are frequently overlaid on each other. Explain how to identify how many miles were undergrounded, covered conductored or removed, as well as how to understand the as-built configuration of the system. Additionally, answer the following: a. SPD assumed the feature in the data set which states “ugfeet” and “ccfeet” would distinguish between undergrounding and covered conductor, but is finding that these numbers do not add up to the reported completed miles in a given WMP year. What is “ugfeet” and “ccfeet” and why do they not add up to the completed miles? b. SPD found the length of the polylines added up to 291 miles for GH-01 (Status=Complete, Completion Date = All), but the reported actual number of miles completed in the tabular QDR is 348. Explain why the length of the polylines is not equal to the 348 miles. c. Some GH-01 data is in points instead of polylines – explain why polylines are not used since there is either a portion of a line being removed, cover conductored or undergrounded. | The DescriptionOfWork data field can be used to see the current planned removal feet, underground feet, and covered feet, which can then be converted into miles for each project. Please note, this is not a required field by Energy Safety, but rather an additional detail PG&E provides to help the user get additional information related to the work performed. PG&E started providing the feet and activity type to the DescriptionOfWork field since the Q2 2024 submission. As PG&E indicates in our metadata, as well as in previous data request responses to the CPUC and Energy Safety, data in the Spatial QDR represents a snapshot in time only. The data evolves as more work is performed against the projects. The quarterly reports are interim draft work products used to provide visibility to work performed. They are not final versions for initiative and should not be used for verification. Project work expands beyond a single quarter so the data about each project evolves. For complete details of work performed including schematics, job packages should be used and reviewed. As-built configuration of the system PG&E’s Geographic Information System (GIS), Electric Transmission GIS, and Electric Distribution GIS mapping systems represent assets associated with construction work when that work has been received and mapped by electric GIS mapping technicians. Construction jobs that are partially complete or fully complete may be mapped in the GIS systems once construction “as-built” information has been submitted and accepted by the GIS Mapping Department. Prior to being received by the GIS Mapping Department, completed job packages must undergo several processing steps including clerical review, processing, and paperwork scanning. Sometimes, completed job packages require additional information from the field or post-estimating work. The processing steps take time to complete. Until a project is completed and mapped, detailed information remains in the design systems and paper job packages. When spatial quarterly reports are created, there will be varying levels of mapping available for each project. PG&E provides spatial data to the extent each job has been mapped. Please note, when a job status changes to “complete” in the GIS Data Standard submissions the GIS Mapping Department may still be undergoing processing steps to reflect the completed job package in GIS mapping systems. As such, construction field complete, does not mean mapping complete. a. As stated above, the DescriptionOfWork data field can be used to see the current planned removal feet, underground feet, and covered feet. This is an optional field and PG&E started providing activity feet since our Q2 2404 submission as an additional way to support understanding of each system hardening project. Given the schema character limit assigned to the DescriptionOfWork field, “ugfeet” and “ohfeet” are short for undergrounding of electric lines and/or equipment feet, covered conductor installation feet. There is also “removal” which is removal and retirement of overhead conductor to reduce risk of ignition in HFTDs. Covered conductor installation, undergrounding of electric lines and/or equipment, and removal and retirement of overhead conductor to reduce risk of ignition in HFTDs are the three primary activities that collectively represent system hardening work captured in our WMP GH-01 commitment. Should the undergrounding, covered conductor, and removal feet be added up and converted to miles across both the Grid Hardening Line and Grid Hardening Point feature classes, they do total up to 348 miles. Please see below for a breakdown of the values. b. As indicated above, the Spatial Quarterly Reports generate mappings to the extent mappings exist in our GIS source system at the time the reporting is generated. Until a project has been completely mapped, the line geometry may not measure to show the actual mileage of the projects. Construction complete in the field, does not mean mapping is complete in our source systems. Furthermore, as PG&E also states in our metadata, the spatial submission will not align to the official projection numbers in the WMP tabular filing. The official projection used to calculate line mines uses UTM Zone 10 NAD 83. However, the OEIS GDB is in WGS_1984_California_Teale_Albers_FtUS, so when re-projected the translation will result in different line lengths. c. PG&E first attempts to put project data in the Grid Hardening Line feature class if there is line geometry available in our source system for that project. If no line geometry is available, projects are placed in the Grid Hardening Point feature class to show them as a latitude and longitude in the Spatial Quarterly Data Report. This ensures all projects are counted to avoid omitting any from the quarterly reports. | Henry Sweat | 2025-04-23 | 2025-04-29 | 2025-04-29 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_003.zip | 0 | No | GH-04 | GH-04 | GH-04 | GH-04
17 | 148 | SPD | 003 | SPD_003 | 11 | No | SPD_003_Q11 | Provide an update for full 2024 year data to “WMP-Discovery2023-2025_DR_SPD_019-Q012.pdf” and the supplemental response. | For the year 2024, PG&E confirms the average number of strike trees per mile of lines inspected on Focused Tree Inspection (FTI) prior to removal is 785.84. Please see the calculation below for how this number was determined: For the year 2024, PG&E confirms the average number of strike trees per mile of lines inspected after removals is 748.41. Please see the calculation below for how this number was determined: Please see the following data for the requested information for the year 2024: • Number of trees prescribed to be worked: 71,284 trees • Number of total trees worked: 56,342 trees • Number of total trees prescribed for removal: 58,689 trees • Number of total trees removed: 46,237 trees • Number of miles inspected: 1,568.1 miles • Number of strike trees per mile of lines inspected before removals: 785.84 trees/mile • Number of strike trees per mile after removals: 748.41 trees/mile • Number of trees inspected: 1,232,276 trees | Henry Sweat | 2025-04-23 | 2025-04-29 | 2025-04-29 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_003.zip | 0 | No | 9 | Vegetation Management and Inspections | 9 | Vegetation Management and Inspections
17 | 149 | SPD | 003 | SPD_003 | 12 | No | SPD_003_Q12 | Provide the data in Tables 1 through 3 for each of PG&E’s 2023-2025 WMP planned Vegetation Management Programs and PG&E’s 2026-2028 WMP Programs. There should be one spreadsheet for each of the Vegetation Management Programs listed in Tables 4 and 5. a. Discuss how PG&E’s evaluation of Focused Tree Inspection, Tree Removal Inventory, and Vegetation Management for Operational Mitigations for consolidation into its distribution inspections may change the forecasts in Table 3. For the 2023-2025 WMPs, SPD expects the individual programs to be reported on to include: Table 4: List of Vegetation Management Programs 2023-2025 For the 2026-2028 WMPs, SPD expects the individual programs to be reported on to include: Table 5: List of Vegetation Management Programs 2026-2028 | Please refer to “WMP-Discovery2026-2028_DR_SPD_003-Q012Atch01.xlsx” for the requested tables for Vegetation Management programs. Please note the following: • “Forecasted to be worked” includes an estimate of how many trees may be either pruned or removed as part of that program. “Number of total trees removed” is a forecast. Vegetation Management does not forecast “total number of trees prescribed for removal” for any programs. • Transmission vegetation management programs do not forecast number of total trees removed. The extent of tree work will be prescribed as needed based on the findings during the programs’ inspection cycles. • Total mileage is not applicable to the Tree Removal Inventory (TRI) and Vegetation Management for Operational Mitigations (VMOM) programs. TRI is intended to work down the risk associated with the Enhanced Vegetation Management (EVM) trees that were remaining from the program over a period of years. • Transmission Integrated Vegetation Management (TIVM) is not measured in terms of prescribed trees. Please note the unit of measure for TIVM inspections is acres. Where applicable, acres inspected have been provided in lieu of miles inspected. a. At this time, PG&E does not expect further changes to its forecasts in Table 3 due to consolidation of Focused Tree Inspection, Tree Removal Inventory, and Vegetation Management for Operational Mitigations into its distribution programs. | Henry Sweat | 2025-04-23 | 2025-05-07 | 2025-05-07 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_003.zip | 1 | No | 9 | Vegetation Management and Inspections | 9 | Vegetation Management and Inspections
17 | 150 | SPD | 003 | SPD_003 | 13 | No | SPD_003_Q13 | Complete the Tables 1 through 3 at the systemwide and HFTD scale for all of PG&E’s Vegetation Management work (ie, the total number of trees removed systemwide and separately the total number of trees removed in the HFTD). | Please refer to “WMP-Discovery2026-2028_DR_SPD_003-Q012Atch01.xlsx” for the requested tables for Vegetation Management programs systemwide. Please refer to “WMP-Discovery2026-2028_DR_SPD_003-Q013Atch01.xlsx” for the requested tables for Vegetation Management programs in HFTD only. Please note the following: • “Forecasted to be worked” includes an estimate of how many trees may be either pruned or removed as part of that program. “Number of total trees removed” is a forecast. Vegetation Management does not forecast “total number of trees prescribed for removal” for any programs. • Transmission vegetation management programs do not forecast number of total trees removed. • Total mileage is not applicable to the Tree Removal Inventory (TRI) and Vegetation Management for Operational Mitigations (VMOM) programs. TRI is intended to work down the risk associated with the Enhanced Vegetation Management (EVM) trees that were remaining from the program over a period of years. • Transmission Integrated Vegetation Management (TIVM) is not measured in terms of prescribed trees. Please note the unit of measure for TIVM inspections is acres. Where applicable, acres inspected have been provided in lieu of miles inspected. • Distribution and Transmission Second Patrol/Hazard Patrol miles to be inspected in HFTD may be lower than overall program miles to be inspected as the programs include HFRA. • FTI and VMOM do not forecast units to be inspected or worked in HFTD. • TIVM did not track acres worked in HFTD in 2023. • For 2025-2028 data, PG&E does not have a breakdown by HFTD/non-HFTD of forecasted trees to be worked and/or removed for Distribution Routine and Hazard Patrol programs. | Henry Sweat | 2025-04-23 | 2025-05-07 | 2025-05-07 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_003.zip | 1 | No | 9 | Vegetation Management and Inspections | 9 | Vegetation Management and Inspections
17 | 151 | SPD | 003 | SPD_003 | 14 | No | SPD_003_Q14 | For each vegetation management program in the 2026-2028 WMP, specify if the Quality Assurance and Quality Controls assessments include verification of the height and distance to the conductor of each strike vegetation point specified for removal, and each vegetation strike point noted as an inventory tree. | Quality Assurance and Quality Controls assessments do NOT include verification of the height and distance to the conductor of each strike vegetation point specified for removal, and each vegetation strike point noted as an inventory tree. | Henry Sweat | 2025-04-23 | 2025-04-29 | 2025-04-29 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_003.zip | 0 | No | 9 | Vegetation Management and Inspections | 9 | Vegetation Management and Inspections
17 | 152 | SPD | 003 | SPD_003 | 15 | No | SPD_003_Q15 | Provide PG&E’s latest estimate for the number of strike trees in PG&E’s HFTD with an explanation of how this estimate was obtained. Discuss PG&E’s confidence in the estimate. | PG&E currently estimates approximately 5.6 million trees that have overhead electric system strike potential within HFTD only. This estimate is based on 2019 (distribution) and 2023 (transmission) aerial LiDAR data collection. Due to known limitations of aerial LiDAR associated with tree counts, especially in closed canopy environments, this is likely an underestimation. Due to these factors our confidence level is low. | Henry Sweat | 2025-04-23 | 2025-04-29 | 2025-04-29 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_003.zip | 0 | No | 9 | Vegetation Management and Inspections | 9 | Vegetation Management and Inspections
17 | 153 | MGRA | 005 | MGRA_005 | 1 | No | MGRA_005_Q1 | Follow-ups to Data Request Responses: WMP-Discovery 2026-2028_DR_OEIS_001-Q022 MGRA-5-1 For the three technologies listed in PG&E’s response to the OEIS data request EFD, DFA, Gridscope), please provide a per-year estimate of the deployment of these devices for 2026, 2027, and 2028 in the HFRA+HFTD: a. The number of devices to be deployed. b. The miles of overhead conductor to be monitored by these technologies in the HFTD in miles. c. The fractional coverage of the overhead conductor system. d. The estimated cumulative risk reduction due to the deployment of that technology. | a. PG&E plans to deploy 180 EFD devices/year and 15 DFA devices/year during 2026-2028 WMP period. PG&E is still in the deployment strategy development phase for Gridscope devices. b. EFD devices planned for deployment in 2026 will monitor approximately 467 primary overhead miles of HFTD conductor. DFA devices planned for deployment in 2026 will monitor approximately 1,616 primary overhead miles of HFTD conductor. Deployment results in 2027 and 2028 are expected to be comparable to 2026. c. The approximately 467 miles of primary overhead conductor HFTD miles on the circuits planned for deployment of EFD devices in 2026 account for 1.9% of all primary overhead conductor HFTD miles in PG&E service territory. The 1,616 miles of primary overhead conductor HFTD miles on the circuits planned for deployment of DFA devices in 2026 account for 6.4% of all primary overhead conductor HFTD miles in PG&E service territory. Deployments results in 2027 and 2028 are expected to be comparable to 2026. WMP-Discovery 2026-2028_DR_MGRA_005-Q001 Page 2 d. Like asset inspections, sensors provide eyes-on-risk, detecting conditions that could create a wildfire or public safety risk. Actual risk reduction is accomplished when identified conditions are addressed by maintenance. • EFD – 2.52% EOR per year. • DFA – 9.92% EOR per year. | Joseph Mitchell | 2025-04-25 | 2025-05-13 | 2025-05-13 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-MGRA_005.zip | 0 | No | 10 | Situational Awareness and Forecasting | 10.4/10.31 | Real-Time Sensors
17 | 154 | MGRA | 005 | MGRA_005 | 2 | No | MGRA_005_Q2 | Suppression MGRA-5-2 During a meeting of the Risk Mitigation Working Group, I recall one of the PG&E team stating that they had looked at the CalFire ignition database to determine whether weather local conditions affected the probability of successful initial attack. a. Did PG&E ever perform an analysis similar to that described? a) If the answer is yes, please provide the results. b. Is the PG&E FPI model available through a public interface? i.e. If a latitude, longitude, and time is provided can a corresponding FPI value be retrieved? c. If the answer to b) is no, what is the approximate volume of PG&E’s FPI history, could it potentially be exported, and how much time (days) and effort (personhours) would it require? d. As PG&E’s FPI algorithm has changed over time, has PG&E segregated historical periods with different FPI approaches? Or has it re-run its history with the most recent FPI version? | a. PG&E did not perform a study that evaluated if local weather conditions affected the probability of successful initial attack. We did perform a study briefly discussed during a recent Risk Mitigation Working Group meeting that evaluated classes of the FPI model. This did show that most buildings damaged/destroyed occur during the first 24 hours from the initial fire detection. See the table below. b. While the PG&E FPI is not available through a public interface, daily FPI 5.0 ratings by Fire Index Area (FIA) back to 2008 are provided in “WMP-Discovery2026- 2028_DR_MGRA_005-Q002Atch01.” This allows for a daily FPI 5.0 FIA rating to be retrieved with a latitude, longitude and date. c. N/A d. PG&E both retains the FPI ratings that were forecast using the operational FPI model at the time and re-runs a FPI historical dataset via hindcast (using the weather/fuels climatology) using the latest model in production. See attachment associated with part B. | Joseph Mitchell | 2025-04-25 | 2025-04-30 | 2025-04-30 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-MGRA_005.zip | 1 | No | Appendix D | Appendix D: Areas of Continued Improvement | ACI PG&E-23B-03 | Incorporation of Extreme Weather Scenarios in Planning Models
17 | 155 | MGRA | 005 | MGRA_005 | 3 | No | MGRA_005_Q3 | Covered Conductor MGRA-5-3 In Table PG&E-8.2.1-4: COVERED CONDUCTOR AND UNDERGOUNDING IMPACTS ON THE LIKELIHOOD OF IGNITION, PG&E’S analysis of Wire-to- Wire contact lists the effectiveness of Covered Conductor as medium it reducing this risk source, whereas other parties rank this as a high effectiveness. a. Please justify why wire-to-wire contact is only reduced to a medium outage prevention. b. Please provide examples in which wire to wire contact between covered conductors. resulted in an outage and under what conditions. | a. The referenced line item in table PG&E-8.2.1-4 was mislabeled as wire-to-wire contact. This driver should have been labeled: Equipment / facility failure - Secondary damage or failure. This update will be reflected in a forthcoming nonsubstantive errata targeted for May 16, 2025. PG&E’s qualitative assessment of the effectiveness of covered conductor for wire-to-wire contact is rated as Very High. b. PG&E does not track covered conductor outages vs bare wire outages and does not have examples of wire-to-wire contact readily available. | Joseph Mitchell | 2025-04-25 | 2025-04-30 | 2025-04-30 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-MGRA_005.zip | 0 | No | 8 | Grid Design, Operations, and Maintenance | 8.2.1 | Covered Conductor Installation
17 | 156 | MGRA | 005 | MGRA_005 | 4 | No | MGRA_005_Q4 | Advanced Technology MGRA-5-4 Please direct us to or provide the technical details of Gridscope a. Please provide the differences in action and function and purpose between Gridscope and EFD. | Gridscope is a distributed reactive real time sensor technology with sensors on approximately every other pole that detect conditions where equipment has failed including downed conductors, broken or leaning poles, vegetation, animal or foreign object in conductors, and loss of power. EFD is a distributed proactive sensor technology with sensors every few miles that detect equipment emerging issues, prior to failure, deteriorating conductors, connections, tie wires, insulators, degraded service transformers, and close vegetation proximity. | Joseph Mitchell | 2025-04-25 | 2025-04-30 | 2025-04-30 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-MGRA_005.zip | 0 | No | 10 | Situational Awareness and Forecasting | 10.3.1 | Existing Systems, Technologies, and Procedures
17 | 157 | MGRA | 005 | MGRA_005 | 5 | No | MGRA_005_Q5 | Weather MGRA-5-5 Provide a list of the 571 worst weather days, along with a. geographic limits associated with the designation (polygon, counties, etc. ), b. FPI, c. Diablo wind event classifier, d. associated catastrophic wildfire e. any other notes or comments added by the meteorological team | a. The geographic limit associated with the worst weather days is based on the geographic domain of the PG&E service territory. b. Daily FPI 5.0 ratings by Fire Index Area (FIA) since 2008 are provided for the worst weather days at “WMP-Discovery2026-2028_DR_MGRA_005-Q005Atch01.xlsx.” c. The quantitative Diablo wind event classifier is provided for the worst weather days through 2019 using an analysis described above. For 2020, we leveraged our “North East” weather signal classification, which is a qualitative designation made by an operational meteorologist. “North East” days are intended to capture Diablo wind events. The Diablo wind event classifier is created based on the POMMS climatology at “WMP-Discovery2026-2028_DR_MGRA_005-Q005Atch02.xlsx.” The Diablo Event criteria is defined here as dates where a wind direction between 350 and 112.5 degrees, windspeeds of 20 mph or greater, relative humidity of 25% or less over at least 225 or more POMMS 2x2km grid cells for at least 6 consecutive hours. These values were determined from a review of academic literature available. d. Catastrophic wildfires, defined here as those with a final fire size over 5,000 acres since 2012, are provided for the worst weather days at “WMP-Discovery2026- 2028_DR_MGRA_005-Q005Atch03.xlsx.” WMP-Discovery 2026-2028_DR_MGRA_005-Q005 Page 2 e. N/A | Joseph Mitchell | 2025-04-25 | 2025-04-30 | 2025-04-30 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-MGRA_005.zip | 3 | No | Appendix D | Appendix D: Areas of Continued Improvement | ACI PG&E-23B-03 | Incorporation of Extreme Weather Scenarios in Planning Models
17 | 158 | OEIS | 006 | OEIS_006 | 1 | No | OEIS_006_Q1 | Regarding PSPS Impact In response to data request OEIS-P-WMP_2025-PG&E-003, Question 3, PG&E states that "the criteria for determining whether a circuit protection zone is affected by PSPS is binary and PG&E considers the distinction of whether there is PSPS impact or not." Provide the following based on the CPZs in which there is PSPS impact: a. The percentage by total circuit mileage b. The associated total circuit mileage impacted c. The percentage by total number of CPZs in the HFRA d. The associated number of CPZs impacted | a. The geographic limit associated with the worst weather days is based on the geographic domain of the PG&E service territory. b. Daily FPI 5.0 ratings by Fire Index Area (FIA) since 2008 are provided for the worst weather days at “WMP-Discovery2026-2028_DR_MGRA_005-Q005Atch01.xlsx.” c. The quantitative Diablo wind event classifier is provided for the worst weather days through 2019 using an analysis described above. For 2020, we leveraged our “North East” weather signal classification, which is a qualitative designation made by an operational meteorologist. “North East” days are intended to capture Diablo wind events. The Diablo wind event classifier is created based on the POMMS climatology at “WMP-Discovery2026-2028_DR_MGRA_005-Q005Atch02.xlsx.” The Diablo Event criteria is defined here as dates where a wind direction between 350 and 112.5 degrees, windspeeds of 20 mph or greater, relative humidity of 25% or less over at least 225 or more POMMS 2x2km grid cells for at least 6 consecutive hours. These values were determined from a review of academic literature available. d. Catastrophic wildfires, defined here as those with a final fire size over 5,000 acres since 2012, are provided for the worst weather days at “WMP-Discovery2026- 2028_DR_MGRA_005-Q005Atch03.xlsx.” WMP-Discovery 2026-2028_DR_MGRA_005-Q005 Page 2 e. N/A | Nathan Poon | 2025-04-25 | 2025-04-30 | 2025-04-30 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_006.zip | 0 | No | 8 | Grid Design, Operations, and Maintenance | 8.2.1 | Covered Conductor Installation
17 | 159 | OEIS | 006 | OEIS_006 | 2 | No | OEIS_006_Q2 | Regarding the Wildfire Risk Bow Tie Figure PG&E-5.1.1-2 shows the risk bow tie for wildfire risk on page 47 of the 2026-2028 Base WMP. a. Provide two updated versions of this figure for distribution-only risk and transmission-only risk. b. The figure shows that equipment/facility failure and vegetation contact make up 49% and 23%, respectively, of the risk events per year based on frequency. However, it shows that both make up 39% of the risk. i. Provide the timeframe used to determine the number of events per year within the figure. ii. Provide a definition for what qualifies as an “event” within the figure (i.e. outage, ignition). iii. Given the lower likelihood based on frequency of risk event, provide a detailed description of the factors that led to vegetation contact having a similar risk percentage to equipment/facility failures (i.e., proportionally higher consequence or p(i¦o) after accounting for the lower frequency). | a. Please see the figures below for the distribution- and transmission-only versions of Figure PG&E-5.1.1-2. Please note that the model used to generate Figure PG&E5.1.1-2 includes 5 tranches of data (Distribution-HFRA, Transmission-HFRA, Substation-HFRA, Underground-HFRA, and non-HFRA). These new bowties only include the distribution and transmission tranches (including disaggregated distribution and transmission portions of the non-HFRA tranche) and exclude the underground and substation tranches. As a result, the sum of events shown in the provided distribution and transmission figures in this response does not equal the aggregate sum of events in the model shown in Figure PG&E-5.1.1-2. WMP-Discovery 2026-2028_DR_OEIS_006-Q002 Page 2 Also note that PG&E determined that the “Exposure” value presented in Figure PG&E-5.1.1-2 in its 2026-2028 WMP inadvertently double-counted miles. The correct aggregated Exposure value is 236,744 miles as of the date of the WMP filing. Please note that, for the reasons explained above, the sum of the distribution and transmission exposures in the figures provided in this response does not equal this aggregate exposure. b. i. The timeframe used to determine the number of events per year within the figure was from 2015-2024. ii. The definition of “event” within the figure is defined as a PG&E-caused ignition. iii. In general, areas with high probability of ignition from vegetation related branch and trunk failures tend to be located in areas of high consequence, particularly foothills and lower mountain regions. Ignition probabilities for equipment failures tend to be more dispersed between areas of low and high consequence. The clustering of high vegetation ignition probabilities in high consequence areas results in a higher average effective consequence and, therefore, higher risk for vegetation related failures. | Nathan Poon | 2025-04-25 | 2025-04-30 | 2025-04-30 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_006.zip | 0 | No | 5 | Risk Methodology & Assessment | 5.1.1 | Overview
17 | 160 | OEIS | 006 | OEIS_006 | 3 | No | OEIS_006_Q3 | Regarding Weather Model Validation a. Page 57 of the 2026-2028 Base WMP states that “The models use PSPS guidance criteria to perform a back-cast using our 30+ year climatological dataset.” i. Provide documentation describing this climatological dataset ii. Provide a list of the variables contained within the dataset iii. Provide a detailed description of the validation performed on the dataset and results of the validation, as well as documentation similar in technical detail to the operational weather modeling presented in (https://doi.org/10.3390/atmos15101244). b. Table 5-1 on page 82 of the 2026-2028 Base WMP includes a description of FPI and IPW models, stating that the weather model forecasts are “skillful and well validated.” i. Provide documentation describing these weather model forecasts ii. Provide a list of variables that these weather models forecast iii. Provide a detailed description of the validation performed on the weather model forecasts and results of the validation, as well as documentation similar in technical detail to the operational weather modeling presented in https://doi.org/10.3390/atmos15101244. | a. i. Documentation that describes the climatological dataset can be found at the sources below. 1. The POMMS 3.0 Configuration Report provided as “WMPDiscovery2026-2028_DR_OEIS_006-Q003Atch01.pdf. 2. Section 8.6 of the PSPS Model White Paper provided as “WMPDiscovery2026-2028_DR_OEIS_006-Q003Atch02.pdf.” WMP-Discovery 2026-2028_DR_OEIS_006-Q003 Page 2 3. For documentation on the Weather Research and Forecasting model, please see: https://www.mmm.ucar.edu/models/wrf. The WRF model can be used in forecast mode or utilized to create historical (climatological) data using global weather model forcing or climatological reanalyzes, respectively. 4. For information on the Climate Forecast System Version 2 (CFSv2) Operational reanalysis, please reference this site: https://www.ncei.noaa.gov/access/metadata/landingpage/bin/iso?id=gov.noaa.ncdc:C00878 5. For information on the Climate Forecast System Reanalysis (CFSR) please see this location. https://www.ncei.noaa.gov/access/metadata/landingpage/bin/iso?id=gov.noaa.ncdc:C00765 ii. The list of variables available at the surface or near surface can be found in “WMP-Discovery2026-2028_DR_OEIS_006-Q003Atch03.txt.” The list of variables that can be extracted from the 3D climatology and forecast dataset can be found in “WMP-Discovery2026-2028_DR_OEIS_006- Q003Atch04.txt.” iii. Please see “WMP-Discovery2026-2028_DR_OEIS_006-Q003Atch01.pdf” and “WMP-Discovery2026-2028_DR_OEIS_006-Q003Atch02.pdf.” b. i. Documentation of the FPI and IPW models can be found in sections 3 and 4, respectively, of “WMP-Discovery2026-2028_DR_OEIS_006- Q003Atch02.pdf.” ii. Please see response to B.i. iii. Please see response to B.i. | Nathan Poon | 2025-04-25 | 2025-04-30 | 2025-04-30 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_006.zip | 4 | No | Appendix D | Appendix D: Areas of Continued Improvement | ACI PG&E-23B-03 | ACI PG&E-23B-03 - Incorporation of Extreme Weather Scenarios in Planning Models
17 | 161 | OEIS | 006 | OEIS_006 | 4 | No | OEIS_006_Q4 | Regarding EPSS Risk On page 65 of the 2026-2028 Base WMP, PG&E states that the EPSS outage risk model “considers the fraction of failures that turn into sustained outages when EPSS is not enabled so that the baseline outage risk can be subtracted from the EPSS enabled risk.” a. Provide the number of outages that are within that fraction, including the number of customer minutes interrupted associated with those outages. b. Provide the number of outages used prior to the removal of baseline outages discussed in part (a), including the associated customer minutes interrupted. | a. When EPSS is not enabled, roughly 85-90% of the outages are sustained and 10- 15% are momentary, due to the installed reclosers. Momentary outages need to be excluded from the calculation of baseline risk as they do not cause additional customer minutes of interruption. The EPSS Outage Risk model does not use historical customer minutes interrupted within the calculation methodology. Therefore, customer minutes cannot be provided as part of the response. b. For outages that occurred in HFTD/HFRA during wildfire season, approximately 120,000 outages were sustained out of approximately 136,000 total failures in the historical records dating back to 2008. Please see subpart (a) above for why customer minutes cannot be provided as part of the response. | Nathan Poon | 2025-04-25 | 2025-05-14 | 2025-05-14 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_006.zip | 0 | No | Appendix D | Appendix D: Areas of Continued Improvement | ACI PG&E-25U-06 | Evaluation and Reporting of Safety Impacts Relating to EPSS
18 | 162 | OEIS | 007 | OEIS_007 | 1 | No | OEIS_007_Q1 | Regarding Distribution Hazard Patrol Page 367 of the 2026-2028 Base WMP states: “PG&E is transitioning the Distribution Hazard Patrol Program scope from focusing on all HFTD and HFRA locations to focusing on areas categorized by risk, which may represent a subset of HFTD miles.” PG&E includes the following figure describing inspection methods used within the HFTD/HFRA: a. Provide footnotes (1), (2), and (3) for the figure above. b. Provide the number of vegetation-caused ignitions that have occurred on the miles identified in the Inspection Selection Matrix above for 2020-2024. Provide a value for each combination of Consequence and Wildfire Risk as shown in the Inspection Selection Matrix. Provide this data in tables with the same x- and y-axes as the Inspection Selection Matrix (see example below). Provide a separate table for each year 2019-2024 and a summary table with 5-year totals (six tables total). c. Provide the number of vegetation-caused outages that have occurred on the miles identified in the Inspection Selection Matrix above for 2020-2024. Provide a value for each combination of Consequence and Wildfire Risk as shown in the Inspection Selection Matrix. Provide this data in tables with the same x- and y-axes as the Inspection Selection Matrix (see example above). Provide a separate table for each year 2019-2024 and a summary table with 5-year totals (six tables total). d. Provide a GIS file showing the miles identified in the Inspection Selection Matrix above color-coded to show the circuits that will be inspected by “Routine” only, by “Routine/Hazard” only, and by “Routine/Hazard/Remote Sensing.” Include the following attributes: i. CircuitID (as defined by the Energy Safety Data Guidelines) ii. CircuitName (as defined by the Energy Safety Data Guidelines) iii. Inspection category (i.e., Routine only, Routine/Hazard only, and Routine/Hazard/Remote Sensing) iv. Consequence category (i.e., Low, Medium, High, Severe, and Extreme) v. Wildfire Risk category (i.e., Low, Medium, High, Severe, and Extreme) e. Explain PG&E’s decision-making process for defining the Consequence categories in the Inspection Selection Matrix above. Include the Consequence score range for each category as a percentile of scores from within the HFTD and HFRA. f. Explain PG&E’s decision-making process for defining the Wildfire Risk categories in the Inspection Selection Matrix above. Include the Wildfire Risk score range for each category as a percentile of scores from within the HFTD and HFRA. g. Explain PG&E’s decision-making process for choosing to limit the scope of Hazard Patrol to 75.14% of its risk. Discuss the variables that contributed to this decision (e.g., geography, workforce, resources, effectiveness of other mitigations, etc.). h. Explain how PG&E plans to mitigate the remaining 24.86% of the risk that is not in scope for Hazard Patrol. | a. Please see below for footnotes: WMP-Discovery 2026-2028_DR_OEIS_007-Q001 Page 3 (1) Groupings for consequence are based on the percentiles of circuit segments in the following categories: Extreme 0-1%, Severe 1-2%, High 2-10%, Medium 10- 20%, Low 20-100%. (2) Groupings for wildfire risk are based on the percentiles of circuit segments in the following categories: Extreme 0-1%, Severe 1-2%, High 2-10%, Medium 10-20%, Low 20-100%. (3) “Eyes on risk” demonstrates the anticipated average “eyes on risk” value per year and may fluctuate per year depending on changes in overhead circuit mileage. b. Please see tables below for the number of vegetation-caused ignitions that have occurred on the miles identified in the Inspection Selection Matrix above for 2020- 2024 c. Please see tables below for the number of vegetation-caused outages that have occurred on the miles identified in the Inspection Selection Matrix above for 2020-2024. d. See “WMP-Discovery2026-2028_DR_OEIS_007-Q001Atch01.kmz”, which shows the miles identified in the Inspection Selection Matrix above. Circuits are color-coded to show those that will be inspected by “Routine” only; by “Routine/Hazard” only; and by “Routine/Hazard/Remote Sensing. Within the .kmz file are the requested attributes listed below: I. CircuitID (as defined by the Energy Safety Data Guidelines) II. CircuitName (as defined by the Energy Safety Data Guidelines) III. Inspection category (i.e., Routine only, Routine/Hazard only, and Routine/Hazard/Remote Sensing) IV. Consequence category (i.e., Low, Medium, High, Severe, and Extreme) V. Wildfire Risk category (i.e., Low, Medium, High, Severe, and Extreme) WMP-Discovery 2026-2028_DR_OEIS_007-Q001 Page 6 e. Consequence categories capture locations that if a failure occurs, these locations could result in a higher catastrophic outcome. As such, as part of defining an inspection strategy, these locations should be patrolled, independent of whether there was a high probability of vegetation failures in the past as defined from the WDRM model. In essence, these locations could have limited vegetation, but any such vegetation failures could lead to a higher chance of a catastrophic outcome. For the Consequence score range for each category, please see footnote [1] referenced in response to 7a above. f. Wildfire risk categories capture the locations in which the overall vegetation-related wildfire risk is high, given historical failure events and consequence driven by the WDRM. For the Wildfire Risk score range for each category, please see footnote [1] referenced in response to 7a above. g. PG&E’s decision-making process is based on creating a risk-based prioritization for its inspections, balancing between targeting the highest risk locations, with consideration of reducing customer touchpoints to the extent possible. This further allows the vegetation work to be focused at higher risk locations as PG&E optimizes resources utilized for vegetation work. Additionally, given PG&E’s portfolio of wildfire mitigations, those resources can be deployed to focus on permanent risk mitigation programs like system hardening, continuous monitoring devices, and electric corrective maintenance work. h. The 24.86% of risk not within scope for the Hazard Patrol program will still be inspected on the Distribution Routine program, as that program will continue to inspect all portions of the distribution overhead electric system not impacted by external factors. • Please note: The percentage of risk not within scope for the Hazard Patrol program may change as we continue to assess and develop our plans for 2026. | Nathan Poon | 2025-04-29 | 2025-05-07 | 2025-05-07 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_007.zip | 1 | No | 9 | Vegetation Management and Inspections | 9.2.2 | Hazard Patrol - Distribution
18 | 163 | OEIS | 007 | OEIS_007 | 2 | No | OEIS_007_Q2 | Regarding PG&E’s Pole Clearing Program target (VM-02) On page 356 of its 2026-2028 Base WMP, PG&E sets cumulative quarterly targets for Q4 in 2026, 2027, and 2028 of 70,000 distribution poles, and states that “the target will be adjusted as determined by inspections in the previous year and may additionally be impacted by changes to facilities or based on other utility risk mitigation reasons.” Table 1 of PG&E’s Q4 2024 non-spatial QDR submission indicates that PG&E completed pole clearing work at 79,988 distribution poles in 2024. The delta between PG&E’s targets in the 2026-2028 Base WMP and PG&E’s 2024 pole clearing work is nearly 10,000 poles. a. Provide justification and details of planned activities which support that the volume of pole clearing work PG&E will execute will decrease by nearly 10,000 poles between 2024 and 2026. | The 70,000 distribution poles for 2026-2028 is a target that can and will change year after year based on various factors that can impact the VM Pole Clearing program. Factors that impacted our 2026-2028 target forecasts included system hardening, which involves changing non-exempt equipment to exempt equipment (and thus removing the PRC 4292 compliance requirement), as well as undergrounding efforts, which will result in removing the pole completely from inventory upon completion. In addition to these efforts, each year, poles are removed, added or have a change in status during the Pole Clearing program cycle, thereby affecting targets for the following year. | Nathan Poon | 2025-04-29 | 2025-05-02 | 2025-05-02 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_007.zip | 0 | No | VM-02 | VM-02 | VM-02 | VM-02
18 | 164 | OEIS | 007 | OEIS_007 | 3 | No | OEIS_007_Q3 | Regarding Previous Overhead Assessment Job Aid Revisions a. Provide TD-2305M-JA02 Overhead Assessment revisions 9, 10, 11 and 13. | Please see the attachments below for the requested documents: • Rev. 9: “WMP-Discovery2026-2028_DR_OEIS_007-Q003Atch01CONF.pdf.” • Rev. 10: “WMP-Discovery2026-2028_DR_OEIS_007-Q003Atch02CONF.pdf.” • Rev. 11: “WMP-Discovery2026-2028_DR_OEIS_007-Q003Atch03CONF.pdf.” • Rev. 13: “WMP-Discovery2026-2028_DR_OEIS_007-Q003Atch04CONF.pdf.” | Nathan Poon | 2025-04-29 | 2025-05-02 | 2025-05-02 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_007.zip | 4 | No | 8 | Grid Design, Operations, and Maintenance | 8.3.12.3 | Distribution - Overhead Equipment Inspections - Accomplishments, Roadblocks, and Updates
18 | 165 | SPD | 004 | SPD_004 | 1 | No | SPD_004_Q1 | List the locations in the 2026-2028 Base WMP where PG&E’s risk scaling function has been applied to the calculation of a value or risk, consequence, risk reduction, or CBR. a. If the values are in a figure, list the Figure number. b. If the values are in a table, list the Table Number. c. If the values are in the text of the 2026-2028 Base WMP, provide the sentence and the page number. d. SPD is aware that PG&E used a risk scaling function in its RAMP A.24-05-008. For each of a-c, describe if the risk scaling function used is the same as that described in the RAMP. If it is different, describe how the risk scaling function is different. | PG&E has identified the figures, tables, and text values below as utilizing the risk scaling function. a. The following are figures where a risk scaling function has been applied: • Figure PG&E-5.1.1-2 Risk Bow Tie for Wildfire Risk • Figure PG&E-5.1.1-3 Risk Bow Tie for PSPS Risk • Figure PG&E-5.1.1-4 Risk Bow Tie for EPSS • Figure PG&E-6.1.3.2-1 2026 Year Baseline (With and Without Operational Mitigation) • Figure 6-1 Projected Overall Service Territory Risk. b. The following are tables where a risk scaling function has been applied: • Table 5-5: Summary of Top Risk Circuit Segments • Table 6-1: PG&E Prioritized Areas Based on Overall Utility Risk • Table PG&E-6.1.3-1 Mitigation Effectiveness Alone and In Combination • Table 6-3: Risk Impact of Activities • Table 6-4 Summary of Risk Reduction for Top Risk Circuits • Table 8-1 Grid Design, Operation, and Maintenance Targets by Year • Table PG&E-8.2.1-3 Ignition Mitigation Effectiveness Representative Blended Average Values • Appendix F, Table 5-5 Summary of Top-Risk Circuits, Segments, or Spans • Appendix F, Table 6-1 PG&E Prioritized Areas Based on Overall Utility Risk • Appendix F, Table 6-4 Summary of Risk Reduction for Top Risk Circuits. c. The following are page numbers and sentences where a risk scaling function has been applied: d. The same risk scaling function from PG&E’s 2024 RAMP was used in the 2026-2028 Base WMP. | Eddie Schmitt | 2025-04-30 | 2025-05-30 | 2025-05-30 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_004.zip | 0 | No | 5 | Risk Methodology & Assessment | 5 | Risk Methodology and Assessment
18 | 166 | SPD | 004 | SPD_004 | 2 | No | SPD_004_Q2 | n an Administrative Law Judge Ruling dated April 22 2025 in the PG&E 2024 RAMP Proceeding (A.24-05-008), PG&E was directed to conduct a parallel risk evaluation using a risk-neutral, linear scaling function in preparation for PG&E’s 2027 GRC Rate Case. For each of the locations listed in 1a.-1c. provide a new calculation without applying PG&E’s risk scaling function. a. If the values are in a figure, recreate the figure without the scaling function applied to the calculation that generated the value(s) in the figure. b. If the values are in a table, recreate the table without the scaling function applied to the calculation that generated the value(s) in the table. c. If the values are in the text of the 2026-2028 Base WMP, provide the sentence with the new value that was generated without the scaling function being applied to the calculation. | Please see below for risk-neutral versions of the figures, tables, and text values identified in PG&E’s response to Question No. 1, below. Please note that PG&E is continuing to work to produce risk-neutral versions of some of the identified values and will supplement this response as soon as possible to provide them. a. The following figures are regenerated without a risk scaling function on the April 2025 vintage models for the 2026 Baseline: • Figure PG&E-5.1.1-2 Risk Bow Tie for Wildfire Risk (Risk Neutral, April 2025 vintage). • Figure PG&E-5.1.1-3 Risk Bow Tie for PSPS Risk (Risk Neutral, April 2025 vintage). • Figure PG&E-5.1.1-4 Risk Bow Tie for EPSS (Risk Neutral, April 2025 vintage). • Figure PG&E-6.1.3.2-1 2026 Year Baseline (With and Without Operational Mitigation). b. The following tables are regenerated without a risk scaling function: • Table PG&E-6.1.3-1 Mitigation Effectiveness Alone and In Combination • Table 6-3: Risk Impact of Activities • Table PG&E-8.2.1-3 Ignition Mitigation Effectiveness Representative Blended Average Values. • Appendix F, Table 5-5 Summary of Top-Risk Circuits, Segments, or Spans • Appendix F, Table 6-1 PG&E Prioritized Areas Based on Overall Utility Risk c. The following formulas and sentences are regenerated without a risk scaling function on the April 2025 vintage models for the 2026 Baseline: | Eddie Schmitt | 2025-04-30 | 2025-05-30 | 2025-05-30 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_004.zip | 0 | No | 5 | Risk Methodology & Assessment | 5 | Risk Methodology and Assessment
18 | 167 | SPD | 004 | SPD_004 | 3 | No | SPD_004_Q3 | List the locations in the 2026-2028 Base WMP where PG&E applied a territory-wide monetized value of electric reliability generated by the ICE (Interruption Cost Estimator) Calculator 1.0 to calculate a value or risk, consequence, risk reduction, or CBR. a. If the values are in a figure, list the Figure number. b. If the values are in a table, list the Table Number. c. If the values are in the text of the 2026-2028 Base WMP, provide the sentence and the page number | PG&E has identified the figures, tables, and text values below as utilizing an aggregated ICE 1.0 value. a. The following are figures where an aggregated ICE 1.0 value has been applied: • Figure PG&E-5.1.1-2 Risk Bow Tie for Wildfire Risk; • Figure PG&E-5.1.1-3 Risk Bow Tie for PSPS Risk; • Figure PG&E-5.1.1-4 Risk Bow Tie for EPSS; • Figure PG&E-6.1.3.2-1 2026 Year Baseline (With and Without Operational Mitigation); and • Figure 6-1 Projected Overall Service Territory Risk. b. The following are tables where an aggregated ICE 1.0 value has been applied: • Table 5-5 Summary of Top Risk Circuit Segments; • Table 6-1 PG&E Prioritized Areas Based on Overall Utility Risk; • Table 6-3 Risk Impact of Activities; • Table 6-4 Summary of Risk Reduction for Top Risk Circuits; WMP-Discovery 2026-2028_DR_SPD_004-Q003 Page 2 • Appendix F, Table 5-5 Summary of Top-Risk Circuits, Segments, or Spans; • Appendix F, Table 6-1 PG&E Prioritized Areas Based on Overall Utility Risk; and • Appendix F, Table 6-4 Summary of Risk Reduction for Top Risk Circuits. c. The following are page numbers and sentences where an aggregated ICE 1.0 value has been applied: | Eddie Schmitt | 2025-04-30 | 2025-06-20 | 2025-06-20 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_004.zip | 0 | No | 5 | Risk Methodology & Assessment | 5 | Risk Methodology and Assessment
18 | 168 | SPD | 004 | SPD_004 | 4 | No | SPD_004_Q4 | In an Administrative Law Judge Ruling dated April 22 2025 in the PG&E 2024 RAMP Proceeding (A.24-05-008), PG&E was directed to provide a parallel reliability cost calculation using the disaggregated approach recommended in the SPD Evaluation Report on PG&E’s 2024 RAMP Application in preparation for PG&E’s 2027 GRC Rate Case. For each of the locations listed in 3a.- 3c. provide a new calculation by applying the disaggregated approach recommended in the SPD Evaluation Report. a. If the values are in a figure, recreate the figure by applying the disaggregated approach recommended in the SPD Evaluation Report to the calculation that generated the value(s) in the figure. b. If the values are in a table, recreate the table by applying the disaggregated approach recommended in the SPD Evaluation Report to the calculation that generated the value(s) in the table. c. If the values are in the text of the 2026-2028 Base WMP, provide the sentence with the new value that was generated by applying the disaggregated approach recommended in the SPD Evaluation Report to the calculation. | a. The following figures are regenerated by applying the ICE 2.0 disaggregated values ($0.08/CMI for residential, $23.11/CMI for nonresidential) on the April 2025 vintage models for the 2026 Baseline: WMP-Discovery 2026-2028_DR_SPD_004-Q004 Page 2 • Figure PG&E-5.1.1-2 Risk Bow Tie for Wildfire Risk • Figure PG&E-5.1.1-3 Risk Bow Tie for PSPS Risk WMP-Discovery 2026-2028_DR_SPD_004-Q004 Page 3 • Figure PG&E-5.1.1-4 Risk Bow Tie for EPSS • Figure PG&E-6.1.3.2-1 2026 Year Baseline (With and Without Operational Mitigation) $19,398 $(15,863)$3,535 $1,464 $696 $5,695 Wildfire (pre-EPSS/PSPS)Wildfire Mitigation …Wildfire (post-EPSS/PSPS)PSPS ConsequenceEPSS ConsequenceWildfire + EPSS + PSPSMonetized Levels ( 2024 $ M)$-$5,000 $10,000 $15,000 $20,000 $25,000 Wildfire Risk with PSPS and EPSS(when applying ICE2.0 disaggregation) WMP-Discovery 2026-2028_DR_SPD_004-Q004 Page 4 • Figure 6-1 Projected Overall Service Territory Risk b. The following tables are regenerated by applying the ICE 2.0 disaggregated values ($0.08/CMI for residential, $23.11/CMI for nonresidential): 0% 20% 40% 60% 80% 100% 2023 2025 2027 2029 2031 2033 Projected Overall Utility Risk Year Residual Risk with Resiliency Mitigations Residual Risk with Resiliency and Operational Mitigations WMP-Discovery 2026-2028_DR_SPD_004-Q004 Page 5 • Table 6-3: Risk Impact of Activities | Eddie Schmitt | 2025-04-30 | 2025-06-20 | 2025-06-20 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_004.zip | 3 | No | 5 | Risk Methodology & Assessment | 5 | Risk Methodology and Assessment
18 | 169 | SPD | 004 | SPD_004 | 5(s) | Yes | SPD_004_Q5(s) | Fill in the data requested in the attached workbook titled “Decision Tree Results by Circuit Segment.xlsx”. This workbook is modeled upon the PGE_2023_WMP_R0_Section_642_Atch01.xlsx workbook that was submitted with the PG&E 2023-2025 Base WMP and the PG&E response to a CalAdvocates Data Request that included the workbook titled WMP-Discovery2023- 2025_DR_CalAdvocates_041-Q005Atch01.xlsx. a. Follow the Field Descriptions in the “Instruction” spreadsheet to complete the corresponding cells in the “Primary”, “S&S” and “DistTotal” spreadsheets. b. Responses in the “Primary” spreadsheet must be limited to the primary lines found on the corresponding “Circuit Segment Name” listed in Column A. c. Responses in the “S&S” spreadsheet must be limited to the secondary and service lines found on the corresponding “Circuit Segment Name” listed in Column A. d. Responses in the “DistTotal” spreadsheet must include both the primary, secondary and service lines found on the corresponding “Circuit Segment Name” listed in Column A. e. If any of the data requested in this dataset workbook would be impacted by the Administrative Law Judge Ruling described in Questions 1 and 3, provide a second version of this dataset using a risk-neutral, linear scaling function and using the disaggregated approach to reliability cost calculation recommended in the SPD Evaluation Report. | As indicated in the previous response to this question, PG&E is providing the following tranche-level data in attachment “WMP-Discovery2026-2028_DR_SPD_004-Q005Supp01Atch01.xlsx”, worksheet ‘EORM WLDFR Values’, ‘EORM EPSS Values’, ‘EORM PSPS Values’1: • Pre-Mitigated Ignition LoRE • Pre-Mitigated Ignition Safety CoRE (Natural Units) • Unscaled Ignition Pre-Mitigated Safety CoRE ($) • Pre-Mitigated Ignition Reliability CoRE (Natural Units) • Unscaled Pre-Mitigated Ignition Reliability CoRE ($) • Pre-Mitigated Ignition Financial CoRE (Natural Units) • Unscaled Pre-Mitigated Ignition Financial CoRE ($) • Unscaled Pre-Mitigated Ignition Risk ($) • Pre-Mitigated Outage Program LoRE • Pre-Mitigated Outage Program Safety CoRE (Natural Units) • Unscaled Outage Program Pre-Mitigated Safety CoRE ($) • Pre-Mitigated Outage Program Reliability CoRE (Natural Units) • Unscaled Pre-Mitigated Outage Program Reliability CoRE ($) • Pre-Mitigated Outage Program Financial CoRE (Natural Units) • Unscaled Pre-Mitigated Outage Program Financial CoRE ($) • Unscaled Pre-Mitigated Outage Program Risk ($) • Unscaled Pre-Mitigated Overall Risk ($). PG&E is also providing the mapping between circuit segments to tranches for WLDFR, EPSS, and PSPS in the respective ‘EORM WLDFR Mapping’, ‘EORM EPSS Mapping’, and ‘EORM PSPS Mapping’ tabs. The fields pertaining to “Ignition” would refer to the WLDFR mapping and WLDFR values. For the fields pertaining Outage Programs, refer to the EPSS and PSPS values and mapping. As indicated in the previous response to this question, PG&E is providing the following data in attachment “WMP-Discovery2026-2028_DR_SPD_004-Q005Supp01Atch01.xlsx”, worksheet ‘Primary’: • Miles of OH (columns AN:AS) • Miles of UG (columns AT:AY) • Miles of Line Removal (columns AZ:BE) • Total Miles of System Hardening (columns BF:BK) • Total Expenditure of OH Completed in Year (columns EF:EH) • Total Expenditure of UG Completed in Year (columns EL:EN) • Total Expenditure of Line Removal Completed in Year (columns ER:ET) • Total Expenditure of System Hardening Completed in Year (columns EX:EZ). Please note the following regarding the data provided: • The information provided includes PG&E’s System Hardening and Community Rebuild work. • The information reported in the provided template may not fully represent System Hardening and Rebuild work in its entirety because the provided circuit segment list is based on WDRM v4. There are miles and costs associated to circuit segments that are not present in the provided template, therefore that data is not included in this response. • Regarding expenditures: o Expenditure values reported are represented in thousands ($000). o The “Total Expenditure of System Hardening Completed in Year” field is not a direct sum of the preceding values of OH, UG, and Line Removal expenditure for that year. This value may include additional costs that are not part of the categories in the provided template, such as project management costs. o Forecasted 2026-2028 costs are currently not broken out into circuit segments. As an alternative, PG&E is providing program-level forecasts for these years. Values are represented as thousands ($000). Year Total OH Forecasted Expenditure ($000) Total UG Forecasted Expenditure ($000) Total Line Removal Forecasted Expenditure ($000) Total System Hardening Forecasted Expenditure ($000) 2026 $284,906 $1,153,619 $22,418 $1,460,943 2027 $197,265 $1,060,346 $17,607 $1,275,218 2028 $197,501 $1,184,019 $17,645 $1,399,165 o As a reminder, comparing the reported expenditures and the reported miles will not yield an accurate unit cost because a project’s costs may be spread across multiple years. Unit cost is calculated using total costs-since-inception (multi-year) and total miles completed (which can be multi-year) of the subprojects that are 100% complete in the associated year. Unit cost is not calculated by dividing the total program cost spent by the total miles completed in a given year because it would: ▪ Inaccurately include both the readiness/pre-construction costs for future subprojects that are not yet complete and the post-construction/closeout costs for previously completed subprojects; and ▪ Inaccurately include subprojects with partially completed miles at year-end. | Eddie Schmitt | 2025-04-30 | 2025-05-30 | 2025-05-30 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_004.zip | 1 | No | 5 | Risk Methodology & Assessment | 5.5.2 | Top Risk-Contributing Circuits/Segments/Spans
18 | 169 | SPD | 004 | SPD_004 | 5(s2) | Yes | SPD_004_Q5(s2) | Fill in the data requested in the attached workbook titled “Decision Tree Results by Circuit Segment.xlsx”. This workbook is modeled upon the PGE_2023_WMP_R0_Section_642_Atch01.xlsx workbook that was submitted with the PG&E 2023-2025 Base WMP and the PG&E response to a CalAdvocates Data Request that included the workbook titled WMP-Discovery2023- 2025_DR_CalAdvocates_041-Q005Atch01.xlsx. a. Follow the Field Descriptions in the “Instruction” spreadsheet to complete the corresponding cells in the “Primary”, “S&S” and “DistTotal” spreadsheets. b. Responses in the “Primary” spreadsheet must be limited to the primary lines found on the corresponding “Circuit Segment Name” listed in Column A. c. Responses in the “S&S” spreadsheet must be limited to the secondary and service lines found on the corresponding “Circuit Segment Name” listed in Column A. d. Responses in the “DistTotal” spreadsheet must include both the primary, secondary and service lines found on the corresponding “Circuit Segment Name” listed in Column A. e. If any of the data requested in this dataset workbook would be impacted by the Administrative Law Judge Ruling described in Questions 1 and 3, provide a second version of this dataset using a risk-neutral, linear scaling function and using the disaggregated approach to reliability cost calculation recommended in the SPD Evaluation Report. | PG&E is providing the following data in attachment “WMP-Discovery2026-2028_DR_SPD_004-Q005Supp02Atch01.xlsx,” worksheet “Primary:” • Miles of Tree Removal; WMP-Discovery 2026-2028_DR_SPD_004-Q005Supp02 Page 2 • Miles of Pole Clearing;1 • Total Expenditure of Tree Removal Completed in Year; and • Total Expenditure of Pole Clearing Completed in Year. Please note the following regarding the data provided: • As previously indicated, PG&E cannot unitize the “Tree Removal” or “Pole Clearing” mitigations by circuit mile. Instead, PG&E is providing the number of units mitigated per circuit segment per year. • As previously indicated, PG&E cannot provide data for 2026-2028 for these mitigations. However, please note that PG&E is providing a forecast of units and total expenditure (subject to the note below) for “Pole Clearing” for these years. These forecasts represent estimates only. • As previously indicated, PG&E cannot provide specific expenditures for these mitigations at a circuit segment level. Instead, PG&E has multiplied units completed per segment by average unit cost to populate the “Total Expenditure” fields. | Eddie Schmitt | 2025-04-30 | 2025-06-20 | 2025-06-20 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_004.zip | 1 | No | 5 | Risk Methodology & Assessment | 5.5.2 | Top Risk-Contributing Circuits/Segments/Spans
18 | 169 | SPD | 004 | SPD_004 | 5 | No | SPD_004_Q5 | Fill in the data requested in the attached workbook titled “Decision Tree Results by Circuit Segment.xlsx”. This workbook is modeled upon the PGE_2023_WMP_R0_Section_642_Atch01.xlsx workbook that was submitted with the PG&E 2023-2025 Base WMP and the PG&E response to a CalAdvocates Data Request that included the workbook titled WMP-Discovery2023- 2025_DR_CalAdvocates_041-Q005Atch01.xlsx. a. Follow the Field Descriptions in the “Instruction” spreadsheet to complete the corresponding cells in the “Primary”, “S&S” and “DistTotal” spreadsheets. b. Responses in the “Primary” spreadsheet must be limited to the primary lines found on the corresponding “Circuit Segment Name” listed in Column A. c. Responses in the “S&S” spreadsheet must be limited to the secondary and service lines found on the corresponding “Circuit Segment Name” listed in Column A. d. Responses in the “DistTotal” spreadsheet must include both the primary, secondary and service lines found on the corresponding “Circuit Segment Name” listed in Column A. e. If any of the data requested in this dataset workbook would be impacted by the Administrative Law Judge Ruling described in Questions 1 and 3, provide a second version of this dataset using a risk-neutral, linear scaling function and using the disaggregated approach to reliability cost calculation recommended in the SPD Evaluation Report. | Please see attachment “WMP-Discovery2026-2028_DR_SPD_004-Q005Atch01.xlsx.” In this delivery, PG&E is providing the data fields in the table below, subject to the following clarifications. As discussed at PG&E’s meeting with the SPD on May 9, 2025, PG&E is also providing its assessment of the fields that it has determined are not possible to provide as requested and what it proposes to provide in lieu of those fields. PG&E also provides a brief explanation of each field that PG&E has determined is not WMP-Discovery 2026-2028_DR_SPD_004-Q005 Page 2 possible to provide. Please note that, as PG&E’s subject matter experts continue to engage with this data request, further clarifications and challenges may emerge. Please note that PG&E is still determining the dates by which those fields not provided with this delivery or identified below can be produced. PG&E is working diligently to respond to this request and will endeavor to provide as many fields as reasonably possible on May 30, 2025. PG&E will provide updates to SPD as timelines are determined, and appreciates SPD’s patience. PG&E will endeavor to respond to this data request to the fullest extent possible. At this time, PG&E expects to provide the following fields on May 30, 2025: • Miles of OH • Miles of UG • Miles of Line Removal • Total Miles of System Hardening • Total Expenditure of OH Completed in Year • Total Expenditure of UG Completed in Year • Total Expenditure of Line Removal Completed in Year • Total Expenditure of system Hardening Completed in Year PG&E is still determining the dates by which those fields not provided with this delivery or identified here can be produced. Fields PG&E has Determined Are Impossible to Provide as Requested In addition to the limitations described below, please note that the following mitigation programs are not unitized by circuit mile and cannot be provided as such. Unless otherwise noted, PG&E will provide the total number of units mitigated per circuit segment: • Expulsion Fuse Replacement • Surge Arrestor Replacement • Aerial Inspection • Ground Inspection • Non-Pole Backlog • Tree Removal • Down Conductor Detection (DCD) • Line Sensors • Pole Backlog • Pole Clearing. Further, in addition to the limitations described below, please note that the following mitigation programs do not forecast work at the circuit-segment level. As a result, PG&E cannot provide the Units/Miles, Total Expenditure, or Present Value Cost for 2026, 2027, or 2028 for these mitigation programs: • Expulsion Fuse Replacement • Surge Arrestor Replacement • Aerial Inspection • Ground Inspection • Non-Pole Backlog • Tree Removal • Line Sensors • Pole Backlog • Pole Clearing. Further, in addition to the limitations described below, please note that, for the following mitigation programs, PG&E is unable to determine actual expenditure and present value cost of specific work done on a circuit segment. For these mitigation programs, PG&E will provide estimates for these fields based on the average cost to complete one unit of the mitigation program. • Expulsion Fuse Replacement • Surge Arrestor Replacement • Aerial Inspection • Ground Inspection • Non-Pole Backlog1 • Tree Removal • Line Sensors • Pole Backlog • Pole Clearing. Further, in addition to the limitations described below, PG&E does not track breakaway connector installations and cannot provide any fields related to this mitigation program. Finally, PG&E is still determining the feasibility of providing circuit-segment level CBR values. | Eddie Schmitt | 2025-04-30 | 2025-05-13 | 2025-05-13 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_004.zip | 1 | No | 5 | Risk Methodology & Assessment | 5.5.2 | Top Risk-Contributing Circuits/Segments/Spans
18 | 170 | SPD | 004 | SPD_004 | 6 | No | SPD_004_Q6 | Per PG&E’s response to Question 26c in SPD-PGE-WMP2026-001, where was Figure SRN-PG&E23-05-06C from PG&E’s 2023-2025 Base WMP published? | In our response to Question 26c in SPD-PGE-WMP2026-001 we inadvertently referenced SRN-PG&E- 23-05-06C. Figure SRN-PG&E-23-06 from PGE’s 2023-2025 Base WMP is PG&E’s System Hardening Decision Tree. PG&E showed the decision tree in its entirety and then separated the figure into two individual figures (Figure SRN-PG&E-23-06A and Figure SRN-PG&E-23-06B), three figures in total, because Figure SRN-PG&E-23-06 is difficult to read. When we responded to SPD-PGE-WMP2026-001, Question 26c we mistakenly referred to the three decision tree figures as SRN-PG&E- 23-05-06A, SRN-PG&E- 23-05-06B and SRN-PG&E- 23-05-06C. The decision tree was published in the 2023-2025 Base WMP. | Eddie Schmitt | 2025-04-30 | 2025-05-06 | 2025-05-06 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_004.zip | 0 | No | 5 | Risk Methodology & Assessment | 5.4 | Summary of Risk Models
18 | 171 | SPD | 004 | SPD_004 | 7 | No | SPD_004_Q7 | Provide copies of Figures SRN-PG&E-23-05-06A, SRN-PG&E-23-05-06B, SRN-PG&E-23-05-06C from PG&E’s 2023-2025 Base WMP in their native format. a. If the native format was not .pptx, convert all three figures into the .pptx format and provide them with this response. All objects and text in the figures must manipulatable in the .pptx format | See attached “WMP-Discovery2026-2028_DR_SPD_004-Q007Atch01.pptx”. The slides provided represent FIGURE SRN-PG&E-23-05-06, SRN-PG&E-23-05-06A, and SRNPG&E-23-05-06B. As noted in WMP-Discovery2026-2028_DR_SPD_004-Q006, SRNPG&E- 23-05-06C was inadvertently referenced. | Eddie Schmitt | 2025-04-30 | 2025-05-06 | 2025-05-06 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_004.zip | 1 | No | 5 | Risk Methodology & Assessment | 5.4 | Summary of Risk Models
18 | 172 | SPD | 004 | SPD_004 | 8(s) | Yes | SPD_004_Q8(s) | Provide copies of Figures PG&E-5.2.1-1, PG&E -5-2-1, PG&E 5-2-2, PG&E-5-2-3, PG&E-5-2-4, PG&E-5-2-5, PG&E-5.2.2.2-1, PG&E-6.1.3.1-4, PG&E-8-1-1, PG&E-8-1-2, PG&E-8.2.1-1, PG&E-8.2.1-2, and PG&E-8.2.1-3 in the 2026-2028 Base WMP in their native format. a. If the native format was not .pptx, convert all thirteen figures into the .pptx format and provide them with this response. All objects and text in the figures must manipulatable in the .pptx format. | Please see attachment “WMP-Discovery2026-2028_DR_SPD_004-Q008Supp01Atch01.pptx” for copies of Figures PG&E-5.2.1-1, PG&E -5-2-1, PG&E 5-2-2, PG&E-5-2-3, PG&E-5-2-4, PG&E-5-2-5, PG&E-5.2.2.2-1 in their native .pptx (PowerPoint) format. Figure PG&E-6.1.3.1-4 is included, but please note that Visio drawings cannot be converted into modifiable PowerPoint graphics, they can only be copied into PowerPoint as a picture. Figures PG&E-8-1-1 and PG&E-8-1-2 are also included, but please note that these figures were generated in a non-PowerPoint graphic design software and cannot be converted into modifiable PowerPoint graphics. Please see attachment “WMP-Discovery2026-2028_DR_SPD_004-Q008Supp01Atch02.vsdx” for a copy of Figure PG&E-6.1.3.1-4 in its native Visio (vsdx) format. Please see attachments “WMP-Discovery2026-2028_DR_SPD_004-Q008Supp01Atch03.png” and “WMP-Discovery2026-2028_DR_SPD_004-Q008Supp01Atch04.png” for copies of Figures PG&E-8-1-1 and PG&E-8-1-2 in their native format. | Eddie Schmitt | 2025-04-30 | 2025-05-30 | 2025-05-30 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_004.zip | 4 | No | 5 | Risk Methodology & Assessment | 5.2.1 | Risk and Risk Component Identification
18 | 172 | SPD | 004 | SPD_004 | 8 | No | SPD_004_Q8 | Provide copies of Figures PG&E-5.2.1-1, PG&E -5-2-1, PG&E 5-2-2, PG&E-5-2-3, PG&E-5-2-4, PG&E-5-2-5, PG&E-5.2.2.2-1, PG&E-6.1.3.1-4, PG&E-8-1-1, PG&E-8-1-2, PG&E-8.2.1-1, PG&E-8.2.1-2, and PG&E-8.2.1-3 in the 2026-2028 Base WMP in their native format. a. If the native format was not .pptx, convert all thirteen figures into the .pptx format and provide them with this response. All objects and text in the figures must manipulatable in the .pptx format. | Please see attachment “WMP-Discovery2026-2028_DR_SPD_004-Q008Atch01.pptx” for Figures PG&E-8.2.1-1, PG&E-8.2.1-2, and PG&E-8.2.1-3 in their native .pptx format. | Eddie Schmitt | 2025-04-30 | 2025-05-13 | 2025-05-13 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_004.zip | 1 | No | 5 | Risk Methodology & Assessment | 5.2.1 | Risk and Risk Component Identification
18 | 173 | SPD | 004 | SPD_004 | 9 | No | SPD_004_Q9 | Which bowtie workpaper was used to generate Figure PG&E-5.1.1-2 in the 2026-2028 Base WMP? a. Has this bowtie workpaper been updated since it was submitted with the 2024 RAMP Application? If so, explain how. b. If this bowtie workpaper was submitted with PG&E’s 2024 RAMP Application and has been updated since the 2024 RAMP Application, provide SPD with a copy of the updated workpaper. c. Provide the exact settings that were used on the bowtie workpaper to generate Figure PG&E-5.1.1-2 in the 2026-2028 Base WMP. d. How did this bowtie workpaper inform mitigation selection in this WMP? Provide a step-bystep example demonstrating how this bowtie workpaper informed and resulted in the mitigation selections on the circuit segment named CORNING 110185152. e. Figure 1-5 of the 2024 RAMP Application exhibited an exposure of 222,209 miles. Figure PG&E-5.1.1-2 of the 2026-2028 Base WMP exhibits an exposure of 472,475 miles. Explain why the number of miles increased from the 2024 RAMP to the 2026-2028 Base WMP. f. Does PG&E intend to update this bowtie workpaper, between now and when it submits its 2027 GRC? If so, explain how and why this bowtie workpaper will be updated between now and when PG&E submits its 2027 GRC. | The workpaper, Exhibit (PG&E-4) EO-WLDFR-2a_Bow Tie (System).xlsm, was provided in the RAMP application. An updated version was used to generate Figure PG&E-5.1.1-2 for the 2026-2028 Base WMP. a. Yes, this bowtie workpaper has been updated since it was submitted with the 2024 RAMP application. The updates include the following: WMP-Discovery 2026-2028_DR_SPD_004-Q009 Page 2 • Historical source data used to predict frequency and consequence of ignitions have been updated to include incidents from 2023 and 2024; • The WDRM used for distribution tranches has updated from version 3 to version 4; and • The EPSS and PSPS effectiveness as well as the EPSS multiplier have been updated. b. Please see attachment “WMP-Discovery2026-2028_DR_SPD_004- Q009Atch01.xlsm” for the requested document. c. Please refer to the sheet “Bowtie” in the attachment “WMP-Discovery2026- 2028_DR_SPD_004-Q009Atch01.xlsm”. The settings are defaulted to the following: d. The bowtie provides an overall picture of risk drivers and consequences. The tranche level is the most granular view. The enterprise risk model aggregates WDRM circuit segments into 42 tranches (10 HFRA Primary, 10 non-HFRA Primary, 10 HFRA Secondary, 10 HFRA Services, 1 non-HFRA Secondary, and 1 non-HFRA Services) of similar risk profiles. Most of the program workplans are developed at the circuit segment or circuit level and then mapped to the tranche level. The bowtie does not inform mitigation selection at the circuit segment level in the WMP. e. There was a cell reference error that caused the near doubling of exposure miles in the WMP graphic. The attachment provided corrects the error. The exposure miles should be 235,746 miles. f. Yes, the bowtie will be updated to include these updates: • The safety monetized value changes from $15.23 million to $16.2 million using the value of a statistical life from the Bureau of Labor Statistics, adjusted to California dollars. • The value of service increases from $3.17 to $3.33 based on PG&E 2024 recorded customer counts and consumption values. • Updated programs based on latest information. | Eddie Schmitt | 2025-04-30 | 2025-05-06 | 2025-05-06 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_004.zip | 1 | No | 5 | Risk Methodology & Assessment | 5.1.1 | Overview
18 | 174 | SPD | 004 | SPD_004 | 10 | No | SPD_004_Q10 | Which bowtie workpaper was used to generate Figure PG&E-5.1.1-3 in the 2026-2028 Base WMP? a. Has this bowtie workpaper been updated since it was submitted with the 2024 RAMP Application? If so, explain how. b. If this bowtie workpaper was submitted with PG&E’s 2024 RAMP Application and has been updated since the 2024 RAMP Application, provide SPD with a copy of the updated workpaper. c. Provide the exact settings that were used on the bowtie workpaper to generate Figure PG&E-5.1.1-3 in the 2026-2028 Base WMP. d. How did this bowtie workpaper inform mitigation selection in this WMP? Provide a step-bystep example demonstrating how this bowtie workpaper informed and resulted in the mitigation selections on CORNING 110185152. e. Figure 1-8 of the 2024 RAMP Application exhibited an exposure of 1,208,023 customers. Figure PG&E-5.1.1-3 of the 2026-2028 Base WMP exhibits an exposure of 611,246 customers. Explain why the number of customers decreased from the 2024 RAMP to the 2026-2028 Base WMP. f. Does PG&E intend to update this bowtie workpaper, between now and when it submits its 2027 GRC? If so, explain how and why this bowtie workpaper must be updated between now and when it submits its 2027 GRC. | d. The bowtie provides an overall picture of risk drivers and consequences. The tranche level is the most granular view. The enterprise risk model aggregates WDRM circuit segments into 42 tranches (10 HFRA Primary, 10 non-HFRA Primary, 10 HFRA Secondary, 10 HFRA Services, 1 non-HFRA Secondary, and 1 non-HFRA Services) of similar risk profiles. Most of the program workplans are developed at the circuit segment or circuit level and then mapped to the tranche level. The bowtie does not inform mitigation selection at the circuit segment level in the WMP. e. There was a cell reference error that caused the near doubling of exposure miles in the WMP graphic. The attachment provided corrects the error. The exposure miles should be 235,746 miles. f. Yes, the bowtie will be updated to include these updates: • The safety monetized value changes from $15.23 million to $16.2 million using the value of a statistical life from the Bureau of Labor Statistics, adjusted to California dollars. • The value of service increases from $3.17 to $3.33 based on PG&E 2024 recorded customer counts and consumption values. • Updated programs based on latest information. d. The bowtie provides an overall picture of risk drivers and consequences. The tranche level is the most granular view, which is grouped by customer classification (Extreme, Significant, Elevated, and Regular). It does not inform mitigation selection at the circuit segment level in the WMP. e. The reason for the decrease in exposure is due to removing the PotentiallyImpacted Customers (PIC) dataset and using PSPS 5.0 Guidance for the lookback events and including the years 2023 and 2024. PSPS events are smaller in size and less frequent as our PSPS guidance evolves. f. Yes, the bowtie will be updated to include these updates: • Corrections to the PSPS lookback analysis. • The safety monetized value changes from $15.23 million to $16.2 million using the value of a statistical life from the Bureau of Labor Statistics, adjusted to California dollars. • The value of service increases from $3.17 to $3.33 based on PG&E 2024 recorded customer counts and consumption values. • Updated programs based on latest information. | Eddie Schmitt | 2025-04-30 | 2025-05-06 | 2025-05-06 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_004.zip | 1 | No | 5 | Risk Methodology & Assessment | 5.1.1 | Overview
18 | 175 | SPD | 004 | SPD_004 | 11 | No | SPD_004_Q11 | Which bowtie workpaper was used to generate Figure PG&E-5.1.1-4 in the 2026-2028 Base WMP? a. Has this bowtie workpaper been updated since it was submitted with the 2024 RAMP Application? If so, explain how. b. If this bowtie workpaper was submitted with PG&E’s 2024 RAMP Application and has been updated since the 2024 RAMP Application, provide SPD with a copy of the updated workpaper. c. Provide the exact settings that were used on the bowtie workpaper to generate Figure PG&E-5.1.1-4 in the 2026-2028 Base WMP. d. How did this bowtie workpaper inform mitigation selection in this WMP? Provide a step-bystep example demonstrating how this bowtie workpaper informed and resulted in the mitigation selections on CORNING 110185152. e. Figure 1-9 of the 2024 RAMP Application exhibited an exposure of 43,433 miles. Figure PG&E-5.1.1-4 of the 2026-2028 Base WMP exhibits an exposure of 43,506 miles. Explain why the number of miles increased from the 2024 RAMP to the 2026-2028 Base WMP. f. Does PG&E intend to update this bowtie workpaper, between now and when it submits its 2027 GRC? If so, explain how and why this bowtie workpaper must be updated between now and when it submits its 2027 GRC. | The workpaper, Exhibit (PG&E-4) EO-WEPSS-2_Bow tie.xlsm, was provided in the RAMP application. An updated version was used to generate Figure PG&E-5.1.1-4 for the 2026-2028 Base WMP. a. Yes, this bowtie workpaper has been updated since it was submitted with the 2024 RAMP application. The updates include the following: WMP-Discovery 2026-2028_DR_SPD_004-Q011 Page 2 • The 2026-2028 Base WMP version of the bowtie includes updated outage data to include 2023 and 2024 whenever applicable. • The WDRM used for developing tranches has been updated from version 3 to version 4. • EPSS lookback analysis is updated based on Fire Potential Index (FPI) version 5. • The EPSS multiplier has been updated from 6.8 to 5.9. b. Please see attachment “WMP-Discovery2026-2028_DR_SPD_004- Q011Atch01.xlsm” for the requested document. c. Please refer to the sheet “Bowtie” in the attachment “WMP-Discovery2026- 2028_DR_SPD_004-Q011Atch01.xlsm”. The settings are defaulted to the following: d. The bowtie provides an overall picture of risk drivers and consequences. The tranche level is the most granular view. The tranche is a group of circuit segments of similar risk profile. Most of the program workplans are developed at the circuit segment or circuit level and then mapped to the tranche level. It does not inform mitigation selection at the circuit segment level in the WMP. e. The RAMP Workpaper is based on older vintage of GIS data that informs our exposure mapping. The marginal change in exposure miles is from using updated version of the GIS data. f. Yes, the bowtie will be updated to include these updates: • The monetized safety value changes from $15.23 million to $16.2 million using the value of a statistical life from the Bureau of Labor Statistics, adjusted to California dollars. • The value of service increases from $3.17 to $3.33 based on PG&E 2024 recorded customer counts and consumption values. • Updated programs based on the latest information | Eddie Schmitt | 2025-04-30 | 2025-05-06 | 2025-05-06 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_004.zip | 1 | No | 5 | Risk Methodology & Assessment | 5.1.1 | Overview
18 | 176 | SPD | 004 | SPD_004 | 12 | No | SPD_004_Q12 | Question 11e. highlights a marginal change in exposure for EPSS risk between the 2024 RAMP and 2026-2028 Base WMP filings. Questions 9e and 10e highlight a significant change in exposure for Wildfire and PSPS risk between the 2024 RAMP and 2026-2028 Base WMP filings. Explain why exposure to EPSS risk exhibits a marginal change, despite significant changes in the exposure to Wildfire and PSPS risk. a. The significant decrease in exposure to PSPS risk highlighted in Question 10e resulted in a significant decrease in risk value between the 2024 RAMP and 2026-2028 Base WMP filings.1 The significant increase in exposure to Wildfire risk highlighted in Question 9e did not result in a significant increase in risk value between the 2024 RAMP and 2026-2028 Base WMP filings.2 Explain why the change in exposure to PSPS risk resulted in a corresponding change in risk value, but the change in exposure to Wildfire risk did not result in a corresponding change in risk value. | EPSS risk is quantified as the difference between the Failure of Distribution Overhead Assets risk with and without EPSS. EPSS exposure is the mileage of overhead primary circuits that are EPSS capable. EPSS capable means the circuits could have EPSS enabled when the enablement criteria are met. Marginal change in EPSS exposure resulted in marginal change in EPSS risk. EPSS risk is not directly correlated to Wildfire and PSPS. a. PSPS risk had changes in customer count to drive a significant decrease in risk value. The Wildfire exposure is an error and should have read 235,746 miles. | Eddie Schmitt | 2025-04-30 | 2025-05-06 | 2025-05-06 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_004.zip | 0 | No | Appendix D | Appendix D: Areas of Continued Improvement | ACI PG&E-25U-06 | Evaluation and Reporting of Safety Impacts Relating to EPSS
18 | 177 | SPD | 004 | SPD_004 | 13 | No | SPD_004_Q13 | Explain why the x% of Ignitions in HFTD/HFRA column in Table 3-1 in the PG&E 2026-2028 Base WMP does not total to 100%. | In reviewing Table 3-1 submitted in the WMP, we determined that a non-final version of the table was included. The correct version of Table 3-1 is provided below. Please note, due to rounding of numbers, the total percentage of ignitions in HFTD/HFRA equals 100.1%. | Eddie Schmitt | 2025-04-30 | 2025-05-06 | 2025-05-06 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_004.zip | 0 | No | 3 | Overview of WMP | 3.4 | Prioritized List of Wildfire Risks and Risk Drivers
18 | 178 | SPD | 004 | SPD_004 | 14 | No | SPD_004_Q14 | Table 4-1 in 6th Revision of the PG&E 2023-2025 Base WMP shows a ramp up in expenditures from 2020-2022 and from 2023-2025. Table 3-3 in the PG&E 2026-2028 Base WMP, shows a similar ramp up in expenditures. a. Explain what causes the low forecasts in the first year of each WMP. b. Explain what caused the significant variances in 2020-2022 in Table 4-1 from the 6th Revision of the PG&E 2023-2025 Base WMP. c. Provide an update to Table 4-1 from the 6th Revision of the PG&E 2023-2025 Base WMP that includes the actuals and variance for 2023 and 2024. d. Provide an explanation for any variances in the update created in response to Question 14c. | a. The forecast for each year is driven by the workplan and target commitments for wildfire mitigation work. As the workplan increases, so does the forecast. b. Please refer to the explanations provided in PG&E’s Annual Report on Compliance (ARC), which is included here as attachments “WMP-Discovery2026-2028_DR_SPD_004-Q014Atch01.xlsx” and “WMP-Discovery2026-2028_DR_SPD_004-Q014Atch02.pdf”. c. Please refer to attachment “WMP-Discovery2026-2028_DR_SPD_004-Q014Atch01.xlsx” for the updated Actual amounts for 2023 and 2024 and updated plan for 2025. d. The variance explanations can be found in the ARC report for each year. | Eddie Schmitt | 2025-04-30 | 2025-05-13 | 2025-05-13 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_004.zip | 2 | No | 3 | Overview of WMP | 3.6 | Projected Expenditures
18 | 179 | SPD | 004 | SPD_004 | 15 | No | SPD_004_Q15 | Pg. 135 explains each of the elements in the waterfall figure PG&E-6.1.3.2-1 in the 2026-2028 Base WMP. PG&E states that Wildfire (pre-EPSS/PSPS) is the “inherent wildfire risk based on the data from 2017 to 2024, absent of the use of PSPS and EPSS operational mitigations”. a. Was the Wildfire (pre-EPSS/PSPS) calculated as a product of LoRE and CoRE? b. Explain why PSPS Consequence and EPSS Consequence were included in this figure, rather than PSPS Risk and EPSS Risk. i. Explain why PG&E did not use the product of LoRE and CoRE for PSPS and EPSS when generating this figure. | a. Yes, Wildfire (pre-EPSS/PSPS) is calculated as a product of LoRE and CoRE. The pre-EPSS/PSPS Wildfire LoRE is 945.66 events per year and the CoRE is $20.7M, resulting in approximately $19,578M as the risk value. b. In this instance, the terms “PSPS Consequence” and “EPSS Consequence” are interchangeable with “PSPS Risk” and “EPSS Risk.” i. PSPS Consequence and EPSS Consequence is still the product of LoRE and CoRE. PSPS LoRE is 3.286 events per year and the CoRE is $594M, resulting in approximately $1,953M as the risk value. EPSS Consequence is 2,467 events per year and the CoRE is $0.425M, resulting in approximately $1,049M as the risk value. | Eddie Schmitt | 2025-04-30 | 2025-05-13 | 2025-05-13 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_004.zip | 0 | No | 6 | Wildfire Mitigation Strategy Development | 6.1.3 | Activity Selection Process
18 | 180 | SPD | 004 | SPD_004 | 16 | No | SPD_004_Q16 | Provide a copy of Figure 1-2 in PG&E-4 Chapter 1 of the PG&E 2024 RAMP without the scaling function (a neutral risk attitude). a. Explain any variances in the values displayed in the Figure 1-2 without the scaling function when compared with PG&E’s response to WMP-Discovery2026-2028_DR_MGRA_003- Q007. | Please see the attachment “WMP-Discovery2026-2028_DR_SPD_004-Q016Atch01.xlsx” for the requested information. WMP-Discovery 2026-2028_DR_SPD_004-Q016 Page 2 a. The variances between the two charts are from 1) the differences in the year: RAMP chart shows the TY Baseline for 2027 while MGRA Discovery and WMP chart shows Baseline for 2026; and 2) the various updates made to the inputs to the risk models since RAMP filing. The table below outlines the key changes leading to variances between the two charts: | Eddie Schmitt | 2025-04-30 | 2025-05-13 | 2025-05-13 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_004.zip | 1 | No | 6 | Wildfire Mitigation Strategy Development | 6.1.3.2 | Activity Prioritization
18 | 181 | SPD | 004 | SPD_004 | 17 | No | SPD_004_Q17 | In Question 1c of PG&E’s data request response to titled WMP-Discovery2026- 2028_DR_TURN_002-Q001, PG&E said that “The inclusion of PICs results in an increased risk associated with customers in locations where PSPS thresholds were not met in our historical lookback, but have exposure to PSPS risk based on HFTD/HFRA location and system configuration.” a. What does HFTD/HFRA location mean in this sentence? i. Does PG&E mean that every customer living within the HFTD/HFRA was included in the historical lookback? ii. Does this include customers who might be downstream of circuit segment that is exposed to PSPS risk? b. Define “system configuration”. c. Include a list of the components that were considered within the “system configuration” and explain their relationship to PSPS thresholds. d. List each procedural step used to determine whether customers were exposed to PSPS risk based on HFTD/HFRA location and system configuration. Provide an explanation for each step. | a. HFTD/HFRA refers to the applicable HFRA version at the time of the lookback analysis. i. No. Customers living within the HFTD/HFRA were included in the Potentially Impacted Customers dataset, not in the historical lookback dataset. HFTD/HFRA customers included in the historical lookback dataset would have to have met the PSPS 5.0 Guidance threshold. ii. Yes. Customers who might be downstream of a circuit segment in HFRA would be included. WMP-Discovery 2026-2028_DR_SPD_004-Q017 Page 2 b. System configuration in this sentence refers to customers who might be physically located in non-HFRA but are included because they are downstream of a circuit segment in HFRA that would have been de-energized. c. Please see PG&E’s response to subpart (b) regarding the definition of “system configuration” in this context. “System configuration” does not have “components” or impact on PSPS thresholds. PSPS thresholds may have an impact on which customers may be de-energized (in context of the historical lookback not PIC) due to system configuration. d. The process for PIC is the same process for historical PSPS lookback analyses, however, there is no PSPS thresholds and the “weather polygon” is the latest approved HFRA version. Circuit segments that are within HFRA are included, as well as any downstream customers that would be affected by a de-energization. Any commonly used mitigations like microgrids and backfeeds, if applicable, would be assumed to operate, so those customers would be mitigated in the PIC dataset. | Eddie Schmitt | 2025-04-30 | 2025-05-13 | 2025-05-13 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_004.zip | 0 | No | 5 | Risk Methodology & Assessment | 5.2.1 | Risk and Risk Component Identification
18 | 182 | SPD | 004 | SPD_004 | 18 | No | SPD_004_Q18 | PG&E’s Response to TURN-PG&E-3 Question 1 stated that with regard to the risk score in the attached datasets (e.g. WMP-Discovery2026-2028_DR_TURN_003-Q001Atch02CONF.xlsx), PG&E replaced the previously provided “mean risk score” with the “estimated wildfire risk reduction”. Provide an example for a subproject where both the “mean risk score” and “estimated wildfire risk reduction” is calculated. | Please see attachment “WMP-Discovery2026-2028_DR_SPD_004- Q018Atch01CONF.xlsx” for an example of wildfire risk reduction and mean risk for multiple subprojects on the same circuit segment. This appends a new column (Column S) to the previous attachment “WMPDiscovery2026-2028_DR_TURN_003-Q001Atch02CONF.xlsx” for one sample circuit segment. PG&E originally included estimated wildfire risk reduction for each subproject because this is an indicator of absolute risk reduction to be achieved by the subproject. The mean risk is the total risk score divided by the number of primary overhead miles on a circuit segment and is an indicator of the risk density of a subproject. It does not consider the total risk exposure associated with the length of the subproject. | Eddie Schmitt | 2025-04-30 | 2025-05-06 | 2025-05-06 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_004.zip | 1 | No | 5 | Risk Methodology & Assessment | 5.4 | Summary of Risk Models
18 | 183 | SPD | 004 | SPD_004 | 19 | No | SPD_004_Q19 | PG&E’s Response to TURN-PG&E-3 Question 1 included the dataset titled WMP-Discovery2026- 2028_DR_TURN_003-Q001Atch02CONF.xlsx. PG&E’s Response to SPD-PGE-WMP2026-001 Question 2 included the same dataset titled WMP-Discovery2026-2028_DR_SPD_001- Q002Supp01Atch01CONF.xlsx. Why do these datasets include TBD Orders where the Applicable Risk Model is Version 2 and Version 3? a. Why do these TBD Orders exhibit a pre-scoping status? b. Why do these TBD Orders only report Forecast UG Miles in 2027? c. Will WDRM v2 and v3 be used to scope projects that are Forecasted for 2028? If so, explain why. | “TBD” orders with an applicable risk model of v2 and v3 represent circuit protection zones (CPZs) which were originally identified for scoping when the applicable risk model was v2 or v3 at the time. These TBD orders fall into three categories: 1. On Hold Projects: Projects on these CPZs were paused following the 2023-2026 GRC decision. They will remain in a pre-scoping status and be re-evaluated and rescoped under WDRM v4. There are 2 CPZs in this category representing approximately 37 miles. 2. Carryover Projects: These CPZs represent projects that will carry over from the current GRC period and will remain as v2 or v3 projects. The pre-scoping status was an error. There are six CPZs in this category representing approximately 5.6 miles. 3. Inadvertently Included: These CPZs were initially identified as potential undergrounding projects due to mitigations being previously planned on a portion of the CPZ prior to 2027. The high-level workplan was developed based on the assumption that remaining mileage on these CPZs should be mitigated. For TBD orders in category 3, these projects were inadvertently included and will not be pursued as part of PG&E’s 2027 workplan. There are four CPZs in this category representing less than 1 mile of work and 0.00085% risk reduction. Based on the current scoping process described by the System Hardening Project Scoping Decisions Trees: Figures PG&E-8.2.1-1, PG&E-8.2.1-2, and PG&E-8.2.1-3, these projects would not have met the WDRM V4 criteria for inclusion in the work plan, and would not have proceeded beyond their inadvertent inclusion in this high-level workplan. For categorization of each of the CPZs with TBD orders in v2 and v3, please reference the table below: a. At the time of PG&E’s WMP submission, the 2027 and 2028 work plan had not yet been fully scoped. For purposes of estimating risk reduction associated with PG&E’s GH-04 WMP initiative mileage target, PG&E identified a list of circuit segments that would be considered for scoping and thus when producing attachment WMPDiscovery2026-2028_DR_SPD_001- Q002Supp01Atch01CONF.xlsx all line items with an end date in 2027 or 2028 were listed with a “pre-scoping” status. The workplan is dynamic and will continue to evolve as work is scoped in accordance with the System Hardening Project Scoping Decisions Trees provided in the WMP Figures PG&E-8.2.1-1, PG&E-8.2.1- 2, and PG&E-8.2.1-3. b. These TBD orders are only reported in 2027 because they were identified as part of the 2027 workplan. c. No, WDRM v2/v3 will not be used to scope projects forecasted for 2028 and beyond. However, if a project selected using v2 or v3 is delayed, it may carry over into 2028 and beyond. | Eddie Schmitt | 2025-04-30 | 2025-05-09 | 2025-05-09 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_004.zip | 0 | No | 5 | Risk Methodology & Assessment | 5.4 | Summary of Risk Models
18 | 184 | SPD | 004 | SPD_004 | 20 | No | SPD_004_Q20 | PG&E’s Response to SPD-PGE-WMP2026-003 Question 9 included Tables 1, 2 and 3. Provide Excel versions of these tables. a. Confirm that the Advice Letter PG&E referred to in response to SPD-PGE-WMP2026-003 Question 9 was not “PG&E Advice 7130 E-A” but rather PG&E Advice 7150 E-A. b. Include the “Workplan Detail” Worksheet that was used to generate Tables 1 and 2 and is required by PG&E Advice 7150 E-A. c. Include the worksheet that PG&E used to generate Table 3. d. Ensure that all of the cells in Tables 1, 2 and 3 include formulas for calculating each number by referencing the worksheets requested in Questions 20b and 20c. e. Check the submitted Table 1 – some cells appear merged when in fact they should not be merged. For instance, for WDRM v2 total where Mitigation Type is listed as Line Removal the Total and 2026 are merged. Correct the table or explain why the cells are merged. i. Similarly, some cells appear to be split – for instance for 2023, there are two values for many of the mitigation types. | Please see attachment “WMP-Discovery2026-2028_DR_SPD_004-Q020Atch01.xlsx”, worksheet “Summary FINAL_WMP_Discovery”. a. Yes, PG&E intended to reference PG&E Advice 7150 E-A in response to SPD-PGE-WMP2026-003 Question 9. b. See attached “WMP-Discovery2026-2028_DR_SPD_004-Q020Atch01.xlsx” – Project Details, 2025 + 2026 UG, 2025 + 2026 OH, and 2025 + 2026 LR Tabs. c. See attached “WMP-Discovery2026-2028_DR_SPD_004-Q020Atch01.xlsx” – Project Details and the 2026 Workplans Tabs. WMP-Discovery 2026-2028_DR_SPD_004-Q020 Page 2 d. See attached “WMP-Discovery2026-2028_DR_SPD_004-Q020Atch01.xlsx”, each calculation includes the requested formula. e. Merged cells in the attached “WMP-Discovery2026-2028_DR_SPD_004- Q020Atch01.xlsx” have been corrected. i. Split cells in the attached “WMP-Discovery2026-2028_DR_SPD_004- Q020Atch01.xlsx” have been corrected. Please note that in the attachment, PG&E has included “unallocated” risk reduction for circuit segments that have been fully mitigated, but where discrepancies exist between circuit segment length data (as specified in the applicable version of the WDRM) and field as-built data. For example, unallocated overhead removal occurs when the mitigation footage recorded in our as-built dataset is less than the total length of the original overhead line being mitigated. As an example, this can occur when a moredirect route with fewer bends than the original route is installed. Although the risk associated with the original overhead line is still addressed, it may not be reflected under the three mitigation categories (OH, UG, or Removal). To ensure every part of the original overhead line is accounted for in the risk reduction calculation, this “unallocated” difference must be included for a comprehensive assessment. | Eddie Schmitt | 2025-04-30 | 2025-05-06 | 2025-05-06 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_004.zip | 1 | No | GH-04 | GH-04 | GH-04 | GH-04
18 | 185 | SPD | 004 | SPD_004 | 21 | No | SPD_004_Q21 | Figure PG&E-5-2-1 in the 2026-2028 Base WMP presents “Outage Probability Vegetation” as a Model. Section 3.5.2.3 Distribution Event Probability Models Version 4 (DEPM v4) Documentation is dedicated to describing “Vegetation Models”. Pg. 60 presents “asset-based event models” and “contact from object” models but does not present “vegetations models.” Does the “contact from object” description apply to “vegetation models?” If not: a. Why are vegetation models not discussed on pg. 60 of the 2026-2028 Base WMP? b. How are vegetation models integrated into the calculation of probability of ignition given outage? c. Compared with the Asset Equipment or Contact from Object models, are there any differences in how vegetation models are integrated into the calculation of probability of ignition? If so, list them and explain why there are differences. | a. PG&E categorizes “vegetation models” within “contact from object” models (i.e. vegetation contacted the lines). Thus, vegetation models, which are pixel-based, are described on page 60 of the WMP as part of the description of contact from object models. b. Vegetation models are integrated as described for “contact from object” models, which are all pixel-based. c. Vegetation models are integrated as described for “contact from object” models, which are all pixel-based. | Eddie Schmitt | 2025-04-30 | 2025-05-13 | 2025-05-13 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_004.zip | 0 | No | 5 | Risk Methodology & Assessment | 5.2.1 | Risk and Risk Component Identification
18 | 186 | SPD | 004 | SPD_004 | 22 | No | SPD_004_Q22 | Provide a description of each of the alphanumeric customer categories listed in Table PG&E 5.2.2.2- 2 in the 2026-2028 Base WMP. a. Include in the description an explanation of how PG&E established each category. b. What justification did PG&E use to establish the relative customer weightings? PG&E explains that CC1 has higher consequence, but why is “Extreme” weighted 20x more than “Significant?” | a. PG&E categorizes Critical Customers according to both the California Public Utilities Commission (CPUC) definition and PG&E’s internal designations. See table below for description and explanation of how PG&E established each category: b. The relative customer weightings provided in Table PG&E 5.2.2.2-2 were derived from discussions with Customer Care and PG&E’s Wildfire Risk team as a starting point to integrate weightings into the different types of critical customers. PG&E subject matter experts used their best judgment to develop the relative weighting multipliers. For example, “Extreme” is weighted 20x higher than “Significant” because PG&E’s subject matter experts determined that public emergency response infrastructure warranted such relative prioritization. | Eddie Schmitt | 2025-04-30 | 2025-05-13 | 2025-05-13 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_004.zip | 0 | No | 5 | Risk Methodology & Assessment | 5.2.2.2 | Consequence of Risk Event
18 | 187 | SPD | 004 | SPD_004 | 23 | No | SPD_004_Q23 | Related to Figure PG&E 5.2.2.3-1 in the 2026-2028 Base WMP, on pg. 72, PG&E states “…the two circuit segments share a common pixel, F6, and a that support structure (pole) asset also located in pixel F6. To keep the total sum of risk on the network constant, these shared risk results must be partially distributed to each of the circuit segments. The aggregation methodology, in this case, would assign half of the F6 pixel risk and half of the support structure risk to each of the circuit segments.” a. Submit “RaDA Algorithms and Methodologies” b. If not explained in “RaDA Algorithms and Methodologies” please explain: i. Why, in this example, was the risk distributed to each of the circuit segments equally? ii. Are there instances where the risk is not distributed equally? a) If so, explain what those instances would be and how PG&E determines the proportion of risk that should be attributed to each circuit segment. Provide examples from a specific circuit segment. b) If not, explain why. c. Are there instances of a pixel sharing more than two circuit segments? i. If so, explain why a pixel can share more than two circuit segments. Provide examples by citing circuit segment names. ii. If not, explain why not | a. Please see attachment “WMP-Discovery2026-2028_DR_SPD_004-Q023Atch01.pdf” for the requested information. | Eddie Schmitt | 2025-04-30 | 2025-05-06 | 2025-05-06 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_004.zip | 1 | No | 5 | Risk Methodology & Assessment | 5.2.2.2 | Consequence of Risk Event
18 | 187 | SPD | 004 | SPD_004 | 23(s) | Yes | SPD_004_Q23(s) | Related to Figure PG&E 5.2.2.3-1 in the 2026-2028 Base WMP, on pg. 72, PG&E states “…the two circuit segments share a common pixel, F6, and a that support structure (pole) asset also located in pixel F6. To keep the total sum of risk on the network constant, these shared risk results must be partially distributed to each of the circuit segments. The aggregation methodology, in this case, would assign half of the F6 pixel risk and half of the support structure risk to each of the circuit segments.” a. Submit “RaDA Algorithms and Methodologies” b. If not explained in “RaDA Algorithms and Methodologies” please explain: i. Why, in this example, was the risk distributed to each of the circuit segments equally? ii. Are there instances where the risk is not distributed equally? a) If so, explain what those instances would be and how PG&E determines the proportion of risk that should be attributed to each circuit segment. Provide examples from a specific circuit segment. b) If not, explain why. c. Are there instances of a pixel sharing more than two circuit segments? i. If so, explain why a pixel can share more than two circuit segments. Provide examples by citing circuit segment names. ii. If not, explain why not | b. Section 4.2 of “RaDA Algorithms and Methodologies” explains circuit segment aggregation of pixel and asset risk. i. MaxEnt models produce risk values for each pixel location that contains one or more assets. However, when a pixel is intersected by multiple circuit segments, it is very difficult to understand which circuit segment might be impacted by a failure event. For example, if a branch falls near a pole that supports multiple primary conductors that belong to two different circuit segments, the branch may cause a failure to the first circuit segment, the second circuit segment or both circuit segments. Since there is no way to know a specific outcome until the event occurs, the risk of the event is distributed evenly to the two circuit segments as the best estimate of future risk. ii. Shared pixel risk is always distributed equally. There are no instances of inequal distribution. a) Risk from shared pixels is always distributed equally. b) Explained in answer (i) above. c. There are many pixels that are intersected by more than two circuit segments. i. Pixels that are intersected by more than two circuit segments can typically be found near substations. An example of a pixel with more than two intersecting circuit segments is Pixel 4356_1929, located in Vallejo: Pixel 4356_1929 is intersected by three circuit segments VALLEJO B 1102CB: VALLEJO B 1101CB: VALLEJO B 0415CB ii. A pixel can be intersected by more than two circuit segments as demonstrated above. | Eddie Schmitt | 2025-04-30 | 2025-05-30 | 2025-05-30 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_004.zip | 1 | No | 5 | Risk Methodology & Assessment | 5.2.2.2 | Consequence of Risk Event
18 | 188 | SPD | 004 | SPD_004 | 24 | No | SPD_004_Q24 | When discussing PSPS Risk on pages 74-75 in the 2026-2028 Base WMP, PG&E states that “…PSPS likelihood and PSPS consequence are calculated by the probability and consequence of each individual customer service_point_ID (SPID).” Describe each step in the procedure that PG&E takes to estimate the PSPS likelihood and consequence of each individual customer service_point_ID. a. Explain how PG&E predicts where PSPS events will occur for customers that PG&E has not had a PSPS event. b. Explain how PG&E uses each of the Model Inputs listed in Figure PG&E-B-1.3 to estimate PSPS likelihood for each individual customer service_point_ID. c. Page 68 notes that the “combination of weather, switching, and restoration is represented as total CMI”. Are the values associated with weather, switching and restoration measured in CMI and just added together? Additionally, explain the following: i. How does PG&E estimate the severity of an expected weather period in which a customer is expected to be de-energized? ii. How did PG&E come up with the estimate that patrol and restoration typically take 11 hours? iii. Why did PG&E not use Estimated Time of Restoration? | a. PG&E’s Outage PSPS Risk model does not predict future PSPS events in the traditional sense. Instead, it uses a data-driven approach that incorporates both historical and forecasted event data to estimate risk at the individual customer service_point_ID (SPID) level that has seen a PSPS outage in the past. b. The lookback events are leveraged by utilizing the frequency of events. The lookback includes all potential weather events and identifies the customer impacted and duration. In addition, the lookback also identifies what type of event it was (i.e. Dx only, Tx only, Dx/Tx). Additionally, a customer weighting is applied to prioritize customers at higher risk. Essentially, there is a risk for each historical customer event, and that can be aggregated to the granularity of a customer, isolation zone, CPZ, or circuit. c. Yes, the values associated with weather, switching and restoration measured in Customer Minutes Interrupted (CMI) are added together. i. PG&E estimates severity through PG&E's Meteorology models and historic weather events. ii. This is a historical average over a few years; it was used to reflect a value as close to reality as possible, and it is included in the lookback events data as part of the total outage duration. iii. PG&E didn’t use Estimated Time of Restoration (ETOR) because the default value in the lookback dataset is a placeholder (24 hours after All Clear) which is a conservative estimate. For real PSPS events, this gets updated based on actual conditions like terrain, daylight, and crew availability. But for hypothetical lookback events, no such updates were made. Also, ETOR reflects the time to restore the last customer on a Time Place (TP), which overstates the average restoration time for most customers. So, using it would misrepresent the typical customer experience. | Eddie Schmitt | 2025-04-30 | 2025-05-30 | 2025-05-30 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_004.zip | 0 | No | 7 | Public Safety Power Shutoff | 7 | Public Safety Power Shutoff
18 | 189 | SPD | 004 | SPD_004 | 25 | No | SPD_004_Q25 | In its description of CoRE on page 56 in the 2026-2028 Base WMP, PG&E states “Our perspective is that the Burn Probability is a deterministic assessment of local conditions at the time of an ignition event rather than a probabilistic outcome.” There is no mention of Burn Probability in the Wildfire Consequence Model Version 4 (WFC v4) Documentation. Provide a step-by-step description of PG&E’s deterministic assessment of Burn Probability. a. If PG&E’s deterministic assessment of Burn Probability is conducted with SME judgement, list the criteria SME’s are required to consider in their assessment. b. If PG&E’s deterministic assessment of Burn Probability is conducted with SME judgement, explain how many SMEs participated in an estimation of Burn Probability based on the local conditions for each circuit segment. | Clarification of the terminology used in the documentation. Those paragraphs are intended to link the terminology used in the WMP guidelines to the terminology used by the WFC modeling team. In the WMP guidelines, Burn Probability is the frequency with which a fire reaches a given location over a range of different conditions. For the WFC v4, the range of conditions used are the worst fire weather days (approximately 30 each year), determined by the meteorology department, for 2012-2022 and the outcomes of each set of real-world fire weather conditions is evaluated via Technosylva wildfire simulations. Given the conditions of a specific weather day, the fire simulations are deterministic, which is why the description uses the term “deterministic” even though a variety of outcomes under varying conditions are captured across all the weather days. The WFC ultimately needs to assign consequences to ignition locations (i.e. grid equipment), so the acres burned, structures reached, and flame length and rate of spread for each simulation (calculated based on conditions within the fire footprint) are assigned to the originating location for each weather day. For that reason, the actual “burn probability” values for locations reached by fires are not directly used in the WFC calculations and are therefore not called out by name in the documentation. a. Not applicable based on the explanation above. b. Not applicable based on the explanation above. | Eddie Schmitt | 2025-04-30 | 2025-05-30 | 2025-05-30 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_004.zip | 0 | No | 5 | Risk Methodology & Assessment | 5.4 | Summary of Risk Models
18 | 190 | SPD | 004 | SPD_004 | 26 | No | SPD_004_Q26 | What steps has PG&E taken to archive any data or models related to WDRM v3? a. Have any aspects of WDRM v3 not been archived? If so, explain why they were not archived. i. If any aspects of WDRM v3 were not archived, would this prevent a party from asking for data analysis using WDRM v3 in the future? b. How long will PG&E maintain its archive of the data or models related to WDRM v3? c. What data is PG&E maintaining of its previous asset data? What data would be missing if PG&E wanted to backcast the risk in pre-2023 years using WDRM v4? How is PG&E working to ensure that future models have the data necessary to backcast the risk to current system configurations? | a. WDRM v3 has been archived. The WDRM version archival includes all source data, model code, and output data. i. All aspects of WDRM v3 have been archived and will be available for future analysis requests. b. Currently, WDRM v3 has been archived indefinitely. However, as additional WDRM versions are produced for future WMPs, PG&E may adopt an end-of-life retention policy in the future to deprecate older model versions once all mitigation project work supported by a version has been completed or cancelled. c. Pursuant to agreement with SPD, PG&E will respond to this subpart by May 13, 2025. | Eddie Schmitt | 2025-04-30 | 2025-05-06 | 2025-05-06 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_004.zip | 0 | No | 5 | Risk Methodology & Assessment | 5.4 | Summary of Risk Models
18 | 190 | SPD | 004 | SPD_004 | 26(s) | Yes | SPD_004_Q26(s) | What steps has PG&E taken to archive any data or models related to WDRM v3? a. Have any aspects of WDRM v3 not been archived? If so, explain why they were not archived. i. If any aspects of WDRM v3 were not archived, would this prevent a party from asking for data analysis using WDRM v3 in the future? b. How long will PG&E maintain its archive of the data or models related to WDRM v3? c. What data is PG&E maintaining of its previous asset data? What data would be missing if PG&E wanted to backcast the risk in pre-2023 years using WDRM v4? How is PG&E working to ensure that future models have the data necessary to backcast the risk to current system configurations? | c. What data is PG&E maintaining of its previous asset data? Asset history is not currently tracked in PG&E’s GIS database. Historical asset data can be accessed through annually archived GIS database backups. Note that historical backups don’t include future data quality improvements. As detailed for WDRM v3 for subparts (a) and (b), WDRM v4 source data, model code, and output data has been archived indefinitely. In addition, GIS configuration data going forward from January 1, 2023 only, has been snapshotted and archived monthly. What data would be missing if PG&E wanted to backcast the risk in pre-2023 years using WDRM v4? PG&E is assuming ‘backcast the risk’ means taking a version of the WDRM aligned around a specific configuration of the system (e.g. Jan 1, 2023 for WDRM v4) and re-aggregating the risk to a configuration of the system representing a prior date. WMP-Discovery 2026-2028_DR_SPD_004-Q026Supp01 Page 2 Primarily, the assignment of asset model risk to circuit segments would be missing prior to Jan 1, 2023. Additionally, there would be other missing data when backcasting to a previous circuit segment configuration. The distribution system is continuously changing; circuit segments are reconfigured, added, and deleted, GIS location data errors are corrected, equipment assets are replaced, etc. All these accumulated changes will result in a mismatch with grid configuration data from the January 1, 2023 snapshot used to generate WDRM v4. The further a backcast date is from the original snapshot, the more severe the mismatches will become. For each mismatch, the likelihood that the WDRM v4 would be unable to produce a risk value for a given asset or location increase. In turn, the aggregated risk value for any given circuit segment would likely be underreported, as any missing asset/pixel risk values would be assumed to be zero. How is PG&E working to ensure that future models have the data necessary to backcast the risk to current system configurations? PG&E is archiving monthly snapshots of data related to WDRM v4 to enable recreating historical configurations of the system. However, many of the issues mentioned previously around the risk data becoming stale over time will still be true, even when a historical configuration can be created. Additionally, it’s challenging to foresee what data would be required in a future model release to initiate historical archival of the data. | Eddie Schmitt | 2025-04-30 | 2025-05-13 | 2025-05-13 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_004.zip | 0 | No | 5 | Risk Methodology & Assessment | 5.4 | Summary of Risk Models
18 | 191 | SPD | 004 | SPD_004 | 27 | No | SPD_004_Q27 | List all the feasibility constraints that are relevant to the decision trees found in Figures PG&E-8.2.1- 1, PG&E-8.2.1-2, and PG&E-8.2.1-3 in the 2026-2028 Base WMP. a. How are these feasibility constraints operationalized within these decision trees? b. How are these feasibility constraints quantified? c. How are these feasibility constraints addressed in PG&E’s Cost Benefit Analysis? | PG&E objects that the request is overbroad because there are many potential feasibility constraints depending on the specific circumstances of a given case. Due to the extensive range of feasibility constraints that may be considered in the design of undergrounding, covered conductor, and line removal projects, it is impracticable, if not impossible, to enumerate all potential factors. Therefore, although the list provided below attempts to thoroughly set forth common feasibility constraints that significantly impact the program, it may not be an exhaustive list. Below are primary examples of feasibility constraints considered within the scoping process : • High-impact dependencies and permitting requirements from federal, state and local agencies. • Soil impacts, such as granite/hard rock, waterway crossings, bio, cultural and environmental. • Terrain impacts, such as the need for retaining walls, grading/access, and vegetation removal. • Asbestos and other contaminants that are known to exist in the project scope. • Construction and restoration restrictions such as bird nests, helicopter sets, special equipment. • Easement and customer engagement limitations to building the scope • Constructability of alternatives whether it be due to overhead limitations or underground. a. Feasibility constraints are operationalized within the decision tree starting with a lead engineer who conducts a desktop feasibility review and determines a preliminary proposed scope that we compare to available alternatives. This preliminary proposed scope is sent out to a greater scoping team who completes a combination of field and desktop reviews targeted at the locations proposed for work. The various reviews are evaluated in a desktop scoping meeting where the proposed scope may be modified to ensure constructability and to address dependencies that may impact timing and cost. b. Feasibility constraints influence the construction route of projects. For example, if there is steep terrain or significantly hard rock, the route will be adjusted based on the location of the constraints. Cost-related feasibility factors are incorporated into cost assumptions as a quantifiable cost modifier, which are then included in the estimated unit cost of the proposed construction. c. During the scoping process, PG&E adjusts the estimated costs to account for feasibility constraints, including suggesting construction methodologies based on the feasibility factors identified. Going forward, PG&E’s cost benefit analysis will account for the project-specific cost estimates including the feasibility constraints. | Eddie Schmitt | 2025-04-30 | 2025-05-06 | 2025-05-06 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_004.zip | 0 | No | 8 | Grid Design, Operations, and Maintenance | 8.2.1 | Covered Conductor Installation
18 | 192 | SPD | 004 | SPD_004 | 28 | No | SPD_004_Q28 | On page 124 in the 2026-2028 Base WMP, PG&E states that it has adopted a consistent treatment of risk tolerance in its risk assessment and mitigation strategies. In an Administrative Law Judge Ruling dated April 22 2025 in the PG&E 2024 RAMP Proceeding (A.24-05-008), PG&E was ordered to not refer to “risk tolerance” to justify risk mitigation activities in the 2027 GRC Rate Case. a. Explain which mitigations discussed in the 2026-2028 WMP will need to be reconsidered in light of this order. i. Explain how and why risk tolerance was used as a justification for selecting those mitigation strategies. b. Explain what role risk tolerance played in the decision trees found in Figures PG&E-8.2.1-1, PG&E-8.2.1-2, and PG&E-8.2.1-3 in the 2026-2028 Base WMP. i. Explain how these three decision trees will change in light of the ALJ Ruling. c. Explain any other decision-making procedure, protocol, tool or other approach where a treatment of risk tolerance was integrated into PG&E’s mitigation selection process. i. Explain how these approaches will change in light of the ALJ Ruling. | To date the CPUC has not adopted any Risk Tolerance standard. Accordingly we do not rely on any determination by PG&E or the CPUC regarding a Risk Tolerance standard as justification for our proposed mitigation strategies. However, in proposing our mitigation strategies we employ our professional experience, expertise, and prudent operator judgment to assess the level of safety event risk posed by wildfire. We do not assert that these risk levels are “intolerable.” As the ALJ ruling correctly points out, and PG&E agrees, establishing Risk Tolerance standards for California is the Commission’s responsibility. We believe, however, that understanding the potential for catastrophic WMP-Discovery 2026-2028_DR_SPD_004-Q028 Page 2 risk consequences is an important factor to be considered along with cost-benefit analysis. a. There is no mitigation that needs to be reconsidered in light of this order. A specific risk tolerance threshold was not used as a justification for selecting those mitigation strategies. b. A specific risk tolerance threshold was not used in the decision trees. c. Risk tolerance thresholds have not been integrated into PG&E's mitigation selection process for the 2026-2028 WMP. | Eddie Schmitt | 2025-04-30 | 2025-05-06 | 2025-05-06 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_004.zip | 0 | No | 5 | Risk Methodology & Assessment | 5 | Risk Methodology and Assessment
18 | 193 | SPD | 004 | SPD_004 | 29 | No | SPD_004_Q29 | Provide a detailed explanation of how PG&E addresses tail risk in its risk models presented in the 2026-2028 Base WMP? a. Is the EORM impacted by PG&E's approach to addressing wildfire tail risk? If so, how? If not, why not? b. Is the WDRM impacted by PG&E's approach to addressing wildfire tail risk? If so, how? If not, why not? c. Is the WTRM impacted by PG&E's approach to addressing wildfire tail risk? If so, how? If not, why not? | a. Yes, Wildfire Risk Bow-tie Model is impacted by PG&E’s approach to addressing wildfire tail risk by using a risk-averse Risk Attitude Function (also known as a Risk Scaling Function) which gives a greater weight in the risk model to low frequency, high consequence events than to high frequency, low consequence events.1 b. Yes, the WDRM is impacted by PG&E’s approach to addressing wildfire tail risk as it influences the Cost Benefit Analysis (CBA) provided by Enterprise Operational Risk Management. The CBA influences the MAVf that is used as a transform to produce a single Wildfire Consequence Model value for historical fire outcomes (acres burned, structures destroyed, and fatalities) during model data processing. This, in turn, impacts the risk values produced by the WDRM. c. Yes, the WTRM is impacted by PG&E’s approach to addressing wildfire tail risk as it influences the Cost Benefit Analysis (CBA) provided by Enterprise Operational Risk Management. The CBA influences the MAVf that is used as a transform to produce a single Wildfire Consequence Model value for historical fire outcomes (acres burned, structures destroyed, and fatalities) during model data processing. This, in turn, impacts the risk values produced by the WTRM. | Eddie Schmitt | 2025-04-30 | 2025-05-30 | 2025-05-30 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_004.zip | 0 | No | 5 | Risk Methodology & Assessment | 5.4 | Summary of Risk Models
18 | 194 | SPD | 004 | SPD_004 | 30 | No | SPD_004_Q30 | Provide a detailed explanation of how PG&E applies the risk scaling function in its risk models presented in the 2026-2028 Base WMP? a. Is the risk scaling function applied to the EORM? If so, how? If not, why not? b. Is the risk scaling function applied to the WDRM? If so, how? If not, why not? c. Is the risk scaling function applied to the WTRM? If so, how? If not, why not? | a. Yes, the same risk scaling function used in 2024 RAMP is applied to the EORM risk models presented in the 2026-2028 Base WMP. Please refer to 2024 RAMP Exhibit (PG&E-2), Chapter 2, Section C.6b, for the details on how PG&E applies the risk scaling function to convert monetized levels of an attribute into risk-adjusted levels of an attribute to prioritize the mitigation of risks characterized as low frequency/high consequence events, even though their expected loss might be the same as multiple high frequency events with low consequences. b. WDRM risk values are only scaled for calculating overall utility risk, which combines wildfire risk with outage program risk. For overall utility risk, the WDRM v4 risk results are scaled to match the absolute value of distribution wildfire risk determined by the EORM risk bow tie model. This is necessary because WDRM produces a set of relative, not absolute, risk values, and must be scaled before summing with other types of risks. c. WTRM risk values are only scaled for calculating overall utility risk, which combines wildfire risk with outage program risk. For overall utility risk, the WTRM v2 risk results are scaled to match the absolute value of transmission wildfire risk determined by the EORM risk bow tie model. This is necessary because WTRM produces a set of relative, not absolute, risk values, and must be scaled before summing with other types of risks. | Eddie Schmitt | 2025-04-30 | 2025-05-30 | 2025-05-30 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_004.zip | 0 | No | 5 | Risk Methodology & Assessment | 5.4 | Summary of Risk Models
18 | 195 | SPD | 004 | SPD_004 | 31 | No | SPD_004_Q31 | On page 124 in the 2026-2028 Base WMP, PG&E states “PG&E’s Investment Planning group leverages the CBRs and the RDF to prioritize the proposed investments to achieve risk reduction at a reasonable cost as part of its GRC forecast.” a. How does PG&E leverage CBRs to prioritize investments in risk reduction? Explain. b. List which non-CBR aspects of the RDF PG&E leverages to prioritize investments in risk reduction. i. Explain how PG&E leverages those non-CBR aspects of the RDF to prioritize investments in risk reduction. c. Define “reasonable cost”. Explain how PG&E incorporates “reasonable cost” as a constraint in its risk models. | a. PG&E notes that while the wildfire mitigations in its WMP are consistent with those that will be proposed in the GRC, there is a distinction between GRC forecasting activities and the work planning as described in the WMP. In the GRC, CBRs are one component that PG&E utilizes for the purpose of developing its overall funding request across all mitigation programs (gas transmission vintage pipe replacement programs, dam spillway remediation, wildfire undergrounding, etc.). Hence program-level CBRs are determined across all PG&E’s Functional Areas and utilized as described in Exhibit (PG&E-2), Chapter 1 and Exhibit (PG&E-4), Chapter 3 of its 2027 GRC Testimony, which will be filed on May 15, 2025. In the WMP, the portfolio of projects are selected, partly based on project-level CBRs, but also based on other factors as described on page 125. b. Row 26 of the RDF states that mitigation programs can be selected based on other factors besides their CBRs. These factors are: • PG&E’s obligation to consider Safety as the Top Priority WMP-Discovery 2026-2028_DR_SPD_004-Q031 Page 2 • The exercise of PG&E’s Prudent Operator Judgement • Modeling Limitations and Uncertainty • Compliance Requirements. Exhibit (PG&E-2), Chapter 1 of PG&E’s 2027 GRC Testimony provides an in-depth discussion on each of these factors. i. PG&E considers CBRs, and the factors mentioned above on a case-by-case basis for each of its mitigations and documents the rationale for selecting them in the GRC Testimony. c. PG&E does not apply a strict definition of “reasonable cost” but considers the circumstances around each of its mitigation programs in its determination of reasonableness. Some programs have reasonable cost based on the risk reduction benefits they provide, i.e., their CBRs. Others are reasonable because they are the most economical way to address known vulnerabilities and threats or meet compliance requirements in an efficacious manner. | Eddie Schmitt | 2025-04-30 | 2025-05-13 | 2025-05-13 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_004.zip | 0 | No | 3 | Overview of WMP | 3.6 | Projected Expenditures
18 | 196 | SPD | 004 | SPD_004 | 32 | No | SPD_004_Q32 | On page 125 in the 2026-2028 Base WMP, PG&E explains that SME Judgement is integrated into the process of mitigation selection through “cross-functional working groups”. Provide a detailed narrative description of how these cross-functional working groups operate. a. List each type of document or other kinds of information that is created at these crossfunctional working groups. i. How are these documents or other kinds of information retained? ii. Provide an example of each type of document or other kinds of information that was generated by the cross-functional working group when selecting mitigations on circuit segment CORNING 110185152. b. Do the working groups evaluate every asset within a circuit segment to determine which mitigation should be implemented? i. If so, explain how this is done. ii. If not, explain why not. c. List the inputs the SME's review to support the cross-functional working group’s decision about which mitigation should be selected at a given circuit segment. i. Explain how the SME’s use each of those inputs to support the cross-functional working group’s decision about which mitigation should be selected at a given circuit segment. | a. During the cross-functional Scoping working group, PG&E creates the Design Basis Memorandum document for each job, which includes information on job location and authorities having jurisdiction, functional and estimating team notes, design considerations, and the following appendices: o APPENDIX A – ENROACHMENT KMZ & SUPPORTING DOCUMENTS o APPENDIX B – SEGMENTATION KMZ o APPENDIX C – SUBORDER TABLE o APPENDIX D – WORKSHEET DESCRIPTION o APPENDIX E – KEY SKETCHES o APPENDIX F – WILDFIRE BENEFIT COST ALALYSIS (WBCA) TOOL OUTPUTS o APPENDIX G – EC TAG LIST o APPENDIX H – LAND RIGHTS KMZ & SUPPORTING DOCUMENTS o APPENDIX I – VEGETATION MANAGEMENT & SUPPORTING DOCUMENTS o APPENDIX J – ENVIRONMENTAL KMZ & SUPPORTING DOCUMENTS o APPENDIX K – PUBLIC SAFETY KMZ & SUPPORTING DOCUMENTS o APPENDIX L – P6 SCHEDULE o APPENDIX M – IDLE FACILITY i. The documents are retained in PG&E’s Electronic Document Routing System (EDRS). ii. CORNING 110185152 is still at the early stages of scoping, and we have not developed the full job package. b. No, we do not evaluate every asset within a circuit segment to determine which mitigation should be evaluated. i. N/A ii. The Scoping working groups evaluate the circuit segment for overall feasibility, vegetation risk exposure, constructability, cost estimate, ingress/egress concerns, land and environmental impacts, permitting requirements, and risk reduction benefit to help develop the best mitigation. c. The cross-functional Scoping working group may provide the following insights and recommendations, which would help drive our decision for the mitigation selection. Although the list provided below attempts to thoroughly set forth common insights and recommendations provided during the working group, it may not be an exhaustive list, and additional factors could be discussed depending on the nature of the project: • Land / Encroachment / Environmental – Reviews work proposal and provides approximate time for land acquisition or permitting based on environmental issues. • Public Safety Specialist (PSS) – Provides recommendations on which poles to underground based on ingress/egress concerns. • Vegetation – Provides input if enhanced vegetation work is required if proceeding with overhead hardening. • Construction Management – Review underground route proposals and will confirm if it is feasible or recommend an alternative route. i. See above response in subpart (c). | Eddie Schmitt | 2025-04-30 | 2025-05-21 | 2025-05-21 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_004.zip | 0 | No | 6 | Wildfire Mitigation Strategy Development | 6.1.3 | Activity Selection Process
18 | 197 | SPD | 004 | SPD_004 | 33 | No | SPD_004_Q33 | On page 125 in the 2026-2028 Base WMP, PG&E explains that the cross-functional working groups leverage both quantitative risk assessments and qualitative operational insights. Provide a list of the qualitative operational insights. a. Describe how each of these qualitative operational insights can contribute to the mitigation selection. i. Provide an example. Explain how and why each of these qualitative operational insights either did or did not inform the selection of mitigations on circuit segment CORNING 110185152. b. Describe how each of these qualitative operational insights are integrated into the decision trees found in Figures PG&E-8.2.1-1, PG&E-8.2.1-2, and PG&E-8.2.1-3 in the 2026-2028 Base WMP. i. Which of the steps in the decision-trees reviews these qualitative operational insights? How is that performed? | The following is a list of the key qualitative operational insights used by the crossfunctional working groups. Although the list provided below attempts to thoroughly set forth common qualitative insights that contribute to mitigation selection, it may not be an exhaustive list. t: • High tree strike potential, including an assessment of the current quantitative data with the vegetation management team. • Ingress/egress concerns and major historical fire data identified by the Public Safety Specialist (PSS). • Construction management feasibility, which accounts for local geology, including presence of hard rock, steep terrain, water crossings. • Environmental considerations, including sensitive habitats. • Cultural or historical considerations, including tribal lands. • Customer/community impacts, such as significant construction in a neighborhood by PG&E or another utility, land rights and/or permitting challenges. a. The CORNING 110185152 project is still in the early stages of scoping and PG&E can provide information on the qualitative operational insights once the analysis is complete. b. Qualitative insights on any given project are discussed during the Hybrid Analysis and Desktop Scoping Meeting (Figures 8.2.1-2 and 8.2.1-3). i. During the Desktop Scoping Meeting, the cross-functional team reviews the qualitative insights to answer the question “Are there any significant dependency or constructability limitations in the areas of impact?” (Figure 8.2.1-3). | Eddie Schmitt | 2025-04-30 | 2025-05-21 | 2025-05-21 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_004.zip | 0 | No | 6 | Wildfire Mitigation Strategy Development | 6.1.3 | Activity Selection Process
18 | 198 | SPD | 004 | SPD_004 | 34 | No | SPD_004_Q34 | On page 125 in the 2026-2028 Base WMP, PG&E explains that when selecting a mitigation it considers relevant local factors on a case-by-case basis. a. Provide a list of local factors that PG&E considers when selecting a mitigation. b. Describe how this list of local factors was established by PG&E. i. Were any other factors considered in this process but removed from the final list? If so, explain why. c. Describe how each of these local factors can inform mitigation selection. d. Describe how each of these local factors are integrated into the decision trees found in Figures PG&E-8.2.1-1, PG&E-8.2.1-2, and PG&E-8.2.1-3 in the 2026-2028 Base WMP. i. Which of the steps in the decision-trees reviews these local factors? How is that performed? | a. When a mitigation alternative is evaluated at the circuit segment level, all aspects of the decision tree are considered for the circuit segment. PG&E defines local factors (factors that are unique to that project location) to be the same as the qualitative factors described in response to WMP 2026-2028 SPD_004_Q33 (with the exception the PSPS factors, which is a quantitative measurement and included below). The primary local factors considered when selecting a mitigation include items listed below. Although the list provided below attempts to thoroughly set forth common local factors that PG&E considers when selecting a mitigation, it may not be an exhaustive list. • High tree strike potential, including an assessment of the current quantitative data provided by the vegetation management team. • Ingress/egress concerns and major historical fire data identified by the Public Safety Specialist (PSS) . • Construction management feasibility assessment, which accounts for local geology, including presence of hard rock, steep terrain, and water crossings. • Environmental considerations, such as sensitive habitats. • Cultural or historical considerations, such as tribal lands. • Customer/community impacts, such as significant construction in a neighborhood by PG&E or another utility, or land rights and permitting challenges. • Public Safety Power Shutoff (PSPS) history in the area, assessed by reviewing the PSPS polygon data. The polygon data shows the area identified for each PSPS event in the lookback period that identifies which of the overhead assets will have required deenergization. b. PG&E’s list of local factors was developed by participants in the cross-functional Scoping working groups who leverage their historical knowledge and local requirements. These participants offer feedback informed by their engagement with key stakeholders, such as agencies, cities, counties, tribes, and local communities, to ensure alignment with relevant local regulations and address local needs. This collective input helped shape the list, ensuring PG&E effectively addresses local considerations when selecting mitigations. i. No additional factors were considered but removed from the list. c. These local factors can inform PG&E’s mitigation selection at two key stages leading up to and during the scoping process: 1. When PG&E completes its initial Cost Benefit Analysis (Figure 8.2.1-2), and a Circuit Protection Zone (CPZ) does not meet the Cost Benefit Ratio (CBR) and Net Benefit requirements for an undergrounding solution, PG&E initiates a hybrid analysis. As part of the hybrid analysis, PG&E considers local factors such as tree strike potential, ingress/egress, and/or PSPS polygons affecting the CPZ. PG&E continues the reevaluation of Overhead to Underground ratios until the CBR and Net Benefit requirements are met; in some cases, this analysis will result in a 100% covered conductor solution. For example, a CPZ that is selected for a hybrid solution could have a section that has a high tree strike risk and a significant ingress/egress concern. In the feedback loop tool, PG&E would select the number of miles to underground due to tree strike potential, and the number of miles to underground based on ingress/egress concerns. These miles will be entered into the feedback loop tool to identify what ratio of OH and UG meets the CBR and Net Benefit requirements. 2. PG&E also considers additional local factors in addition to tree strike, ingress/egress, and PSPS polygons, during the Desktop Scoping Meeting (Figure 8.2.1-3) and integrates these findings into our analysis (Figure 8.2.1-3). For example, if a water crossing is identified, undergrounding that portion of the CPZ may not be the preferred solution, and an overhead solution would be applied instead. d. Local insights on any given project are discussed during the Hybrid Analysis and Desktop Scoping Meeting (Figures 8.2.1-2 and 8.2.1-3). i. During the Hybrid Analysis, local insights are discussed as the first step in the second row “Begin Hybrid Analysis” (Figure 8.2.1-2). During the Desktop Scoping Meeting, the cross-functional team reviews the local insights to answer the question “Are there any significant dependence or constructability limitations in the areas of impact?” (Figure 8.2.1-3). | Eddie Schmitt | 2025-04-30 | 2025-05-21 | 2025-05-21 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_004.zip | 0 | No | 6 | Wildfire Mitigation Strategy Development | 6.1.3 | Activity Selection Process
18 | 199 | SPD | 004 | SPD_004 | 35 | No | SPD_004_Q35 | On page 132 in the 2026-2028 Base WMP, PG&E states that it looks at its “highest risk circuit segments” to determine where to target the work included in the WMP. a. Within these “highest risk circuit segments”, what aspects does PG&E consider in order to determine the timing of implementing mitigations on these “highest risk circuit segments”? i. Does PG&E consider the LoRE and CoRE values of these circuit segments when determining the timing of implementing mitigations on these “highest risk circuit segments”? If so, how? If not, why not? | a. PG&E is providing a response to this question for system hardening and undergrounding. PG&E selects system hardening and undergrounding based on the risk model’s ranking of the highest risk circuit segments. Other WMP programs reference the risk model but focus on addressing the location where the specific risk is present. Circuit segments are selected for scoping from 1-N based on ignition risk rank. Certain circuit segments may be excluded if, for example, they are already hardened, are privately owned, are very short, or are already in a workplan. PG&E generally prioritizes execution of projects in the same order that scoping is completed. Once a project has completed scoping and other pre-construction activities (e.g. design, estimating and permitting) are complete, PG&E will begin construction as soon as practicable. While our approach is to begin hardening as soon as practicable after scoping is complete, there are limiting factors identified through the design/estimating and permitting process that impact when projects can be implemented, such as: • Construction management feasibility which accounts for local geology, including presence of hard rock, steep terrain, water crossings; • Environmental considerations including sensitive habitats; • Cultural or historical considerations including tribal lands; and • Customer/community impacts, such as significant construction in a neighborhood by PG&E or another utility, land rights and/or permitting challenges. When it seems like a project may be delayed, PG&E also works to improve timing (complete mitigations more quickly) by separating projects into multiple phases and/or sub-phases and limiting the timing constraints to smaller sections of work. i. No, LoRE and CoRE values are not considered independently when planning for the sequencing and timing of projects or sub-projects. While both likelihood and consequence are important components of risk, their product (i.e., risk) is the primary focus when prioritizing mitigations. More specifically, PG&E uses the density of risk, such as risk per mile, to rank circuit segments 1-n. PG&E then prioritizes projects for execution in ascending risk rank order based on the model used at the time of selection, while considering the operational limitations noted in response to part a above. | Eddie Schmitt | 2025-04-30 | 2025-05-21 | 2025-05-21 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_004.zip | 0 | No | 5 | Risk Methodology & Assessment | 5.5.2 | Top Risk-Contributing Circuits/Segments/Spans
18 | 200 | SPD | 004 | SPD_004 | 36 | No | SPD_004_Q36 | Throughout the 2026-2028 Base WMP, PG&E uses the terms system hardening, grid hardening, and resiliency mitigation activities to describe the same category of mitigations, namely undergrounding, covered conductor and distribution line removal. Explain why PG&E uses three different terms for this category of mitigations. a. Are there differences between these terms? If so, explain. | Note: all references in this response are specific to distribution-related terms in PG&E’s 2026-2028 Base WMP, R0, April 4, 2025. Resilience Mitigations Resilience Mitigations describe one of the four categories of mitigations that support PG&E’s foundational framework of risk-information decision-making designed to minimize ignition risk and outage impacts.1 PG&E’s system resilience activities are critical to permanently reducing wildfire risk, minimizing negative aspects of PSPS and EPSS, and strengthening the grid against extreme weather events (p. 6). System Resilience describes mitigations designed to reduce ignition risk by changing how PG&E’s grid is constructed and operated (2023-2025 Base WMP, R8, p. 255). Resilience Mitigation describe a broader category of mitigations than just system hardening. While Resiliency Mitigations include system hardening activities (distribution undergrounding, distribution covered conductor, distribution line removal), it also includes non-system hardening mitigations, such as distribution pole replacement and reinforcement and HFTD/HFRA open tag reduction - distribution (2026-2028 Base WMP, R0, Figure PG&E-6.1.3.3-1). System Hardening System hardening describes two distribution system hardening initiatives: 1. Covered conductor (CC) installation and line removal, including remote grids (GH-12); and 2. Distribution undergrounding (GH-04). Grid Hardening WMP Section 8.8.2 is called “Grid Hardening.” PG&E uses the term “grid hardening” in our Section 8.8.2 narrative to align to the title of WMP Section 8.8.2 as specified by Energy Safety in its 2026-2028 WMP Guidelines2. In PG&E’s Section 8.8.2 narrative, we state that grid hardening projects include undergrounding (p. 345). The term is also specified by Energy Safety in Area for Continuous Improvement (ACI) PG&E-25U-03, Continuation of Grid Hardening Joint Studies, so PG&E uses the term in its response to that ACI. a. While grid hardening and system hardening are basically synonymous, the key distinction among the three terms PG&E uses in the WMP is that Resilience Mitigations refers to a broader category of mitigations than just grid hardening or system hardening. | Eddie Schmitt | 2025-04-30 | 2025-05-06 | 2025-05-06 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_004.zip | 0 | No | 8 | Grid Design, Operations, and Maintenance | 8 | Grid Design, Operations, and Maintenance
18 | 201 | SPD | 004 | SPD_004 | 37 | No | SPD_004_Q37 | On page 135 in the 2026-2028 Base WMP, PG&E states “Over time, undergrounding also has lower operations and maintenance expenses.” Provide documentation that corroborates this statement. a. What is the time scale of the analysis that led to this statement? Why was that timescale used? b. How would the results of the analysis be different if an alternative time scale was used? Consider the possible results of the analysis if the following time scales were used: i. Annual, ii. Decadal, iii. Multi-decadal (this must include the decommissioning and replacement costs) | a. PG&E recognizes that the term “time scale” in the question could be interpreted in multiple ways. In our response, we address two possible interpretations: (1) the timeframe of the data used to develop the analysis and (2) the timeframe associated with the application of the results of the analysis. 1) The average annual cost considers between 1 to 5 years of historical or forecast data for the O&M activity. The timescales considered in the underlying data vary due to the availability of data for each of the O&M cost types (e.g., some cost types leverage yearly historical costs, whereas other cost types are based on the 2023-2026 GRC forecast). Undergrounding can reduce some O&M costs, such as routine maintenance, vegetation management costs, patrols and inspections, Enhanced Power Safety Settings (EPSS) and Public Safety Power Shutoffs (PSPS). 2) The time scale of the analysis that led to this statement is one year. This statement is based on an expected average annual cost per mile for operations and maintenance (O&M) activities. The assumption is that the average annual cost per mile would be applicable for the useful life of the asset (i.e., 55 years for undergrounding). Please see “WMP-Discovery2026-2028_DR_SPD_004-Q037Atch01.xlsx”, which outlines examples of expected O&M costs as an average annual cost for a mile of undergrounding primary lines compared to an unhardened baseline scenario. The lower operations and maintenance costs are assumed to be relative to a hypothetical baseline assumption for the cost of operations and maintenance for an unhardened mile in the current system. As more of the system is undergrounded, the average annual avoided costs will increase. This cumulative effect leads to long-term benefits. Further information on the cost assumptions and underlying data will be included in the final Wildfire Benefit Cost Analysis (WBCA). b. The total O&M avoided costs are not effected by the time period considered. i. It is assumed that any avoided costs are on an average annual cost per mile basis and would not be significantly impacted by the time-scale considered. ii. It is assumed that any avoided costs are on an average annual cost per mile basis and would not be significantly impacted by the time-scale considered. iii. It is assumed that any avoided costs are on an average annual cost per mile basis and would not be significantly impacted by the time-scale considered. This analysis does not consider time scaled degradation of assets but does consider aspects of O&M capital replacement over time including conductor and cable replacement, where relevant, and as based on historic averages. | Eddie Schmitt | 2025-04-30 | 2025-05-09 | 2025-05-09 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_004.zip | 1 | No | 8 | Grid Design, Operations, and Maintenance | 8.2.2 | Undergrounding of Electric Lines and/or Equipment
18 | 202 | SPD | 004 | SPD_004 | 38 | No | SPD_004_Q38 | On page 136 in the 2026-2028 Base WMP, PG&E states “For many of the mitigation programs, wildfire risk is the primary driver of prioritization.” List the mitigation programs where wildfire risk is not the primary driver of prioritization. a. For each mitigation program in this list, explain what is the primary driver of prioritization and why | Wildfire risk is a primary driver of prioritization for all of PG&E’s mitigation programs. On page 136 of the 2026-2028 Base WMP, PG&E explains that it may also consider reliability risk when prioritizing mitigation programs pursuant to the requirements of Senate Bill 884. As such, certain mitigation programs may have reliability risk as a driver for prioritization as well as wildfire risk, but there are no mitigation programs for which wildfire risk is not a primary driver of prioritization. Please see, for example, Table 5-5 in the 2026-2028 Base WMP and the column titled “Top Risk Contributors.” | Eddie Schmitt | 2025-04-30 | 2025-05-13 | 2025-05-13 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_004.zip | 0 | No | 5 | Risk Methodology & Assessment | 5 | Risk Methodology and Assessment
18 | 203 | SPD | 004 | SPD_004 | 39 | No | SPD_004_Q39 | For Table 6-3 in the 2026-2028 Base WMP, PG&E provided an “Activity-Effectiveness-Wildfire Risk” value for each activity listed. However, for six of these activities PG&E did not provide CostBenefit Ratios.3 a. Provide the Cost-Benefit Ratios for each of these activities as is required by D.22-12-027. b. If these calculations of CBR vary from what was submitted in PG&E’s 2024 RAMP Application, explain how much they vary and why.4 c. Complete Table 6-3 for all activities listed in this WMP. Add the Initiative Activity Tracking ID as a column in the completed Table. Present this completed version of Table 6-3 in an Excel spreadsheet. | a. The following table uses 2026-2028 program Cost Benefit Ratios (CBR) values (unless otherwise noted) from the enterprise risk models and investment planning forecasts to be submitted as part of our May 2027 GRC filing. The two transmission programs (conductor segment replacement and shunt splice installation) cost benefit scores are currently unavailable and will be provided later. b. The table below compares the RAMP CBRs and CBRs provided in subpart (a). The original CBR submitted in Table 6-3 are based on February vintage GRC bowties and analysis that was available at the time of the 2026-2028 WMP filing. The values provided in subpart (a) are from PG&E’s finalized bowties and analysis to be submitted in our May filing of the 2027 GRC using Baseline 2026. A brief description on the variance drivers are described below. a) Reduction driven by higher percentage of pole work that has a lower CBR value when compared to non-pole capital and expense projects b) New program for 2027 GRC c) Increase driven by a lower estimated unit cost of work and refreshed outage to ignition ratio when compared to RAMP filing d) Risk Reduction from RAMP to GRC is lower while costs remained relatively the same e) Increase driven by the exclusion of secondary and service mile scoped f) Reduction driven by the increase in allocated costs tied to PSPS g) Reduction driven by lower EPSS effectiveness | Eddie Schmitt | 2025-04-30 | 2025-05-13 | 2025-05-13 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_004.zip | 0 | No | 6 | Wildfire Mitigation Strategy Development | 6 | Wildfire Mitigation Strategy
18 | 203 | SPD | 004 | SPD_004 | 39(s) | Yes | SPD_004_Q39(s) | For Table 6-3 in the 2026-2028 Base WMP, PG&E provided an “Activity-Effectiveness-Wildfire Risk” value for each activity listed. However, for six of these activities PG&E did not provide CostBenefit Ratios.3 a. Provide the Cost-Benefit Ratios for each of these activities as is required by D.22-12-027. b. If these calculations of CBR vary from what was submitted in PG&E’s 2024 RAMP Application, explain how much they vary and why.4 c. Complete Table 6-3 for all activities listed in this WMP. Add the Initiative Activity Tracking ID as a column in the completed Table. Present this completed version of Table 6-3 in an Excel spreadsheet. | a. This table has been updated to include the two transmission programs (conductor segment replacement and shunt splice installation) cost benefit scores. Additionally, the PSPS and EPSS CBR were updated as an error was noted in the original submission. WMP activity name Cost Benefit Score - Overall Risk (2026-2028) Cost-Benefit Score - Wildfire Risk (2026-2028) Cost Benefit Score - Outage Program Risk (2026-2028) PSPS (2027-2030 CBR) 25.3 41.5 -16.2 EPSS (2027-2030 CBR) 33.8 38.1 -4.3 WMP activity name Cost Benefit Score - Overall Risk (2026-2028) Cost-Benefit Score - Wildfire Risk (2026-2028) Cost Benefit Score - Outage Program Risk (2026-2028) Transmission – Shunt Splice Installation 30.43 28.36 2.07 Transmission – Conductor Segment Replacement 5.43 3.93 1.5 | Eddie Schmitt | 2025-04-30 | 2025-05-21 | 2025-05-21 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_004.zip | 0 | No | 6 | Wildfire Mitigation Strategy Development | 6 | Wildfire Mitigation Strategy
18 | 204 | SPD | 004 | SPD_004 | 40 | No | SPD_004_Q40 | On page 152 in the 2026-2028 Base WMP, PG&E provides an explanation for how it calculated Activity Effectiveness – Overall Utility Risk. The total value for Wildfire Risk (Dx, Tx, Sub) is $19,424 Million. Explain why this value is different from the $19,578 Million expressed in Figure 6.1.3.2-1. a. Explain why the PSPS and EPSS values here are presented as “Risk” but in Figure 6.1.3.2-1 these values are referred to as “Consequence”. b. Explain why the value of Wildfire Risk (Dx, Tx, Sub) is different, but the values for PSPS and EPSS Risk on page 152 remain exactly the same as the values for PSPS and EPSS Consequence in Figure 6.1.3.2-1. | The value expressed in Figure 6.1.3.2-1 is the aggregated baseline risk value and includes underground. This is why the sum of the Dx, Tx, and Sub Wildfire Risk differs on page 152 from Figure 6.1.3.2-1. a. “Consequence” in Figure 6.1.3.2-1 means the total consequence of all risk events which represents the same value as “Risk” on page 15. This is because Risk Value is calculated as the product of Exposure, Likelihood of Risk Event (LoRE) and Consequence of Risk Event (CoRE), and as such, the words Risk and Consequence are used interchangeably from page 152 to Figure 6.1.3.2-1. b. The $19,424 million value of Wildfire Risk (Dx, Tx, Sub) on page 152 includes overhead distribution, overhead transmission, and substation wildfire risk, whereas the $19,578 million value in Figure 6.1.3.2-1 also includes underground wildfire risk. The values for PSPS and EPSS Risk on page 152 remain exactly the same as the values for PSPS and EPSS Consequence in Figure 6.1.3.2-1 for the reason explained in the answer to subpart (a) above. | Eddie Schmitt | 2025-04-30 | 2025-05-13 | 2025-05-13 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_004.zip | 0 | No | 6 | Wildfire Mitigation Strategy Development | 6.1.3 | Activity Selection Process
18 | 205 | SPD | 004 | SPD_004 | 41 | No | SPD_004_Q41 | On page 153 in the 2026-2028 Base WMP, PG&E describes the Activity Effectiveness – Wildfire Risk calculation and notes that a study was conducted with subject matter experts (SME) who were asked to “fill out a questionnaire about the effectiveness of these activities against roughly 2,000 failure modes”. a. How many SMEs participated in this study? i. Provide a list of the expertise for each SME that participated in this study. b. How does the questionnaire compare with the mitigation effectiveness study submitted to SPD as “WMP-Discovery2026-2028_DR_SPD_001-Q010Atch01”? c. Provide a narrative explanation of the questionnaire and how SMEs were expected to fill it out. i. Describe what is meant by categorical level of effectiveness. ii. If a scale was used for SMEs to respond to the questionnaire, provide a detailed explanation of that scale and how it was established. iii. If a scale was used, was a variance and standard deviation calculated for the SME responses to each failure mode? If so, provide a table that displays the mean, variance and standard deviation for the SME’s scaled responses to each of the failure modes. d. Provide a copy of the questionnaire about the effectiveness of these activities against the failure modes. e. Provide a copy of the results of the study PG&E notes on page 153 in the 2026-2028 Base WMP. | a. Approximately 3-4 SMEs from the Grid Design team participated in the study. i. The SMEs are Senior Electric Distribution Engineers whose position requires a Bachelor of Science in Electrical Engineering from a college or university accredited by the Accreditation Board of Engineering and Technology. The Senior Electric Distribution Engineers have a minimum of 8 years’ experience in engineering and design. Some of the Grid Design Engineers are licensed professional engineers with the state of California though this license was not required for the completion of the study. b. The mitigation effectiveness study submitted to SPD as “WMP-Discovery2026- 2028_DR_SPD_001-Q010Atch01.xlsx” are the outputs from the mitigation effectiveness study. SMEs were asked to provide an estimated level of effectiveness for each mitigation activity considering various combinations of outage cause, supplemental cause, equipment affected, and equipment condition. c. The questionnaire listed observed combinations of outage cause, supplemental cause, equipment affected, and equipment condition. For each combination, and for each mitigation activity, SMEs were asked a to assign a level of effectiveness such as “None,” “Medium,” or “High.” Table PG&E-8.2.1-2 in PG&E’s 2026-2028 WMP is an example of this analysis. i. Categorical level of effectiveness refers to a qualitative description of the estimated mitigation effectiveness of an activity against an outage considering combinations of the cause, supplemental cause, equipment affected, and equipment condition that have been observed across historic outages. ii. The scale used by SMEs to respond to the questionnaire is described in PG&E’s 2026-2028 Base WMP (pages 188-189): • All: 100 percent effective – Assumes no ignition events; • Very High: 90 percent effective – Assumes the mitigation addresses most ignition concerns, but still leaves a potential for ignition; • High: 75 percent effective – Assumes the mitigation provides significant ignition reduction; however, there is still a chance for contact or failure; • Medium High: 60 percent effective – More than likely ignition reduction for an event; • Medium: 40 percent effective – Less probable ignition reduction for an event; • Low: 10 percent effective – Some ignition reduction mitigation but not significant; and • None: 0 percent effective – No protection against ignition. These average effectiveness ratings were developed based on a review of ten years of unplanned outage history between 2015 and 2024. iii. No, the scale does not use calculations of standard deviation or variance. d. The questionnaire was an Excel workbook listing each combination of failure mode (each row of the workbook showed a different combination) and each mitigation alternative (the columns included the mitigations such as underground all, underground primary, etc.). The SMEs were asked to input an effectiveness value for each mitigation alternative and each failure mode combination. Please see worksheet “Effectiveness Analysis Detail” in attachment “WMPDiscovery2026-2028_DR_SPD_001-Q010Atch01.xlsx,” which is the summary view of the individual questionnaires. e. The study referenced on page 153 is the same study discussed in Section 8.2. The results of the study were submitted to SPD as “WMP-Discovery2026- 2028_DR_SPD_001-Q010Atch01.xlsx.” | Eddie Schmitt | 2025-04-30 | 2025-05-06 | 2025-05-06 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_004.zip | 0 | No | 6 | Wildfire Mitigation Strategy Development | 6.1.3 | Activity Selection Process
18 | 206 | SPD | 004 | SPD_004 | 42 | No | SPD_004_Q42 | Related to the explanation of the Cost Benefit Ratios described on pages 154-155 in the 2026-2028 Base WMP, provide an explanation of how PG&E addressed “discounting of inflation”. a. Did PG&E use a discount rate scenario specified in D.24-05-064? i. If so, explain which scenario and why that was chosen. ii. If not, explain why not. Also explain how PG&E addressed discounting and why it chose that method. | PG&E addressed “discounting of inflation” by discounting values by a real discount rate in its present value evaluations. In these evaluations, the effects of inflation are incorporated by multiplying values by the inflation rate to obtain nominal future values before discounting by the nominal discount rate over the applicable timeframe to obtain the present value. The effective multiplier resulting from these operations is equivalent to discounting by a real discount rate evaluated as 𝑟𝑟𝑒𝑎𝑙=1+𝑟𝑛𝑜𝑚1+𝑟𝑖𝑛𝑓−1 Where 𝑟𝑟𝑒𝑎𝑙 is the real discount rate, 𝑟𝑛𝑜𝑚 is the nominal discount rate, and 𝑟𝑖𝑛𝑓 is the inflation rate. PG&E utilized its After-Tax Weighted Average Cost of Capital (ATWACC) as the nominal discount rate for discounting in present value evaluations which corresponds to the “WACC Discount Rate Scenario” in D.24-05-064. The ATWACC was selected as the nominal discount rate in alignment with PG&E’s current Enterprise Risk Model evaluations, which similarly use the ATWACC rounded to the nearest 50 basis points (or 0.5 percent) as the nominal discount rate. PG&E chose to use ATWACC because it reflects PG&E’s financing costs, and also believes that it is also a proper discount rate for the benefits in the numerator as well as costs in the denominator because benefits WMP-Discovery 2026-2028_DR_SPD_004-Q042 Page 2 are monetized based on willingness to pay (safety), market/replacement costs (financial, gas reliability), or both (electric reliability). | Eddie Schmitt | 2025-04-30 | 2025-05-13 | 2025-05-13 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_004.zip | 0 | No | 3 | Overview of WMP | 3.6 | Projected Expenditures
18 | 207 | TURN | 004 | TURN_004 | 1 | No | TURN_004_Q1 | Regarding Table 5-5 on page 103 and PG&E’s risk prioritization, why doesn’t PG&E prioritize circuit by risk per mile rather than absolute risk? Does PG&E agree that risk per mile of each CPZ is a more accurate way to capture the risk of each CPZ relative to each other? Please explain why or why not. | Table 5-5 is a list of CPZs with the highest overall utility risk in PG&E’s service territory; however, PG&E does not prioritize work based on this table. PG&E typically prioritizes work based on the normalized risk, or risk per mile. PG&E agrees that risk per mile is a more accurate metric than total risk to compare the relative risk of each CPZ. Historically, PG&E has emphasized wildfire risk per mile, or per pixel in some versions of the WDRM, but also recognizes the importance of overall utility risk per mile. | A Mireille Fall-Fry | 2025-05-01 | 2025-05-09 | 2025-05-09 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-TURN_004.zip | 0 | No | 5 | Risk Methodology & Assessment | 5 | Risk Methodology and Assessment
18 | 208 | TURN | 004 | TURN_004 | 2 | No | TURN_004_Q2 | Regarding Table 6.1.3-1 on page 128: a. Why does line removal with remote grid result in 98% effectiveness? Are all overhead lines removed in each of these instances or are lines undergrounded? Please provide an explanation using an example project to illustrate the mitigation effectiveness. b. Please provide the combined mitigation effectiveness of PSPS and EPSS. i. Please provide all supporting calculations/assumptions in Excel. | REGARDING TABLE 6.1.3-1 ON PAGE 128: a. Remote grid systems typically serve customers through low voltage overhead lines. While all high voltage overhead lines are removed, the analysis for this mitigation assumed that the remaining secondary and service lines still pose an ignition risk, resulting in approximately 98% reduction of the overall wildfire risk. The absolute removal of all lines, including both primary and secondary voltage, would result in the elimination of all ignition risk, or 100% effectiveness, since no source for ignition would be present. b. Based on Table 6.1.3-1 on page 128 and “WMP-Discovery2026- 2028_DR_TURN_002-Q005Atch01.xlsx”, PSPS effectiveness is estimated to be 84%. Based on “WMP-Discovery2026-2028_DR_TURN_004- Q002Atch01.xlsx”, tab “EPSS_effectiveness_calculation”, EPSS effectiveness is estimated to be 69%. PSPS and EPSS mitigation programs are assumed to operate independently. Effectiveness represents the probability that a program successfully mitigates a risk. The ineffectiveness is the chance that the program does not mitigate the risk. When programs operate independently, the chance that both programs do not mitigate the risk is the product of their individual ineffectiveness: The combined effectivenes of two independent mitigation programs is then the chance that at least one of the programs mitigates the risk, which is the same as the complement of both programs being ineffective: Therefore, the combined effectiveness is approximately 95%. i. The supporting calculations are provided in file “WMP-Discovery2026- 2028_DR_TURN_004-Q002Atch01.xlsx”, tab “Combined_effectiveness_calc”. | A Mireille Fall-Fry | 2025-05-01 | 2025-05-06 | 2025-05-06 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-TURN_004.zip | 1 | No | 6 | Wildfire Mitigation Strategy Development | 6.1.3 | Activity Selection Process
18 | 209 | TURN | 004 | TURN_004 | 3 | No | TURN_004_Q3 | Regarding Figure 6.1.3.2-1 on page 136 a. Please provide this figure in Excel with all supporting data, calculations, and assumptions. b. Please re-calculate this figure when implementing planned mitigations for PSPS and EPSS consequences in 2026. i. Please provide in Excel with all supporting data, calculations, and assumptions | a. Please see the attachment “WMP-Discovery2026-2028_DR_TURN_004- Q003Atch01.xlsx” for the requested information. The response to subpart (a) is located in “Q003_a” worksheet and the response to subpart (b) is located in the “Q003_b” worksheet of the attachment. b. Please see above. | A Mireille Fall-Fry | 2025-05-01 | 2025-05-06 | 2025-05-06 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-TURN_004.zip | 1 | No | 6 | Wildfire Mitigation Strategy Development | 6.1.3 | Activity Selection Process
18 | 210 | TURN | 004 | TURN_004 | 4 | No | TURN_004_Q4 | Section 6.2.1.2, page 150 states “The total number of miles within the HFTD and HFRA = 4,250 circuit miles.” a. Shouldn’t the total number of circuit miles be closer to 25,000? b. Please explain the 4,250 figure and what it represents. | To clarify, the quoted language on page 150 of the WMP is part of Energy Safety’s prompt for this section and was provided by Energy Safety in the WMP Guidelines. It was included as an example to help understand the information provided in this section and is not language that PG&E provided. PG&E’s response to Energy Safety’s prompt begins after the solid divider line at the bottom of page 150. | A Mireille Fall-Fry | 2025-05-01 | 2025-05-09 | 2025-05-09 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-TURN_004.zip | 0 | No | 6 | Wildfire Mitigation Strategy Development | 6.2.1.2 | Risk Impact of Activities
18 | 211 | TURN | 004 | TURN_004 | 5 | No | TURN_004_Q5 | Section 8.2.1, page 181 states “PG&E will analyze the proposed CC route to determine if there are areas with tree strike risk or locations that could be subject to ingress/egress issues.” a. Please define “tree strike risk.” b. If “tree strike risk” is found to be present, does this mean the CC is ruled out? Please explain. c. Please define ingress/egress issues as used here. | a. For purposes of the System Hardening program, tree strike risk refers to the likelihood of trees falling into the overhead span, regardless of wind speed or direction, and breaking a proposed overhead hardened span. An area with a tree strike score of 6 or higher is identified as “Area of impact identified, relocate to underground preferred.” In both cases an area with a tree strike score of 0-5 is identified as “No area of impact identified, OH in place preferred.” The logic surrounding tree strike is shown in Figure PG&E-8.2.1-2 and in Figure SRN-PG&E23-05-06A of PG&E’s 2026-2028 Base WMP. b. If a high tree strike potential is identified, our preferred approach is to underground at that location, provided that it meets the Cost-Benefit Ratio (CBR) and Net Benefit criteria as described in Section 8.2, Figure PG&E-8.2.1-2, of the WMP. However, if undergrounding is not feasible or does not satisfy the CBR and/or Net Benefit requirements, we will collaborate with PG&E’s vegetation management team to determine whether covered conductor (CC) and associated vegetation removal is an acceptable alternative. c. Ingress and egress routes are evaluated by a PG&E Public Safety Specialist, whose guidance ensures our underground design supports safe and efficient movement for civilians and first responders during an emergency. As noted in “WMP-Discovery2026-2028_DR_TURN-002_Q010.pdf”, the PSS considers many factors when evaluating ingress and egress concerns, and it is not possible to identify each and every criterion and how that criterion particularly impacts risk in every situation. The specific facts and circumstances of each situation must be considered on a case by case basis. The specific facts and circumstances of a case, when taken together, form our understanding of the real time risk associated with a particular area. Some of the factors considered include, but are not limited to: • Population density • Time of day (there are differences between evacuating communities at night when most people are at home compared to during the day when fewer people are at home) • Amount of time the public would need to evacuate or shelter in place • Notifications and information made available to the public • Road infrastructure (e.g., road size, number of lanes, type of surface, destination) • Fuel types along an evacuation corridor (e.g., grass vs. brush vs. timber) • Elevated Weather conditions (e.g., red flag days including high temperatures, high winds, low relative humidities) • Topography/terrain (do evacuation routes place evacuees in danger due to steep slopes, drainages, and chimneys along a corridor which are often associated with extreme fire behavior) • Human factors (e.g., elderly, special needs, evacuating large and small pets, knowledge or experience of citizens living in high fire hazard areas) • Location of overhead electrical assets (e.g., poles proximity to the road’s shoulder and conductor crossings over those ingress/egress thoroughfares should they become impacted by fire and fail onto the evacuation corridor) • Firefighting ingress (e.g., number, type, size of equipment, staging areas, etc. | A Mireille Fall-Fry | 2025-05-01 | 2025-05-06 | 2025-05-06 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-TURN_004.zip | 0 | No | 8 | Grid Design, Operations, and Maintenance | 8.2.1 | Covered Conductor Installation
18 | 212 | TURN | 004 | TURN_004 | 6 | No | TURN_004_Q6 | Regarding PG&E’s System Hardening Project Process Decision Tree and Process Figures 8.2.1-1, 8.2.1-2, and 8.2.1-3 on pages 182–84: a. Does PG&E utilize project-specific unit costs for CC and UG as opposed to generic averages? Please explain. | c. Ingress and egress routes are evaluated by a PG&E Public Safety Specialist, whose guidance ensures our underground design supports safe and efficient movement for civilians and first responders during an emergency. As noted in “WMP-Discovery2026-2028_DR_TURN-002_Q010.pdf”, the PSS considers many factors when evaluating ingress and egress concerns, and it is not possible to identify each and every criterion and how that criterion particularly impacts risk in every situation. The specific facts and circumstances of each situation must be considered on a case by case basis. The specific facts and circumstances of a case, when taken together, form our understanding of the real time risk associated with a particular area. Some of the factors considered include, but are not limited to: • Population density • Time of day (there are differences between evacuating communities at night when most people are at home compared to during the day when fewer people are at home) • Amount of time the public would need to evacuate or shelter in place • Notifications and information made available to the public • Road infrastructure (e.g., road size, number of lanes, type of surface, destination) • Fuel types along an evacuation corridor (e.g., grass vs. brush vs. timber) • Elevated Weather conditions (e.g., red flag days including high temperatures, high winds, low relative humidities) • Topography/terrain (do evacuation routes place evacuees in danger due to steep slopes, drainages, and chimneys along a corridor which are often associated with extreme fire behavior) • Human factors (e.g., elderly, special needs, evacuating large and small pets, knowledge or experience of citizens living in high fire hazard areas) • Location of overhead electrical assets (e.g., poles proximity to the road’s shoulder and conductor crossings over those ingress/egress thoroughfares should they become impacted by fire and fail onto the evacuation corridor) • Firefighting ingress (e.g., number, type, size of equipment, staging areas, etc. | A Mireille Fall-Fry | 2025-05-01 | 2025-05-06 | 2025-05-06 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-TURN_004.zip | 0 | No | 8 | Grid Design, Operations, and Maintenance | 8.2.1 | Covered Conductor Installation
18 | 213 | TURN | 004 | TURN_004 | 7 | No | TURN_004_Q7 | Regarding Table 8.2.1-2 on page 189, please explain whether mitigation effectiveness is calculated based on SME judgement. In each case where SME judgement is used, please explain why PG&E does not utilize datadriven methods to calculate mitigation effectiveness. | All effectiveness ratings in Table 8.2.1-2 are calculated based on SME review. These ratings are used in combination with available outage data (as a proxy for ignitions) to estimate mitigation effectiveness. The SME-based approach allows PG&E to calculate a realistic effectiveness estimate based on limited mitigation-specific outage data. Relying entirely on a data-based approach to calculate effectiveness for these mitigations would not yield meaningful results. For example, as detailed in “RAMP-2024_DR_TURN_006-Q004.pdf” and “WMP-Discovery2026-2028_DR_TURN_003-Q008.pdf”, observed ignition data is quite limited for novel system hardening mitigations. Only three reportable ignitions have been observed on covered conductor since its broad application began around 2018. Much of PG&E’s covered conductor installation has also been in wildfire rebuild areas (in burned-scarred areas with limited vegetation growth) or purposefully installed in areas of low tree strike risk in alignment with PG&E’s decision tree. Furthermore, limited degradation of these assets has occurred due to their recent installation, biasing observed effectiveness estimates. For all of these reasons, it is necessary to rely on SME input to inform these estimates. Another potential issue with purely data-driven calculation methods, is the overlap between mitigations deployed simultaneously. For example, EPSS and covered conductor can be complimentary mitigations, but using only observed data, it is difficult to bifurcate their effectiveness contributions ,or even identify a statistically valid data sample where these mitigations were concurrently operational. The SME-based analysis allows PG&E’s experts to apply their knowledge and experience to assess those scenarios despite the limited deployment of these mitigations. WMP-Discovery 2026-2028_DR_TURN_004-Q007 Page 2 Finally, the actual application of the effectiveness values referenced in Table 8.2.1-2 is much more detailed than depicted in this simple table. Specifically, driver-level effectiveness values are applied to the unique risk drivers of WDRM, which themselves are derived from data-driven observations and events in PG&E’ system of record. This allows PG&E to calculate specific mitigation effectiveness values for each individual circuit segment and ultimately yields a hybrid, SME-informed, data-driven result. | A Mireille Fall-Fry | 2025-05-01 | 2025-05-06 | 2025-05-06 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-TURN_004.zip | 0 | No | 8 | Grid Design, Operations, and Maintenance | 8.2.1 | Covered Conductor Installation
18 | 214 | TURN | 004 | TURN_004 | 8 | No | TURN_004_Q8 | Regarding Table 8.2.1-5 on page 195: a. Please provide this table in Excel with supporting calculations. b. Please add the following information to the Excel table and include all data, calculations, and assumptions: i. Annual and cumulative number of overhead miles in each year from 2023 (recorded) to 2026 (forecast) for each activity separately (covered conductor and undergrounding). ii. Annual and cumulative costs in each year from 2023 to 2026 (including forecast years) for each activity separately (covered conductor and undergrounding). Please provide supporting calculations. iii. Annual and cumulative risk reduction from all other primary wildfire mitigations from 2023-2026 (including forecast years). iv. Annual and cumulative costs from all other primary wildfire mitigations from 2023-2026 (including forecast years). v. Annual and cumulative costs to implement EPSS and PSPS in each year (separately) from 2023-2026 (including forecast years), if not previously included. | a. Please see “WMP-Discovery2026-2028_DR_TURN_004-Q008Atch01.xlsx” at the tab titled “Table 8.2.1-5” for a version of Table 8.2.1-5 in Excel format. Please see “WMP-Discovery2026-2028_DR_TURN_004-Q008Atch01.xlsx” at the tab titled “Supporting Data” for the risk reduction data upon which Table 8.2.1-5 is based. Please note that, for clarity, PG&E has removed circuit segments with no listed risk reduction from the “Supporting Data” tab. The risk reduction values provided in Table 8.2.1-5 are sums of the segment-level risk reduction values provided. Please note that the calculations underlying each segment-level risk reduction value were WMP-Discovery 2026-2028_DR_TURN_004-Q008 Page 2 conducted in the Foundry Platform, and PG&E is not able to re-create them in Excel in a reasonably timely manner. | A Mireille Fall-Fry | 2025-05-01 | 2025-05-12 | 2025-05-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-TURN_004.zip | 1 | No | 8 | Grid Design, Operations, and Maintenance | 8.2.1 | Covered Conductor Installation
18 | 214 | TURN | 004 | TURN_004 | 8(s) | Yes | TURN_004_Q8(s) | Regarding Table 8.2.1-5 on page 195: a. Please provide this table in Excel with supporting calculations. b. Please add the following information to the Excel table and include all data, calculations, and assumptions: i. Annual and cumulative number of overhead miles in each year from 2023 (recorded) to 2026 (forecast) for each activity separately (covered conductor and undergrounding). ii. Annual and cumulative costs in each year from 2023 to 2026 (including forecast years) for each activity separately (covered conductor and undergrounding). Please provide supporting calculations. iii. Annual and cumulative risk reduction from all other primary wildfire mitigations from 2023-2026 (including forecast years). iv. Annual and cumulative costs from all other primary wildfire mitigations from 2023-2026 (including forecast years). v. Annual and cumulative costs to implement EPSS and PSPS in each year (separately) from 2023-2026 (including forecast years), if not previously included. | b. Please see attachment “WMP-Discovery2026-2028_DR_TURN_004- Q008Supp01Atch01.xlsx”, worksheet ’8bi, 8bii’ for the requested information. Please note the following regarding the response to subparts 8(b)(i) and 8(b)(ii): • The values reported in the Covered Conductor category include Line Removal work. • The values reported in the Undergrounding category include Community Rebuild work. • The values reported represent work under PG&E’s System Hardening and Undergrounding programs. i. Annual and cumulative miles for overhead hardening and undergrounding (2023-2026) have been provided. • Includes miles from non-System Hardening programs (Work Requested by Others, Capacity, Idle Facilities, etc.) in HFTD. No financial is provided for those sub-projects. ii. Annual and cumulative costs for overhead hardening and undergrounding (2023-2026) have been provided. • Includes readiness costs for sub-projects to be completed in future years. • Includes close-out costs for sub-projects that have been completed in prior years. iii. Per confirmation received from TURN on May 13, 2025, this response will be provided by May 16, 2025. For the purposes of responding to subpart 8(b)(iii) and (iv), PG&E interprets “other primary wildfire mitigations” as: • PSPS (MAT Codes: WFN, WFP). • EPSS (MAT Codes: 05#, 09B, 21#, 3US, 48D, 49#, 49B, 49D, 49E, 49G, 63C, BAF, BAH, BFJ, BHE, DD#, FZA, FZE, GC2, HGD, HXA, IG#). iv. Annual and cumulative costs for other primary mitigations (2023-2026) have been provided. Please see attachment “WMP-Discovery2026- 2028_DR_TURN_004-Q008Supp01Atch01.xlsx” , worksheet “8biv, 8bv,” for the requested information. v. Annual and cumulative costs to implement EPSS and PSPS (2023-2026) have been provided. Please see attachment “WMP-Discovery2026- 2028_DR_TURN_004-Q008Supp01Atch01.xlsx”, worksheet “8biv, 8bv,” for the requested information. | A Mireille Fall-Fry | 2025-05-01 | 2025-05-13 | 2025-05-13 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-TURN_004.zip | 1 | No | 8 | Grid Design, Operations, and Maintenance | 8.2.1 | Covered Conductor Installation
18 | 214 | TURN | 004 | TURN_004 | 8(s2) | Yes | TURN_004_Q8(s2) | Regarding Table 8.2.1-5 on page 195: a. Please provide this table in Excel with supporting calculations. b. Please add the following information to the Excel table and include all data, calculations, and assumptions: i. Annual and cumulative number of overhead miles in each year from 2023 (recorded) to 2026 (forecast) for each activity separately (covered conductor and undergrounding). ii. Annual and cumulative costs in each year from 2023 to 2026 (including forecast years) for each activity separately (covered conductor and undergrounding). Please provide supporting calculations. iii. Annual and cumulative risk reduction from all other primary wildfire mitigations from 2023-2026 (including forecast years). iv. Annual and cumulative costs from all other primary wildfire mitigations from 2023-2026 (including forecast years). v. Annual and cumulative costs to implement EPSS and PSPS in each year (separately) from 2023-2026 (including forecast years), if not previously included. | b. iii. For the purposes of this response, please note that PG&E interprets “other primary wildfire mitigations” as PSPS and EPSS. Please see “WMPDiscovery2026-2028_DR_TURN_004-Q008Supp02Atch01.xlsx” for PG&E’s best available estimates of the annual and cumulative percent risk reductions requested. | A Mireille Fall-Fry | 2025-05-01 | 2025-05-19 | 2025-05-19 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-TURN_004.zip | 1 | No | 8 | Grid Design, Operations, and Maintenance | 8.2.1 | Covered Conductor Installation
18 | 215 | TURN | 004 | TURN_004 | 9 | No | TURN_004_Q9 | Regarding Table 8-5-2 on page 321, please provide these figures on an annual basis, from December 31, 2015, through 2023. At a minimum, please provide the 181+ figures. | Please see the table below for the requested information. Please note that, to align with Table 8-5-2 on page 321, the counts in this table include notifications that: (1) were open as of Dec 31st of each year; (2) were open past their authorized end date; (3) were GO 95 Level 2 or Level 3; and (4) had MAT codes included in the Quarterly Data Report. | A Mireille Fall-Fry | 2025-05-01 | 2025-05-06 | 2025-05-06 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-TURN_004.zip | 0 | No | 8 | Grid Design, Operations, and Maintenance | 8.5 | Quality Assurance and Quality Control
18 | 216 | TURN | 004 | TURN_004 | 10 | No | TURN_004_Q10 | Please provide a list of mitigations PG&E has examined for how to reduce the “consequence” (outages and outage time) of PSPS and EPSS. Please include the following: a. Mitigation effectiveness of each mitigation, including all workpapers and an explanation. b. Unit cost or other relevant metrics. c. All supporting data and workpapers. | For PSPS, see “Section 10 – Mitigations to Reduce Impact” of each of the post-event report1 where we discuss the reduction of impacted customers driven by the different mitigation efforts. Additionally, see section “B. Direction” in the Post-Season1 report for revisions made to the counts of customers mitigated. For System Hardening: The System Hardening Program has examined four mitigations for reducing consequences of PSPS and EPSS: undergrounding all; undergrounding primary distribution lines; overhead hardening; and line removal with remote grid. a. Provided in the table below is the outage mitigation effectiveness for the System Hardening mitigations: (A) Underground assets and remote grids are exempt from PSPS and EPSS protocols. There are upstream dependencies that could result in an underground line being deenergized, but EPSS and PSPS events are not targeted for underground or remote grid assets. (B) 52% effectiveness applies only to EPSS reliability mitigation effectiveness. It is assumed that covered conductor provides 0% reliability mitigation effectiveness for PSPS. See “WMP-Discovery2026-2028_DR_TURN_004-Q010Atch01.xlsx” b. Provided in the table below are the 2024 unit costs for the System Hardening mitigations: (A) PG&E has not yet pursued Undergrounding All (primary and secondary lines) and does not have recorded unit cost data. For reference, please see “WMP-Discovery2026-2028_DR_TURN_004-Q010Atch02.xlsx”, with a few notes about the assumptions included: • Unit cost is calculated based on the total costs-since-inception (multi-year) of the subprojects that are 100% complete each year – in this case, for 2024. • For Undergrounding, we have included the unit costs for system hardening undergrounding, which excludes Community Rebuild undergrounding. • Note, unit cost is not calculated by dividing the total program cost spent in one year by the total miles completed in one year because this would inaccurately include the readiness costs for future work that is not yet complete and post-construction costs for previously completed projects. c. Supporting workpapers are provided as attachments for mitigation effectiveness and unit cost, respectively: “WMP-Discovery2026-2028_DR_TURN_004-Q010Atch01.xlsx” and “WMP-Discovery2026-2028_DR_TURN_004-Q010Atch02.xlsx.” | A Mireille Fall-Fry | 2025-05-01 | 2025-05-13 | 2025-05-13 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-TURN_004.zip | 2 | No | 7 | Public Safety Power Shutoff | 7 | Public Safety Power Shutoff
18 | 217 | OEIS | 008 | OEIS_008 | 1 | No | OEIS_008_Q1 | Regarding Tree Strike Potential On page 184 of PG&E’s 2026-2028 Base WMP, in Figure PG&E-8.2.1-2, PG&E shows that it considers a tree strike potential of five or greater as “High”. On page 432 of PG&E’s 2023-2025 Base WMP R8, Figure SRN-PG&E-23-05-6A shows a tree strike potential of fifteen or greater as “High.” a. Explain why PG&E has changed the threshold for determining the significance of tree strike potential. b. Provide an analysis of the magnitude of impact changing this threshold has had. This should include: i. The number of projects that meet this threshold at five compared to fifteen. ii. The number of circuit segments that meet this threshold at five compared to fifteen. | a. PG&E has not changed the threshold for determining whether the significance of tree strike potential warrants consideration for undergrounding. The changes in tree strike language between Figure SRN-PG&E-23-05-06A and Figure PG&E-8.2.1-2 reflect the fact that we have simplified the tree strike risk categories/label to align with the decision tree logic. The logic surrounding tree strike has not changed and is the same in Figure PG&E-8.2.1-2 and in Figure SRN-PG&E-23-05-06A. In both cases, an area with a tree strike score of 6 or higher is identified as “Area of impact identified, relocate to underground preferred.” In both cases an area with a tree strike score of 0-5 is identified as “No area of impact identified, OH in place preferred.” b. There has been no impact because there has been no change to the threshold. i. N/A ii. N/A | Nathan Poon | 2025-05-02 | 2025-05-07 | 2025-05-07 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_008.zip | 0 | No | 8 | Grid Design, Operations, and Maintenance | 8.2.1 | Covered Conductor Installation
18 | 218 | OEIS | 008 | OEIS_008 | 2 | No | OEIS_008_Q2 | Regarding PG&E’s Response to OEIS-P-WMP_2025-PG&E-004 Question 04 a. In part (c) of PG&E’s response to data request OEIS-P-WMP_2025-PG&E-004 question 04, PG&E identifies four circuit protection zones as being “privately owned lines.” i. PG&E states within this data request response that two of the lines were identified as not being privately owned through the validation process. Given this change, describe how PG&E intend to adjust its current hardening plan in order to reduce risk along these lines. ii. Provide a list of who owns each of these lines. iii. If the lines are owned by someone other than PG&E, why is PG&E including the lines as part of their highest risk circuit segments? iv. Provide a description of PG&E’s procedures for working with line owners to decrease risk along their lines. b. In part (c) of PG&E’s response to data request OEIS-P-WMP_2025-PG&E-004 question 04, PG&E identifies many of the circuit segments to not be included based on not being a “part of selection criteria” as work is “based on density of risk per mile” and “not total risk on the circuit segment.” i. Provide an updated version of Table 6-4 based on risk density opposed to total risk score. This must also include the total mileage for each circuit segment, and mileage. | a. i. At the time of PG&E’s WMP submission, the 2027 and 2028 work plan had not yet been fully scoped. For purposes of estimating risk reduction associated with PG&E’s GH-04 WMP initiative mileage target, PG&E identified a list of circuit segments that would be considered for scoping. The workplan is dynamic and will continue to evolve as circuit segments, including work on BIG BEND 1101CB and MIDDLETOWN 1101644756, are considered for scoping in accordance with the System Hardening Project Scoping Decisions Trees provided in the WMP Figures PG&E-8.2.1-1, PG&E-8.2.1-2, and PG&E-8.2.1-3. ii. Please see attachment “WMP-Discovery2026-2028_DR_OEIS_008- Q002Atch01CONF.xlsx” for owners of the two privately-owned lines. iii. PG&E’s risk model reflects all lines mapped in the PG&E service area, not just those that are PG&E-owned. Ultimately, the privately owned lines get filtered out during the mitigation selection process when the ownership of the line is confirmed. iv. PG&E sends annual notices to private line owners, informing them of their maintenance responsibilities. See attachment “WMP-Discovery2026- 2028_DR_OEIS_008-Q002Atch02CONF.pdf”, which is an example of the letter sent by PG&E. While inspecting PG&E-owned transformers on private lines, PG&E personnel will send third-party notifications to line owners for infractions observed on their facilities. The Privately-Owned Lines group within PG&E’s Asset Strategy team will communicate with owners to ensure repairs are made in a timeframe commensurate with the infraction and fire threat risk designation of the location. We do not recommend any hardening standards. Pursuant to agreement with OEIS, PG&E will supplement this response to provide part (b) by Friday, May 16. | Nathan Poon | 2025-05-02 | 2025-05-07 | 2025-05-07 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_008.zip | 2 | No | 6 | Wildfire Mitigation Strategy Development | 6.2.1.3 | Projected Risk Reduction on Highest-Risk Circuits Over the Three-Year WMP Cycle
18 | 218 | OEIS | 008 | OEIS_008 | 2(s) | Yes | OEIS_008_Q2(s) | Regarding PG&E’s Response to OEIS-P-WMP_2025-PG&E-004 Question 04 a. In part (c) of PG&E’s response to data request OEIS-P-WMP_2025-PG&E-004 question 04, PG&E identifies four circuit protection zones as being “privately owned lines.” i. PG&E states within this data request response that two of the lines were identified as not being privately owned through the validation process. Given this change, describe how PG&E intend to adjust its current hardening plan in order to reduce risk along these lines. ii. Provide a list of who owns each of these lines. iii. If the lines are owned by someone other than PG&E, why is PG&E including the lines as part of their highest risk circuit segments? iv. Provide a description of PG&E’s procedures for working with line owners to decrease risk along their lines. b. In part (c) of PG&E’s response to data request OEIS-P-WMP_2025-PG&E-004 question 04, PG&E identifies many of the circuit segments to not be included based on not being a “part of selection criteria” as work is “based on density of risk per mile” and “not total risk on the circuit segment.” i. Provide an updated version of Table 6-4 based on risk density opposed to total risk score. This must also include the total mileage for each circuit segment, and mileage. | b. i. In this context, PG&E understands “risk density” to mean risk per Primary Overhead Mile. Table 6-4 consists of the circuit segments that make up the top 20% of overall utility risk. The table is not re-ranked based on the “risk density”. Additionally, we have only included the total mileage of the circuit segment in the tables as we interpret “total mileage for each circuit segment, and mileage” to be identical. Please see attachment “WMP-Discovery2026- 2028_DR_OEIS_008-Q002Supp01Atch01.xlsx”. | Nathan Poon | 2025-05-02 | 2025-05-16 | 2025-05-16 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_008.zip | 1 | No | 6 | Wildfire Mitigation Strategy Development | 6.2.1.3 | Projected Risk Reduction on Highest-Risk Circuits Over the Three-Year WMP Cycle
19 | 219 | MGRA | 006 | MGRA_006 | 1 | No | MGRA_006_Q1 | Please provide all information available on the following risk events, including detailed cause information, lessons learned, the type of conductor or equipment involved in particular whether the segment had been converted to covered conductor. a. On 8/3/2024, at 6:14 am, an ignition was reported related to PG&E infrastructure at latitude 39.0932719 longitude -121.308724 b. On 11/8/2024, at 11:42 AM, a post PSPS inspection revealed a damage event at latitude 37.102827 and longitude -121.900178. | a. PG&E confirmed with MGRA that this question intends to refer to an ignition on August 23, 2024, not August 3, 2024. Please see “WMP-Discovery2026-2028_DR_MGRA_006-Q001Atch01.xlsx” for information regarding the ignition. b. Please see “WMP-Discovery2026-2028_DR_MGRA_006-Q001Atch02.xlsx” for information regarding this PSPS damage event. Please note that PG&E does not collect information regarding the type of conductor during PSPS patrols. | Joseph Mitchell | 2025-05-05 | 2025-05-08 | 2025-05-08 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-MGRA_006.zip | 2 | No | 5 | Risk Methodology & Assessment | 5.2.2.2 | Consequence of Risk Event
19 | 220 | MGRA | 006 | MGRA_006 | 2 | No | MGRA_006_Q2 | With reference to PG&E’s Wildfire Consequence model v4 documentation, Sections 4.1, 4.2, and 4.3 please provide substantive answers to OEIS_001-Q025 c. and d. | c. As documented in Section 4.1, the covariates used in the suppression model, which predicts the survival fraction of structures involved in a fire, are Terrain Difficulty Index (TDI), live fuel moisture, and wind speed. Among these, only TDI relates to “access”. d. As documented in Section 4.2, the covariates used in the egress model are Access and Functional Needs (AFN) and wind speed. | Joseph Mitchell | 2025-05-05 | 2025-05-12 | 2025-05-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-MGRA_006.zip | 0 | No | 5 | Risk Methodology & Assessment | 5.4 | Summary of Risk Models
19 | 221 | MGRA | 006 | MGRA_006 | 3 | No | MGRA_006_Q3 | WFC v4 Section 4.1.3.1 states that “The TDI is composite index from 1 to 5 that uses local topography and other factors to determine speed and ease of access from public roads and fire line feasibility for service territory equipment asset locations” a. List all “other factors” that are included other than local topography. b. What are the topographic variables that are included in TDI? c. How are the topographic and other variables combined and weighted to compose the TDI? d. What metrics were used to validate that the TDI accurately “determine[s] speed and ease of access from public roads and fire line feasibility for service territory equipment asset locations”? e. Please provide this validation. | a. The Terrain Difficulty Index (TDI) is a proprietary, quantitative measure developed by Technosylva that is designed to assess how challenging it may be to contain a wildfire, particularly during initial attack operations. It reflects terrain-related factors that influence suppression efforts and the complexity of fuel conditions. TDI supports wildfire response planning by combining multiple indicators into a single, interpretable score. Given the proprietary nature of this information, Technosylva would not disclose the information without a non-disclosure agreement. Please let us know if you would like to meet and confer to discuss this request further. b. Technosylva proprietary inputs and sub-indices relate to suppression and the complexity of fuel conditions. Given the proprietary nature of this information, Technosylva would not disclose the information without a non-disclosure agreement. Please let us know if you would like to meet and confer to discuss this request further. WMP-Discovery 2026-2028_DR_TURN_001-Q003 Page 2 c. The set of sub-indices to calculate the final TDI is Technosylva proprietary within their operational and planning tools. Given the proprietary nature of this information, Technosylva would not disclose the information without a non-disclosure agreement. Please let us know if you would like to meet and confer to discuss this request further. d. Preliminary validation has shown that higher TDI, FBI (Fire Behavior Index), and IAA values correlate with lower initial attack success rates, helping agencies and utilities better anticipate when a fire may exceed available suppression capabilities. e. The methodology described in subpart (d) above is currently undergoing peer review and is expected to be published soon in the International Journal of Wildland Fire. | Joseph Mitchell | 2025-05-05 | 2025-05-12 | 2025-05-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-MGRA_006.zip | 0 | No | 5 | Risk Methodology & Assessment | 5.4 | Summary of Risk Models
19 | 222 | MGRA | 006 | MGRA_006 | 4 | No | MGRA_006_Q4 | With regard to WFC v4 Table 9: a. Table 9 presents an abridged summary of the model regression results. Please provide the full model regression results. b. P value is shown to be 0 (or less than 0.00005) in Table 9. What is the meaning of this P value? Does this imply a perfect fit? c. In the regression, how many variables were used to fit how many bins of data? d. Please also provide the validation that was done to quantify the explanatory value of TDI and other variables | a. Please see the table below for the requested results. Generalized Linear Model Regression Results =============================================================================================== coef std err z P>¦z¦ [0.025 0.975] ----------------------------------------------------------------------------------------------- Intercept -3.3012 0.021 -159.431 0.000 -3.342 -3.261 tdi 0.9263 0.002 508.681 0.000 0.923 0.930 lfm_chamise_1km -0.0207 0.000 -74.746 0.000 -0.021 -0.020 ws_mph_300m 0.0266 0.000 245.897 0.000 0.026 0.027 =============================================================================================== b. We are reporting standard regression model P-values for coefficients as computed by the machine learning python package “statsmodels”. In regression modeling, the P-value for a coefficient quantifies the probability that the Null Hypothesis (that the true value of the coefficient is zero) is true. Small P-values indicate that the coefficient in question is statistically significant (i.e. very unlikely to actually be zero). Small P-values confirm covariance between the explanatory variables and the variable being modeled but do not directly relate to “perfect fit”. c. Three variables and a constant term were used to fit structure loss outcomes from 5,299 fires. It is unclear what “bins of data” would refer to in this context. WMP-Discovery 2026-2028_DR_TURN_001-Q004 Page 2 d. The regression model results table provides diagnostics for the statistical significance of the model coefficients. The worked examples in Section 4.1 also provide a sanity check on the range of possible model predictions in a real-world setting. | Joseph Mitchell | 2025-05-05 | 2025-05-12 | 2025-05-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-MGRA_006.zip | 0 | No | 5 | Risk Methodology & Assessment | 5.4 | Summary of Risk Models
19 | 223 | MGRA | 006 | MGRA_006 | 5 | No | MGRA_006_Q5 | In Section 4.1.2.1 PG&E’s model asserts that 𝑆𝑡𝑟𝑢𝑐𝑡𝑢𝑟𝑒 𝐿𝑜𝑠𝑠 𝐹𝑟𝑎𝑐𝑡𝑖𝑜𝑛 ≅𝑓(𝐹𝑢𝑒𝑙𝑠,𝑇𝑒𝑟𝑟𝑎𝑖𝑛,𝑊𝑒𝑎𝑡ℎ𝑒𝑟) The literature on structure loss in wildfire is extensive and lists a number of variables that have been shown to correlate with structure loss. These include housing materials, age of neighborhood, density of neighborhood and separation of houses, proximity of vegetation to the structure, enclosed eves and vents, and others. a. How does PG&E’s structure loss model incorporate other variables that are implicit to the structures, maintained landscapes, and neighborhoods? b. Please provide the numerical values that went into Figures 9 and 10. c. Figure 10 implies that for TDI=1 that the probability of structure is very small (counts for loss < 0.3 >> loss > 0.3), and that for TDI=5 probability of structure loss is very large (counts for loss > 0.7 >> loss < 0.7). Does this imply that PG&E’s model assumes that home survival fraction is primarily dependent on the availability of firefighting resources? If so, what justification (analysis or citations) does it provide for this assertion? | a. The structure loss fraction model is focused on fire behavior, not community vulnerability. The empirical data on structure losses from historical fires used to train the model is, by definition, inclusive of a wide range of conditions in the built environment. However, given the sensitivity of outcomes to weather and fire behavior extremes, where extreme fire behavior can overwhelm even the best firefighting resources and landscape and building measures, the modeling team did not feel it would be appropriate to report lower consequence, and therefore discourage mitigation, in locations with expected destructive fire behavior but potentially favorable structure spacing or characteristics. As a practical matter, the vast majority of the building stock is untouched by fire building codes and we expect all Wildland Urban Interface (WUI) communities in CA (and beyond) to have structures with characteristics favorable to ignition. We WMP-Discovery 2026-2028_DR_TURN_001-Q005 Page 2 also note that we have consulted experts in the fire research community and have not identified reliable sources of data on housing materials, landscaping vegetation, roof conditions, etc. that cover PG&E’s territory. We have found that the literature on structure loss (likely consistent with research referenced in the question) is primarily focused on explaining the survival of specific structures after specific fires, where such data is gathered locally and after the fact – and therefore not suitable to our purposes. The relative vulnerability of specific communities to fire is a topic of ongoing research and model development both inside PG&E and in the wider wildfire modeling community. b. As discussed during a call with MGRA on May 8, 2025, we anticipate responding to this question on May 14, 2025. c. The suppression model is a regression model that quantifies correlations between the survival fraction of structures and the TDI, fuel moisture, and wind speed covariates from the fire footprint. The model provides the best statistical fit to the training data; it does not make assumptions. The model fit indicates that all three major covariates are statistically significant, with the value of the coefficients multiplied by the underlying covariate values determining the size of the contribution to the predicted structure loss for each fire. The TDI coefficient values is larger than the wind speed and fuel moisture coefficients, but TDI values range from 1 to 5, wind speeds range from 0 to 90+ mph, and fuel moisture is mainly between 60 and 150, so the magnitude of relative contributions from TDI vs. wind speed vs. fuel moisture will vary by fire without consistently being dominated by TDI. We assume the contribution from TDI relates to the fact that fires that are harder to reach, further from roads, and in more rugged terrain are more likely to escape “initial attack” becoming more established and more likely to spread further in the process. Also presumably related to TDI, surrounding slopes can also aid fire spread as fire prefers to burn uphill. | Joseph Mitchell | 2025-05-05 | 2025-05-12 | 2025-05-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-MGRA_006.zip | 0 | No | 5 | Risk Methodology & Assessment | 5.4 | Summary of Risk Models
19 | 223 | MGRA | 006 | MGRA_006 | 5(s) | Yes | MGRA_006_Q5(s) | In Section 4.1.2.1 PG&E’s model asserts that 𝑆𝑡𝑟𝑢𝑐𝑡𝑢𝑟𝑒 𝐿𝑜𝑠𝑠 𝐹𝑟𝑎𝑐𝑡𝑖𝑜𝑛 ≅𝑓(𝐹𝑢𝑒𝑙𝑠,𝑇𝑒𝑟𝑟𝑎𝑖𝑛,𝑊𝑒𝑎𝑡ℎ𝑒𝑟) The literature on structure loss in wildfire is extensive and lists a number of variables that have been shown to correlate with structure loss. These include housing materials, age of neighborhood, density of neighborhood and separation of houses, proximity of vegetation to the structure, enclosed eves and vents, and others. a. How does PG&E’s structure loss model incorporate other variables that are implicit to the structures, maintained landscapes, and neighborhoods? b. Please provide the numerical values that went into Figures 9 and 10. c. Figure 10 implies that for TDI=1 that the probability of structure is very small (counts for loss < 0.3 >> loss > 0.3), and that for TDI=5 probability of structure loss is very large (counts for loss > 0.7 >> loss < 0.7). Does this imply that PG&E’s model assumes that home survival fraction is primarily dependent on the availability of firefighting resources? If so, what justification (analysis or citations) does it provide for this assertion? | The calculations in the section of documentation that includes Figures 9 and 10 were included as examples from a development version of the model, notably before weights were added to emphasize model fit against fires with more buildings in their footprints compared to those with fewer buildings, and fit using an earlier version of the fires data set. For these reasons, the data highlighted in the documentation example was not aligned with the values used in the v4 release. The number of fires in the deciles of predicted loss fraction consistent with the v4 model are provided in the table below: | Joseph Mitchell | 2025-05-05 | 2025-05-14 | 2025-05-14 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-MGRA_006.zip | 0 | No | 5 | Risk Methodology & Assessment | 5.4 | Summary of Risk Models
19 | 224 | MGRA | 006 | MGRA_006 | 6 | No | MGRA_006_Q6 | The analysis provided estimated TDI values for the Dixie fire. Please provide a TDI for other major fires as well including: a. Eaton (2025) b. Palisades (2025) c. Lahaina (2023) | TDI data was licensed from Technosylva for PG&E’s service territory and is proprietary. We do not have access to TDI values for any of the requested fire locations, all of which were outside of PG&E’s service territory. We observe that the primary suppressionrelevant characteristic shared by those fires was their rate of spread, supported by extremely dangerous fuel and wind conditions. | Joseph Mitchell | 2025-05-05 | 2025-05-12 | 2025-05-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-MGRA_006.zip | 0 | No | 5 | Risk Methodology & Assessment | 5.4 | Summary of Risk Models
19 | 225 | MGRA | 006 | MGRA_006 | 7 | No | MGRA_006_Q7 | Was PG&E’s suppression model developed internally or by a third party vendor, and if the latter which vendor? | PG&E’s suppression model is a regression model that was developed internally. As discussed in the previous responses in this set of data requests, the TDI covariate was developed by and licensed from Technosylva. | Joseph Mitchell | 2025-05-05 | 2025-05-12 | 2025-05-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-MGRA_006.zip | 0 | No | 5 | Risk Methodology & Assessment | 5.4 | Summary of Risk Models
19 | 226 | MGRA | 006 | MGRA_006 | 8 | No | MGRA_006_Q8 | With regard to Table 12 a. Please provide the full model regression results. b. P value is shown to be 0 (or less than 0.00005) in Table 12. What is the meaning of this P value? Does this imply a perfect fit? c. In the regression, how many variables were used to fit how many bins of data? d. Please also provide the validation that was done to quantify the explanatory value of AFN and other variables. | a. The calculations in the section of documentation were included as examples and were not aligned with the values used in the v4 release. The results in the table below, and the discussion that follows, are based on the model fit with coefficients aligned with the released v4 model. Generalized Linear Model Regression Results ============================================================================================== coef std err z P>¦z¦ [0.025 0.975] ---------------------------------------------------------------------------------------------- Intercept -7.2095 0.224 -32.156 0.000 -7.649 -6.770 afn_10km_pct 3.0006 0.453 6.621 0.000 2.112 3.889 ws_mph_300m 0.0133 0.002 6.607 0.000 0.009 0.017 ============================================================================================== b. We are reporting standard regression model P-values for coefficients as computed by the well-known machine learning python package “statsmodels”. In regression modeling, the P-value for a coefficient quantifies the probability that the Null Hypothesis (that the true value of the coefficient is zero) is true. Small P-values indicate that the coefficient in question is statistically significant (i.e. very unlikely to actually be zero). Small P-values confirm covariance between the explanatory variables and the variable being modeled but do not directly relate to “perfect fit”. WMP-Discovery 2026-2028_DR_TURN_001-Q008 Page 2 c. The regression uses two variables and an intercept to fit 170 fire outcomes involving fatalities. It is unclear what “bins of data” would refer to in this context. d. The regression model results table provides diagnostics for the statistical significance of the model coefficients. The worked examples in Section 4.2 also provide a sanity check on the range of possible model predictions in a real-world setting. | Joseph Mitchell | 2025-05-05 | 2025-05-12 | 2025-05-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-MGRA_006.zip | 0 | No | 5 | Risk Methodology & Assessment | 5.4 | Summary of Risk Models
19 | 227 | MGRA | 006 | MGRA_006 | 9 | No | MGRA_006_Q9 | In Section 4.2.3, PG&E advances the hypothesis that AFN fraction is a predictor of fatalities, using the Camp fire as an example with high statistics. a. Figure 12 shows an age distribution for the Camp fire fatalities. Please provide an equivalent age distribution graph for the 50,000 people who evacuated from the Camp fire. | a. We are not aware of a survey of evacuees but we did consult the 2010 census results for Paradise: The age distribution was 4,501 people (17.2%) under the age of 18, 1,858 people (7.1%) aged 18 to 24, 4,822 people (18.4%) aged 25 to 44, 8,466 people (32.3%) aged 45 to 64, and 6,571 people (25.1%) who were 65 years of age or older. The median age was 50.2 years. The median age for the victims of the Camp fire is 72 years. Those numbers in a histogram look like the figure below, which depicts the percentage of the population on the y-axis and age-groups on the x-axis. | Joseph Mitchell | 2025-05-05 | 2025-05-12 | 2025-05-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-MGRA_006.zip | 0 | No | 5 | Risk Methodology & Assessment | 5.4 | Summary of Risk Models
19 | 228 | TURN | 005 | TURN_005 | 1 | No | TURN_005_Q1 | Regarding PG&E’s attachment “WMP-Discovery2026- 2028_DR_TURN_003-Q005Atch01,” in Excel please add a column that provides the number of overhead miles for each project listed. | Please see attachment “WMP-Discovery2026-2028_DR_TURN_005-Q001Atch01.xlsx”, workbook “Duration Analysis”, Column J “OH Miles.” A few notes about the data provided: • PG&E has interpreted this request as referring to the original overhead miles that were removed in the subproject and has provided those miles in response. • The primary overhead miles removed and replaced by undergrounding reflect actual overhead miles removed on undergrounding subprojects where data is available. If data is not yet available, we used the adopted1 overhead to undergrounding conversion factor of 1 mile of overhead to 1.25 miles of undergrounding. | A Mireille Fall-Fry | 2025-05-08 | 2025-05-13 | 2025-05-13 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-TURN_005.zip | 1 | No | 6 | Wildfire Mitigation Strategy Development | 6.1.3.1 | Identifying and Evaluating Activities
19 | 229 | TURN | 005 | TURN_005 | 2 | No | TURN_005_Q2 | Regarding TURN-3 PG&E attachment “WMP-Discovery2026- 2028_DR_TURN_003-Q001Atch01”: a. Please provide a definition of each column header. b. What column represents the total risk score of each circuit segment? c. Does PG&E rank circuit segments for prioritization by highest risk by column “(i)” — “SH Wildfire Risk per PriOH Mile” — or something else? Please explain, including what column or calculation is used to rank circuit segments from highest to lowest risk for PG&E’s prioritization of “high risk” miles. d. Does multiplying column “(i)” by “PriOH Miles” (column AY) equal the total risk score for each circuit segment? Please explain. | a. Please see the table below for the definition of each column header. b. The circuit segment total risk score is not shown in any column in this data set. It was not required for the original Cal Advocates data request. c. PG&E ranks circuit segments by the System Hardening composite wildfire risk per primary overhead mile, which is reported as identical values in both columns (i) and (t,2). PG&E orders the wildfire risk per primary overhead mile values from largest to smallest to establish the relative risk rank values. WMP-Discovery 2026-2028_DR_TURN_005-Q002 Page 3 d. Yes, multiplying column (i) or (t,2), the System Hardening wildfire risk per primary overhead mile, times the primary overhead mile length provided in column AY, will generally produce the total wildfire risk sum for a circuit segment. However, there are six circuit segments for which there is no primary overhead mileage and hence the original risk sums will not be recovered. These six segments have only underground primary conductors and a limited amount of secondary overhead conductor miles. Their risk sums are essentially zero. | A Mireille Fall-Fry | 2025-05-08 | 2025-05-13 | 2025-05-13 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-TURN_005.zip | 0 | No | 5 | Risk Methodology & Assessment | 5.4 | Summary of Risk Models
19 | 230 | TURN | 005 | TURN_005 | 3 | No | TURN_005_Q3 | Regarding the decision tree in Figure PG&E 8.2.1-2 on page 184: a. On the first row, third box, “is the UG NB > OH NB,” does “OH NB” include EPSS? Please explain. b. In the first row, why is PSPS and EPSS not evaluated? Please explain. c. Regarding the second row “Begin Hybrid Analysis,” what happens if an answer to one of the questions in a yellow box (e.g. “Are there areas identified with High tree strike potential…” is no? Please explain. d. Regarding the second row “Begin Hybrid Analysis,” what happens if the answer to all three questions in a yellow box (e.g. “Are there areas identified with High tree strike potential…” is no? Please explain. e. Regarding a “Hybrid” project, is it possible for such a project to contain 99% undergrounding and 1% overhead hardening? Please explain. | a. Yes, the comparison is to OH hardening + EPSS. b. The assumed savings associated with PSPS and EPSS are included as appropriate in the benefit associated with the economic comparison between the UG vs OH alternatives. c. If the answer to one of the questions in a yellow box is “no”, then OH hardening + EPSS is assumed to be an acceptable alternative for mitigation for these areas for that reason. d. If the answer to all three questions in a yellow box is “no”, then OH hardening + EPSS would be the selected mitigation, and undergrounding would not be proposed/included in the scope. e. Yes, it is possible, although unlikely, that a “hybrid” project could be 99% undergrounding and 1% overhead hardening. In projects where undergrounding is WMP-Discovery 2026-2028_DR_TURN_005-Q003 Page 2 the primary solution, there are often specific construction limitations that make it unfeasible to underground the entire location. Examples include locations where risers near line reclosers or water crossings prevent underground installation. In these cases, alternative solutions, such as bridge attachments or boring, may not be viable either. | A Mireille Fall-Fry | 2025-05-08 | 2025-05-13 | 2025-05-13 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-TURN_005.zip | 0 | No | 8 | Grid Design, Operations, and Maintenance | 8.2.1 | 8.2.1 - Covered Conductor Installation
19 | 231 | OEIS | 009 | OEIS_009 | 1(s2) | Yes | OEIS_009_Q1(s2) | Regarding 2026 Risk Reduction for Undergrounding and Covered Conductor Table 8-1 of PG&E’s 2026-2028 Base WMP includes risk reduction percentages for 2026 based on its current risk models WDRM v4 and WTRM v2. Given that the year 2026 is part of its current General Rate Case Decision, Energy Safety cannot currently compare its risk reduction as calculated by WDRM v3 and WTRM v1. a. Provide the percentage risk reductions planned for 2026 for the following activities based on WDRM v3 and WTRM v1. i. System Hardening – Undergrounding (GH-04) ii. System Hardening – Transmission Shunt Splices (GH-06) iii. System Hardening – Transmission Conductor Segment Replacement (GH-11) iv. Overhead Hardening and Line Removal – Distribution (GH-12) | Per request from the Office of Energy Infrastructure Safety, we are re-producing the attachments provided with “WMP-Discovery2026-2028_DR_TURN_003-Q001.pdf” for this request. Please note, “WMP-Discovery2026-2028_DR_TURN_003-Q001Atch02CONF.xlsx” is now being produced as “WMP-Discovery2026-2028_DR_OEIS_009- Q001Supp02Atch01CONF.xlsx” and “WMP-Discovery2026-2028_DR_TURN_003- Q001Atch03CONF.xlsx” is now being produced as “WMP-Discovery2026- 2028_DR_OEIS_009-Q001Supp02Atch02CONF.xlsx.” No changes have been made to these files. | Nathan Poon | 2025-05-09 | 2025-06-06 | 2025-06-06 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_009.zip | 2 | No | 5 | Risk Methodology & Assessment | 5.4 | Summary of Risk Models
19 | 231 | OEIS | 009 | OEIS_009 | 1(s) | Yes | OEIS_009_Q1(s) | Regarding 2026 Risk Reduction for Undergrounding and Covered Conductor Table 8-1 of PG&E’s 2026-2028 Base WMP includes risk reduction percentages for 2026 based on its current risk models WDRM v4 and WTRM v2. Given that the year 2026 is part of its current General Rate Case Decision, Energy Safety cannot currently compare its risk reduction as calculated by WDRM v3 and WTRM v1. a. Provide the percentage risk reductions planned for 2026 for the following activities based on WDRM v3 and WTRM v1. i. System Hardening – Undergrounding (GH-04) ii. System Hardening – Transmission Shunt Splices (GH-06) iii. System Hardening – Transmission Conductor Segment Replacement (GH-11) iv. Overhead Hardening and Line Removal – Distribution (GH-12) | a. i. The v3 risk reduction and risk rank values for the 2026 System Hardening – Undergrounding (GH-04) workplan has been provided in response to data request WMP-Discovery2026-2028_DR_TURN_003-Q001 and associated attachment “WMP-Discovery2026-2028_DR_TURN_003- Q001Atch02CONF.xlsx.” Please reference worksheet ‘GH-04 Workplan 2026- 28’, filter column V (End Year) for 2026, and see column P (Risk Rank (V3)), and column Q (Est. Wildfire Risk Reduction (V3)). The response and associated attachment have been attached to this response as “WMP-Discovery2026-2028_DR_OEIS_009-Q001Atch01CONF.zip.” ii. Please note that transmission shunt splices are not part of the General Rate Case Decision. Cost recovery for shunt splices occurs through the FERC Transmission Owners Filing. PG&E will supplement this response to provide this information by May 23, 2025. iii. PG&E will supplement this response to provide this information by May 23, 2025. iv. The v3 risk reduction and risk rank values for the 2026 Overhead Hardening and Line Removal – Distribution (GH-12) workplan has been provided in response to data request WMP-Discovery2026-2028_DR_TURN_003-Q001 and associated attachment WMP-Discovery2026-2028_DR_TURN_003- Q001Atch03CONF.xlsx. Please reference worksheet ‘GH-12 Workplan 2026- 28’, filter column V (End Year) for 2026, and see column P (Risk Rank (V3)) and column Q (Est. Wildfire Risk Reduction (V3)). The response and associated attachment have been attached to this response as “WMP-Discovery2026-2028_DR_OEIS_009-Q001Atch01CONF.zip.” | Nathan Poon | 2025-05-09 | 2025-05-23 | 2025-05-23 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_009.zip | 0 | No | 5 | Risk Methodology & Assessment | 5.4 | Summary of Risk Models
19 | 231 | OEIS | 009 | OEIS_009 | 1 | No | OEIS_009_Q1 | Regarding 2026 Risk Reduction for Undergrounding and Covered Conductor Table 8-1 of PG&E’s 2026-2028 Base WMP includes risk reduction percentages for 2026 based on its current risk models WDRM v4 and WTRM v2. Given that the year 2026 is part of its current General Rate Case Decision, Energy Safety cannot currently compare its risk reduction as calculated by WDRM v3 and WTRM v1. a. Provide the percentage risk reductions planned for 2026 for the following activities based on WDRM v3 and WTRM v1. i. System Hardening – Undergrounding (GH-04) ii. System Hardening – Transmission Shunt Splices (GH-06) iii. System Hardening – Transmission Conductor Segment Replacement (GH-11) iv. Overhead Hardening and Line Removal – Distribution (GH-12) | a. i. The v3 risk reduction and risk rank values for the 2026 System Hardening – Undergrounding (GH-04) workplan has been provided in response to data request WMP-Discovery2026-2028_DR_TURN_003-Q001 and associated attachment “WMP-Discovery2026-2028_DR_TURN_003- Q001Atch02CONF.xlsx.” Please reference worksheet ‘GH-04 Workplan 2026- 28’, filter column V (End Year) for 2026, and see column P (Risk Rank (V3)), and column Q (Est. Wildfire Risk Reduction (V3)). The response and associated attachment have been attached to this response as “WMP-Discovery2026-2028_DR_OEIS_009-Q001Atch01CONF.zip.” ii. Please note that transmission shunt splices are not part of the General Rate Case Decision. Cost recovery for shunt splices occurs through the FERC Transmission Owners Filing. iii. PG&E will supplement this response to provide this information by May 23, 2025. iv. PG&E will supplement this response to provide this information by May 23, 2025. v. The v3 risk reduction and risk rank values for the 2026 Overhead Hardening and Line Removal – Distribution (GH-12) workplan has been provided in response to data request WMP-Discovery2026-2028_DR_TURN_003-Q001 and associated attachment WMP-Discovery2026-2028_DR_TURN_003- Q001Atch03CONF.xlsx. Please reference worksheet ‘GH-12 Workplan 2026- 28’, filter column V (End Year) for 2026, and see column P (Risk Rank (V3)) and column Q (Est. Wildfire Risk Reduction (V3)). The response and associated attachment have been attached to this response as “WMP-Discovery2026-2028_DR_OEIS_009-Q001Atch01CONF.zip.”. | Nathan Poon | 2025-05-09 | 2025-05-16 | 2025-05-16 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_009.zip | 1 | No | 5 | Risk Methodology & Assessment | 5.4 | Summary of Risk Models
19 | 232 | GPI | 001 | GPI_001 | 1 | No | GPI_001_Q1 | (1.1) Please provide documentation detailing the MAVf applied in the WFC model, including the method for how “non-linear, risk adjustment increases the consequences of more extreme events,” as referenced in the wildfire-consequence-model-documentation-v4.pdf (at p. 8). (1.2) In regard to wildfire-consequence-model-documentation-v4.pdf, please clarify whether the reported “MAVf” values (e.g. at p. 18, Table 8) and “consequence values using the MAVf function (e.g. at p. 28)” are reported in standard units (e.g. 1 = 1 serious injury) or cost normalized units at the rate of “$1M per risk-adjusted 2023 dollars per unit of MAVf” (e.g. 3.125 = 1 serious injury*$3.125M/ $1M) | a. For the requested information, please refer to PG&E’s 2024 RAMP Report (https://www.cpuc.ca.gov/-/media/cpuc-website/divisions/safety-policydivision/ reports/2024-ramp-application-pge051524.pdf), Chapter 2, Section C. Cost- Benefit Approach, starting from page 2-3 through 2-27. MAVf in WFC v4 used earlier versions of the PG&E’s 2024 RAMP CBA, with slight differences in the monetized value of safety and reliability. The non-linear scaling is described in pages 2-19 through 2-27 of the RAMP Report. b. MAVf values are in millions risk-adjusted 2023 dollars. | Zoe Harrold | 2025-05-09 | 2025-05-14 | 2025-05-14 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-GPI_001.zip | 0 | No | 5 | Risk Methodology & Assessment | 5.4 | Summary of Risk Models
19 | 233 | GPI | 001 | GPI_001 | 2(s) | Yes | GPI_001_Q2(s) | WFC model questions: (2.1) In OEIS_001_Q24, OEIS asked (a.iii) “How many “worst weather days” are included within the set used for WFC?” PG&E responded: “PG&E includes 571 worst weather days from March 2003 to Dec 2020.” Of the total 571 worst weather days modeled with 24-h Technosylva fire spread simulations, how many simulations are included in the quantification of each CoRE pixel? If a subset of the 571 worst weather day simulations are applied in the WFC for each CoRE pixel, what is the basis for selecting whether a Technosylva worst weather day 24-h simulation is used as a WFC input to calculate CoRE for a given pixel? (2.2) Confirm that the only outputs from 24-h Technosylva fire spread simulations input into the WFC to determine granular CoRE values are Flame Length and Rate of Spread. If other fire spread simulation outputs (e.g. acreage, buildings destroyed, etc.) are included in any aspect of the WFC and final CoRE valuation, please list them and describe the methods used. (2.3) It is our understanding that PG&E previously calibrated Technosylva simulation Flame Length and Rate of Spread “Destructive Fire” thresholds based on 8-h simulations (PG&E 2023- 2025 WMP R5, p. 173). Did PG&E analyze the relationship between 24-h Technosylva simulation Flame Length and Rate of Spread and its revised “Predicted Destructive Potential” binned fire classifications? If so, provide the calibration results. (2.4) PG&E validates its use of 24-h versus 8-h Technosylva simulations based on the correlation between simulated historical fires versus actual acres burned (wildfire-consequencemodel-documentation-v4.pdf, p. 13). Did PG&E complete a similar assessment for simulated historical fires versus actual buildings destroyed? If so, please provide the results. Does PG&E apply the simulated acres burned from 24-h Technosylva simulations in any of its risk quantification models? (2.5) FPI outputs are an input to the WFC Model. FPI fuel data is sourced from Technosylva and is reported as being updated annually (PGE 2026-2028 MWP vol. 1, p. 470). Please clarify if a 2030 fuels layer was used as an input to generate the backcast FPI R values that are input into the WFC for the “11 fire seasons covering 2012 through 2022 (wildfireconsequence-model-documentation-v4.pdf, p. 30).” If not, please provide the the fuel data vintage(s) used in the FPI backcast for the WFC model. | a. i. The v4 WFC model requires all inputs for a pixel to be present to characterize expected consequence at a pixel. The temporal overlap between Technosylva simulations and the FPI model backcast data used as WFC v4 inputs spans 2012 through 2020. Therefore all “worst weather days” spanning 2012-2020, 268 days, were used. ii. Please see the response to subpart (i) above. The temporal overlap between Technosylva simulations and the FPI model backcast data determined the data used. b. We confirm that flame length and rate of spread are the only fire simulation characteristics used as inputs to the WFC. c. i. Yes, PG&E confirmed the same thresholds were valid for both 8 and 24 hour simulations. Because the flame length and rate of spread values used are the maximum values observed during the simulation interval, in many cases they are unchanged between 8 and 24 hour simulations. Even when the 24 hour simulation increased one or both values, the same thresholds were found necessary to achieve “full recall” of historically destructive fires. d. i. The validation on page 13 confirms that the acres burned after 24 hours of simulation better correlate with final acres of historical fires than their 8-hour counterparts, but only after binning the data. For structures destroyed, there is poor correlation. Please note that the acres burned correlation was only clear when the results were binned and averaged. The vast majority of fires do not destroy any structures, so there are fewer fires to aggregate into bins, resulting in inherently noisier relationships. Additionally, the Technosylva wildfire simulation engine does not currently treat buildings as fuels, with structures reported based on fire footprints without accounting for the contribution of structure fire itself. However, fires with the greatest number of structures destroyed feature structure to structure spread not captured by Technosylva’s approach. ii. No, Technosylva simulations are only used to support wildfire risk planning models and those models do not apply the simulated acres burned from Technosylva simulations. | Zoe Harrold | 2025-05-09 | 2025-05-20 | 2025-05-20 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-GPI_001.zip | 0 | No | 5 | Risk Methodology & Assessment | 5.4 | Summary of Risk Models
19 | 233 | GPI | 001 | GPI_001 | 2 | No | GPI_001_Q2 | WFC model questions: (2.1) In OEIS_001_Q24, OEIS asked (a.iii) “How many “worst weather days” are included within the set used for WFC?” PG&E responded: “PG&E includes 571 worst weather days from March 2003 to Dec 2020.” Of the total 571 worst weather days modeled with 24-h Technosylva fire spread simulations, how many simulations are included in the quantification of each CoRE pixel? If a subset of the 571 worst weather day simulations are applied in the WFC for each CoRE pixel, what is the basis for selecting whether a Technosylva worst weather day 24-h simulation is used as a WFC input to calculate CoRE for a given pixel? (2.2) Confirm that the only outputs from 24-h Technosylva fire spread simulations input into the WFC to determine granular CoRE values are Flame Length and Rate of Spread. If other fire spread simulation outputs (e.g. acreage, buildings destroyed, etc.) are included in any aspect of the WFC and final CoRE valuation, please list them and describe the methods used. (2.3) It is our understanding that PG&E previously calibrated Technosylva simulation Flame Length and Rate of Spread “Destructive Fire” thresholds based on 8-h simulations (PG&E 2023- 2025 WMP R5, p. 173). Did PG&E analyze the relationship between 24-h Technosylva simulation Flame Length and Rate of Spread and its revised “Predicted Destructive Potential” binned fire classifications? If so, provide the calibration results. (2.4) PG&E validates its use of 24-h versus 8-h Technosylva simulations based on the correlation between simulated historical fires versus actual acres burned (wildfire-consequencemodel-documentation-v4.pdf, p. 13). Did PG&E complete a similar assessment for simulated historical fires versus actual buildings destroyed? If so, please provide the results. Does PG&E apply the simulated acres burned from 24-h Technosylva simulations in any of its risk quantification models? (2.5) FPI outputs are an input to the WFC Model. FPI fuel data is sourced from Technosylva and is reported as being updated annually (PGE 2026-2028 MWP vol. 1, p. 470). Please clarify if a 2030 fuels layer was used as an input to generate the backcast FPI R values that are input into the WFC for the “11 fire seasons covering 2012 through 2022 (wildfireconsequence-model-documentation-v4.pdf, p. 30).” If not, please provide the the fuel data vintage(s) used in the FPI backcast for the WFC model. | e. Pre-fire fuels layers were used as input to generate the backcast of the FPI climatology. Specifically, a pre-fire fuels snapshot was created for years 2012-2020. A spring 2021 snapshot was used for 2021, and a spring 2022 snapshot for 2022. Pre-fire fuels layers represent the state of the fuels before being changed by wildfire. | Zoe Harrold | 2025-05-09 | 2025-05-14 | 2025-05-14 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-GPI_001.zip | 0 | No | 5 | Risk Methodology & Assessment | 5.4 | Summary of Risk Models
20 | 234 | MGRA | 007 | MGRA_007 | 1 | No | MGRA_007_Q1 | Please provide a shapefile or geodatabase containing the Fire Index Area (FIA) used for PG&E’s analysis. | Please see “WMP-Discovery2026-2028_DR_MGRA_007-Q001Atch01.zip” for the shapefiles containing the Fire Index Area (FIA) used in PG&E’s analysis explained in its response to “WMP-Discovery2026-2028_DR_MGRA_005-Q005.pdf”. | Joseph Mitchell | 2025-05-12 | 2025-05-14 | 2025-05-14 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-MGRA_007.zip | 1 | No | 10 | Situational Awareness and Forecasting | 10.6 | Fire Potential Index
20 | 235 | OEIS | 010 | OEIS_010 | 1 | No | OEIS_010_Q1 | Regarding Vegetation Management Quality Control Population and Sample Unit Sizes In its response to OEIS-P-WMP_2025-PGE-005, PG&E states that for both Vegetation Management Quality Control Distribution Routine (VM-22D) and Vegetation Management Quality Control Transmission Routine (VM-22T) PG&E “selects [the sample] from a population of Work Packets.” On page 410 of its 2026-2028 WMP, PG&E lists the Population/Sample Size for VM-22D and VM-22T as “Inspections.” a. Explain the difference between Work Packets and Inspections. b. Using the table below, considering Work Packets to be the Population/Sample Unit for both WM-22D&T, provide: i. The Work Packet population size in the “2026, 2027, or 2028 Work Packet Population Size” column. ii. The Work Packet sample size in the “2026, 2027, or 2028 Work Packet Sample Size” column. “Refer to table in data request response” as public versions of DR responses will have the initial question and response tables. | a. ‘Work Packets’ are a group of inspected distribution spans and/or transmission locations created by VM Operations. Work Packets are an organizational tool to consolidate inspection records and do not skew the overall population of spans/locations inspected by VM Operations. b. Since the Work Packets are created by VM Operations at the time of their inspection assignments, we do not yet have the total population or sample size for the future years of 2026 to 2028. | Nathan Poon | 2025-05-13 | 2025-05-16 | 2025-05-16 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_010.zip | 0 | No | 9 | Vegetation Management and Inspections | 9.11.2 | QA/QC Procedures
20 | 236 | OEIS | 010 | OEIS_010 | 2 | No | OEIS_010_Q2 | Regarding Tree Worker Qualifications and Training On pages 419-421 of its 2026-2028 WMP, in Table 9-9, PG&E provides information on vegetation management personnel including titles related to inspecting and auditing. a. Provide information on vegetation management personnel with titles related to tree crews in the format required by the WMP Guidelines, Chapter III, Section 9.13, Table 9-9. | Please see the table provided below for the requested information. Please also note that the employee counts listed are current as of May 07, 2025. The certifications, training, and knowledge of the workers are the responsibility of the vendors and are not vetted by PG&E. | Nathan Poon | 2025-05-13 | 2025-05-16 | 2025-05-16 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_010.zip | 0 | No | 9 | Vegetation Management and Inspections | 9.13.2 | Training and Retention
20 | 237 | SPD | 005 | SPD_005 | 1 | No | SPD_005_Q1 | In PG&E’s response to SPD-001 Question 21, SPD did not prescribe formulas but rather presented the best attempt to present units planned or completed, total costs and average cost per unit for each mitigation. SPD asked PG&E adjustments to each of these three columns according to what they believe would be the most accurate values. a. Notwithstanding exceptions discussed by PG&E in regards to GH-01, does PG&E generally agree with the methodology SPD used in SPD-001 Question 21? Explain why or why not? b. For many mitigation initiatives, SPD’s and PG&E’s calculations were exactly the same, such as GH-08. Why did some mitigation initiatives appear to not require an update from PG&E but others required a significant revision? | a. PG&E generally agrees with SPD’s methodology when it comes to expense programs as they can be reviewed in specific fiscal years for units and dollars comparison. For Capital programs, unit cost is derived from the total cost of projects that could span multiple years, and the overall completion of units, not just units completed in one fiscal year. b. The example of GH-08 did not change for 2023 as most of the figures for 2023 did not change except for VM-03 and VM-04 which seems to be due to an error in the original formula in column G and GH-04 which had the original response number instead of the updated table PG&E submitted on February 14, 2025. The other initiatives requested for 2024 had change due to the SPD numbers being derived from forecasts and PG&E providing actuals. For 2025, the changes are due to old forecasts, whereas PG&E provided values derived from updated 2025 forecasts. | Eddie Schmitt | 2025-05-13 | 2025-05-16 | 2025-05-16 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_005.zip | 0 | No | 3 | Overview of WMP | 3.6 | Projected Expenditures
20 | 238 | SPD | 005 | SPD_005 | 2 | No | SPD_005_Q2 | PG&E indicates that “Mitigation SA-02 includes both capital and operational expenditures. PG&E has split SA-02 to reflect separate calculations for each of capital and operational expenditures.” However, PG&E’s response to SPD-001 Question 21 appears to only provide the CapEx portion. Is this an error? | SA-02 refers to line sensors, which may include both original installation and operational expenses. As a result, SA-02 has both capital and operational expenditures. However, only the capital portion has units associated with it, so that was the relevant information provided with this request for unit costs. PG&E’s narrative statement that split SA-02 into separate rows was made in error. | Eddie Schmitt | 2025-05-13 | 2025-05-16 | 2025-05-16 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_005.zip | 0 | No | 3 | Overview of WMP | 3.6 | Projected Expenditures
20 | 239 | SPD | 005 | SPD_005 | 3 | No | SPD_005_Q3 | For 2024, the QDR indicates that GM-03’s unit of measure is “# of Distribution EC Tags”. PG&E’s response to SPD-001 Question 21 records a percentage of 73.4%. Explain what this difference means. Why PG&E presented GM-03 as a percentage in its response to to SPD-001 Question 21. a. PG&E states that “Costs for GM-03 are not separated but included in the Activity level ' Equipment maintenance and repair”. Did PG&E report on GM-03 in the QDR in this manner? If not, explain why PG&E updated SPD-001 Question 21 in this way | In PG&E’s 2023-25 WMP, PG&E defines the unit of measure for GM-03 (HFTD/HFRA Open Tag Reduction – Distribution Backlog) with two components: (1) the number of EC notifications to be closed each year; and (2) a percentage of risk reduction that would be achieved by closing the tags.1 PG&E acknowledges that it has inconsistently presented these units in past QDRs, but has represented the bipartite nature of this unit of measure definition by providing the number of distribution EC tags for Table 1 of the QDR and the percentage of risk reduction for Table 12. This is also represented in both the 2023 and 2024 Annual Reports on Compliance where we provide both the numbers of tags closed as well as the percentage of risk reduction achieved in Table 3. For 2024, the 73.4% backlog ignition risk reduction corresponds to 53,526 backlog ignition risk tags closed.2 a. PG&E does not separate out costs for GM-03 in the QDR. It is rolled up under the Activity Equipment maintenance and repair. | Eddie Schmitt | 2025-05-13 | 2025-05-16 | 2025-05-16 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_005.zip | 0 | No | 3 | Overview of WMP | 3.6 | Projected Expenditures
20 | 240 | SPD | 005 | SPD_005 | 4 | No | SPD_005_Q4 | PG&E indicates that: “Upon consultation with mitigation owners, PG&E has made corrections to the “Total Cost” and, accordingly, “updated Average Cost per Unit” columns for the following mitigations for 2023: AI-02, AI04, AI-05, AI-06, AI-07, VM-04.” a. SPD reviewed mitigations AI-02, AI-04, AI-05, AI-06, AI-07 based on the units provided in PGE’s tabular QDR (Q4, 2023) and the Cost Tracking Template data1 . As noted above, PG&E has made corrections to the average cost per unit of each of these mitigations in its response to SPD-001 Question 21. For instance, for AI-07 SPD calculated a unit cost $0.28 and PG&E calculated a unit cost of $0.14. For each of these five mitigations, explain why PG&E’s response to SPD-001 Question 21 exhibits such a large variance? b. SPD presented the Total Cost for VM-04 in 2024 as $309,050,000, which was based on PG&E’s response to the Cost Tracking Template data. PG&E corrected this value to be $26,655,530. Explain why PG&E made this correction and what data sources were used to support this correction. | a. This correction was made to the AI initiatives listed as the costs provided previously were inclusive of both HFTD and non-HFTD work. b. This correction was made to correct the data for the identified program. The $309,050,000 previously provided represents the 2024 Original Budget for three utility initiatives: (1) VM-03 (Focused Tree Inspections $216.37M); (2) VM-04 1 PG&E's Supplemental Data Response to SPD_021 (SPD_WSPS_PG&E_2024_011) Q001Supp07. WMP-Discovery 2026-2028_DR_SPD_005-Q004 Page 2 (Tree Removal Inventory $71.77M), and; (3) VM-18 (VM for Operational Mitigations $20.91M). This correction was made to report the actual $26.656M 2024 spend for VM-04 (Tree Removal Inventory). PG&E made these changes to better reflect the budget and costs of the VM-04 program | Eddie Schmitt | 2025-05-13 | 2025-05-16 | 2025-05-16 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_005.zip | 0 | No | 3 | Overview of WMP | 3.6 | Projected Expenditures
20 | 241 | SPD | 005 | SPD_005 | 5 | No | SPD_005_Q5 | PG&E indicates that “With regard to values for 2025, PG&E notes that the values used by SPD reflect forecasts first made in 2022. PG&E has provided updated values reflecting more current forecasts.” Why are 2022 forecasts used as late as 2024 Q4? Does Energy Safety provide guidance on updating these forecasts throughout the WMP cycle? See pg. 165 of Energy Safety guidance “_v32”.2 a. For each 2025 forecast that PG&E updated in its response to SPD-001 Question 21, list what data sources were used to support this correction. | PG&E had planned to provide an updated 2025 forecast in the Q1 2025 QDR, however, with the elimination of the financial table in the new quarterly template, PG&E did not provide an updated Table 11 with financial forecast. Per the guidelines and template from Energy Safety, 2025 forecasts were not required. | Eddie Schmitt | 2025-05-13 | 2025-05-16 | 2025-05-16 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_005.zip | 0 | No | 3 | Overview of WMP | 3.6 | Projected Expenditures
20 | 242 | SPD | 005 | SPD_005 | 6 | No | SPD_005_Q6 | For 2023, SPD was not expecting any variance in the units relative to the latest tabular QDR (2023, Q4). For example, for GM-06 during 2023 SPD presented 720 units, but PG&E corrected this to 482 units. a. Explain the variance in units for 2023 for each mitigation initiative that PG&E corrected in its response to SPD-001 Question 21. i. List what sources were used to support each of these corrections. | With regard to AI-05, PG&E has determined that the updated unit count of 1,749 was an error. The correct unit count is that presented by SPD: 1,786. PG&E will submit an amendment to its response to WMP-Discovery2026-2028_DR_SPD_001-Q021. With regard to AI-07, PG&E has determined that the updated unit count of 274,000 was an error and inadvertently included aerial inspection units that were not part of AI-07 in 2023. PG&E will submit an amendment to its response to WMP-Discovery2026-2028_DR_SPD_001-Q021. The unit counts provided in the QDRs are correct. In our previous data request response, we inadvertently underreported the total number of units. We reported 482 units for GM-06 in 2023, as well as incorrectly reported 400 units for GM-06 in 2024. However, these units were associated with PG&E’s controller retrofit program under GM-06, but did not include all units installed under GM-06. The correct unit counts for 2023 and 2024 for GM-06 are 720 and 705, respectively, as described in our QDRs. Further, we determined that the reported total cost values in our previous data request response for GM-06 inadvertently included only costs for the controller retrofit program. GM-06 includes installation of DCD settings under three circumstances: controller retrofit; substation relay replacement, and; installation of DCD WMP-Discovery 2026-2028_DR_SPD_005-Q006 Page 2 settings during other work, such as replacement of a device as part of a pole replacement. Of the three, only DCD installation under the controller retrofit and substation relay replacement programs have unit costs. The unit cost for DCD settings installation as part of other work is $0. PG&E’s prior data request response included costs only for the controller retrofit program, and not for DCD units installed under substation relay replacement. PG&E will amend its prior data request response to correct the unit and cost values for GM-06 accordingly. With regard to GH-05, GM-02, and VM-01, PG&E provided updated values derived from its 2023 Annual Report on Compliance (ARC). There may be variance as between PG&E’s Q4 QDRs and a given year’s ARC due to the data being provided at a different point in time as records from the previous year are finalized. | Eddie Schmitt | 2025-05-13 | 2025-05-16 | 2025-05-16 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_005.zip | 0 | No | 3 | Overview of WMP | 3.6 | Projected Expenditures
20 | 243 | OEIS | 011 | OEIS_011 | 1 | No | OEIS_011_Q1 | In sections 8.2.10.5 (page 219) and 8.4.12.1 (page 287) of its 2026-2028 Base WMP, PG&E describes its non-exempt expulsion fuse removal/replacement program. a. In the second paragraph of section 8.2.10.5 on page 219, PG&E states that it will replace additional “non-exempt surge arrestors” should they be found. Explain the difference between these “non-exempt surge arrestors” and the “non-exempt expulsion fuses” described in this section. b. PG&E states that it plans to complete the “remaining known population” of non-exempt expulsion fuse removals in 2025. Does the “known population” refer to: i) the target for non-exempt expulsion fuse removals from the 2023-2025 WMP (GH-10), ii) the full population of non-exempt expulsion fuses in PG&E’s service territory, iii) a filtered subset of ii) above (e.g., only line-protection-related fuses in the HFTD/HFRA); or iv) a different population. If iii) or iv), explain how the population was defined and filtered, and what methodology or criteria were used to exclude other known non-exempt fuses. c. After PG&E completes its planned removals and replacements of non-exempt expulsion fuses in 2025, how many non-exempt expulsion fuses will remain in PG&E’s HFTD/HFRA? i. Of the remaining non-exempt fuses, how many are intended for “line protection” versus “transformer protection?” ii. Of the remaining non-exempt fuses, how many are solid blade disconnects, universal fuse, open link fuse, or other type? d. Does PG&E plan to replace all non-exempt fuses in the HFTD/HFRA by 2028? If not, explain the rationale and provide the criteria used to determine which non-exempt fuses will not be replaced. | a. This is a typographical error. The statement should have been written to say: “Should we find additional non-exempt expulsion fuses; we will promptly replace them.” The statement should not have included mention of surge arrestors. b. PG&E initially queried the EDGIS database in 2022 to identify the known population of non-exempt line protection fuses in HFTD areas. This original population was used to set non-exempt line protection fuse replacement targets in the 2023-2025 WMP. Subsequently, annually, as we create the following year’s work plan, we have refreshed the EDGIS query to identify the updated known population of non-exempt line protection fuses. We use the refreshed known population of non-exempt line protection fuses to create the replacement work plans and ensure that all known non-exempt line protection fuses have either been remediated or are included in the 2025 work plan. c. PG&E will complete the identified population of its non-exempt expulsion fuses that were part of this WMP commitment, which include all known non-exempt line protection fuses in HFTD areas described in part b above. PG&E is aware that there may be additional non-exempt expulsion fuses in HFTD areas. Please see subpart (d) for our risk-based approach to addressing non-exempt expulsion fuses. i. All known non-exempt line protection fuses in HFTD areas will be remediated by the end of 2025. ii. Solid blade disconnects are considered switches, not fuses. There are approximately 1,400 solid blade disconnects deployed as part of this WMP commitment. d. At this time, PG&E does not plan to programmatically replace non-exempt fuses associated with equipment, as the program was developed in 2019 with a focus on the replacement of known non-exempt line protection fuses at that time. As PG&E reviewed the effectiveness of this program in reducing ignitions, it was revealed there was only one CPUC reportable ignition associated with a non-exempt fuse for the period from 2021 to 2024. Given that we patrol our assets in HFTD areas annually to determine vegetation clearing under all poles in HFTD where there is any non-exempt equipment on the pole in conformance with PRC 4292, PG&E elected to not expand the program. In addition to the pole clearing measure to mitigate against this ignition risk, we opportunistically replace all non-exempt equipment with exempt equipment when performing system hardening, as specified in our Electric Design Manual TD-9001M. | Nathan Poon | 2025-05-16 | 2025-05-28 | 2025-05-28 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_011.zip | 0 | No | 8 | Grid Design, Operations, and Maintenance | 8.2.10.5 | Non-Exempt Expulsion Fuses
21 | 243 | SPD | 006 | SPD_006 | 1 | No | SPD_006_Q1 | The following questions are all related to PG&E’s first response to SPD-PGE-WMP2026-SPD-004 Question 5. a. In the 2024 RAMP Tranche, PG&E has listed 630 circuit segments as “#NA”. Provide an Excel workbook that lists the WDRM v.4 Circuit Segment Name for each of the 630 circuit segments in the first column. The second column should explain why this circuit segment was listed as #NA, such as this circuit segment was split from a larger circuit segment in WDRM v.3 due to the addition of a recloser. The third column should list the name of the previous circuit segment as it was used in WDRM v.3 and presented in PGE_2023_WMP_R0_Section_642_Atch01.xlsx. If this is a newly constructed circuit segment, the response in the third column must be “New”. 2026-2028 Base WMP WDRM v.4 Circuit Segment Name Explanation for #NA 2024 RAMP WDRM v.3 Circuit Segment Name CAMP EVERS 2106737512 b. Explain why PG&E in its 2026-2028 Base WMP did not include a file similar to PGE_2023_WMP_R0_Section_642_Atch01.xlsx in its submission. i. For each mitigation listed below, explain why it is now impossible for PG&E to unitize the mitigation by circuit mile (as it was in PGE_2023_WMP_R0_Section_642_Atch01.xlsx): a) Expulsion Fuse Replacement b) Surge Arrestor Replacement c) Aerial Inspection d) Ground Inspection e) Non-Pole Backlog f) Tree Removal g) Down Conductor Detection (DCD) h) Line Sensors i) Pole Backlog j) Pole Clearing ii. For each mitigation listed above, explain why PG&E was able to complete the corresponding “% of Segment” field in the TopRisk_Table Worksheet of PGE_2023_WMP_R0_Section_642_Atch01.xlsx.1 c. For the years 2023-2025, PG&E states that it is unable to determine actual expenditure and present value cost of specific work done on a circuit segment for each of the mitigations listed in Question 1.b.i., but PG&E can provide the average cost to complete one unit of the mitigation program. For each of the mitigations listed in Question 1.b.i., provide an explanation for why PG&E is unable to determine the actual expenditure and present value cost of specific work done on a circuit segment. i. Since PG&E is unable to determine the actual expenditures, provide a step-by-step method PG&E used to estimate the average cost to complete one unit of each of the mitigations listed in Question 1.b.i. Be sure to include the unit cost and the range of the unit cost for each mitigation in your response. ii. PG&E’s SAP system allows for the presentation of monthly detail of undergrounding projects by using the Analyses for Office (AO) report PROJ002-PS Monthly Detail function.2 Explain how PG&E records cost-related data in SAP for orders related to each of the mitigations listed in Question 1.b.i. a) Can PG&E use Analyses for Office (AO) report PROJ002-PS Monthly Detail function to generate a report similar to EUP_DR_SPD_013_Q001Atch02CONF.xlsx for each of the mitigations listed in Question 1.b.i.? a. If so, provide a copy of the report for an order associated with the CORNING 110185152 circuit segment for each of the mitigations listed in Question 1.b.i. 1 For instance, on the OAKHURST 110310140 circuit segment, PG&E stated that Tree Removal occurred on 42.3% of the circuit segment in 2023, on 24.5% of the circuit segment in 2024 and on 14.4% of the circuit segment in 2025. 2 See SPD-PGE-SB884-013 (PG&E Ref. DRU14491-Case-EUP-SB 884), Question 1c. and EUP_DR_SPD_013_Q001Atch02CONF.xlsx. b. If not, explain why not. d. Table 8-1 in PG&E’s 2026-2028 Base WMP states that PG&E intends to install 200 service breakaway connectors in 2026, 1,400 in 2027 and 1,400 in 2028. Explain why PG&E in response to SPD-PGE-WMP2026-SPD-004 Question 5 stated that it does not track any information related to breakaway connector installations. i. What is the MAT Code for this mitigation activity (GM-14) that PG&E used in its 2027 Test Year GRC Application? ii. How will PG&E calculate the risk reduced by service breakaway connectors if the location of service breakaway connectors and identify future locations for work if the location of the service breakaway connector is not tracked? e. Figure PG&E 5-2-5 in PG&E’s 2026-2028 Base WMP presents the EORM Risk Model as contributing to the calculation of Wildfire Consequence (i.e. WFC v4). Pg. 71 of PG&E’s 2026-2028 Base WMP states that “Ignition Risk (WDRM v4) for distribution is determined for equipment asset locations for each risk driver causal model LoRE, p(i), and CoRE, WFC.” Table 5-4 states that Ignition/Wildfire Risk (WDRM/WTRM) provides a key output of “Circuit Segment Risk”. In response to SPD-PGE-WMP2026-SPD-004 Question 5 PG&E states that it is impossible to provide circuit segment EORM Values because “PG&E’s EORM values are not calculated to the circuit segment level, but at the “tranche” level.” Explain how PG&E uses tranche level EORM values to develop the key output of “Circuit Segment Risk” from the WDRM. i. Provide a step-by-step calculation of “circuit segment risk”. At each stage PG&E must explain what is the scale of analysis (i.e. tranche, circuit segment, etc.) and must clearly note the units (i.e. dollars, number of deaths, CMI etc.).3 This step-by-step calculation must include a description of a) what CalFire Fire Data is input into the EORM Risk Model b) How the CalFire Fire Data is used within the EORM Risk Model to develop the MAVf intermediate results c) How the MAVf intermediate results are used within the Wildfire Consequence Model to generate the output of Consequence Pixel Values d) How the Consequence Pixel Values are used to calculate Ignition Risk ii. Explain how the EORM and WDRM methods differ. iii. SPD understands that PG&E scales the WDRM v4 risk values to the predicted risk dollar amount from the CBRs (see Table PG&E-6.2.1.2-2). What are the benefits/drawbacks from scaling a bottoms-up relative risk model to the top-down EORM model? a) For instance, it appears that WDRM v4 predicts more risk outside of the HFTD than the EORM model does – is this type of discrepancy reconciled in the model? b) How does the EORM predicted values in tranches (safety, reliability, financial, combined) compare to a risks from WDRM v4 when combined at the tranche level? iv. Use the calculation of Ignition Risk on CORNING 110185152 circuit segment to create a concrete example of the step-by-step calculation of “circuit segment risk” provided in PG&E’s response to Question 1.e.i. 3 Please note, tables such as PG&E-6.2.1.2-4 are confusing because it is not clear what the scale of analysis is in the example, nor is it clear which units are used for each number in the example. f. Does PG&E intend to only present WDRM data in its Electrical Undergrounding Plan submission to Energy Safety? i. If a party wished to know the EORM values for a circuit segment that PG&E includes in its Electrical Undergrounding Plan, is PG&E able to generate those values? g. In PG&E’s response to SPD-PGE-WMP2026-SPD-001 Question 26, PG&E stated that in the 2026-2028 Base WMP Submission it used a preliminary version of the WBCA Tool to conduct mitigation effectiveness analysis. Since PG&E has stated that the post-mitigation values requested in SPD-PGE-WMP2026-SPD-004 Question 5 cannot be provided through the WDRM v.4 model, can PG&E provide these values through its use of the preliminary version of the WBCA tool? i. If so, please complete the following variables that were included in Decision Tree Results by Circuit Segment.xlsx along with PG&E’s response SPD-PGE-WMP2026-SPD-004 Question 5 on May 30th 2025: a) Post-Mitigated LoRE b) Unadjusted Post-Mitigated CoRE c) Adjusted Post-Mitigated CoRE d) Unadjusted Post-Mitigated Risk e) Adjusted Post-Mitigated Risk ii. If not, explain why not and in which dataset the five data points listed in Question 1.g.i is located. Provide SPD with that data along with PG&Es response to SPD-PGE-WMP2026-SPD-004 Question 5 on May 30th 2025. | a. Pursuant to agreement with SPD, PG&E will provide this response on June 5, 2025. b. Pursuant to agreement with SPD, PG&E will provide this response on May 28, 2025. c. Pursuant to agreement with SPD, PG&E will provide this response on May 28, 2025. d. Pursuant to agreement with SPD, PG&E will provide this response on May 28, 2025. e. In Figure PG&E-5-2-5, the MAVf intermediate result as depicted in the procedural schematic is the delivery of the MAVf by EORM for the completing the development of the WFC v4 model. i. Please see PG&E’s responses to parts (a), (b), (c), and (d), below, as well as PG&E’s WDRM documentation suite, which includes: “Wildfire Distribution Risk Model Version 4(WDRM v4) Documentation”. “Distribution Event Probability Models Version 4 (DEPM v4) Documentation”, “Wildfire Consequence Model Version 4 (WFC v4) Documentation”, and “RaDA Modeling Algorithms and Methodologies Version 1 Documentation”. a) Cal Fire data are not used in developing the MAVF which feeds into the WFC v4 model. b) Please see the answer to part a). c) The MAVf used by the Enterprise Risk Models is used to determine consequence values for asset locations location as detailed in Sections 3 and 4 of the “Wildfire Consequence Model Version 4 (WFC v4) Documentation”. A procedural overview of the consequence modeling process is provided in Figure PG&E-5.2.2.2-1 on page 68 of the “PG&E Wildfire Mitigation Plan R0 2026-2028 ¦ volume 1 of 2”. d) The Wildfire (Ignition) Risk calculation using consequence pixels for distribution is explained in Sections 3.1 and 4 of the “Wildfire Distribution Risk Model v4 Documentation”. ii. Simply, the EORM risk model develops the MAVf function that transforms burned acreage, structure loss, and potential fatalities into a single consequence value, while the WFC v4 uses MAVf function to estimate seasonal consequence values for all distribution asset locations. WMP-Discovery2026-2028_DR_SPD_006-Q001Supp01 Page 6 iii. The benefits/drawbacks from scaling a bottoms-up relative risk model to the top-down EORM model (Wildfire Risk Bowtie Model) are as follows: • The grouping of circuit segments into tranches and the relative risk value among tranches in the top-down Wildfire Risk Bowtie Model model are informed by the bottoms-up circuit-segment level risk model, and hence more predictive than simply summarizing historical data. • The scaling is needed to enable the cost and benefit of wildfire risk mitigations with non-wildfire risk mitigations, e.g. reliability risk mitigation. a) Yes. Wildfire Risk Bowtie Model scales the non-HFTD/HFRA risk so that the percentage of risk from non-HFTD/HFRA is the same as that predicted by WDRM v4. b) The Wildfire Risk Bowtie Model’s risk values for combined attributes in tranches are the product of a scaling factor and those from WDRM v4 when combined at the tranche level. The scaling factor is calculated as the ratio of the Wildfire Risk Bowtie Model’s total distribution baseline risk over the total WDRM v4 risk, and the same scaling factor applies to every tranche. The split of total risk by safety, reliability and financial can be different between two models. For example, the choice of groupings of fires and their associated modeled frequency and consequence per event, as well as the historical fires used in the modeling are different. Although there is a great overlap between historical fires used in both models, especially destructive fires, WFC v4 uses NASA Visible Infrared Imaging Radiometer Suite (VIIRS) data in addition to PG&E ignition data, Cal Fire data and CPUC Safety and Enforcement Division (SED) reports. iv. Pursuant to agreement with SPD, PG&E will provide this response on June 5, 2025. f. PG&E intends to use WDRM v4 as the basis for ignition data in the Electrical Undergrounding Plan. i. PG&E’s EORM values are not calculated at the circuit segment level, but at the tranche level. If desired, as an alternative, PG&E can provide tranchelevel values which will be identical for all circuit segments in the same tranche. g. PG&E believes we can provide the requested values through use of the preliminary version of the WBCA tool, dependent on completion of mapping of mitigation activities to the given list of circuit segments. | Eddie Schmitt | 2025-05-19 | 2025-06-02 | 2025-05-22 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_006.zip | 0 | No | 5 | Risk Methodology & Assessment | 5.5.2 | Top Risk-Contributing Circuits/Segments/Spans
21 | 243 | SPD | 006 | SPD_006 | 1(s) | Yes | SPD_006_Q1(s) | The following questions are all related to PG&E’s first response to SPD-PGE-WMP2026-SPD-004 Question 5. a. In the 2024 RAMP Tranche, PG&E has listed 630 circuit segments as “#NA”. Provide an Excel workbook that lists the WDRM v.4 Circuit Segment Name for each of the 630 circuit segments in the first column. The second column should explain why this circuit segment was listed as #NA, such as this circuit segment was split from a larger circuit segment in WDRM v.3 due to the addition of a recloser. The third column should list the name of the previous circuit segment as it was used in WDRM v.3 and presented in PGE_2023_WMP_R0_Section_642_Atch01.xlsx. If this is a newly constructed circuit segment, the response in the third column must be “New”. 2026-2028 Base WMP WDRM v.4 Circuit Segment Name Explanation for #NA 2024 RAMP WDRM v.3 Circuit Segment Name CAMP EVERS 2106737512 b. Explain why PG&E in its 2026-2028 Base WMP did not include a file similar to PGE_2023_WMP_R0_Section_642_Atch01.xlsx in its submission. i. For each mitigation listed below, explain why it is now impossible for PG&E to unitize the mitigation by circuit mile (as it was in PGE_2023_WMP_R0_Section_642_Atch01.xlsx): a) Expulsion Fuse Replacement b) Surge Arrestor Replacement c) Aerial Inspection d) Ground Inspection e) Non-Pole Backlog f) Tree Removal g) Down Conductor Detection (DCD) h) Line Sensors i) Pole Backlog j) Pole Clearing ii. For each mitigation listed above, explain why PG&E was able to complete the corresponding “% of Segment” field in the TopRisk_Table Worksheet of PGE_2023_WMP_R0_Section_642_Atch01.xlsx.1 c. For the years 2023-2025, PG&E states that it is unable to determine actual expenditure and present value cost of specific work done on a circuit segment for each of the mitigations listed in Question 1.b.i., but PG&E can provide the average cost to complete one unit of the mitigation program. For each of the mitigations listed in Question 1.b.i., provide an explanation for why PG&E is unable to determine the actual expenditure and present value cost of specific work done on a circuit segment. i. Since PG&E is unable to determine the actual expenditures, provide a step-by-step method PG&E used to estimate the average cost to complete one unit of each of the mitigations listed in Question 1.b.i. Be sure to include the unit cost and the range of the unit cost for each mitigation in your response. ii. PG&E’s SAP system allows for the presentation of monthly detail of undergrounding projects by using the Analyses for Office (AO) report PROJ002-PS Monthly Detail function.2 Explain how PG&E records cost-related data in SAP for orders related to each of the mitigations listed in Question 1.b.i. a) Can PG&E use Analyses for Office (AO) report PROJ002-PS Monthly Detail function to generate a report similar to EUP_DR_SPD_013_Q001Atch02CONF.xlsx for each of the mitigations listed in Question 1.b.i.? a. If so, provide a copy of the report for an order associated with the CORNING 110185152 circuit segment for each of the mitigations listed in Question 1.b.i. 1 For instance, on the OAKHURST 110310140 circuit segment, PG&E stated that Tree Removal occurred on 42.3% of the circuit segment in 2023, on 24.5% of the circuit segment in 2024 and on 14.4% of the circuit segment in 2025. 2 See SPD-PGE-SB884-013 (PG&E Ref. DRU14491-Case-EUP-SB 884), Question 1c. and EUP_DR_SPD_013_Q001Atch02CONF.xlsx. b. If not, explain why not. d. Table 8-1 in PG&E’s 2026-2028 Base WMP states that PG&E intends to install 200 service breakaway connectors in 2026, 1,400 in 2027 and 1,400 in 2028. Explain why PG&E in response to SPD-PGE-WMP2026-SPD-004 Question 5 stated that it does not track any information related to breakaway connector installations. i. What is the MAT Code for this mitigation activity (GM-14) that PG&E used in its 2027 Test Year GRC Application? ii. How will PG&E calculate the risk reduced by service breakaway connectors if the location of service breakaway connectors and identify future locations for work if the location of the service breakaway connector is not tracked? e. Figure PG&E 5-2-5 in PG&E’s 2026-2028 Base WMP presents the EORM Risk Model as contributing to the calculation of Wildfire Consequence (i.e. WFC v4). Pg. 71 of PG&E’s 2026-2028 Base WMP states that “Ignition Risk (WDRM v4) for distribution is determined for equipment asset locations for each risk driver causal model LoRE, p(i), and CoRE, WFC.” Table 5-4 states that Ignition/Wildfire Risk (WDRM/WTRM) provides a key output of “Circuit Segment Risk”. In response to SPD-PGE-WMP2026-SPD-004 Question 5 PG&E states that it is impossible to provide circuit segment EORM Values because “PG&E’s EORM values are not calculated to the circuit segment level, but at the “tranche” level.” Explain how PG&E uses tranche level EORM values to develop the key output of “Circuit Segment Risk” from the WDRM. i. Provide a step-by-step calculation of “circuit segment risk”. At each stage PG&E must explain what is the scale of analysis (i.e. tranche, circuit segment, etc.) and must clearly note the units (i.e. dollars, number of deaths, CMI etc.).3 This step-by-step calculation must include a description of a) what CalFire Fire Data is input into the EORM Risk Model b) How the CalFire Fire Data is used within the EORM Risk Model to develop the MAVf intermediate results c) How the MAVf intermediate results are used within the Wildfire Consequence Model to generate the output of Consequence Pixel Values d) How the Consequence Pixel Values are used to calculate Ignition Risk ii. Explain how the EORM and WDRM methods differ. iii. SPD understands that PG&E scales the WDRM v4 risk values to the predicted risk dollar amount from the CBRs (see Table PG&E-6.2.1.2-2). What are the benefits/drawbacks from scaling a bottoms-up relative risk model to the top-down EORM model? a) For instance, it appears that WDRM v4 predicts more risk outside of the HFTD than the EORM model does – is this type of discrepancy reconciled in the model? b) How does the EORM predicted values in tranches (safety, reliability, financial, combined) compare to a risks from WDRM v4 when combined at the tranche level? iv. Use the calculation of Ignition Risk on CORNING 110185152 circuit segment to create a concrete example of the step-by-step calculation of “circuit segment risk” provided in PG&E’s response to Question 1.e.i. 3 Please note, tables such as PG&E-6.2.1.2-4 are confusing because it is not clear what the scale of analysis is in the example, nor is it clear which units are used for each number in the example. f. Does PG&E intend to only present WDRM data in its Electrical Undergrounding Plan submission to Energy Safety? i. If a party wished to know the EORM values for a circuit segment that PG&E includes in its Electrical Undergrounding Plan, is PG&E able to generate those values? g. In PG&E’s response to SPD-PGE-WMP2026-SPD-001 Question 26, PG&E stated that in the 2026-2028 Base WMP Submission it used a preliminary version of the WBCA Tool to conduct mitigation effectiveness analysis. Since PG&E has stated that the post-mitigation values requested in SPD-PGE-WMP2026-SPD-004 Question 5 cannot be provided through the WDRM v.4 model, can PG&E provide these values through its use of the preliminary version of the WBCA tool? i. If so, please complete the following variables that were included in Decision Tree Results by Circuit Segment.xlsx along with PG&E’s response SPD-PGE-WMP2026-SPD-004 Question 5 on May 30th 2025: a) Post-Mitigated LoRE b) Unadjusted Post-Mitigated CoRE c) Adjusted Post-Mitigated CoRE d) Unadjusted Post-Mitigated Risk e) Adjusted Post-Mitigated Risk ii. If not, explain why not and in which dataset the five data points listed in Question 1.g.i is located. Provide SPD with that data along with PG&Es response to SPD-PGE-WMP2026-SPD-004 Question 5 on May 30th 2025. | b. PG&E provided the required data in Table 6-4 on the risk reduction activities for the top-risk circuits. PG&E was not required to update the file submitted for the 2023=- 2025 WMP cycle. i. PG&E unitizes each of the mitigations listed in Question 1(b)(i) by a measure other than circuit mile and it is not possible to meaningfully convert PG&E’s units into circuit miles. When PG&E submitted PGE_2023_WMP_R0_Section_642_Atch01.xlsx with its 2023-2025 Base WMP, PG&E was similarly unable to unitize these mitigations by circuit mile. ii. The listed mitigations were not unitized by circuit mile in PGE_2023_WMP_R0_Section_642_Atch01.xlsx to the 2023-2025 Base WMP. PG&E provided data in the “% of Segment” field based on forecast estimates of the proportion of work possible to be performed and forecast estimates of the work performed or to be performed on a given segment. For example, if one fuse existed on a segment and it was subject to replacement under PG&E’s WMP mitigation program, that segment was listed as 100% mitigated. This field does not purport to unitize non-circuit mile mitigations by circuit mile. c. Pursuant to agreement with SPD, PG&E will provide this response on June 2, 2025. WMP-Discovery2026-2028_DR_SPD_006-Q001Supp01 Page 5 d. PG&E does not currently track installation details or location of service breakaway connectors. However, PG&E is internally working to map service breakaway connectors in our system of record. Service breakaway connectors are newly approved equipment at PG&E, which mitigate ignition risk, so we chose to deploy opportunistic field installations immediately, instead of delaying, as we work through the mapping process. Additionally, as breakaway connectors are currently installed opportunistically, and not programmatically, PG&E lacks the means to forecast installation locations. i. The MAT code for this mitigation activity used in the 2027 GRC is 08J. ii. The team is internally working to map service breakaway connectors in our system of record, which will enable future risk reduction calculations. | Eddie Schmitt | 2025-05-19 | 2025-05-28 | 2025-05-28 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_006.zip | 0 | No | 5 | Risk Methodology & Assessment | 5.5.2 | Top Risk-Contributing Circuits/Segments/Spans
21 | 243 | SPD | 006 | SPD_006 | 1(a) | Yes | SPD_006_Q1(a) | The following questions are all related to PG&E’s first response to SPD-PGE-WMP2026-SPD-004 Question 5. a. In the 2024 RAMP Tranche, PG&E has listed 630 circuit segments as “#NA”. Provide an Excel workbook that lists the WDRM v.4 Circuit Segment Name for each of the 630 circuit segments in the first column. The second column should explain why this circuit segment was listed as #NA, such as this circuit segment was split from a larger circuit segment in WDRM v.3 due to the addition of a recloser. The third column should list the name of the previous circuit segment as it was used in WDRM v.3 and presented in PGE_2023_WMP_R0_Section_642_Atch01.xlsx. If this is a newly constructed circuit segment, the response in the third column must be “New”. 2026-2028 Base WMP WDRM v.4 Circuit Segment Name Explanation for #NA 2024 RAMP WDRM v.3 Circuit Segment Name CAMP EVERS 2106737512 b. Explain why PG&E in its 2026-2028 Base WMP did not include a file similar to PGE_2023_WMP_R0_Section_642_Atch01.xlsx in its submission. i. For each mitigation listed below, explain why it is now impossible for PG&E to unitize the mitigation by circuit mile (as it was in PGE_2023_WMP_R0_Section_642_Atch01.xlsx): a) Expulsion Fuse Replacement b) Surge Arrestor Replacement c) Aerial Inspection d) Ground Inspection e) Non-Pole Backlog f) Tree Removal g) Down Conductor Detection (DCD) h) Line Sensors i) Pole Backlog j) Pole Clearing ii. For each mitigation listed above, explain why PG&E was able to complete the corresponding “% of Segment” field in the TopRisk_Table Worksheet of PGE_2023_WMP_R0_Section_642_Atch01.xlsx.1 c. For the years 2023-2025, PG&E states that it is unable to determine actual expenditure and present value cost of specific work done on a circuit segment for each of the mitigations listed in Question 1.b.i., but PG&E can provide the average cost to complete one unit of the mitigation program. For each of the mitigations listed in Question 1.b.i., provide an explanation for why PG&E is unable to determine the actual expenditure and present value cost of specific work done on a circuit segment. i. Since PG&E is unable to determine the actual expenditures, provide a step-by-step method PG&E used to estimate the average cost to complete one unit of each of the mitigations listed in Question 1.b.i. Be sure to include the unit cost and the range of the unit cost for each mitigation in your response. ii. PG&E’s SAP system allows for the presentation of monthly detail of undergrounding projects by using the Analyses for Office (AO) report PROJ002-PS Monthly Detail function.2 Explain how PG&E records cost-related data in SAP for orders related to each of the mitigations listed in Question 1.b.i. a) Can PG&E use Analyses for Office (AO) report PROJ002-PS Monthly Detail function to generate a report similar to EUP_DR_SPD_013_Q001Atch02CONF.xlsx for each of the mitigations listed in Question 1.b.i.? a. If so, provide a copy of the report for an order associated with the CORNING 110185152 circuit segment for each of the mitigations listed in Question 1.b.i. 1 For instance, on the OAKHURST 110310140 circuit segment, PG&E stated that Tree Removal occurred on 42.3% of the circuit segment in 2023, on 24.5% of the circuit segment in 2024 and on 14.4% of the circuit segment in 2025. 2 See SPD-PGE-SB884-013 (PG&E Ref. DRU14491-Case-EUP-SB 884), Question 1c. and EUP_DR_SPD_013_Q001Atch02CONF.xlsx. b. If not, explain why not. d. Table 8-1 in PG&E’s 2026-2028 Base WMP states that PG&E intends to install 200 service breakaway connectors in 2026, 1,400 in 2027 and 1,400 in 2028. Explain why PG&E in response to SPD-PGE-WMP2026-SPD-004 Question 5 stated that it does not track any information related to breakaway connector installations. i. What is the MAT Code for this mitigation activity (GM-14) that PG&E used in its 2027 Test Year GRC Application? ii. How will PG&E calculate the risk reduced by service breakaway connectors if the location of service breakaway connectors and identify future locations for work if the location of the service breakaway connector is not tracked? e. Figure PG&E 5-2-5 in PG&E’s 2026-2028 Base WMP presents the EORM Risk Model as contributing to the calculation of Wildfire Consequence (i.e. WFC v4). Pg. 71 of PG&E’s 2026-2028 Base WMP states that “Ignition Risk (WDRM v4) for distribution is determined for equipment asset locations for each risk driver causal model LoRE, p(i), and CoRE, WFC.” Table 5-4 states that Ignition/Wildfire Risk (WDRM/WTRM) provides a key output of “Circuit Segment Risk”. In response to SPD-PGE-WMP2026-SPD-004 Question 5 PG&E states that it is impossible to provide circuit segment EORM Values because “PG&E’s EORM values are not calculated to the circuit segment level, but at the “tranche” level.” Explain how PG&E uses tranche level EORM values to develop the key output of “Circuit Segment Risk” from the WDRM. i. Provide a step-by-step calculation of “circuit segment risk”. At each stage PG&E must explain what is the scale of analysis (i.e. tranche, circuit segment, etc.) and must clearly note the units (i.e. dollars, number of deaths, CMI etc.).3 This step-by-step calculation must include a description of a) what CalFire Fire Data is input into the EORM Risk Model b) How the CalFire Fire Data is used within the EORM Risk Model to develop the MAVf intermediate results c) How the MAVf intermediate results are used within the Wildfire Consequence Model to generate the output of Consequence Pixel Values d) How the Consequence Pixel Values are used to calculate Ignition Risk ii. Explain how the EORM and WDRM methods differ. iii. SPD understands that PG&E scales the WDRM v4 risk values to the predicted risk dollar amount from the CBRs (see Table PG&E-6.2.1.2-2). What are the benefits/drawbacks from scaling a bottoms-up relative risk model to the top-down EORM model? a) For instance, it appears that WDRM v4 predicts more risk outside of the HFTD than the EORM model does – is this type of discrepancy reconciled in the model? b) How does the EORM predicted values in tranches (safety, reliability, financial, combined) compare to a risks from WDRM v4 when combined at the tranche level? iv. Use the calculation of Ignition Risk on CORNING 110185152 circuit segment to create a concrete example of the step-by-step calculation of “circuit segment risk” provided in PG&E’s response to Question 1.e.i. 3 Please note, tables such as PG&E-6.2.1.2-4 are confusing because it is not clear what the scale of analysis is in the example, nor is it clear which units are used for each number in the example. f. Does PG&E intend to only present WDRM data in its Electrical Undergrounding Plan submission to Energy Safety? i. If a party wished to know the EORM values for a circuit segment that PG&E includes in its Electrical Undergrounding Plan, is PG&E able to generate those values? g. In PG&E’s response to SPD-PGE-WMP2026-SPD-001 Question 26, PG&E stated that in the 2026-2028 Base WMP Submission it used a preliminary version of the WBCA Tool to conduct mitigation effectiveness analysis. Since PG&E has stated that the post-mitigation values requested in SPD-PGE-WMP2026-SPD-004 Question 5 cannot be provided through the WDRM v.4 model, can PG&E provide these values through its use of the preliminary version of the WBCA tool? i. If so, please complete the following variables that were included in Decision Tree Results by Circuit Segment.xlsx along with PG&E’s response SPD-PGE-WMP2026-SPD-004 Question 5 on May 30th 2025: a) Post-Mitigated LoRE b) Unadjusted Post-Mitigated CoRE c) Adjusted Post-Mitigated CoRE d) Unadjusted Post-Mitigated Risk e) Adjusted Post-Mitigated Risk ii. If not, explain why not and in which dataset the five data points listed in Question 1.g.i is located. Provide SPD with that data along with PG&Es response to SPD-PGE-WMP2026-SPD-004 Question 5 on May 30th 2025. | Please note we only produced an attachment as part of this amendment | Eddie Schmitt | 2025-05-19 | 2025-06-06 | 2025-06-06 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_006.zip | 1 | No | 5 | Risk Methodology & Assessment | 5.5.2 | Top Risk-Contributing Circuits/Segments/Spans
21 | 243 | SPD | 006 | SPD_006 | 1(s2) | Yes | SPD_006_Q1(s2) | The following questions are all related to PG&E’s first response to SPD-PGE-WMP2026-SPD-004 Question 5. a. In the 2024 RAMP Tranche, PG&E has listed 630 circuit segments as “#NA”. Provide an Excel workbook that lists the WDRM v.4 Circuit Segment Name for each of the 630 circuit segments in the first column. The second column should explain why this circuit segment was listed as #NA, such as this circuit segment was split from a larger circuit segment in WDRM v.3 due to the addition of a recloser. The third column should list the name of the previous circuit segment as it was used in WDRM v.3 and presented in PGE_2023_WMP_R0_Section_642_Atch01.xlsx. If this is a newly constructed circuit segment, the response in the third column must be “New”. 2026-2028 Base WMP WDRM v.4 Circuit Segment Name Explanation for #NA 2024 RAMP WDRM v.3 Circuit Segment Name CAMP EVERS 2106737512 b. Explain why PG&E in its 2026-2028 Base WMP did not include a file similar to PGE_2023_WMP_R0_Section_642_Atch01.xlsx in its submission. i. For each mitigation listed below, explain why it is now impossible for PG&E to unitize the mitigation by circuit mile (as it was in PGE_2023_WMP_R0_Section_642_Atch01.xlsx): a) Expulsion Fuse Replacement b) Surge Arrestor Replacement c) Aerial Inspection d) Ground Inspection e) Non-Pole Backlog f) Tree Removal g) Down Conductor Detection (DCD) h) Line Sensors i) Pole Backlog j) Pole Clearing ii. For each mitigation listed above, explain why PG&E was able to complete the corresponding “% of Segment” field in the TopRisk_Table Worksheet of PGE_2023_WMP_R0_Section_642_Atch01.xlsx.1 c. For the years 2023-2025, PG&E states that it is unable to determine actual expenditure and present value cost of specific work done on a circuit segment for each of the mitigations listed in Question 1.b.i., but PG&E can provide the average cost to complete one unit of the mitigation program. For each of the mitigations listed in Question 1.b.i., provide an explanation for why PG&E is unable to determine the actual expenditure and present value cost of specific work done on a circuit segment. i. Since PG&E is unable to determine the actual expenditures, provide a step-by-step method PG&E used to estimate the average cost to complete one unit of each of the mitigations listed in Question 1.b.i. Be sure to include the unit cost and the range of the unit cost for each mitigation in your response. ii. PG&E’s SAP system allows for the presentation of monthly detail of undergrounding projects by using the Analyses for Office (AO) report PROJ002-PS Monthly Detail function.2 Explain how PG&E records cost-related data in SAP for orders related to each of the mitigations listed in Question 1.b.i. a) Can PG&E use Analyses for Office (AO) report PROJ002-PS Monthly Detail function to generate a report similar to EUP_DR_SPD_013_Q001Atch02CONF.xlsx for each of the mitigations listed in Question 1.b.i.? a. If so, provide a copy of the report for an order associated with the CORNING 110185152 circuit segment for each of the mitigations listed in Question 1.b.i. 1 For instance, on the OAKHURST 110310140 circuit segment, PG&E stated that Tree Removal occurred on 42.3% of the circuit segment in 2023, on 24.5% of the circuit segment in 2024 and on 14.4% of the circuit segment in 2025. 2 See SPD-PGE-SB884-013 (PG&E Ref. DRU14491-Case-EUP-SB 884), Question 1c. and EUP_DR_SPD_013_Q001Atch02CONF.xlsx. b. If not, explain why not. d. Table 8-1 in PG&E’s 2026-2028 Base WMP states that PG&E intends to install 200 service breakaway connectors in 2026, 1,400 in 2027 and 1,400 in 2028. Explain why PG&E in response to SPD-PGE-WMP2026-SPD-004 Question 5 stated that it does not track any information related to breakaway connector installations. i. What is the MAT Code for this mitigation activity (GM-14) that PG&E used in its 2027 Test Year GRC Application? ii. How will PG&E calculate the risk reduced by service breakaway connectors if the location of service breakaway connectors and identify future locations for work if the location of the service breakaway connector is not tracked? e. Figure PG&E 5-2-5 in PG&E’s 2026-2028 Base WMP presents the EORM Risk Model as contributing to the calculation of Wildfire Consequence (i.e. WFC v4). Pg. 71 of PG&E’s 2026-2028 Base WMP states that “Ignition Risk (WDRM v4) for distribution is determined for equipment asset locations for each risk driver causal model LoRE, p(i), and CoRE, WFC.” Table 5-4 states that Ignition/Wildfire Risk (WDRM/WTRM) provides a key output of “Circuit Segment Risk”. In response to SPD-PGE-WMP2026-SPD-004 Question 5 PG&E states that it is impossible to provide circuit segment EORM Values because “PG&E’s EORM values are not calculated to the circuit segment level, but at the “tranche” level.” Explain how PG&E uses tranche level EORM values to develop the key output of “Circuit Segment Risk” from the WDRM. i. Provide a step-by-step calculation of “circuit segment risk”. At each stage PG&E must explain what is the scale of analysis (i.e. tranche, circuit segment, etc.) and must clearly note the units (i.e. dollars, number of deaths, CMI etc.).3 This step-by-step calculation must include a description of a) what CalFire Fire Data is input into the EORM Risk Model b) How the CalFire Fire Data is used within the EORM Risk Model to develop the MAVf intermediate results c) How the MAVf intermediate results are used within the Wildfire Consequence Model to generate the output of Consequence Pixel Values d) How the Consequence Pixel Values are used to calculate Ignition Risk ii. Explain how the EORM and WDRM methods differ. iii. SPD understands that PG&E scales the WDRM v4 risk values to the predicted risk dollar amount from the CBRs (see Table PG&E-6.2.1.2-2). What are the benefits/drawbacks from scaling a bottoms-up relative risk model to the top-down EORM model? a) For instance, it appears that WDRM v4 predicts more risk outside of the HFTD than the EORM model does – is this type of discrepancy reconciled in the model? b) How does the EORM predicted values in tranches (safety, reliability, financial, combined) compare to a risks from WDRM v4 when combined at the tranche level? iv. Use the calculation of Ignition Risk on CORNING 110185152 circuit segment to create a concrete example of the step-by-step calculation of “circuit segment risk” provided in PG&E’s response to Question 1.e.i. 3 Please note, tables such as PG&E-6.2.1.2-4 are confusing because it is not clear what the scale of analysis is in the example, nor is it clear which units are used for each number in the example. f. Does PG&E intend to only present WDRM data in its Electrical Undergrounding Plan submission to Energy Safety? i. If a party wished to know the EORM values for a circuit segment that PG&E includes in its Electrical Undergrounding Plan, is PG&E able to generate those values? g. In PG&E’s response to SPD-PGE-WMP2026-SPD-001 Question 26, PG&E stated that in the 2026-2028 Base WMP Submission it used a preliminary version of the WBCA Tool to conduct mitigation effectiveness analysis. Since PG&E has stated that the post-mitigation values requested in SPD-PGE-WMP2026-SPD-004 Question 5 cannot be provided through the WDRM v.4 model, can PG&E provide these values through its use of the preliminary version of the WBCA tool? i. If so, please complete the following variables that were included in Decision Tree Results by Circuit Segment.xlsx along with PG&E’s response SPD-PGE-WMP2026-SPD-004 Question 5 on May 30th 2025: a) Post-Mitigated LoRE b) Unadjusted Post-Mitigated CoRE c) Adjusted Post-Mitigated CoRE d) Unadjusted Post-Mitigated Risk e) Adjusted Post-Mitigated Risk ii. If not, explain why not and in which dataset the five data points listed in Question 1.g.i is located. Provide SPD with that data along with PG&Es response to SPD-PGE-WMP2026-SPD-004 Question 5 on May 30th 2025. | Please see below for an explanation for why PG&E is unable to determine the actual expenditure and, consequently, present value cost of specific work done on a circuit segment: • Expulsion Fuse Replacement: While each expulsion fuse replacement job is charged to a separate PM order, divisions, at their discretion and for ease of accounting, may charge the entire amount of material stock (i.e. fuses) needed for their region to a single PM order. Disaggregation of bundled material costs would entail assumptions and estimates that would prevent final determination of “actual” cost. • Surge Arrestor Replacement: While each Surge Arrester job is charged to a separate PM order, divisions, at their discretion and for ease of accounting, may charge the entire amount of material stock (i.e. surge arrestors) needed for their region to a single PM order. Disaggregation of bundled material costs would entail assumptions and estimates that would prevent final determination of “actual” cost. • Aerial Inspection: PG&E’s aerial inspections are billed to PM orders on a map-by-map basis and the cost to inspect one specific unit is not able to be disaggregated from the total. WMP-Discovery2026-2028_DR_SPD_006-Q001Supp02 Page 5 • Ground Inspection: PG&E’s ground inspections are billed to PM orders on a map-by-map basis and the cost to inspect one specific unit is not able to be disaggregated from the total. • Non-Pole Backlog: Electric corrective notifications may be charged to a single PM order per notification, or may be bundled together with many other notifications in one PM order. • Tree Removal: PG&E’s tree removal program records costs in one of two ways: unit cost, and under “time and materials.” “Time and materials” cost cannot be linked to specific underlying work, which prevents PG&E from providing an “actual” expenditure at the circuit segment level. • Down Conductor Detection (DCD): PG&E’s DCD program involves the installation of software on devices in the field. DCD “units” may be installed in one of three ways: (1) through PG&E’s controller retrofit program; (2) through PG&E’s substation relay replacement program, and; (3) in the course of other work in the field (e.g. a pole replacement that includes replacement of devices). With regard to units installed via the controller retrofit program and substation relay program, while each unit is charged to a separate PM order, the entire amount of material stock (i.e. controllers) needed for a set of jobs may be charged to a single PM order. Disaggregation of bundled material costs would entail assumptions and estimates that would prevent final determination of “actual” cost. With regard to DCD units installed via other work, the unit cost is $0 and will be reported as such. • Line Sensors: PG&E generates a unique PM order for each location where sensors are installed. However, design and commissioning cost associated with each unit are not charged to the unique PM orders, and are instead charged at the program level. Those expenditures are a significant proportion of sensor unit costs and cannot be linked to specific units. This prevents PG&E from providing “actual expenditure” at the circuit segment level. • Pole Backlog: Electric corrective notifications may be charged to a single PM order per notification, or may be bundled together with many other notifications in one PM order. • Pole Clearing: Prior to 2025, the contractual structure for Pole Clearing was based upon a negotiated lump sum amount. As such it is not possible to trace an individual billed cost amount to an individual completed pole clearing unit. i. Please see below for an explanation of unit costs for each of the listed mitigations: • Expulsion Fuse Replacement: PG&E will utilize the unit cost calculation provided for 2025 in its response to WMP-Discovery2026-2028_DR_SPD_001-Q021. • Surge Arrestor Replacement: PG&E will utilize the unit cost calculation provided for 2025 in its response to WMP-Discovery2026-2028_DR_SPD_001-Q021. • Aerial Inspection: PG&E will utilize the unit cost calculation provided for 2025 in its response to WMP-Discovery2026-2028_DR_SPD_001-Q021. WMP-Discovery2026-2028_DR_SPD_006-Q001Supp02 Page 6 • Ground Inspection: PG&E will utilize the unit cost calculation provided for 2025 in its response to WMP-Discovery2026-2028_DR_SPD_001-Q021. • Non-Pole Backlog: PG&E is still evaluating methods for providing unit cost for this mitigation due to the wide variety of conditions that may be addressed in an electric corrective notification. • Tree Removal: As noted above, PG&E’s billing system includes two (2) types of billing for tree work: a) unit cost basis and b) time and materials. Unit cost billing can be linked to the underlying tree work to determine if it is related to tree removal, tree trimming or brush work. Time and Materials billing cannot be similarly linked to the underlying tree work. PG&E plans to estimate the total value of expenditures for Tree Removal as follows: o For 2023 – 2024, total expenditures reflect billed data (unit) increased by a T&M adder (based upon total program billings for all tree work), then multiplied by the units identified as trees worked per segment. o For 2025 – 2028, forecasted expenditures are being reported consistent with our 2027 GRC filing whereby a number of forecasted removals are multiplied by an average programmatic cost. Chapter 8, Exhibit PG&E-4, Workpaper Tables 8-7 (Annual/ Routine Patrol Trim and Removal Work) & 8-9 (Hazard Parol) • Down Conductor Detection (DCD): PG&E will utilize the unit cost calculation provided for 2025 in its response to WMP-Discovery2026-2028_DR_SPD_001-Q021. • Line Sensors: PG&E will utilize the unit cost calculation provided for 2025 in its response to WMP-Discovery2026-2028_DR_SPD_001-Q021. • Pole Backlog: PG&E is still evaluating methods for providing unit cost for this mitigation. • Pole Clearing: PG&E will utilize the pole clearing unit cost calculated in its 2027 GRC testimony to provide the specific Pole Clearing unit costs and apply that to circuit-segment pole clearing unit data. ii. Please see below for an explanation of how PG&E records cost-related data in SAP for orders related to each of the listed mitigations: • Expulsion Fuse Replacement: As noted above, PG&E records cost-related data in SAP for this mitigation using a unique PM order for each unit. However, divisions, at their discretion and for ease of accounting, may charge the entire amount of material stock (i.e. fuses) needed for their region to a single PM order. • Surge Arrestor Replacement: As noted above, PG&E records cost-related data in SAP for this mitigation using a unique PM order for each unit. However, divisions, at their discretion and for ease of accounting, WMP-Discovery2026-2028_DR_SPD_006-Q001Supp02 Page 7 may charge the entire amount of material stock (i.e. fuses) needed for their region to a single PM order. • Aerial Inspection: As noted above, PG&E’s aerial inspections are billed to PM orders on a map-by-map basis. • Ground Inspection: As noted above, PG&E’s ground inspections are billed to PM orders on a map-by-map basis • Non-Pole Backlog: As noted above, Electric corrective notifications may be charged to a single PM order per notification, or may be bundled together with many other notifications in one PM order. • Tree Removal: Costs related to tree removal are recorded in SAP within Controlling Orders (CO orders) organized on a geographic division area for each mitigation program. Tree Removal costs are a subset of total tree work and are recognized based upon billed amounts from contractors both on a unit-billed and time & material basis. • Down Conductor Detection (DCD): As explained in part (c), above, PG&E records costs related to DCD units in one of three ways: (1) units installed under the controller retrofit program have costs charged to a unique PM order in SAP4; (2) units installed under the substation relay replacement program have costs charged to a unique PM order in SAP; (3) units installed in the course of other work are not charged and have a unit cost of $0. • Line Sensors: PM orders at location level, but labor and design not disaggregable to specific circuit segment. • Pole Backlog: As noted above, Electric corrective notifications may be charged to a single PM order per notification, or may be bundled together with many other notifications in one PM order. • Pole Clearing: Costs related to Pole Clearing are recorded in SAP within CO orders organized on geographic regional areas. Pole Clearing costs are recognized based upon billed amounts from contractors. Prior to 2025, these amounts were billed under a lump sum contract format. a) PG&E can use the Analyses for Office (AO) report PROJ002-PS Monthly Detail function to generate a report using PM orders. As a result, PG&E believes it can generate reports for specific PM orders or lists of PM orders using this function for the listed mitigations, though PG&E notes that the PROJ002-PS Monthly Detail function is not generally used in the normal course of business for these mitigations. However, PG&E is not able to do so with regard to Tree Removal and Pole Clearing. 4 Please note, however, that some units installed in 2025 are non-capital, and are charged at the program level and not to unique PM orders. Further, as noted above, instances arise in which larger volumes of material stock are charged to a single PM order and not to each individual order. WMP-Discovery2026-2028_DR_SPD_006-Q001Supp02 Page 8 a. PG&E cannot provide reports for orders associated with CORNING 110185152 until it has completed mapping units to the circuit segment list. At this time, PG&E is still determining the approximate time to complete that exercise. PG&E will supplement this response when able upon completion of unit mapping. b. PG&E is not able to generate a report using the Analyses for Office (AO) report PROJ002-PS Monthly Detail function for Tree Removal or Pole Clearing because PG&E’s vegetation management costs are not recorded in SAP in a way that this report can capture. Please see our explanation of how PG&E records costs for these two mitigations in SAP, above. | Eddie Schmitt | 2025-05-19 | 2025-06-02 | 2025-06-02 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_006.zip | 0 | No | 5 | Risk Methodology & Assessment | 5.5.2 | Top Risk-Contributing Circuits/Segments/Spans
18 | 243 | SPD | 006 | SPD_006 | 1(s3) | Yes | SPD_006_Q1(s3) | The following questions are all related to PG&E’s first response to SPD-PGE-WMP2026-SPD-004 Question 5. a. In the 2024 RAMP Tranche, PG&E has listed 630 circuit segments as “#NA”. Provide an Excel workbook that lists the WDRM v.4 Circuit Segment Name for each of the 630 circuit segments in the first column. The second column should explain why this circuit segment was listed as #NA, such as this circuit segment was split from a larger circuit segment in WDRM v.3 due to the addition of a recloser. The third column should list the name of the previous circuit segment as it was used in WDRM v.3 and presented in PGE_2023_WMP_R0_Section_642_Atch01.xlsx. If this is a newly constructed circuit segment, the response in the third column must be “New”. 2026-2028 Base WMP WDRM v.4 Circuit Segment Name Explanation for #NA 2024 RAMP WDRM v.3 Circuit Segment Name CAMP EVERS 2106737512 b. Explain why PG&E in its 2026-2028 Base WMP did not include a file similar to PGE_2023_WMP_R0_Section_642_Atch01.xlsx in its submission. i. For each mitigation listed below, explain why it is now impossible for PG&E to unitize the mitigation by circuit mile (as it was in PGE_2023_WMP_R0_Section_642_Atch01.xlsx): a) Expulsion Fuse Replacement b) Surge Arrestor Replacement c) Aerial Inspection d) Ground Inspection e) Non-Pole Backlog f) Tree Removal g) Down Conductor Detection (DCD) h) Line Sensors i) Pole Backlog j) Pole Clearing ii. For each mitigation listed above, explain why PG&E was able to complete the corresponding “% of Segment” field in the TopRisk_Table Worksheet of PGE_2023_WMP_R0_Section_642_Atch01.xlsx.1 c. For the years 2023-2025, PG&E states that it is unable to determine actual expenditure and present value cost of specific work done on a circuit segment for each of the mitigations listed in Question 1.b.i., but PG&E can provide the average cost to complete one unit of the mitigation program. For each of the mitigations listed in Question 1.b.i., provide an explanation for why PG&E is unable to determine the actual expenditure and present value cost of specific work done on a circuit segment. i. Since PG&E is unable to determine the actual expenditures, provide a step-by-step method PG&E used to estimate the average cost to complete one unit of each of the mitigations listed in Question 1.b.i. Be sure to include the unit cost and the range of the unit cost for each mitigation in your response. ii. PG&E’s SAP system allows for the presentation of monthly detail of undergrounding projects by using the Analyses for Office (AO) report PROJ002-PS Monthly Detail function.2 Explain how PG&E records cost-related data in SAP for orders related to each of the mitigations listed in Question 1.b.i. a) Can PG&E use Analyses for Office (AO) report PROJ002-PS Monthly Detail function to generate a report similar to EUP_DR_SPD_013_Q001Atch02CONF.xlsx for each of the mitigations listed in Question 1.b.i.? a. If so, provide a copy of the report for an order associated with the CORNING 110185152 circuit segment for each of the mitigations listed in Question 1.b.i. 1 For instance, on the OAKHURST 110310140 circuit segment, PG&E stated that Tree Removal occurred on 42.3% of the circuit segment in 2023, on 24.5% of the circuit segment in 2024 and on 14.4% of the circuit segment in 2025. 2 See SPD-PGE-SB884-013 (PG&E Ref. DRU14491-Case-EUP-SB 884), Question 1c. and EUP_DR_SPD_013_Q001Atch02CONF.xlsx. b. If not, explain why not. d. Table 8-1 in PG&E’s 2026-2028 Base WMP states that PG&E intends to install 200 service breakaway connectors in 2026, 1,400 in 2027 and 1,400 in 2028. Explain why PG&E in response to SPD-PGE-WMP2026-SPD-004 Question 5 stated that it does not track any information related to breakaway connector installations. i. What is the MAT Code for this mitigation activity (GM-14) that PG&E used in its 2027 Test Year GRC Application? ii. How will PG&E calculate the risk reduced by service breakaway connectors if the location of service breakaway connectors and identify future locations for work if the location of the service breakaway connector is not tracked? e. Figure PG&E 5-2-5 in PG&E’s 2026-2028 Base WMP presents the EORM Risk Model as contributing to the calculation of Wildfire Consequence (i.e. WFC v4). Pg. 71 of PG&E’s 2026-2028 Base WMP states that “Ignition Risk (WDRM v4) for distribution is determined for equipment asset locations for each risk driver causal model LoRE, p(i), and CoRE, WFC.” Table 5-4 states that Ignition/Wildfire Risk (WDRM/WTRM) provides a key output of “Circuit Segment Risk”. In response to SPD-PGE-WMP2026-SPD-004 Question 5 PG&E states that it is impossible to provide circuit segment EORM Values because “PG&E’s EORM values are not calculated to the circuit segment level, but at the “tranche” level.” Explain how PG&E uses tranche level EORM values to develop the key output of “Circuit Segment Risk” from the WDRM. i. Provide a step-by-step calculation of “circuit segment risk”. At each stage PG&E must explain what is the scale of analysis (i.e. tranche, circuit segment, etc.) and must clearly note the units (i.e. dollars, number of deaths, CMI etc.).3 This step-by-step calculation must include a description of a) what CalFire Fire Data is input into the EORM Risk Model b) How the CalFire Fire Data is used within the EORM Risk Model to develop the MAVf intermediate results c) How the MAVf intermediate results are used within the Wildfire Consequence Model to generate the output of Consequence Pixel Values d) How the Consequence Pixel Values are used to calculate Ignition Risk ii. Explain how the EORM and WDRM methods differ. iii. SPD understands that PG&E scales the WDRM v4 risk values to the predicted risk dollar amount from the CBRs (see Table PG&E-6.2.1.2-2). What are the benefits/drawbacks from scaling a bottoms-up relative risk model to the top-down EORM model? a) For instance, it appears that WDRM v4 predicts more risk outside of the HFTD than the EORM model does – is this type of discrepancy reconciled in the model? b) How does the EORM predicted values in tranches (safety, reliability, financial, combined) compare to a risks from WDRM v4 when combined at the tranche level? iv. Use the calculation of Ignition Risk on CORNING 110185152 circuit segment to create a concrete example of the step-by-step calculation of “circuit segment risk” provided in PG&E’s response to Question 1.e.i. 3 Please note, tables such as PG&E-6.2.1.2-4 are confusing because it is not clear what the scale of analysis is in the example, nor is it clear which units are used for each number in the example. f. Does PG&E intend to only present WDRM data in its Electrical Undergrounding Plan submission to Energy Safety? i. If a party wished to know the EORM values for a circuit segment that PG&E includes in its Electrical Undergrounding Plan, is PG&E able to generate those values? g. In PG&E’s response to SPD-PGE-WMP2026-SPD-001 Question 26, PG&E stated that in the 2026-2028 Base WMP Submission it used a preliminary version of the WBCA Tool to conduct mitigation effectiveness analysis. Since PG&E has stated that the post-mitigation values requested in SPD-PGE-WMP2026-SPD-004 Question 5 cannot be provided through the WDRM v.4 model, can PG&E provide these values through its use of the preliminary version of the WBCA tool? i. If so, please complete the following variables that were included in Decision Tree Results by Circuit Segment.xlsx along with PG&E’s response SPD-PGE-WMP2026-SPD-004 Question 5 on May 30th 2025: a) Post-Mitigated LoRE b) Unadjusted Post-Mitigated CoRE c) Adjusted Post-Mitigated CoRE d) Unadjusted Post-Mitigated Risk e) Adjusted Post-Mitigated Risk ii. If not, explain why not and in which dataset the five data points listed in Question 1.g.i is located. Provide SPD with that data along with PG&Es response to SPD-PGE-WMP2026-SPD-004 Question 5 on May 30th 2025. | a. Please see attachment “WMP-Discovery2026-2028_DR_SPD_006- Q001Supp03Atch01.xlsx” for an explanation of the 630 #N/A WDRM v4 Circuit Segments. The #N/A Explanations Key is as follows: merge Two or more v3 circuit segments were combined, either partially or in total, to create a new circuit segment. new additions A circuit segment initially identified as “new construction” was determined to be either replacement construction or a new conductor added to an existing v3 circuit segment. new construction A circuit segment that is either entirely new construction or a newly rebuilt replacement circuit segment. other length changed Circuit segment grew or shrank substantially, due to splits, mergers, or removal of downstream interruptive devices. renamed Circuit segment where the only change was the circuit feeder name or the ID of the interruptive device that heads the segment. split Circuit segment resulted from the split of a v3 circuit segment. split/merged Circuit segment resulted from both split and merged conductors from multiple v3 circuit segments. WMP-Discovery2026-2028_DR_SPD_006-Q001Supp03 Page 5 The methodology and tooling for relating circuit segments between model versions and explaining the change is in the process of being matured. The explanations and matching circuit segments in the attachment are subject to change as the tooling is enhanced and more rigorously tested. e. iv. Please see attachment “WMP-Discovery2026-2028_DR_SPD_006- Q001Supp03Atch02CONF.pdf” for a calculation description for the CORNING 110185152 circuit segment. | Eddie Schmitt | 2025-04-30 | 2025-06-05 | 2025-06-05 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_006.zip | 2 | No | 5 | Risk Methodology & Assessment | 5.5.2 | Top Risk-Contributing Circuits/Segments/Spans
21 | 244 | SPD | 006 | SPD_006 | 2 | No | SPD_006_Q2 | Following up on PG&E’s response to WMP-Discovery2026-2028_DR_MGRA_005 Question 4, provide a technical report that explains the following topics related to Gridscope: a. Description and specifications of the sensors used in Gridscope b. Description of how Gridscope sensors provide real-time monitoring to enhance grid reliability and safety. c. Description of how Gridscope sensors collect asset performance data i. Description of how the performance data collected by Gridscope is used to manage outages in real-time. ii. Description of how the performance data collected by Gridscope is used to plan future reliability programs. d. Description of how many distribution poles on average can be installed with Gridscope technology within a given work day. e. Description of the costs associated with installing Gridscope on the number of distribution poles in PG&E’s answer to 2.d. Provide all documents that PG&E has in its possession related to the effectiveness and cost of Gridscope. | a. The current Gridscope product has been deployed in a pilot capacity. It’s current capabilities include sensing vibration, acceleration, inclination, electric field voltage, infrared readings, temperature, barometric pressure, particulate matter, humidity, audio and imaging. b. Gridscope sensors have been mounted on every other pole to monitor the pole they are attached to and the adjacent pole. It senses the electromagnetic field, vibration, WMP-Discovery2026-2028_DR_SPD_006-Q002 Page 2 pole tilt, and acoustics for changes, faults or interactions that occur at a location. It also “learns” its environment and only reports events that are out of the ordinary, limiting false positives. The devices either communicate via cell, relay to cell or via link to a pole mounted gateway device (which can communicate over cell or satellite). When an interaction occurs, the information is sent to the cloud and Gridware AI interprets the information. A condition is determined to be an outage when an interaction occurs at the same time a loss of power is sensed. If there is no power loss, the interaction is considered to be a potential hazard. c. i. Upon receipt of an alert of an outage or a hazard from a Gridscope sensor, PG&E dispatches a Troubleshooter to go to in the field to either identify the cause of the outage or verify if a hazard exists. The ability of the Gridscope sensor to accurately identify interaction locations enables faster response to an event. ii. Gridscope devices have been deployed in pilot mode and are currently used for outage/hazard response only. d. Based on pilot implementation experience, PG&E estimates that, on average, a crew can install 40 to 50 devices per day depending on accessibility to the locations. e. During pilot phase, PG&E contracted out Gridscope installs to the vendor, the details of which are confidential. Effectiveness - Please see “WMP-Discovery2026-2028_DR_SPD_006-Q002Atch01CONF.xlsx” for all alert information from January 1, 2024 to May 2025. Cost – PG&E has been evaluating Gridscope technology on a pilot agreement with the vendor. We are in the process of negotiating a master services agreement for future deployments. | Eddie Schmitt | 2025-05-19 | 2025-05-22 | 2025-05-22 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_006.zip | 1 | No | 10 | Situational Awareness and Forecasting | 10.3.1 | Existing Systems, Technologies, and Procedures
21 | 245 | SPD | 006 | SPD_006 | 3 | No | SPD_006_Q3 | In PG&E’s 2026 Annual-WMP Template Workbook submitted to Energy Safety on April 30 2025, in column L of Table 11, PG&E listed “2022 WMP”, “2023 WMP” and “refer to 8.4” as the most recent proceeding to review this program. a. Explain what these three responses mean. b. Were the costs of the initiative reviewed in each of these three responses. i. If so, provide evidence of the review of the costs for this initiative. ii. If not, explain where the costs for these initiatives have been reviewed. If the costs for these initiatives have not been reviewed, explain why. | a. PG&E misstated some of the proceedings in Column L of Table 11. PG&E understands that “2022 WMP”, “2023 WMP” and “refer to 8.4” are not valid proceedings. b. No, the most recent proceeding to review costs for non-Transmission-related initiatives is PG&E’s 2023 General Rate Case (GRC). i. Not applicable. ii. The CPUC issued a Final Decision (D.23-11-069) for PG&E’s 2023 GRC on November 17, 2023. This Decision discusses PG&E’s forecast capital expenditures for 2023-2025 and forecast expenses for 2023. Specifically, sections 4.2 – Wildfire Risk Mitigation Forecast, 4.3 – Wildfire System Hardening, 4.9 – Vegetation Management, and 4.4 – Other Wildfire Risk Mitigations address PG&E’s wildfire mitigation forecasts. Forecasts for other programs included in the WMP, such as Overhead Equipment Replacement or Pole Replacement, are also discussed in the Final Decision in other sections. Costs for electric transmission work are reviewed in Transmission Owner (TO) rate cases, the most recent of which is PG&E TO21 (docket number ER-25-624). | Eddie Schmitt | 2025-05-19 | 2025-05-28 | 2025-05-28 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_006.zip | 0 | No | 3 | Overview of WMP | 3.6 | 3.6 - Projected Expenditures
21 | 245 | SPD | 006 | SPD_006 | 4 | No | SPD_006_Q4 | In its response to SPD-004 Question 27b PG&E states “Cost-related feasibility factors are incorporated into cost assumptions as a quantifiable cost modifier, which are then included in the estimated unit cost of the proposed construction.” a. Provide the quantifiable cost modifier for each of the seven “primary examples of feasibility constraints” listed in Question 27. b. Explain how PG&E determined the value for each of the quantifiable cost modifiers listed in Question 27. | a. The primary examples of feasibility constraints listed in Question 27F are not an exhaustive list of cost adders that could be applied to a project during scoping. As we proceed through scoping, we may identify additional cost adders or constraints that could influence how we model the expected cost. The cost at the scoping stage is considered an Association for the Advancement of Cost Engineering (AACE) Class 5 estimate, which is based on limited project definition and serves as a preliminary assessment with a potential accuracy range of -50% to +100%. Class 5 estimates are used for strategic planning, evaluating project viability, and comparing different project options. Please refer to “WMP-Discovery2026-2028_DR_SPD_006-Q004Atch01CONF.xlsx” for a breakdown of cost adders and constraints, including their associated amounts. These costs encompass items related to the feasibility constraints listed in Question 27F, but costs in the scoping stage are not confined to these specific quantitative values. Costs may change throughout the life of the subproject due to existing project conditions. The insights gained during scoping may lead to project modifications, such as route changes, that could impact overall mileage and unit costs. b. PG&E’s project management team established these estimated values based on a review of historical project costs, which are captured and maintained upon project completion. We refine these assumptions as projects are completed and additional historic data becomes available. | Eddie Schmitt | 2025-05-19 | 2025-06-02 | 2025-06-02 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_006.zip | 1 | No | 8 | Grid Design, Operations, and Maintenance | 8.2.1 | Covered Conductor Installation
21 | 246 | SPD | 006 | SPD_006 | 5 | No | SPD_006_Q5 | In a meeting on May 9th to discuss the Wildfire Benefit Cost Analysis (WBCA) Tool, SPD understood from PG&E that a limited number of circuit segments had been evaluated according to the System Hardening Project Scoping Decision Tree and Process found in Figures PG&E-8.2.1-1, PG&E-8.2.1-2, and PG&E-8.2.1-3 in the 2026-2028 Base WMP. Per page 182 of the 2026-2028 WMP SPD understands that the decision trees will inform mitigation selection beginning in 2027. a. Provide the total number of circuit segments where PG&E has already applied the decision tree for mitigation work in 2027 and 2028. b. Provide the total number of circuit segments where PG&E intends to apply the decision tree for work done in 2027 and 2028. | a. As of May 29, 2025, a total of 28 circuit segments have been reviewed against the System Hardening Project Scoping Decision Tree and Process found in Figures PG&E-8.2.1-1, PG&E-8.2.1-2, and PG&E-8.2.1-3 in the 2026-2028 Base WMP and progressed through scoping. Due to size or complexity, not all of these segments will be included in the 2027 workplans. Circuit segments for the 2028 workplan have not yet been evaluated using these decision trees. b. PG&E plans to use the System Hardening Project Scoping Decision Tree and Process found in Figures PG&E-8.2.1-1, PG&E-8.2.1-2, and PG&E-8.2.1-3 in the 2026-2028 Base WMP for an additional 35 circuit segments for consideration in the 2027 workplan. Circuit segments for 2028 have not yet been evaluated using these Decision Trees. | Eddie Schmitt | 2025-05-19 | 2025-06-02 | 2025-06-02 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_006.zip | 0 | No | 3 | Overview of WMP | 3.6 | 3.6 - Projected Expenditures
21 | 247 | SPD | 006 | SPD_006 | 6 | No | SPD_006_Q6 | In a meeting on May 9th to discuss the Wildfire Benefit Cost Analysis (WBCA) Tool, PG&E informed SPD that the baseline value of risk used to calculate CBR is different in the 2024 RAMP and the WBCA Tool. a. Provide a detailed step by step explanation of how CBR is calculated for the 2024 RAMP and WBCA Tool. This should include an example with a table that is similar Table PG&E-6.2.1.2-2 in the 2026-2028 Base WMP but should continue through to the entire CBR calculation. i. In the narrative answer to this question highlight the differences in the baseline value of risk used in each approach. Explain any other differences. b. Explain why PG&E decided to use a baseline value of risk to calculate the CBR in the WBCA Tool that was different than the baseline value of risk used to calculate CBR in the 2024 RAMP. | a. Pursuant to agreement with SPD, PG&E will provide this response on May 28, 2025. b. Historically, the near permanent mitigation of wildfire risk through infrastructure upgrades has been the focus of most system hardening initiatives. Outage programs, such as EPSS and PSPS, are operational mitigations that reduce wildfire risk at the expense of reliability risk. However, to maintain focus on only the infrastructure upgrades, neither the wildfire risk reduction nor the reliability risk increase resulting from EPSS and PSPS were included in the combined CBRs in PG&E’s 2024 RAMP. The WBCA is being developed to comply with EUP requirements to simultaneously analyze the comprehensive costs versus benefits of system hardening mitigations relative to both Wildfire Risk and Outage Program Risk. To do so, PG&E had to adopt a methodology which accounts for the risk trade-offs associated with operational mitigations. | Eddie Schmitt | 2025-05-19 | 2025-05-22 | 2025-05-22 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_006.zip | 0 | No | 3 | Overview of WMP | 3.6 | 3.6 - Projected Expenditures
21 | 247 | SPD | 006 | SPD_006 | 6(s) | Yes | SPD_006_Q6(s) | In a meeting on May 9th to discuss the Wildfire Benefit Cost Analysis (WBCA) Tool, PG&E informed SPD that the baseline value of risk used to calculate CBR is different in the 2024 RAMP and the WBCA Tool. a. Provide a detailed step by step explanation of how CBR is calculated for the 2024 RAMP and WBCA Tool. This should include an example with a table that is similar Table PG&E-6.2.1.2-2 in the 2026-2028 Base WMP but should continue through to the entire CBR calculation. i. In the narrative answer to this question highlight the differences in the baseline value of risk used in each approach. Explain any other differences. b. Explain why PG&E decided to use a baseline value of risk to calculate the CBR in the WBCA Tool that was different than the baseline value of risk used to calculate CBR in the 2024 RAMP. | a. Please see attachment “WMP-Discovery2026-2028_DR_SPD_006- Q006Supp01Atch01.xlsx” for a simplified example CBR calculation using WBCA methodology in similar format to Table PG&E-6.2.1.2-2 on the “WBCA Example” sheet and a CBR calculation example using the 2024 RAMP methodology on the “2024 RAMP Example” sheet. The values and assumptions used in the “WBCA Example” sheet of the attachment are an illustrative example only, as the WBCA is still in development and subject to change. The attachment provides the detailed CBR steps. For the RAMP CBR the calculations, the tranche and multi-year methodology and input values are not transferable to the format of Table PG&E-6.2.1.2-2 in the 2026-2028 Base WMP. i. The RAMP methodology is different than the WBCA methodology for calculating CBRs primarily due to the following factors: WMP-Discovery2026-2028_DR_SPD_006-Q006Supp01 Page 2 • RAMP calculates the CBR at the tranche-level1, whereas the WBCA calculates the CBR at a circuit segment-level. • RAMP calculations use a multi-year period for calculating the CBR (e.g. 2027- 2030), whereas the WBCA will calculate the CBR for a single project (i.e. circuit segment) in a given year (e.g. 2028). Both methodologies consider the benefits and costs of the projects over the life of the asset (e.g. 55 years for undergrounding). • There are differences in the baseline risks used in the CBR calculations: RAMP methodology does not consider operational mitigations or their resulting outage program risks, focusing on permanent infrastructure upgrades to address unmitigated wildfire risk, whereas the WBCA is intended to use post-PSPS wildfire risk for baseline calculations. | Eddie Schmitt | 2025-05-19 | 2025-05-28 | 2025-05-28 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_006.zip | 1 | No | 3 | Overview of WMP | 3.6 | 3.6 - Projected Expenditures
21 | 248 | SPD | 006 | SPD_006 | 7 | No | SPD_006_Q7 | In SPD-PGE-SB884-017 Question 1d., PG&E stated that the WBCA model uses Capital Costs, O&M Costs, and risk reduction inputs to evaluate alternative mitigations at the circuit segment-level. In SPD-PGE-SB884-017 Question 1g., PG&E also stated that the “key evaluation metrics of the WBCA model are the CBRs and Net Benefits for each circuit segment for certain system hardening mitigation alternatives”. In Figure PG&E 8.2.1-2, CBR and Net Benefits are necessary to determine before PG&E can use the Decision-Tree in Figure PG&E 8.2.1-2 in the 2026-2028 Base WMP to determine a system hardening mitigation at a given CPZ. Explain whether or not this means that PG&E must have Capital Costs, O&M Costs and risk reduction inputs at the circuit segment level before PG&E can determine which system hardening mitigation will be selected at a given CPZ. a. For instance, in response to SPD-PGE-WMP2026-004 Question 5, PG&E stated that PG&E cannot provide the units/miles, Total Expenditure, or Present Value Costs for 2026, 2027 or 2028 for Tree Removal. If this is the case, then how does PG&E estimate O&M expenditures on a given CPZ? i. On May 9th, during a discussion about the WBCA Tool, a PG&E representative mentioned that savings from Tree Removal O&M Expenditures, were driving negative CBR results. How are savings estimated if Tree Removal O&M Expenditures are not estimated at the CPZ level? | Yes, Capital Costs, O&M Costs, and risk reduction inputs are necessary to calculate the CBR and Net Benefit values for individual circuit segments during the scoping process as reflected in Figure PG&E 8.2.1-2. a. PG&E has developed estimated O&M expenditures at the circuit segment-level as an input to the WBCA model for system hardening mitigations, including undergrounding, overhead hardening, and remote grids to account for ongoing WMP-Discovery2026-2028_DR_SPD_006-Q007 Page 2 maintenance costs which are expected to continue in perpetuity. Similar O&M estimates are not available at the CPZ level for other wildfire programs and initiatives, such as expulsion fuse replacement, surge arrestor replacement, or line sensors. i. The vegetation management O&M expenditures referenced during the May 9th call were based on an analysis of ongoing routine maintenance at the CPZ level which incorporates historic maintenance costs as well as strike tree data from satellite imagery. These values will be used to estimate the lifetime costs of vegetation management in the WBCA since routine maintenance is a control required in perpetuity to maintain a safely functioning grid. Given that these are estimated values, there are instances in which the lifetime maintenance costs of an overhead system may exceed the capital expenditure of underground mitigations. In these cases, the net cost of an underground mitigation in comparison to the baseline system is negative. Therefore, a simple CBR calculation of Benefit/Cost yields a negative value. For this reason, PG&E strongly encourages the use of Net Benefits (Benefits – Costs) in decision making as this metric reflects the holistic value of a mitigation. | Eddie Schmitt | 2025-05-19 | 2025-05-22 | 2025-05-22 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_006.zip | 0 | No | 3 | Overview of WMP | 3.6 | 3.6 - Projected Expenditures
21 | 249 | OEIS | 012 | OEIS_012 | 1 | No | OEIS_012_Q1 | Regarding Errata for Projected Expenditures On April 18, 2025, PG&E submitted substantive errata for its 2026-2028 Base WMP. On May 16, 2025, PG&E submitted non-substantive errata for its 2026-2028 Base WMP. In both errata, PG&E made updates to Table 3-3: Summary of Projected WMP Expenditures and stated the updates were made “to refine forecast in alignment with upcoming General Rate Case.” a. Explain the forecast refinements that were made for the April 18, 2025, errata. b. Explain the forecast refinements that were made for the May 16, 2025, errata | Given the proximity of the filing dates for PG&E's 2026-2028 Wildfire Mitigation Plan (April 4, 2025) and PG&E's 2027 General Rate Case (May 15, 2025), PG&E aimed to align forecasted projected expenditures reported in Table 11 of the Annual-WMP Template Workbook_vY1 with forecasts for the upcoming GRC. However, PG&E continued to refine its forecast for the GRC beyond the due dates for both the Final Submission of the WMP on April 4th and the Substantive Errata due on April 18th, resulting in the changes reported in both the Substantive and Non-Substantive Errata. To address both subparts of this question, PG&E has provided an Excel file that compares the state of our forecast at three different points in time—April 4th, April 18th, and May 16th—in a format similar to Table 11. Please see “WMP-Discovery2026- 2028_DR_OEIS_012-Q001Atch01.xlsx.” The most significant changes, when comparing Final Data to Non-Substantive errata, occurred in the Distribution Pole Replacement and Reinforcement activity, the Equipment Maintenance and Repair initiative, and the Grid Monitoring Systems initiative. The modifications in Distribution Pole Replacement and Reinforcement and Equipment Maintenance and Repair were due to separating backlog tags and HFTD/non-HFTD work from the original aggregated forecasts. The adjustments in Grid Monitoring Systems were due to PG&E identifying projected expenditures for the Advanced Metering Infrastructure program that were omitted from the original forecast. | Nathan Poon | 2025-05-23 | 2025-06-05 | 2025-05-29 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_012.zip | 1 | No | 3 | Overview of WMP | 3.6 | 3.6 - Projected Expenditures
21 | 250 | OEIS | 012 | OEIS_012 | 2 | No | OEIS_012_Q2 | Regarding Transmission Right-of-Way Maintenance In its 2026-2028 WMP, Section 9.7.3 “IVM Scheduling,” PG&E states that, “For TIVM, previously worked ROWs are reassessed every 2-5 years” (p. 386). In response to data request OEIS-P-WMP_2025-PGE-001, question 16, PG&E stated “[w]ith the availability of LiDAR data, vegetation height and density conditions are analyzed each year.” On page 385, PG&E references Utility Standard: TD-7111S. In section 6 “Annual Planning,” the standard states that “work plans are created annually” and reiterates that “ROWS are reassessed every 2 to 5 years.” In the same standard, PG&E states, “Thresholds for implementing TIVM are considered when incompatible vegetation exceeds 3 feet in height or exceeds 50% ground coverage within the managed area.” These various statements seem to contradict each other, with vegetation data assessed and work plans created on an annual basis, but ROWs reassessed every 2 to 5 years. a. Clarify on what cadence PG&E examines annually collected LiDAR data for vegetation conditions that would trigger TIVM. b. Clarify on what cadence PG&E performs TIVM. An estimate and/or range is acceptable. c. Define “previously worked ROWs.” d. Define the following activities and explain the difference between them and how they interact with each other: i. Annual analysis of LiDAR data ii. Annual work planning iii. Reassessment of ROWs every 2 to 5 years | a. The LiDAR data is examined annually to support the development of the following year’s work plan for Transmission IVM (TIVM). b. PG&E has an annual Transmission IVM program. TIVM ROW maintenance is dependent on annual resource availability along with how well established the community of compatible vegetation is in a ROW. Considering these two key factors and others cited in the WMP, the TIVM ROW cadence may vary. c. “Previously worked ROWs” are those where significant program or project specific vegetation maintenance was performed in a ROW to meet NERC FAC-003 requirements or where other ROW clearing/widening occurred typically as part of previous Transmission ROW reclamation or ROW Expansion program efforts. Previously worked ROWs also include those that have had ongoing TIVM maintenance. d. i. The annual analysis of LiDAR data is a process tied to annual work planning where LiDAR data is examined to help prioritize which projects may be considered as the most important to schedule the following year. • Key elements of the LiDAR data examined include vegetation heights and density within spans. The LiDAR data cannot determine whether the vegetation is compatible or incompatible, so other considerations are used such as whether the ROW was previously worked and when, whether it is within/outside of HFTD, is part of some sort of agency agreement, etc. ii. Annual work planning is a process that includes resource planning, budget allocation, and approval to support execution of various vegetation management programs. It also includes coordination between VM’s VASA (Vegetation Asset Strategy and Analytics) team and ETVM (Electric Transmission Vegetation Management) Operations to develop recommended work plans for the following year. For TIVM, the LiDAR analysis and other factors described above help inform the proposed plan, which is then presented to VM leadership for approval. iii. The reference for reassessing ROWs every 2-5 years was part of a broader WMP question response where PG&E was asked to describe how IVM management activities are scheduled. In hindsight, a better description is: “Scheduling of TIVM maintenance is linked to an annual work planning process where reassessment of previously worked ROWs occurs annually, with followup maintenance typically targeted within a 2-5 year period or as resources may allow.” Summary: LiDAR data and the other contributing factors described are examined as part of an annual work plan development process. That effort allows ROW vegetation conditions to be reassessed annually, which helps inform the project recommendations made for VM leadership to review and approve on an annual basis. It would be more accurate to say ROWs are assessed/reassessed annually and depending on resource availability, are typically targeted for maintenance within a 2-to-5-year period. The overall goal of IVM is to establish a compatible plant community that can help extend maintenance cycles as long as possible. | Nathan Poon | 2025-05-23 | 2025-05-29 | 2025-05-29 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_012.zip | 0 | No | 9 | Vegetation Management and Inspections | 9 | 9 - Vegetation Management and Inspections
21 | 251 | OEIS | 012 | OEIS_012 | 3 | No | OEIS_012_Q3 | Q03. Regarding Table 6-4 In response to data request OEIS-P-WMP_2025-PGE-008, question 2, subpart (b), PG&E provided an updated version of Table 6-4 from its 2026-2028 Base WMP that included risk density. a. Provide a new version of Table 6-4 with an updated risk ranking of circuit segments based on risk per mile, as used for prioritization of projects. The circuit segments within the new table should not be the same as those currently within Table 6-4, which are ranked based on overall risk scores. The updated table should include the following additional columns: i. Total mileage for the circuit segment ii. 2026 planned undergrounding (circuit mileage) iii. 2027 planned undergrounding (circuit mileage) iv. 2028 planned undergrounding (circuit mileage) v. 2026 planned covered conductor (circuit mileage) vi. 2027 planned covered conductor (circuit mileage) vii. 2028 planned covered conductor (circuit mileage) viii. 2026 planned line removals (circuit mileage) ix. 2027 planned line removals (circuit mileage) x. 2028 planned line removals (circuit mileage) xi. HFRA designation (Tier 2, Tier 3, non-HFTD HFRA, or non-HFRA) | Please see attachment “WMP-Discovery2026-2028_DR_OEIS_012-Q003Atch01.xlsx” for the requested information. This revised version of Table 6-4 consists of the 275 circuit segments that make up the top 20% of overall utility risk per primary overhead mile. Please note that total mileage is interpreted to mean total primary overhead miles and is included in Column C. | Nathan Poon | 2025-05-23 | 2025-06-05 | 2025-06-05 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_012.zip | 1 | No | 5 | Risk Methodology and Assessment | 5.5.2 | 5.5.2 - Top Risk-Contributing Circuits/Segments/Spans
23 | 252 | SPD | 007 | SPD_007 | 1 | No | SPD_007_Q1 | The following questions are all related to PG&E’s estimated Mitigation Effectiveness. a. Table PG&E-8.2.1-3 shows the blended average effectiveness for system hardening scenarios. The table is titled “Ignition Mitigation Effectiveness” but SPD understands from footnote (a) and review of “WMP-Discovery2026-2028_DR_SPD_001-Q010Atch02.xlsx” that the blended average effectiveness reported are based off outage data instead of ignition data. SPD also understands that PG&E does not use the mitigation effectiveness values from Table PG&E-8.2.1-3 when calculating the risk mitigated for each circuit segment from various mitigation programs and instead uses the mitigation effectiveness estimate for each specific ignition driver multiplied by the calculated risk for each circuit segment for each driver from the WDRM v4 model. 1 SPD used the driver mitigation effectiveness from ACI 25U and applied those values to the circuit segment ignition driver risk from WDRM v4 to establish the three cases presented in the table below: (1) all circuits segments in the WDRM v4, (2) all circuits segments in the HFTD in the WDRM v4, (3) the top 5% riskiest circuit segments.2 SPD found the values in Table PG&E-8.2.1-3 appears to overestimate the risk reduced compared to the calculated risk reduction which PG&E uses in its risk calculations for covered conductor and underground primary. Mitigation Effectiveness Summary Area where Mit. Effect. is Calculated WDRM SH Risk (natural units) Residual Risk (natural units) Residual Risk (%) Mitigation Effectiveness (%) CC UG Primary UG All CC UG Primary UG All CC UG Primary UG All Total 1097 374 45 16 34.1% 4.1% 1.4% 65.9% 95.9% 98.6% HFTD Only 964 329 38 13 34.1% 4.0% 1.3% 65.9% 96.0% 98.7% Top 5% 503 172 20 7 34.3% 4.0% 1.4% 65.7% 96.0% 98.6% i. Why does PG&E use the mitigation effectiveness estimated based on outages in Table PG&E-8.2.1-3? ii. Why does PG&E not estimate the mitigation effectiveness based on the calculated risk in WDRM v4 when completing Table PG&E-8.2.1-3? a) Would using the mitigation effectiveness based on the calculated risk in WDRM v4 align the values in Table PG&E 8.2.1-3 with the risk reduction values PG&E uses in decision making? Explain why or why not. iii. SPD understands that PG&E does not use the values in Table PG&E-8.2.1-3 for risk calculations but often sees these values in television advertisements and other high-level presentations of PG&E’s wildfire mitigation program. To this end, will PG&E revise Table PG&E-8.2.1-3 to reflect the mitigation effectiveness based on the calculated risk in WDRM v4, which is used when PG&E is making decisions about mitigation selection. Explain why or why not. a) Will PG&E update its television advertisements and other high-level presentations to reflect the mitigation effectiveness based on the calculated risk in WDRM v4? Explain why or why not. b. SPD also calculated a mitigation effectiveness based on the PG&E’s estimated driver mitigation effectiveness3 and the WDRM v4 event model wildfire risk classification for ignitions “WMP-Discovery2026-2028_DR_SPD_001-Q006Supp01Atch01CONF.xlsx.” SPD found the values in Table PG&E-8.2.1-3 for both covered conductor and underground primary exceeded the estimated mitigation effectiveness from this second study. To this end, if PG&E does not plan to update the values in Table PG&E-8.2.1-3 explain why PG&E uses 1 SPD understands that the mitigation effectiveness for many wildfire programs for each ignition driver in WDRM v4 are calculated in “WMP-Discovery2026-2028_DR_SPD_001-Q010Atch02.xlsx” and presented in ACI 25U-03. 2 The mitigation effectiveness for each driver was based on the mitigation effectiveness ratios in ACI 25U-03. The WDRM v4 risk calculations were based off “WMP-Discovery2023-2025_DR_CalAdvocates_041-Q005Atch01” 3 The mitigation effectiveness for each driver was based on the mitigation effectiveness ratios in ACI 25U-03. The ignitions classifications were based off of WMP-Discovery2026-2028_DR_SPD_001-Q006Supp01Atch01CONF.xslx” the outages rather than ignitions for understanding the mitigation effectiveness of various wildfire mitigations? Ignition-Based Mitigation Effectiveness for HFTD OH UG Pri* UG All* 65% 96% 99% *does not account for ignitions related to UG system c. It does not appear that the distribution drivers of ignitions and outages match – which PG&E acknowledges in its response to ACI PG&E-25U-01 where PG&E explains that WDRM v4 has a p(i¦o) model to account for this issue. Despite noting the mismatch in ignitions and outages, PG&E does not appear to account for this issue in its mitigation effectiveness estimations. This may have several impacts on mitigation effectiveness calculations.4 For instance, when the distribution of drivers of ignitions and outages do not match, this could manifest itself in misrepresenting the actual mitigation effectiveness of the ignition drivers. If there was a large percentage of outages that were unlikely to cause ignitions – a mitigation effectiveness based on outages could overstate the mitigation effectiveness of a particular ignition driver. This mismatch in mitigation effectiveness could propagate to misrepresent the risk reduced based off the calculated risk associated with the ignition drivers in WDRM v4. To determine the mitigation effectiveness of a mitigation for each ignition driver, SPD understands that PG&E’s SMEs estimate mitigation effectiveness for a multitude of outage drivers as seen in sheet “Grid Hardening SME Input” of WMP-Discovery2026-2028_DR_SPD_001-Q010Atch02.xlsx. SPD understands the SME inputs are used to develop a mitigation effectiveness for each of the ignition drivers in WDRM v4 based on the outage data in “WMP-Discovery2026-2028_DR_SPD_001-Q010Atch02.xlsx.” For the ignition driver “vegetation_branch,” “WMP-Discovery2026-2028_DR_SPD_001-Q010Atch02.xlsx” indicates there are 8075 outages (excluding those labeled “N/A”). Within the 8075 “vegetation_branch” outages, 296 outages (3.6%) are identified as not being 100% mitigated by Underground Primary Only.5 Based on the SME Mitigation effectiveness estimates for the various outages PG&E associates with the ignition driver “vegetation_branch,” PG&E estimates that Underground Primary Only is 98% effective for the ignition driver “vegetation_branch.” This differs substantially when compared to a study of historical ignitions. Of the 2804 CPUC-reportable ignitions classified as part of the WDRM v4 event model wildfire risk classification (see “WMP-Discovery2026-2028_DR_SPD_001-Q006Supp01Atch01CONF.xlsx.”), 332 ignitions are classified as “vegetation_branch.”6 Of those 332 ignitions, PG&E reported 75 “vegetation_branch” 4 For instance, the outage mitigation effectiveness estimates in Table PG&E-8.2.1-3 appears less conservative when compared to mitigation effectiveness estimates based on ignitions and separately based on the calculated risk mitigated in PG&E’s WDRM v4 as discussed in other sub-questions 5 Note that all of the 296 outages are associated with the secondary voltage levels or customer equipment. 6 SPD understands that PG&E used the classification for ignitions of the “WDRM v4 event model wildfire risk classification” to compute the risk associated with the “animal bird” ignition risk driver from WDRM v4. ignitions related to the secondary system (22%).7 For simplicity when calculating the effectiveness based on historical ignitions, SPD used the “high” effectiveness assigned by PG&E to the 75 secondary ignitions for the outage driver “Vegetation¦Treebranchfellonline¦Secondary¦Normal” and assumed all other ignitions would be 100 percent mitigated to match PG&E’s assessment. SPD finds the “vegetation_branch” driver mitigation effectiveness based on the historical ignition data to be 94.3% effective.8 Using a mitigation effective of ~52% (which is the average of the PG&E SME-estimated mitigation effectiveness for service and secondary conductor ignitions related to the vegetation_branch driver in “WMP-Discovery2026-2028_DR_SPD_001-Q010Atch02.xlsx.”), the mitigation effectiveness computed for the “vegetation_branch” driver is 89%. A similar analysis can be done with ignitions classified as “vegetation_branch” related to HFTD ignitions to compute an effectiveness of 96% and 92% for former and later assumed mitigation effectiveness.9 These differing mitigation effectiveness estimates (the various ignition-based effectiveness and the outage-based effectiveness of 98 percent) imply that the individual mitigation effectiveness computed for each ignition driver that is used to compute the risk reduced for each driver in WDRM v4 may be incorrectly estimating the risk reduced because the distribution of outage drivers does not appear to match the distribution of ignition drivers. For the case of “vegetation_branch,” it appears that the Underground Primary mitigation effectiveness with PG&E’s current outage-based methodology may be overestimating the risk reduced.10 Given this information, explain how PG&E can adjust its outage-based mitigation effectiveness to more directly compute the estimated risk reduction from mitigations. i. If, in the above explanation, PG&E intends to state that ignitions from equipment/lines at secondary voltages (like service conductors and secondary lines) are less risky than ignitions from primary lines, provide computations which show how this impacts the mitigation effectiveness, taking into account that Service Conductors and Secondary lines may remain energized in PSPS/RFW conditions when connected to undergrounded primary lines. d. PG&E submitted “WMP-Discovery2026-2028_DR_SPD_001-Q010Atch02.xlsx” which includes the number of outages in each year (see table below). The number of outages varies extensively on a yearly basis with a low of 6758 outages in 2015 and a high of 26751 outages in 2024. Confirm the correct subset of outages was included in WMP-Discovery2026-2028_DR_SPD_001-Q010Atch02.xlsx. i. If the correct subset of outages as not included in WMP-Discovery2026-2028_DR_SPD_001-Q010Atch02.xlsx, provide SPD with an update to that file. 7 To find the 75 ignitions associated with the secondary system, SPD used a filter on the voltage classification to single out ignitions that PG&E reported occurred at the 750 V, 480 V, 240 V and 120 V levels with a filter for the HFTD. 8 The calculation is ((332-75)*100%+75*75%)/332 = 94.%. SPD is using these mitigation effectiveness values solely to demonstrate how the outage mitigation effectiveness and the ignition mitigation effectiveness for each driver give different results. 9 There are 229 ignitions classified to the “vegetation-branch” driver in PG&E’s HFTD and 20 including the voltage filter described in footnote 7. 10 This effect is similar but less impactful for covered conductor – at least for the “vegetation_branch” driver. PG&E’s outage-based mitigation effectiveness assesses covered conductor as 76% effective for the “vegetation_branch” driver. PG&E’s average mitigation effectiveness for the “vegeation_branch” driver for covered conductor is ~51% for secondary/service conductor outages and 77% for other outages. Using these numbers in the same manner as the previous example computes a 71% effective for the vegetation_branch driver based on historical ignitions across the service territory and 73% effective based on HFTD ignitions. ii. If the correct subset of outages was included in WMP-Discovery2026-2028_DR_SPD_001-Q010Atch02.xlsx, provide an explanation for why 2024 exhibits nearly double the number of outages of any other year on record. Year 2015 2016 2017 2018 2019 2020 2021 2022 2023 2024 Number of Outages 6758 8434 13677 7806 13804 9348 12840 8919 8727 26751 e. The mitigation effectiveness calculation on undergrounding mitigations appears to neglect the impact from undergrounding ignitions – in fact Table PG&E-8.2.1-3 states underground outages are not included in the study. Based on “WMP-Discovery2023_DR_SPD_003-Q004.pdf,” SPD understands that ignitions on undergrounded lines occur at a much lower rate per mile than overhead lines – but also understands that the rate of ignitions on undergrounded lines is not zero. Explain how PG&E accounts for the ignition risk from undergrounded lines in its mitigation effectiveness, especially accounting for unique drivers for undergrounded systems. f. In “WMP-Discovery2026-2028_DR_SPD_003-Q005.pdf,” PG&E states that it estimates 1.25 miles of undergrounding is needed to mitigate 1 mile of overhead. A simplistic per mile ignition-based effectiveness based on “WMP-Discovery2023_DR_SPD_003-Q004.pdf” would imply that undergrounding an overhead line would reduce the ignition rate by 95% on a per mile basis. However, this analysis neglects the twenty five percent increase in underground miles and thus exposure from converting from overhead to underground mileage. How does PG&E account for the increased exposure from undergrounding overhead miles in its analysis of mitigation effectiveness? g. From “WMP-Discovery2023_DR_SPD_003-Q004.pdf,” SPD understands that PG&E’s SMEs assessed that the relative risk of an underground ignition was less than an overhead ignition based on PG&E’s assessment that no underground ignitions between 2015 and 2021 were larger than 10 acres. How has PG&E’s views changed on the relative risk of underground ignitions to overhead ignitions since that response and has PG&E found additional justification for the assessment? i. Explain if this justification includes that the exposure of the lines may be different – for instance - the relative risk of ignition of lines undergrounded as part of wildfire mitigation may be higher than lines that were undergrounded for other reasons. h. Has PG&E experienced any ignitions on lines (including both the primary and hardened overhead secondary portions of the line) which have been undergrounded as part of a wildfire mitigation? i. If so, provide the PIIR. i. In “WMP-Discovery2026-2028_DR_SPD_001-Q007.pdf” PG&E explained that “Support Structure: Electrical” and “Transformer: Leaking” the drivers from WDRM v4 are not included in the system hardening composite. Explain why. i. For “Support Structure: Electrical” in particular – the WDRM v4 event model wildfire risk classification classified 1 ignition related to this driver as larger than 300 acres (out of 31 total) and 5 of these ignitions as greater than 10 acres (out of 136 total). These numbers are both greater than other drivers which are included in the system hardening score. Why is this model not included in the system hardening composite? ii. Per WDRM v4, the Transformer: Leaking driver has a very small amount of risk which may make sense to neglect – but “Support Structure: Electrical” appears to comprise 9% of the total computed risk from WDRM v4 (6% of the HFTD only risk), which is the fourth highest driver. How does PG&E account for the residual risk from non-system hardening composite drivers after performing hardening? iii. If drivers discussed in Question 1.i.ii are not being mitigated by system hardening programs – this would imply that an average system hardening project with 99% effectiveness would leave ~9% of wildfire risk on the system (6% in the HFTD). Is PG&E discounting the mitigation effectiveness calculations for system hardening so that a system hardening project that is estimated to be 99% effective for the system hardening composite is not over-estimating the risk reduced since it is not addressing some of the calculated drivers of wildfire risk in WDRM v4? a) If so, explain how and provide a dataset to demonstrate how it is incorporating this into the mitigation effectiveness calculation. b) If not, explain why PG&E is not discounting the mitigation effectiveness calculations for system hardening. iv. PG&E’s response to “TURN_004_Q10” states that covered conductor is estimated to be 52% effective against EPSS risk, but in Table PG&E-8.2.1-3 PG&E’s mitigation effectiveness for wildfire ignition expects it to be 67% effective, which is based on the number of outages expected to be mitigated. Why are these numbers not more similar given both are related to the number of expected outages? | a. The values provided in Table 8.2.1-3 are blended average effectiveness values using outages as a proxy for ignitions. Limited ignition data is available for hardened assets and therefore we do not have sufficient data to use ignition data as the basis for our mitigation effectiveness analyses. Because we do not have sufficient ignition data, PG&E uses outage data as a reasonable proxy because it is abundantly available and allows for a statistically significant analysis. The unique percentage of risk reduced by these mitigations when applied to a specific circuit segment, or group of segments, will vary above or below the nominal values in the table. WMP-Discovery 2026-2028_DR_SPD_007-Q001 Page 7 • PG&E interprets SPD’s calculations to represent mitigation effectiveness as a function of risk reduction based on the risk drivers at the circuit segment level, then calculating an average of those results. • In WMP Table 8.2.1-3, PG&E reports the Blended Average Effectiveness values to portray an average effectiveness of each mitigation in preventing ignitions, using abundant historic outages as a proxy to support a more statistically significant study than can be performed using historic ignitions. PG&E stands by our analysis results as accurate average effectiveness values. • The difference between the approaches above are: o We plan on employing a mitigation method that is calculated to be, on average, 98% effective at reducing the potential of an ignition at the undergrounded location. o The estimated risk reduction to be achieved in any given location is based on the risk drivers at that specific location, and the amount of risk that exists at that location (independent of the Blended Average Effectiveness). i. PG&E uses outages as a proxy for ignitions since there is abundant data available from thousands of different types of failure events, each with the potential to cause an ignition, to support a statistically significant analysis. ii. The primary objective of the WDRM v4 is to predict wildfire risk associated with the distribution system. The WDRM does not calculate mitigation effectiveness. Further, the WDRM v4 is a set of machine learning (ML) models, and it is not appropriate to extract causal information from the predictive models. The models predict future values based on historical event data. a) We began an analysis with outages as a proxy for ignitions to define driver-level effectiveness values and apply these to estimate risk reduction based on the WDRM predicted risk values. iii. The values in Table 8.2.1-3 are simply averages that are used to present a high-level summary of the more detailed data PG&E uses for location-specific risk reduction analysis. a) PG&E is not planning to update its television commercials. PG&E regularly assesses public messaging as additional data becomes available. b. As described in response to Question (1)(a)(i) above, outage data is more abundantly available than ignition data and supports a more statistically significant analysis. Therefore, outage data is a suitable proxy for ignition data to inform effectiveness calculations. The values in table 8.2.1-3 are reference points that can be used broadly. The driver-level effectiveness values are then applied against their respective WDRM risk drivers to calculate a more precise risk reduction estimate. Please see section 8.2.1 of our WMP for a detailed explanation of the approach applied. WMP-Discovery 2026-2028_DR_SPD_007-Q001 Page 8 c. PG&E interprets the question to be about appropriateness of PG&E's use of outage data at estimating mitigation effectiveness vs. ignition data. Generally, PG&E uses outage data and expert engineering mitigation analysis to model effectiveness, due to the lack of ignition data available to accurately calculate effectiveness across specific circuit segments, lack of observed data on relatively new mitigation methods (e.g. covered conductor), and complexity of calculating effectiveness on overlapping mitigation methods, as PG&E has detailed in "RAMP-2024_DR_TURN_006-Q004.pdf", "WMP-Discovery2026-2028_DR_TURN_003-Q008.pdf", and "WMP-Discovery2026-2028_DR_TURN_004-Q007.pdf". Concerning, SPD's analysis of vegetation_branch failures on secondary and service lines, there are several complications with this assessment and the conclusion drawn that undergrounding primary's effectiveness would be reduced: • The bulk of those ignitions, if not all, have occurred on bare secondary conductor or aged grey service lines without breakaway connectors. • A vegetation_branch failure on a service line which is overhead hardened using breakaway connectors, in the “UG Primary” scenario, is almost guaranteed to disconnect in the case of the failure event, prohibiting any ignition. • This same feature is not available on primary distribution voltage covered conductor lines, therefore it is reasonable to assume that the effectiveness of overhead hardening secondary and service lines is more effective than the effectiveness of overhead hardening primary voltage lines. i. Additionally, PG&E applies conservative assumptions when estimating mitigation effectiveness for secondary and service lines. In the “Underground Primary” (UG Primary) scenario, due to limited granularity in geospatial data for these secondary and service assets, mitigation effectiveness for the “secondary conductor” driver is discounted by approximately 50%, even in areas with minimal or no secondary infrastructure. In practice, many secondary lines are co-located with primary lines and are typically undergrounded together, suggesting that actual effectiveness may be closer to the “UG All” scenario, which assumes ~99% effectiveness. d. The correct subset of outages was included. i. The imported outage dataset for 2024 included a large number of planned maintenance outages which were pre-filtered out from earlier years in the analysis. The additional approximately 19,000 planned maintenance outages in 2024 were assessed consistently with other types of company-initiated events as “N/A” effectiveness and do not impact the results of the analysis. e. PG&E’s analysis already considers the potential for ignitions on underground assets. PG&E does not assume that converting overhead assets to underground assets equates to absolute elimination of ignition risk (which would result in effectiveness outputs of 100% for the underground scenario). PG&E accounts for the fact that underground assets are still an energy source and, although significantly less likely, retain the potential to cause ignitions. f. While it is often necessary to reroute underground lines from the exact route of pre-existing overhead lines, approximately 1.25 miles of undergrounding may be WMP-Discovery 2026-2028_DR_SPD_007-Q001 Page 9 installed to replace 1 mile of overhead lines. However, the wildfire risk exposure of underground lines is directly attributable to the exposed equipment such as riser poles or transformers which are not installed completely subsurface, rather than the cable itself. The supplemental rerouted primary conductor is not expected to impact wildfire risk exposure by any quantifiable measure. Since the additional mileage is underground and protected from environmental exposure, risk factors like wind and vegetation are nearly eliminated compared to overhead lines. Additionally, these lines are often relocated to areas of lower wildfire consequence, including roadways with reduced vegetation and improved access for maintenance; therefore, accounting for additional risk exposure is not applicable. g. PG&E’s view has not changed. i. Not applicable, as our view has not changed. h. PG&E is not aware of any ignitions on lines which have been undergrounded as part of Wildfire Mitigation system hardening. i. Not applicable. i. The “Support Structure: Electrical” model was not included in the System Hardening composite because the model is intended to predict tracking related events. The pole tracking ignitions primarily occur during wet or foggy conditions in urban areas and are typically contained to the pole top. The primary mitigation for the contamination that leads to tracking events is insulator washing. Heavy rainfall can also wash away contamination. To focus the System Hardening composite on the drivers of concern in High Fire areas during dry conditions, the “Support Structure: Electrical” model was excluded from the System Hardening composite. The “Transformer: Leaking” model only included one ignition in the historical ignition data. It was concluded that this failure driver does not present a significant ignition risk and lacked historical data to train the p(i¦o) model. To focus the System Hardening composite on the primary drivers of concern in High Fire areas during dry conditions, the “Transformer: Leaking” model was excluded from the System Hardening composite. i. Please see the starting paragraph for (i) above for why the “Support Structure: Electrical” model was excluded from the System Hardening composite. ii. PG&E addresses wildfire risk on the distribution system through a comprehensive mitigation strategy as described in the WMP. The WDRM was designed to provide each mitigation program with a custom composite of wildfire risk based on the addressable risk drivers. For example, vegetation management composite is composed of three WDRM v4 vegetation models. This ensures that the vegetation mitigation programs are focused on locations with vegetation-related risk. iii. It’s important to understand that mitigation effectiveness represents an average across the system within HFTD at reducing ignitions. Risk reduction is a location specific risk benefit estimated by combining the location specific wildfire risk with the HFTD-wide driver-level mitigation effectiveness values. PG&E only considers the risks defined in the system hardening composite WDRM v4 dataset when analyzing system hardening mitigations. As such, it WMP-Discovery 2026-2028_DR_SPD_007-Q001 Page 10 would not be appropriate to discount effectiveness assumptions based on non-wildfire risk drivers. a. N/A b. PG&E is not discounting the mitigation effectiveness calculations for System Hardening. Since covered conductor and undergrounding are considered to be highly effective mitigations at preventing contamination and arcing during wet weather, including those risks drivers in the System Hardening composite would increase the risk reduced and shift the resiliency mitigations to locations where ignitions occur during wet weather. This would be an undesired impact due to the WDRM v4 model’s inability to isolate wet weather ignitions occurring during the wildfire season months (Jun – Nov). iv. The method of analyzing the effectiveness of covered conductor in preventing ignitions versus preventing outages is quite similar in that both methods use expert engineering assessments of the cause of historic outages. However, the delta lies within the expert engineering assessment of each individual outage combination, otherwise referred to as “failure mode” and the degree to which the mitigation would be effective at preventing an outage from that failure mode and how effective it would be at preventing an ignition from that failure mode. The study referenced in Table PG&E-8.2.1-3 considers how effective the mitigation would be in preventing an ignition from the failure event. The study referenced in PG&E’s response to TURN_004_Q10 instead assesses how effective the mitigation would be in preventing an outage from the failure event. It was assessed that certain failure modes are more apt to result in an outage than an ignition as shown in the table below: Basic Cause Supplemental Cause Failed/ Involved Equipment Equipment Condition Qualitative Ignition Effectiveness Assumption Qualitative Outage Effectiveness Assumption Vegetation Tree - branch fell on line Conductor, Overhead Bent or Twisted Very High Medium | Eddie Schmitt | 2025-06-02 | 2025-06-12 | 2025-06-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_007.zip | 0 | No | 5 | Risk Methodology & Assessment | 5.4 | Summary of Risk Models
23 | 253 | SPD | 007 | SPD_007 | 2 | No | SPD_007_Q2 | Does PG&E’s Pr(I¦O) model used as part of its WDRM v4 vary spatially or are the values presented in TABLE ACI-PG&E-25U-01-1 uniformly applied to all assets? | The p(i¦o) model that contributes to WDRM v4 varies spatially throughout the distribution service territory. Table ACI-PG&E-25U-01-1 illustrates an improvement that was made to the p(i¦o) model in support of WDRM v4. Whereas WDRM v3 considered each asset and pixel sub-model independently, the lack of training data complicated model training for those sub-models with very low ignition counts. Thus model-groups were made to increase ignition counts for the training set of sub-models that had similar ignition characteristics. For WDRM v4, each sub-model’s p(i¦o) outcome considers both model group attributes and individual sub-model attributes that vary spatially over the distribution service territory. A detailed description of the p(i¦o) model is provided in Section 3.6 of the “Distribution Event Probability Models v4 Documentation”, which is part of the WDRM v4 documentation suite provided with the 2026 – 2028 WMP submission | Eddie Schmitt | 2025-06-02 | 2025-06-05 | 2025-06-05 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_007.zip | 0 | Yes | 5 | Risk Methodology & Assessment | 5.4 | Summary of Risk Models
23 | 254 | SPD | 007 | SPD_007 | 3 | No | SPD_007_Q3 | For lines where the wildfire risk is mitigated by undergrounding the primary lines, does PG&E have criteria for PSPS or expect to use PSPS on these lines? Explain a. What role does the remaining risk from overhead hardened secondary lines play in the decision to continue to use PSPS on circuit segments where the primary lines have been undergrounded (assuming no upstream lines are subject to PSPS)? Explain. | The purpose of PSPS is to ensure that primary overhead lines are de-energized when there is a significant weather risk from an offshore wind event. As such, PSPS criteria is primarily influenced by the weather rather than the inherent wildfire risk alone. Primary underground lines are not targeted in the PG&E PSPS process. However, underground lines may become de-energized due to criteria being met upstream or downstream of the undergrounded circuit segment. a. Secondary lines, whether hardened or unhardened, do not impact the decision to initiate a PSPS event. Only primary lines influence the scope of the PSPS event | Eddie Schmitt | 2025-06-02 | 2025-06-05 | 2025-06-05 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_007.zip | 0 | Yes | 6 | Wildfire Mitigation Strategy Development | 6.1.3.1 | Identifying and Evaluating Activities
23 | 255 | SPD | 007 | SPD_007 | 4 | No | SPD_007_Q4 | SPD understood that PG&E was planning to change its replacement criteria for poles intrusively inspected to be primarily based off a calculated safety factor rather than the calculated remaining strength. SPD understood that one of the criteria for pole replacement after an intrusive inspection would be if the remaining strength calculated was less than 25 percent. SPD understood this change would come in 2025, but the WMP only states that PG&E is evaluating a transition. Provide an update on the proposed change and currently anticipated criteria for pole replacement or reinforcement based on this change. | PG&E is currently working through the process mapping and data exchanges for transitioning from remaining strength to safety factor. As part of that process, we are evaluating the necessary system updates (Inspect Application and/or SAP) and working with our IT partners on solutions. In addition, we will be piloting the process to ensure timely and efficient pole safety factor assessment, prior to officially transitioning our rejection criteria to safety factor from remaining strength. Additionally, as a further part of this process, we are continuing to evaluate the appropriate thresholds. We have not committed to the 25% remaining strength, as we are still analyzing what should be the appropriate threshold | Eddie Schmitt | 2025-06-02 | 2025-06-05 | 2025-06-05 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_007.zip | 0 | Yes | 8 | Grid Design, Operations, and Maintenance | 8.3.11 | Distribution - Intrusive Pole Inspections Program
23 | 256 | SPD | 007 | SPD_007 | 5 | No | SPD_007_Q5 | In part c of “WMP-Discovery2026-2028_DR_SPD_003-Q009.pdf,” PG&E stated the estimated risk reduction was approximate for WDRM v4 because the circuit segments may not match up. Question 9 of SPD-PGE-WMP2026-003 requested risk reduction information for work from 2023-2026 using WDRM v4; meaning that work on a circuit segment could have been performed in 2023. PG&E’s response to Question 9 would be logical if WDRM v4 was based off a snapshot of 2025 circuit segments because some of the undergrounding work in question was performed on circuit segments in 2023 and 2024. However, SPD understands that the circuit segments in WDRM v4 are based off a Jan 2023 snapshot of the circuit segments. Since these two timeframes are essentially the same, why would the risk values provided by WDRM v4 risk model not be representative of the risk reduced by projects in 2023, 2024, 2025 and 2026? | PG&E’s historic workplans are recorded based on circuit segment names rather than geospatial asset data. In the 2023-2026 period, most of the work constructed was planned using a prior version of the WDRM, and cannot be accurately represented using WDRM v4B. As stated in PG&E’s response to part c of WMP-Discovery2026- 2028_DR_SPD_003-Q009, actual circuit segmentation varies over time and there is no guarantee that a project originally targeted on a circuit segment will still lie within the bounds of that same circuit segment’s namesake in the updated risk model. Said another way, PG&E’s grid topology is not static and can be affected by increased or reduced sectionalization, line removal, line addition, such as new business installations, or other changes. For example, the circuit segment labeled Hoopa 1101CB contained 39.24 miles of primary overhead according to the GIS snapshot utilized in WDRM v3; however, the circuit segment labeled Hoopa 1101CB in WDRM v4 contains only 0.02 primary overhead miles. Conversely, the circuit segment labeled Molino 1103CB contained only 8.78 miles of primary overhead according to the GIS snapshot utilized in WDRM v3; however, the circuit segment labeled Molino 1103CB in WDRM v4 contains 31.05 primary overhead miles. The risk reduction achieved by mitigation of either of the aforementioned circuit segments would vary significantly if assessed based on WDRM v3 versus v4. | Eddie Schmitt | 2025-06-02 | 2025-06-05 | 2025-06-05 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_007.zip | 0 | Yes | 5 | Risk Methodology & Assessment | 5.4 | Summary of Risk Models
23 | 257 | SPD | 007 | SPD_007 | 6 | No | SPD_007_Q6 | In “WMP-Discovery2026-2028_DR_SPD_003-Q014.pdf,” PG&E states that “Quality Assurance and Quality Controls assessments do NOT include verification of the height and distance to the conductor of each strike vegetation point specified for removal, and each vegetation strike point noted as an inventory tree.” SPD understands this to mean that these programs do not review each and every strike vegetation point specified for removal and each and every vegetation strike point noted as an inventory tree that PG&E creates as part of its Vegetation Management program. However, if a Quality Assurance or Quality Control assessment is performed, and a tree specified for removal is reviewed as part of one of these assessments, do these assessments: a. verify the height and distance to the conductor of the strike vegetation point specified for removal? b. confirm it is actually a strike tree? c. Separately, if these assessments review a vegetation strike point noted as an inventory tree, do these programs: i. verify the height and distance to the conductor of the strike vegetation point specified for removal? ii. confirm the tree is actually a strike tree? | a. No, the QA or QC assessment does not verify height and distance to the conductor of the strike vegetation point specified for removal by VM Operations inspector. b. No, the QA or QC assessment does not confirm the tree is actually a strike tree. c. Responses: i. No, QA or QC assessment reviews do not verify the height and distance to the conductor of the strike vegetation point specified for removal by the VM Operations inspector. ii. QA or QC assessment does not review a vegetation strike point specified for removal by the VM Operations inspector and therefore, the assessments do not confirm whether or not the tree is actually a strike tree. For trees that have not been specified for removal by the VM Operations inspector, if QA or QC determines that a tree is defective and likely to fail within the maintenance cycle, QA or QC would then verify whether it is a strike tree and, if so, report a deficiency finding to VM Operations. | Eddie Schmitt | 2025-06-02 | 2025-06-05 | 2025-06-05 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_007.zip | 0 | Yes | 9 | Vegetation Management and Inspections | 9 | Vegetation Management and Inspections
23 | 258 | SPD | 007 | SPD_007 | 7 | No | SPD_007_Q7 | PG&E-8.2.1-2 in the 2026-2028 Base WMP presents one step in the Hybrid Cost Benefit Analysis that states "Input OH/UG alternative scope mileage and unit cost assumptions into Foundry WPC Feedback Loop Tool". a. Provide a description of the Foundry WPC Feedback Loop Tool. b. Provide a description of any functions or formulas used within the Foundry WPC Feedback Loop Tool. c. Provide an example of a circuit segment where the Foundry WPC Feedback Loop Tool was used to determine the ratio of OH and UG that meets the CBR and Net Benefit requirements. For that example circuit segment, list all of the inputs that were submitted to the Foundry WPC Feedback Loop Tool as well as what the final ratio of OH and UG was for that circuit segment. d. Provide any documentation that exists on the Foundry WPC Feedback Loop Tool. | Note, the Foundry WPC Feedback Loop tool has been initiated and is in the final stages of development in Foundry, however it is not yet ready for use. In the meantime, we are using a preliminary version of this tool in Excel. a. The Foundry WPC Feedback Loop Tool will dynamically calculate the Cost Benefit Ratio (CBR) values for each proposed mitigation scenario on a given circuit segment as the scenarios are evaluated through the scoping process. For example, the WBCA will calculate initial CBR values for a given circuit segment for each mitigation type (100% Underground, 100% Overhead Hardening with EPSS and DCD, and Hybrid Scenario). The WPC Feedback Loop tool will then be used to re-calculate the CBR values using WBCA inputs along with more detailed mitigation scenarios for specific mileage and updated capital cost assumptions. b. The description of the data functions and formulas to calculate the CBRs for each mitigation plan scenario on the circuit segment are included in attachment “WMPDiscovery2026-2028_DR_SPD_007-Q007Atch01CONF.xlsb”, which is the excel version of the WPC Feedback Loop tool. c. Attachment “WMP-Discovery2026-2028_DR_SPD_007-Q007Atch01CONF.xlsb” includes an example circuit segment, French Gulch 11022902, that runs through the WPC Feedback Loop. The “Main” worksheet shows the circuit segment being run through the Feedback Loop tool, and the “Administration” workbook provides the circuit segment data and risk parameters. French Gulch 11022902 was first compared with a purely OH and a purely UG solution. The UG solution was not selected because despite having a CBR above 1 and within 50% of OH (1.35 > 0.5 × 2.25) (see cells E137 and F137), its Net Benefit ($28.48M) was lower than OH solution ($43.96M) (See cells E135 and F135). This result led to an analysis of the Hybrid alternative based on the criteria outlined in the System Hardening Project Scoping Decision Tree and Process (Figures 8.2.1-1-3), which was driven by tree fall-in risk, a small amount of ingress/egress risk from two highway crossings, and a shift from the OH alternative for the end-ofline customer where the UG option required significant relocation. When compared to the OH option, the Hybrid alternative had a greater CBR (2.43 > 2.25) (see cells G137 and F137) and Net Benefit ($49.97M > $43.96M) ) (see cells G135 and F135). The existing WDRM v4 overhead mileage for FRENCH GULCH 11022902 is 7.02 miles (cell F50). The selected hybrid alternative includes 5.96 miles of overhead hardening and 1.40 miles of undergrounding installed to meet the CBR and Net Benefit calculations outlined above. The inputs provided by the scoping team are in green font in attachment “WMPDiscovery2026-2028_DR_SPD_007-Q007Atch01CONF.xlsb” and also below for reference: • Circuit Segment • Mitigation Plan Scenario 1 (UG Primary) o Mileage Allocated – total existing overhead miles impacted by the selected mitigation o Initial Capital Spend ($M) – installation costs of selected mitigation • Mitigation Plan Scenario 2 (OH Primary + EPSS) o Mileage Allocated – total existing overhead miles impacted by the selected mitigation o Initial Capital Spend ($M) – installation costs of selected mitigation • Mitigation Plan Scenario 3 (Hybrid) o Mileage Allocated – total existing overhead miles impacted by the selected mitigation o Initial Capital Spend ($M) – installation costs of selected mitigation d. Reference “WMP-Discovery2026-2028_DR_SPD_007-Q007Atch01CONF.xlsb” for example documentation of the excel version of the WPC Feedback Loop tool. | Eddie Schmitt | 2025-06-02 | 2025-06-05 | 2025-06-05 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_007.zip | 1 | Yes | 8 | Grid Design, Operations, and Maintenance | 8.2.1 | Covered Conductor Installation
23 | 259 | OEIS | 013 | OEIS_013 | 1 | No | OEIS_013_Q1 | On page 363 of its WMP, PG&E states that it is “in the process of evaluating which component(s) of the [Focused Tree Inspection (FTI) and Tree Removal Inventory (TRI)] scope will be incorporated into the Distribution Routine Patrol Program. In response to Energy Safety’s data request 001, question 09, subpart c, PG&E stated that it “expects to determine which, if any, component(s) of FTI and TRI will be incorporated into the Distribution Routine and/or Hazard Patrol programs by the end of 2025.” a. Define “component(s)” as used in this context. b. For FTI: i. Provide a list of all components (as defined in a, above) comprising the program. ii. Provide a list of all data fields collected and indicate which data fields are currently collected under Distribution Routine Patrol. c. For TRI: i. Provide a list of all components (as defined in a, above) comprising the program. ii. Provide a list of all data fields collected and indicate which data fields are currently collected under Distribution Routine Patrol. | a. PG&E's evaluation of the programs entails a holistic assessment of the processes involved in each program, which may include but is not limited to analysis of the relevant data fields to be included in the consolidated programs. For purposes of responses to subparts (b) and (c) below, we have provided the only data fields that are collected for each program. b. FTI: i. Please see the data fields provided in response subpart (b)(ii) below as these are the components collected during inspection on each program. ii. Please refer to attachment “WMP-Discovery2026-2028_DR_OEIS_013-Q001Atch01.xlsx” for a list of all data fields collected under FTI and Distribution Routine Patrol. The worksheet labeled “TRA in OneVM” contains the TRAQ questions answered on the FTI program. The worksheet labeled “OneVM” contains the prescription data fields entered by an inspector during Routine Distribution and FTI Inspections. Please note that not all fields are mandatory. c. TRI: i. Please see the data fields provided in response subpart (c)(ii) below as these are the components collected during inspection on each program. ii. Please refer to attachment “WMP-Discovery2026-2028_DR_OEIS_013-Q001Atch01.xlsx” for a list of all data fields collected under TRI and Distribution Routine Patrol. The worksheets labeled “TRI” and “OneVM” contain the prescription data fields entered by an inspector during TRI and Routine Distribution program inspections respectively. Please note that not all fields are mandatory. | Nathan Poon | 2025-06-03 | 2025-06-06 | 2025-06-06 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_013.zip | 1 | No | 9 | Vegetation Management and Inspections | 9.2.1.6 | Updates
24 | 260 | OEIS | 014 | OEIS_014 | 1 | No | OEIS_014_Q1 | Regarding PG&E’s Response to OEIS-P-WMP_2025-PG&E-013, Question 1. In subpart a to PG&E’s response to OEIS-P-WMP_2025-PG&E-013, PG&E stated “PG&E’s evaluation of the programs [FTI and TRI] entails a holistic assessment of the processes involved in each program”. a. Provide a list of the processes involved in FTI. Include a brief description of each process. Indicate which processes are currently performed under Distribution Routine Patrol. b. Provide a list of the processes involved in TRI. Include a brief description of each process. Indicate which processes are currently performed under Distribution Routine Patrol. | a. FTI currently includes the processes listed in the main bullets below. Please see also “WMP-Discovery2026-2028_DR_OEIS_014-Q001Atch01CONF.pdf.” The subbullets indicate which of these FTI processes are currently performed under the Distribution Routine Patrol program. • Qualification – FTI inspections are performed by International ISA Tree Risk Assessment Qualification (TRAQ)-certified resources o TRAQ certification is not required to perform a Distribution Routine Patrol inspection. However, all inspectors must complete the required PG&E Academy trainings, as outlined in the Distribution Routine Patrol procedure, and a subset of those inspectors are TRAQ certified. • Inspection – FTI requires a Level 2 inspection of all strike trees o Distribution Routine Patrol first performs a Level 1 inspection; and, if vegetation meets any of the conditions described in the Hazard Trees/Vegetation Clearance section of the “California Power Line Fire Prevention Guide”, then the VMI must perform a Level 2 inspection of the strike tree. WMP-Discovery 2026-2028_DR_OEIS_014-Q001 Page 2 • Record – FTI creates records for all strike trees in the system of record o Distribution Routine Patrol creates a record for a tree requiring work or adds a prescription to an existing tree in the system of record. • Document – FTI utilizes a Basic Tree Risk Assessment Form (referred to as TRAQ form) for any tree requiring work o Distribution Routine Patrol does not require, but does provide the optionality, to utilize the TRAQ Form for any tree requiring work. The components available in One VM for Distribution Routine Patrol inspections were included in “WMP-Discovery2026-2028_DR_OEIS_013- Q001Atch01.xlsx”. • Quality – QC is performed on 100% of FTI work. o For Distribution Routine Patrol, QC is based on a random sample set. b. The TRI program addresses existing vegetation points, as outlined in “WMPDiscovery2026- 2028_DR_OEIS_014-Q001Atch02CONF.pdf.” For those existing vegetation points: • PG&E performs an inspection and determines if the tree is present and still requires work. • If so, the tree is marked for work. TRI is currently conducted as a standalone program independent from the existing Distribution Routine Patrol. However, there may be overlap in the trees identified in one program vs the other. | Nathan Poon | 2025-06-10 | 2025-06-13 | 2025-06-13 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_014.zip | 2 | No | 9 | Vegetation Management and Inspections | 9.2.1.6 | Updates
18 | 261 | SPD | 004 | SPD_004 | 39(s2) | Yes | SPD_004_Q39(s2) | For Table 6-3 in the 2026-2028 Base WMP, PG&E provided an “Activity-Effectiveness-Wildfire Risk” value for each activity listed. However, for six of these activities PG&E did not provide CostBenefit Ratios.3 a. Provide the Cost-Benefit Ratios for each of these activities as is required by D.22-12-027. b. If these calculations of CBR vary from what was submitted in PG&E’s 2024 RAMP Application, explain how much they vary and why.4 c. Complete Table 6-3 for all activities listed in this WMP. Add the Initiative Activity Tracking ID as a column in the completed Table. Present this completed version of Table 6-3 in an Excel spreadsheet. | c. PG&E included all of the activities that have a quantified risk reduction value in Table 6-3. Other mitigation programs listed within the WMP are either qualitative in nature or measured in terms of visualizing where risk could manifest. For example, an inspection of a structure does not reduce risk. It does however allow us to identify non-conformances. The inspection metric is measured as “eyes-on-risk” and is not a true measure of risk reduction. For these reasons, there are no additional programs to be added to Table 6-3. | Eddie Schmitt | 2025-04-30 | 2025-05-30 | 2025-05-30 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_004.zip | 0 | No | 6 | Wildfire Mitigation Strategy Development | 6 | Wildfire Mitigation Strategy
18 | 262 | SPD | 004 | SPD_004 | 1(s) | Yes | SPD_004_Q1(s) | List the locations in the 2026-2028 Base WMP where PG&E’s risk scaling function has been applied to the calculation of a value or risk, consequence, risk reduction, or CBR. a. If the values are in a figure, list the Figure number. b. If the values are in a table, list the Table Number. c. If the values are in the text of the 2026-2028 Base WMP, provide the sentence and the page number. d. SPD is aware that PG&E used a risk scaling function in its RAMP A.24-05-008. For each of a-c, describe if the risk scaling function used is the same as that described in the RAMP. If it is different, describe how the risk scaling function is different. | Upon review, we determined that Table 8-1, included in our prior response to subpart (b), below, does not utilize a risk scaling function. | Eddie Schmitt | 2025-04-30 | 2025-05-30 | 2025-06-13 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_004.zip | 0 | No | 5 | Risk Methodology & Assessment | 5 | Risk Methodology and Assessment
18 | 263 | SPD | 004 | SPD_004 | 2(s) | Yes | SPD_004_Q2(s) | n an Administrative Law Judge Ruling dated April 22 2025 in the PG&E 2024 RAMP Proceeding (A.24-05-008), PG&E was directed to conduct a parallel risk evaluation using a risk-neutral, linear scaling function in preparation for PG&E’s 2027 GRC Rate Case. For each of the locations listed in 1a.-1c. provide a new calculation without applying PG&E’s risk scaling function. a. If the values are in a figure, recreate the figure without the scaling function applied to the calculation that generated the value(s) in the figure. b. If the values are in a table, recreate the table without the scaling function applied to the calculation that generated the value(s) in the table. c. If the values are in the text of the 2026-2028 Base WMP, provide the sentence with the new value that was generated without the scaling function being applied to the calculation. | Please see below for risk-neutral versions of the figures, tables, and text values identified in PG&E’s response to Question No. 1, below. a. The following figures are regenerated without a risk scaling function on the April 2025 vintage models1 for the 2026 Baseline: • Figure 6-1 Projected Overall Service Territory Risk 1 April 2025 vintage models are the models that were used in the 2027 GRC Application. WMP-Discovery 2026-2028_DR_SPD_004-Q002Supp01 Page 2 b. The following tables are regenerated without a risk scaling function: • Table 6-4 Summary of Risk Reduction for Top Risk Circuits: Please see attachment “WMP-Discovery2026-2028_DR_SPD_004- Q002Supp01Atch01.pdf.” | Eddie Schmitt | 2025-04-30 | 2025-05-30 | 2025-06-13 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_004.zip | 1 | No | 5 | Risk Methodology & Assessment | 5 | Risk Methodology and Assessment
25 | 264 | OEIS | 015 | OEIS_015 | 1 | No | OEIS_015_Q1 | Q01. Regarding Idle Transmission Power Lines With reference to PG&E’s response to Question 18 in Data Request OEIS-P-WMP_2025-PG&E-001: a. PG&E states that it “has three idle transmission lines totaling 2.25 miles in HFTD and HFRA” and that it “is evaluating induction mitigation options to reduce the risk of the line becoming energized through induction.” i. Provide PG&E’s latest findings or studies on whether idle transmission lines present a potential induction risk that could result in unintended energization. ii. Describe any procedures, policies, or future planned projects to mitigate the ignition risk of idle transmission lines that PG&E is considering. b. PG&E states that “only one of the three lines has sections that could become energized through induction.” i. Specifically for this transmission line, provide PG&E’s findings. | a. i. Studies on de-energized idle transmission lines are pending and not yet complete. ii. PG&E can apply segmenting, grounding or conductor removal to mitigate ignition risk. Our studies will inform the scope for how these three mitigations can be applied on de-energized idle transmission lines. b. i. We determined that the section of this line in HFRA can be mitigated through segmenting. This will mitigate induction driven risk in HFRA. The rest of the line is still under study. | Nathan Poon | 2025-06-20 | 2025-06-25 | 2025-06-25 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_015.zip | 0 | No | 8 | Grid Design, Operations, and Maintenance | 8.2.9.1 | Line Removal (In the HFTD) - Transmission
18 | 265 | SPD | 004 | SPD_004 | 4(s3) | Yes | SPD_004_Q4(s3) | Fill in the data requested in the attached workbook titled “Decision Tree Results by Circuit Segment.xlsx”. This workbook is modeled upon the PGE_2023_WMP_R0_Section_642_Atch01.xlsx workbook that was submitted with the PG&E 2023-2025 Base WMP and the PG&E response to a CalAdvocates Data Request that included the workbook titled WMP-Discovery2023- 2025_DR_CalAdvocates_041-Q005Atch01.xlsx. a. Follow the Field Descriptions in the “Instruction” spreadsheet to complete the corresponding cells in the “Primary”, “S&S” and “DistTotal” spreadsheets. b. Responses in the “Primary” spreadsheet must be limited to the primary lines found on the corresponding “Circuit Segment Name” listed in Column A. c. Responses in the “S&S” spreadsheet must be limited to the secondary and service lines found on the corresponding “Circuit Segment Name” listed in Column A. d. Responses in the “DistTotal” spreadsheet must include both the primary, secondary and service lines found on the corresponding “Circuit Segment Name” listed in Column A. e. If any of the data requested in this dataset workbook would be impacted by the Administrative Law Judge Ruling described in Questions 1 and 3, provide a second version of this dataset using a risk-neutral, linear scaling function and using the disaggregated approach to reliability cost calculation recommended in the SPD Evaluation Report. | PG&E is providing the following data in attachment “WMP-Discovery2026-2028_DR_SPD_004-Q005Supp03Atch01.xlsx,” in the worksheet labeled “Primary:” • WDRM v4 fields • Tranches • Decision Trees WMP-Discovery 2026-2028_DR_SPD_004-Q005Supp03 Page 2 • Miles of Expulsion Fuse Replacement • Miles of Surge Arrestor Replacement • Miles of Aerial inspection • Miles of Ground Inspection • Miles of Non-Pole Backlog • Miles of DCD • Miles of Line Sensors • Miles of Pole Backlog • Total Expenditure of Expulsion Fuse Replacement Completed in Year • Total Expenditure of Surge Arrestor Replacement Completed in Year • Total Expenditure of Aerial Inspections Completed in Year • Total Expenditure of Ground Inspection Completed in Year • Total Expenditure of Down Conductor Detection (DCD) Completed in Year • Total Expenditure of Line Sensors Completed in Year • Present Value Cost of OH Completed in Year • Present Value Cost of UG Completed in Year • Present Value Cost of Line Removal Completed in Year • Present Value Cost of System Hardening Completed in Year • Present Value Cost of Expulsion Fuse Replacement Completed in Year • Present Value Cost of Surge Arrestor Replacement Completed in Year • Present Value Cost of Aerial Inspections Completed in Year • Present Value Cost of Ground Inspections Completed in Year • Present Value Cost of Tree Removal Completed in Year • Present Value Cost of DCD Completed in Year • Present Value Cost of Line Sensors Completed in Year • Present Value Cost of Pole Clearing Completed in Year • Risk Reduction Achieved by Expulsion Fuse Replacement Completed in Year • Risk Reduction Achieved by Surge Arrestor Replacement Completed in Year • Risk Reduction Achieved by Aerial Inspections Completed in Year • Risk Reduction Achieved by Ground Inspections Completed in Year • Risk Reduction Achieved by Non-Pole Backlog Completed in Year • Risk Reduction Achieved by Tree Removal Completed in Year • Risk Reduction Achieved by DCD Completed in Year • Risk Reduction Achieved by Line Sensors Completed in Year • Risk Reduction Achieved by Pole Clearing Completed in Year • Risk Reduction Achieved by Pole Backlog Completed in Year • Mitigation Benefit of Expulsion Fuse Replacement Completed in Year • Mitigation Benefit of Surge Arrestor Replacement Completed in Year • Mitigation Benefit of Aerial Inspections Completed in Year • Mitigation Benefit of Ground Inspections Completed in Year • Mitigation Benefit of Non-Pole Backlog Completed in Year • Mitigation Benefit of Tree Removal Completed in Year • Mitigation Benefit of DCD Completed in Year WMP-Discovery 2026-2028_DR_SPD_004-Q005Supp03 Page 3 • Mitigation Benefit of Line Sensors Completed in Year • Mitigation Benefit of Pole Clearing Completed in Year • Mitigation Benefit of Pole Backlog Completed in Year. Please note the following regarding the data provided: • With regard to the “WDRM v4” fields, please note that PG&E has provided those subfields with the exception of those previously identified as not possible to produce. • With regards to the “Tranche” fields: o 2023 GRC Tranche: Since the list of circuit segments provided in this template are exclusively WDRM v4 circuit segments, PG&E interprets the request here to be for quintile-based tranches based on WDRM v4. o In PG&E’s System Hardening Accountability Report tranches are reported at the sub-project level. • With regard to the “Decision Trees” field, due to the time between the start of a project in scoping and its actual execution, it is common for multiple decision trees and multiple risk models to be in play in any given execution year. Furthermore, the 2023-2026 GRC decision in late 2023 forced not only new segments but also re-scope many projects to decrease the number of planned UG miles, increase the number of OH miles and hit a new risk target that previously was not planned for. This means some CPZ’s may have multiple decision trees applied. To expedite the response, PG&E is providing the following data: 1. For the V2 CPZ’s planned in 2026 that were also scoped utilizing the referenced 2023-2025 Base WMP Decision Tree in Figures SRN-PG&E-23-05-06A, SRN-PG&E-23-05-06B, SRN-PG&E-23-05-06C from PG&E’s 2023-2025 Base WMP, PG&E provided a “yes” response. A “yes” response was provided if any part of that CPZ was rescoped following the 2023-2026 GRC Decision to eliminate UG and produce more OH on high-risk segments. a. These sub-projects were selected based on PSPS or a V2 risk rank and scoped in 2021 and 2022. The V2 geometries had to be compared to the V4 geometries to accurately assign the yes value to the corresponding V4 CPZ. 2. For the 2027 projects scoped with or forecasted to be scoped with the 2026-2028 Base WMP Decision tree in Figures PG&E-8.2.1-1, PG&E-8.2.1-2, and PG&E-8.2.1-3 from PG&E’s 2026-2028 Base WMP, PG&E provided a “yes” response. For the 2028 projects forecasted to be scoped with the Updated 2026-2028 Base WMP Decision Tree (not fina | Eddie Schmitt | 2025-04-30 | 2025-06-27 | 2025-06-27 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_004.zip | 1 | No | 5 | Risk Methodology & Assessment | 5.5.2 | Top Risk-Contributing Circuits/Segments/Spans
19 | 266 | SPD | 004 | SPD_004 | 5(s3) | Yes | SPD_004_Q5(s3) | In Section 4.1.2.1 PG&E’s model asserts that 𝑆𝑡𝑟𝑢𝑐𝑡𝑢𝑟𝑒 𝐿𝑜𝑠𝑠 𝐹𝑟𝑎𝑐𝑡𝑖𝑜𝑛 ≅𝑓(𝐹𝑢𝑒𝑙𝑠,𝑇𝑒𝑟𝑟𝑎𝑖𝑛,𝑊𝑒𝑎𝑡ℎ𝑒𝑟) The literature on structure loss in wildfire is extensive and lists a number of variables that have been shown to correlate with structure loss. These include housing materials, age of neighborhood, density of neighborhood and separation of houses, proximity of vegetation to the structure, enclosed eves and vents, and others. a. How does PG&E’s structure loss model incorporate other variables that are implicit to the structures, maintained landscapes, and neighborhoods? b. Please provide the numerical values that went into Figures 9 and 10. c. Figure 10 implies that for TDI=1 that the probability of structure is very small (counts for loss < 0.3 >> loss > 0.3), and that for TDI=5 probability of structure loss is very large (counts for loss > 0.7 >> loss < 0.7). Does this imply that PG&E’s model assumes that home survival fraction is primarily dependent on the availability of firefighting resources? If so, what justification (analysis or citations) does it provide for this assertion? | PG&E is providing the following data in attachment “WMP-Discovery2026-2028_DR_SPD_004-Q005Supp03Atch01.xlsx,” in the worksheet labeled “Primary:” • WDRM v4 fields • Tranches • Decision Trees • Miles of Expulsion Fuse Replacement • Miles of Surge Arrestor Replacement • Miles of Aerial inspection • Miles of Ground Inspection • Miles of Non-Pole Backlog • Miles of DCD • Miles of Line Sensors • Miles of Pole Backlog • Total Expenditure of Expulsion Fuse Replacement Completed in Year • Total Expenditure of Surge Arrestor Replacement Completed in Year • Total Expenditure of Aerial Inspections Completed in Year • Total Expenditure of Ground Inspection Completed in Year • Total Expenditure of Down Conductor Detection (DCD) Completed in Year • Total Expenditure of Line Sensors Completed in Year • Present Value Cost of OH Completed in Year • Present Value Cost of UG Completed in Year • Present Value Cost of Line Removal Completed in Year • Present Value Cost of System Hardening Completed in Year • Present Value Cost of Expulsion Fuse Replacement Completed in Year • Present Value Cost of Surge Arrestor Replacement Completed in Year • Present Value Cost of Aerial Inspections Completed in Year • Present Value Cost of Ground Inspections Completed in Year • Present Value Cost of Tree Removal Completed in Year • Present Value Cost of DCD Completed in Year • Present Value Cost of Line Sensors Completed in Year • Present Value Cost of Pole Clearing Completed in Year • Risk Reduction Achieved by Expulsion Fuse Replacement Completed in Year • Risk Reduction Achieved by Surge Arrestor Replacement Completed in Year • Risk Reduction Achieved by Aerial Inspections Completed in Year • Risk Reduction Achieved by Ground Inspections Completed in Year • Risk Reduction Achieved by Non-Pole Backlog Completed in Year • Risk Reduction Achieved by Tree Removal Completed in Year • Risk Reduction Achieved by DCD Completed in Year • Risk Reduction Achieved by Line Sensors Completed in Year • Risk Reduction Achieved by Pole Clearing Completed in Year • Risk Reduction Achieved by Pole Backlog Completed in Year • Mitigation Benefit of Expulsion Fuse Replacement Completed in Year • Mitigation Benefit of Surge Arrestor Replacement Completed in Year • Mitigation Benefit of Aerial Inspections Completed in Year • Mitigation Benefit of Ground Inspections Completed in Year • Mitigation Benefit of Non-Pole Backlog Completed in Year • Mitigation Benefit of Tree Removal Completed in Year • Mitigation Benefit of DCD Completed in Year • Mitigation Benefit of Line Sensors Completed in Year • Mitigation Benefit of Pole Clearing Completed in Year • Mitigation Benefit of Pole Backlog Completed in Year. Please note the following regarding the data provided: • With regard to the “WDRM v4” fields, please note that PG&E has provided those subfields with the exception of those previously identified as not possible to produce. • With regards to the “Tranche” fields: o 2023 GRC Tranche: Since the list of circuit segments provided in this template are exclusively WDRM v4 circuit segments, PG&E interprets the request here to be for quintile-based tranches based on WDRM v4. o In PG&E’s System Hardening Accountability Report tranches are reported at the sub-project level. • With regard to the “Decision Trees” field, due to the time between the start of a project in scoping and its actual execution, it is common for multiple decision trees and multiple risk models to be in play in any given execution year. Furthermore, the 2023-2026 GRC decision in late 2023 forced not only new segments but also re-scope many projects to decrease the number of planned UG miles, increase the number of OH miles and hit a new risk target that previously was not planned for. This means some CPZ’s may have multiple decision trees applied. To expedite the response, PG&E is providing the following data: 1. For the V2 CPZ’s planned in 2026 that were also scoped utilizing the referenced 2023-2025 Base WMP Decision Tree in Figures SRN-PG&E-23-05-06A, SRN-PG&E-23-05-06B, SRN-PG&E-23-05-06C from PG&E’s 2023-2025 Base WMP, PG&E provided a “yes” response. A “yes” response was provided if any part of that CPZ was rescoped following the 2023-2026 GRC Decision to eliminate UG and produce more OH on high-risk segments. a. These sub-projects were selected based on PSPS or a V2 risk rank and scoped in 2021 and 2022. The V2 geometries had to be compared to the V4 geometries to accurately assign the yes value to the corresponding V4 CPZ. 2. For the 2027 projects scoped with or forecasted to be scoped with the 2026-2028 Base WMP Decision tree in Figures PG&E-8.2.1-1, PG&E-8.2.1-2, and PG&E-8.2.1-3 from PG&E’s 2026-2028 Base WMP, PG&E provided a “yes” response. For the 2028 projects forecasted to be scoped with the Updated 2026-2028 Base WMP Decision Tree (not finalized for use at this time) referenced in PG&E’s 2026-2028 Base WMP. • With regard to the “Miles of” fields provided with this response, please note that, consistent with PG&E’s prior responses, PG&E is providing units, rather than miles. Further, please note that there are units associated with circuit segments that are not present in the requested list of circuit segments, therefore that data is not included in this response. • With regard to the “Miles of Expulsion Fuse Replacements” field, please note that PG&E is currently expanding its 2025 workplan to include 1400 units pursuant to discussions with the Office of Energy Safety. PG&E has not yet identified the locations of the additional units, and includes here the originally planned 848 units to the extent they are located on circuit segments existing in the WDRM v4 circuit segment list. • With regard to the “Miles of Surge Arrestor Replacements” field, please note that PG&E met its target for GH-08 in 2023. Units reported in 2024 represent remaining remediation work not included in the 2023-2025 Base WMP workplan. • With regard to the “Miles of Aerial Inspections” field, please note that no aerial inspections were performed under AI-07 in 2023. • With regard to the “Miles of Line Sensors” field, please note that, for the purpose of specifying the specific segment on which a sensor was installed, PG&E is including each location at which sensor units are installed. PG&E’s standard unitization for sensors (e.g. as reported in the Annual Report on Compliance) is circuits. Please note that a sensor monitors the entire circuit downstream of its installation location, not just the segment on which it is installed. • Please note that all financial data is represented in thousands ($000). • Please note that PG&E has identified values in the 'Total Expenditure' fields for OH, UG, Line Removal, and System Hardening that require additional validation and possible corrections. PG&E will provide the corrected values on July 2, 2025. • With regard to the “Total Expenditure of Expulsion Fuse Replacement Completed in Year” and “Total Expenditure of Down Conductor Detection (DCD) Completed in Year” fields, PG&E has utilized the unit cost value provided in “WMP-Discovery2026-2028_DR_SPD_001-Q021Rev01Atch01.xlsx” to provide an estimated total expenditure per circuit segment. • With regard to the “Total Expenditure of Surge Arrestor Replacement Completed in year” field, PG&E has utilized the unit cost value provided in “WMP-Discovery2026-2028_DR_SPD_001-Q021Rev01Atch01.xlsx” to provide an estimated total expenditure per circuit segment for 2023. For 2024, PG&E utilized a unit cost value of $10,110.19. • With regard to the “Total Expenditure of Aerial Inspections Completed in Year” and “Total Expenditure of Ground Inspections Completed in Year” fields, PG&E utilized the following unit cost values to provide estimated total expenditure per circuit segment values: o 2023: ▪ Ground: $129 o 2024: ▪ Ground: $77.39 ▪ Aerial: $131.69 o 2024: ▪ Ground: $82 ▪ Aerial: $139.04. • With regard to the “Total Expenditure of Non-Pole Backlog Tags Completed in Year” and “Total Expenditure Pole Backlog Tags Completed in Year” fields, please note that PG&E's financial systems are not designed to capture costs associated specifically with backlog tags. In order to respond to this request, PG&E has estimated per-tag costs by summing the costs of the completed tags’ associated orders and dividing by the number of completed tags. There may be instances in which multiple tags are associated with a single order. Further, the estimated per-tag cost associated with Non-Pole Backlog Tags may not be representative of work done at a specific location due to the wide variety of conditions addressed by “non-pole backlog tags.” The values provided here and the estimated per-tag costs used to generate them have been developed solely for the purposes of responding to this data request. • With regard to the ‘Total Expenditure of Line Sensors Completed in Year” field, PG&E derived unit cost values utilizing sensor installation locations, rather than circuits, as units to provide an estimated total expenditure per circuit segment. • With regard to the “Present Value Cost” fields, please note that PG&E generated these values solely for the purpose of responding to this request. • With regard to the “Risk Reduction Achieved” and “Mitigation Benefit” fields, please note that risk reduction for certain mitigations (e.g. Sensors, DCD) is not confined to the segment on which it was installed. For the purpose of this request, PG&E has provided risk reduction values specific to the segment on which mitigation units are completed. • With regard to the “Risk Reduction Achieved” and “Mitigation Benefit” fields, please note that PG&E’s aerial and ground inspections and sensor programs provide “eyes on risk” rather than risk reduction. • Please note that, for mitigations other than “OH,” “UG,” “Line Removal,” and “System Hardening,” PG&E is unable to generate CBR values because, as previously explained, it is unable to identify actual cost per mitigation per circuit segment. We plan to provide two additional tranches to supplement this response until it is complete, as agreed upon by SPD and PG&E on June 26, 2025. The additional tranches will include: • Risk Reduction values for OH, UG, Line Removal, and System Hardening; • Mitigation Benefit values for OH, UG, Line Removal, and System Hardening; • CBRs for OH, UG, Line Removal, and System Hardening; • Cost Recovery Fields; • Unscaled values responsive to subpart (e). | Joseph Mitchell | 2025-05-05 | 2025-06-27 | 2025-06-27 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_004.zip | 1 | No | 5 | Risk Methodology & Assessment | 5.4 | Summary of Risk Models
19 | 267 | SPD | 004 | SPD_004 | 5(s4) | Yes | SPD_004_Q5(s4) | In Section 4.1.2.1 PG&E’s model asserts that 𝑆𝑡𝑟𝑢𝑐𝑡𝑢𝑟𝑒 𝐿𝑜𝑠𝑠 𝐹𝑟𝑎𝑐𝑡𝑖𝑜𝑛 ≅𝑓(𝐹𝑢𝑒𝑙𝑠,𝑇𝑒𝑟𝑟𝑎𝑖𝑛,𝑊𝑒𝑎𝑡ℎ𝑒𝑟) The literature on structure loss in wildfire is extensive and lists a number of variables that have been shown to correlate with structure loss. These include housing materials, age of neighborhood, density of neighborhood and separation of houses, proximity of vegetation to the structure, enclosed eves and vents, and others. a. How does PG&E’s structure loss model incorporate other variables that are implicit to the structures, maintained landscapes, and neighborhoods? b. Please provide the numerical values that went into Figures 9 and 10. c. Figure 10 implies that for TDI=1 that the probability of structure is very small (counts for loss < 0.3 >> loss > 0.3), and that for TDI=5 probability of structure loss is very large (counts for loss > 0.7 >> loss < 0.7). Does this imply that PG&E’s model assumes that home survival fraction is primarily dependent on the availability of firefighting resources? If so, what justification (analysis or citations) does it provide for this assertion? | PG&E is providing the following data in attachment “WMP-Discovery2026- 2028_DR_SPD_004-Q005Supp04Atch01.xlsx,” in the worksheet labeled “Primary:” • Risk Reduction Achieved by OH in Year; • Risk Reduction Achieved by UG in Year; • Risk Reduction Achieved by Line Removal in Year; WMP-Discovery 2026-2028_DR_SPD_004-Q005Supp04 Page 2 • Risk Reduction Achieved by System Hardening in Year. Additionally, please note that PG&E has determined that 2025 values in the “Total Expenditure” fields for OH, UG, Line Removal, and System Hardening were inadvertently not represented in thousands. PG&E provides amended values with this response. All financial data is represented in thousands ($000s). | Joseph Mitchell | 2025-05-05 | 2025-07-02 | 2025-07-02 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_004.zip | 1 | No | 5 | Risk Methodology & Assessment | 5.4 | Summary of Risk Models
19 | 268 | SPD | 004 | SPD_004 | 5(s5) | Yes | SPD_004_Q5(s5) | In Section 4.1.2.1 PG&E’s model asserts that 𝑆𝑡𝑟𝑢𝑐𝑡𝑢𝑟𝑒 𝐿𝑜𝑠𝑠 𝐹𝑟𝑎𝑐𝑡𝑖𝑜𝑛 ≅𝑓(𝐹𝑢𝑒𝑙𝑠,𝑇𝑒𝑟𝑟𝑎𝑖𝑛,𝑊𝑒𝑎𝑡ℎ𝑒𝑟) The literature on structure loss in wildfire is extensive and lists a number of variables that have been shown to correlate with structure loss. These include housing materials, age of neighborhood, density of neighborhood and separation of houses, proximity of vegetation to the structure, enclosed eves and vents, and others. a. How does PG&E’s structure loss model incorporate other variables that are implicit to the structures, maintained landscapes, and neighborhoods? b. Please provide the numerical values that went into Figures 9 and 10. c. Figure 10 implies that for TDI=1 that the probability of structure is very small (counts for loss < 0.3 >> loss > 0.3), and that for TDI=5 probability of structure loss is very large (counts for loss > 0.7 >> loss < 0.7). Does this imply that PG&E’s model assumes that home survival fraction is primarily dependent on the availability of firefighting resources? If so, what justification (analysis or citations) does it provide for this assertion? | The following response pertains to the information provided in “WMP-Discovery2026- 2028_DR_SPD_004-Q005Supp05Atch01.xlsx.” For the CBRs provided in the “Primary” tab, Columns SZ – TW, please note: 1. PG&E is using a single escalation factor (consisting of nominal discount and inflation rates) for all costs in the CBR calculation for all projects from 2023 through 2028. Escalating costs to a different base year to align with each of the different project years would require us to build a new tool for each year. Building a new tool for each year would be burdensome given that we expect there would be only a minor difference in the CBR using the single escalation factor compared to using a year specific escalation factor since the CBR is mostly influenced by risk and cost. 2. Most undergrounding system hardening projects take approximately three to four years to complete and include pre-construction, construction and project closeout activities. Pre-construction work includes scoping and surveying, design, permitting, materials acquisition and vegetation work. Construction includes both civil and electrical activities such as digging trenches, installing conduit, and pulling cable through the conduit. Project close-out includes paving, restoration, mapping and finalizing project documentation. The costs incurred for undergrounding work do not necessarily correlate with the miles installed. For example, no miles are installed during pre-construction even though costs are incurred for designing, permitting and material acquisition. Therefore, the annual CBRs we are asked to provide in this data request are not necessarily reflective of the work that is occurring. For example, during pre-construction PG&E will incur costs to purchase materials but will not reduce risk because we won’t be relocating primary lines underground and the CBR will reflect costs incurred with no benefits achieved even though we are performing work that is necessary for the undergrounding project. 3. PG&E is using the risk values from WDRM v4 as the basis for the CBRs provided in this data response even though certain projects were selected and planned based on earlier versions of the Wildfire Distribution Risk Model. There are often changes to circuit segments from one version of the WDRM to the next. For example, a circuit segment from WDRM v3 may be split into two circuit segments in WDRM v4 or two circuit segments in WDRM v3 may be merged into a single circuit segment in WDRM v4. Because of the changes to circuit segments from one version of the risk model to another, the miles of hardening work reported complete for each circuit segment in this list may not be reflective of the location where the work was selected or planned. 4. Since the template provided by SPD is a list of only WDRM v4 circuit segments, PG&E is using risk values from WDRM v4 as the basis for the CBRs provided in this data response regardless of which risk model we used to select a project. The CBRs we are providing for projects selected using previous versions of the risk model are likely lower than they would be if we used the risk value from the WDRM model used to select the project. 5. The lifecycle cost information used in the CBR calculations is primarily driven by the imputed adopted values from PG&E’s 2023 GRC. Because the CBR is based solely on wildfire risk, PG&E has excluded the operations and maintenance costs for reliability programs (EPSS and PSPS) from the CBR calculation. 6. Climate escalation is not considered in the supplied CBR calculations. Including climate escalation would lead to higher CBRs for most projects. For the Cost Recovery data provided in the “Primary” tab, Columns WR-WY, please see a few notes about the data provided in these columns: • Column WR “2023 GRC o Represents undergrounding, overhead hardening, and line removal work completed or forecasted to be completed between 2023 and 2026, which is funded by the 2025 GRC Decision. • Column WS “2027 GRC” o Represents overhead hardening and line removal work forecasted to be completed between 2027 and 2028, and undergrounding work forecasted to be completed in 2027. o This work is proposed to be funded in the 2027 GRC and these forecasts are subject to change pending final 2027 GRC approval. • Column WT “Future EUP Application” o Represents forecast undergrounding work to be completed in 2028 as proposed in the 2027 GRC o The forecasts and proposed circuits are subject to change pending the approval of the scope of EUP filing and approval timeline. • Column WV “Which Current BA MA”’ o “D.23-11-069” is the 2023 GRC Decision, which applies to: ▪ CPZs with OH/UG/Removal miles that are completed/forecast from 2023-2026: • The 2023 GRC decision allows PG&E to recover system hardening expenditures through the Wildfire Mitigation Balance Account (WMBA). • PG&E’s WMBA was established following the 2020 GRC decision (D.20-12-005), but was modified with the 2023 GRC decision for costs in the 2023-2026 period. ▪ CPZs with UG/OH/Removal miles completed through the Community Rebuild program. • As directed by the 2023 GRC Decision, the BA/MA for the Butte Rebuild projects starting in 2023 is in the Catastrophic Event Memorandum Account (CEMA), under PG&E's Wildfire Mitigation and Catastrophic Events (WMCE) Application. The proceeding remains open and the cost recovery venue of this Butte Rebuild program is subject to change. Costs beyond those covered by the WMCE application may be proposed in a future cost application. • Miles associated with the Dixie fire rebuild in the HFTD will be recorded in the WMBA as directed by the 2023 GRC decision. • Miles associated with the Dixie fire rebuild outside of the HFTD (Greenville) may be proposed in a future cost recovery application. • Column WX “Which Future BA MA” o “TBD” represents circuit segments that will have worked funded through 2027 GRC Decision, EUP approval, and/or another cost recovery application, such as WMCE. PG&E will not have a decision number until those filings are approved. | Joseph Mitchell | 2025-05-05 | 2025-07-15 | 2025-07-15 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_004.zip | 1 | No | 5 | Risk Methodology & Assessment | 5.4 | Summary of Risk Models
#N/A | 269 | SPD | 008 | SPD_008 | 1 | No | SPD_008_Q1 | On June 20, 2025, PG&E served a Compliance Filing in response to an April 22, 2025 ALJ ruling in A.24-05-008 requiring PG&E to disaggregate its approach generating a monetized value of electric reliability using the Interruption Cost Estimator (ICE) calculator. In its Compliance Filing, PG&E stated that “PG&E has addressed the ALJ ruling requirement using the ICE 2.0 calculator rather than the ICE 1.0 calculator.” PG&E also presented eight workpapers in Appendices A and B. Appendix A included the Excel file named “Appendix A1_PG&E 2027 GRC Risk Values with Electric Reliability Scenarios.xlsx” with a spreadsheet called “PG&E 2027GRC Risk Values”. Explain what are the values associated with Column’s F and N (i.e. the “ICE 1.0 disaggregated” values) in spreadsheet “PG&E 2027GRC Risk Values” and what approach was used to generate those values. a. Is the approach used to generate the values described as “ICE 1.0 disaggregated” the same as the approach used to generate the values in the RM-RMCBR-14 PG&E 2024 RAMP Risk Values_ICECalcAdj_by_Event (add DUNGD).xlsx workbook that PG&E submitted with its supplemental response to the RAMP-2024_DR_SPD_002 data request on July 31, 2024? i. If not, explain what approach was used to generate the “ICE 1.0 disaggregated” values in PG&E 2027GRC Risk Values. ii. If not, explain why PG&E did not use the approach recommended by the SPD evaluation report as requested in the ALJ Ruling from April 22, 2025. b. List each of the monetized value(s) of electric reliability that PG&E generated using the ICE Calculator that then led to results in Columns E, F, G and H in the “PG&E 2027GRC Risk Values” spreadsheet. This should be presented in $/CMI. i. Explain how PG&E generated each of these values with reference to the offline ICE models used by PG&E. | PG&E objects to this request because it is not related to the WMP proceeding and exceeds the scope of that proceeding. This request would be more appropriately served as non-case discovery or in a different regulatory proceeding. Notwithstanding and without waiving this objection, PG&E responds as follows. “Electric Reliability (ICE 1.0 disaggregated)” values in Column F of sheet “PG&E 2027GRC Risk Values” in file Appendix A1 are the electric reliability risk values calculated using disaggregated approach based on ICE 1.0 results. Specifically, the disaggregated approach used tranche-level values of electric reliability attribute ($/CMI), which were derived from ICE 1.0 $/CMI values for residential and non-residential customers obtained using inputs consistent with $3.33/CMI used in monetizing electric reliability risk in PG&E’s 2027 GRC filing. Please see below table for the ICE 1.0 VoS values. Sector ICE 1.0 $/CMI Residential 0.05 Non-Residential 29.17 All 3.33* Notes: $3.33/CMI is used in monetizing electric reliability risk in PG&E’s 2027 GRC filing “Total Risk Value (ICE 1.0 disaggregated)” values in Column N are the sum of “Total Safety”, “Electric Reliability (ICE 1.0 disaggregated)”, “Gas Reliability” and “Financial” values in Columns D, F, I and J. The approach used to generate the values described as “ICE 1.0 disaggregated” was updated and enhanced in granularity to account for updating to ICE 2.0 and improving on the analysis originally used to generate the values supplied in the supplemental response to RAMP-2024_DR_SPD_002 data request on July 31, 2024.Further, to ensure consistency across the update, the approach used to generate the values described as “ICE 1.0 disaggregated” is the same as that used to generate the values described as “ICE 2.0 disaggregated” in Columns H&R in the same spreadsheet. The only additional step taken to get the values described as“ICE 1.0 disaggregate” is that PG&E needed to first combine the $/CMI for Medium and Large Commercial and Industrial (ML C&I) customers with $/CMI for Small Commercial and Industrial customers based on customer counts to get the $/CMI for Non-Residential customers because ICE 1.0 calculator segregates Medium and Large C&I, Small C&I and Non-Residential customers in outputs.The $/CMI values used to get “ICE 1.0 disaggregate” values are updated from those used in the supplemental response to RAMP-2024_DR_SPD_002 data request on July 31, 2024 due to annual update of customer counts, change of reliability input SAIDI, and adjusting for inflation from 2023 to 2024 to express values in 2024 dollars. The table below shows the comparison of $/CMI values. RAMP2024 DRSPD 002- 2027 GRC - ICE 1.0 ICE 1.0 Sector (2023$) (2024$) Medium and Large C&I $77.89 $80.49 Small C&I $9.99 $11.29 RAMP2024 DRSPD 002- 2027 GRC - ICE 1.0 ICE 1.0 Sector (2023$) (2024$) Residential $0.06 $0.05 All Customers $3.17 $3.33 The $/CMI value for Medium and Large C&I customers and the $/CMI value for Small C&I customers in Column “2027 GRC - ICE 1.0 (2024$)” in the above table are then multiplied respectively with the percentage of Medium and Large C&I customers in Non-Residential sector and the percentage of Small C&I customers in Non-Residential sector to get the weighted average Non-Residential $/CMI value of 29.17 as shown in the table below. Sector 2927 GRC - ICE 1.0 (2024$) Non-Residential (ML C&I and Small C&L Weighted Average) $29.17 Residential $0.05 After obtaining the $/CMI values for Residential and Non-Residential customers in the above table, PG&E followed the same approach which generates the values descried as “ICE 2.0 disaggregated” in Columns H&R. PG&E applied the disaggregation approach at the tranche level of each risk model. For this, PG&E gathered Service Point (i.e., customer) level data to determine the percentage of Residential customers at the tranche level of PG&E’s electric risk models, and then took this percentage of Residential customers (%Residential) at the tranche level and multiply [%Residential] to ($/Residential CMI) and [1-%Residential] to ($/Non- Residential CMI) to get the weighted average $/CMI value at the tranche level. This value is then used to monetize the modeled CMI value for the electric reliability attribute. With that, the Enterprise Risk Model runs were performed to calculate risk values in column F. As described above and in the following subpart b., PG&E believes it has fully complied with the ALJ Ruling from Aprill 22, 2025 by using the disaggregation method recommended by SPD in its Evaluation Report and developed by PG&E starting with “RAMP-2024_DR_SPD_002.pdf” and updating it and improving the granularity. See above response. Below table lists the monetized value(s) of electric reliability in $/CMI that PG&E generated using the ICE Calculator that then led to results in Columns E, F, G and H in the “PG&E 2027GRC Risk Values” spreadsheet. Light grey shaded blank cells indicate not applicable. Customer Class ICE1.0 Aggregated (Column E) ICE1.0 Disaggregated (Column F) ICE2.0 Aggregated (Column G) ICE2.0 Disaggregated (Column H) Residential 0.05 0.08 Non-Residential 29.17 23.11 All 3.33 2.72 i. For ICE1.0 Aggregated (Column E), we entered our residential and small, medium/large customer counts as well as all the annually updated PG&E specific input values into ICE calculator to get an overall $/CMI. ICE1.0 Disaggregated (Column F) $/CMI value of small and medium/large customers are combined to get a weighted average value for non-residential customers based on customer counts. For ICE2.0 Aggregated (Column G), we entered our residential and non- residential customer counts as well as all the annually updated PG&E specific input values into ICE calculator. We get an overall $/CMI in 2023 dollars which is converted to 2024 dollars by applying inflation rate of 2.949% based on Consumer Price Index. For ICE2.0 Disaggregated (Column H) we entered our residential and non- residential customer counts as well as all the annually updated PG&E specific input values into ICE calculator to get an $/CMI. We get $/CMI in 2023 dollars which is converted to 2024 dollars by applying inflation rate of 2.949% based on Consumer Price Index. | Edwin Schmitt | 06/23/2025 | 2025-07-03 | 2025-07-03 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_008.zip | 0 | No
#N/A | 270 | SPD | 008 | SPD_008 | 2 | No | SPD_008_Q2 | Provide copies of the four (or more) offline ICE models that PG&E used to generate the values listed in Question 1b. This should be equivalent to RM-RMCBR-8 Module_1-Estimate_Interruption_Costs_w PGE Input.xlsx that was submitted with the 2024 RAMP or the ICE 2.0-Estimate_Interruption_Costs_2025-04-29.xlsx available from Lawerence Berkeley National Lab by request.1 All formulas must remain in the document so that SPD Staff can review how PG&E arrived at the monetized value of electric reliability. a. Provide a copy of the PG&E data that informed each of the offline models described in Question 2. This should be equivalent to RM-RMCBR-9 PG&E Data for ICE Calculator.xlsx that was submitted with PG&E’s 2024 RAMP Application. | PG&E objects to this request because it is not related to the WMP proceeding and exceeds the scope of that proceeding. This request would be more appropriately served as non-case discovery or in a different regulatory proceeding. Notwithstanding and without waiving this objection, PG&E responds as follows. Lawrence Berkeley National Laboratories (LBNL) has established that PG&E is not permitted to share offline ICE 2.0 models outside of the organization. The offline ICE 2.0 model may be requested from LBNL though it is not required to replicate the dollars per customer-minutes-interrupted ($/CMI) values that PG&E generated using ICE 2.0 as there is an online interface available at icecalculator.com. PG&E also offers to meet directly with Safety Policy Division and walk through the offline ICE 2.0 calculator used in support of the ALJ Compliance Filing in A.24-05-008. However, PG&E’s $/CMI values may also be generated through the online ICE 2.0 calculator using the inputs provided in AppendixB_ICE10 to ICE20 Input Comparison.xlsx file of the Compliance Filing. With respect to the ICE 1.0 models, 2027 GRC Exhibit (PG&E-2) WP 1-04_Module_1- Estimate_Interruption_Costs_w PGE Input 2025.xlsm was used for both aggregated and disaggregated approach. a. The customer counts and usage per customer used in ICE 1.0 for the 2027 General Rate Case (GRC) filing are based on recorded 2024 customer data, as provided in the February 24, 2025, version of PG&E’s 2025 Rates Forecast. With respect to the inputs used for ICE 1.0 model, please see 2027 GRC Exhibit (PG&E-2) WP 1- 05_PG&E Data for ICE Calculator 2025.xlsx. For ICE 2.0, customer counts as of May 8, 2025, were sourced from PG&E’s internal live customer dataset, while usage per customer figures were drawn from the same 2025 Rates Forecast. The percentages of manufacturing and health care customers were derived from actual recorded consumption data spanning 2022 through 2024. Estimates for the percentage of customers with Backup Generators (BUG) and those Working From Home (WFH) are based on PG&E-specific customer surveys developed and administered by LBNL and Resource Innovations (LBNL’s subcontractor) for the ICE 2.0 calculator. | Edwin Schmitt | 06/23/2025 | 2025-07-03 | 2025-07-03 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_008.zip | 0 | No
#N/A | 271 | SPD | 008 | SPD_008 | 3 | No | SPD_008_Q3 | Recreate the “Tranche-Outcome_Analysis” spreadsheet from RM-RMCBR-14 PG&E 2024 RAMP Risk Values_ICECalcAdj_by_Event (add DUNGD).xlsx for each of the four approaches to electric reliability presented in the “PG&E 2027GRC Risk Values” spreadsheet: a. ICE 1.0 aggregated (Column E) b. ICE 1.0 disaggregated (Column F) c. ICE 2.0 aggregated (Column G) d. ICE 2.0 disaggregated (Column H) | PG&E objects to this request because it is not related to the WMP proceeding and exceeds the scope of that proceeding. This request would be more appropriately served as non-case discovery or in a different regulatory proceeding. Notwithstanding and without waiving this objection, PG&E responds as follows. For the 2027 General Rate Case (GRC) filing, PG&E utilized an overall aggregated dollar-per-Customer Minute Interruption ($/CMI) value calculated using ICE 1.0, which was the most recent version of ICE calculator available at the time of analysis for the 2027 GRC filing. On June 20, to comply with the ALJ ruling, PG&E provided analysis results with disaggregated approach, utilizing the locational difference on composition of customers by sector (i.e., residential vs non-residential) by which $/CMI values are different per ICE 2.0 Calculator. PG&E notes that the previous analysis in the RM-RMCBR-14 PG&E 2024 RAMP Risk Values_ICECalcAdj_by_Event (add DUNGD).xlsx referred in this DR was performed as a response to the DR (SPD-PGE-2024RAMP_DR_002) by 1) deriving blended $/CMI by four geographic tier (HFTD Tier 2, HFTD Tier 3, Non-HFTD EPSS Capable, Non-HFTD Non-EPSS Capable) based on the mix of customers and $/CMI by customer sector, and then 2) taking the sum of the four blended $/CMI, weighted by the allocation factor of a tranche-outcome CMI to the geographic tier. The attachment WMP-Discovery2026-2028_DR_SPD_008-Q003Atch01.xlsx includes the requested analysis in the “Tranche-Outcome_Analysis” spreadsheet for each of the four approaches to electric reliability whose results were also presented in “PG&E 2027GRC Risk Values” attachment in the June 20 filing. The attachment WMPDiscovery2026- 2028_DR_SPD_008-Q003Atch01.xlsx includes the requested analysis in the “Tranche-Outcome_Analysis” spreadsheet for each of the four approaches to electric reliability whose results are presented in “PG&E 2027GRC Risk Values” attachment in the June 20 filing. Specifically, a. ICE 1.0 aggregated is in Column F of “Tranche-Outcome_Analysis (ICE1)” tab b. ICE 1.0 disaggregated is in Column J of “Tranche-Outcome_Analysis (ICE1)” tab c. ICE 2.0 aggregated is in Column F of “Tranche-Outcome_Analysis (ICE2)” tab d. ICE 2.0 disaggregated is in Column J of “Tranche-Outcome_Analysis (ICE2)” tab The calculation demonstrates the disaggregated approach used in the analysis presented in the June 20 filing. This represents a more granular segmentation than the four geographic tier analysis from the previous DR, SPD-PGE-2024RAMP_DR_002. Specifically, it removes the intermediate step of arbitrarily setting the $/CMI at the geographic tier level and directly utilizes the mix of customers at the tranche level at which the analysis is performed. | Edwin Schmitt | 06/23/2025 | 2025-07-03 | 2025-07-03 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_008.zip | 1 | No
26 | 272 | SPD | 008 | SPD_008 | 4 | No | SPD_008_Q4 | In a supplemental response to SPD-PGE-WMP2026-004 Question 4, PG&E stated that it has responded to the data request by “applying the ICE 2.0 disaggregated values ($0.08/CMI for residential, $23.11/CMI for nonresidential)”. In its Compliance Filing in its 2027 GRC, PG&E stated “PG&E continues to stand by our 2027 GRC risk analysis using a system-wide, aggregated electric reliability value, developed based on the best judgment and analysis available at the time of GRC filing.” a. Confirm that by “aggregated electric reliability value” PG&E is referring to the “ICE 1.0 aggregated” values that were submitted with both the WMP and the initially 2027 GRC Application. b. Is PG&E considering using the ICE 2.0 calculator in a future WMP update? Explain. c. Is PG&E considering using the ICE 2.0 calculator in a future EUP submission to Energy Safety? Explain. d. If the answer to 4a. is yes and either 4b. or 4c. is yes, explain why PG&E stands by its “aggregated electric reliability value” using ICE 1.0 in its 2027 GRC filing. i. Is PG&E concerned that standing behind one value in the 2027 GRC filing but standing behind another value in a future WMP update or future EUP submission would generate confusion? Explain. | PG&E objects to this request because it is not related to the WMP proceeding and exceeds the scope of that proceeding. This request would be more appropriately served as non-case discovery or in a different regulatory proceeding. Notwithstanding and without waiving this objection, PG&E responds as follows. a. Yes, “aggregated electric reliability value” refers to the “ICE 1.0 aggregated” values that were submitted with both the WMP and the initially 2027 GRC Application. b. PG&E is inclined to use the ICE 2.0 or more recent ICE calculator in updates to the WMP filing to benefit from the significant improvement in data and analysis employed by ICE 2.0 compared with ICE 1.0 calculator, and to comply with the Risk-Based Decision-Making Framework Rulemaking (R.20-07-013) (RDF OIR)1. c. PG&E intends to incorporate a disaggregated ICE 2.0 methodology for the forthcoming EUP filing. As indicated in EUP_SPD-PGE-SB884-018_DRCPUC_ D001_REM.pdf and EUP_SPD-PGE-SB884-017.pdf, PG&E is in the final stages of developing its Wildfire Benefit Cost Analysis (WBCA) too l— where this methodology will be implemented—and can share more information in July. d. Since the initial inception and first RAMP filings, PG&E, in partnership with the CPUC, the other IOUs, and Intervening Parties, has endeavored to constantly drive improvement in the Risk Framework. PG&E’s 2027 GRC filing is based on available analysis and data that could be reasonably included. Electric reliability analysis is therefore based on ICE 1.0, and not ICE 2.0 that only became available a few weeks prior to the filing deadline. Models, data, and risk analysis are always subject to changes based on newly available information, and the GRC cannot be constantly updated. For example, further updates to ICE 2.0 are expected in 2025. ICE 2.0 currently does not consider PG&E (and other CA IOU) customer survey data. Thus, when LBNL releases updates to ICE 2.0, the values will be different from the results produced now. Regarding the disaggregated approach ordered by the ruling, as explained in PG&E’s June 20 compliance filing, that approach requires further consideration in the Rulemaking proceeding. The disaggregated approach raises numerous issues, including the potential consequence of treating customers differently based on economic status, location, and other factors. For example, another method of performing the analysis assigns decreased priority for reliability improvements for customers who experience impactful outages such as PSPS and EPSS, and a lower value of outages to low income customers implying that reliability is less important for them. Such issues should be evaluated by the Commission before directing use of the disaggregated approach. Thus, PG&E affirms that it continues to stand by its 2027 GRC filing which is based on ICE 1.0 and a systemwide reliability approach. i. PG&E cannot speculate as to whether the disaggregated approach required by the April 22, 2025 ALJ Ruling, and submitted on June 20, 2025 will cause “confusion” relative to the presentation of electric reliability in the 2027 GRC or future WMP and EUP submissions. | Edwin Schmitt | 2025-06-23 | 2025-07-03 | 2025-07-03 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_008.zip | 0 | No
27 | 273 | SPD | 009 | SPD_009 | 1 | No | SPD_009_Q1 | In PG&E’s third supplemental response to Question 5 of SPD-PGE-WMP2026-004, PG&E stated the following: With regard to the “Miles of” fields provided with this response, please note that, consistent with PG&E’s prior responses, PG&E is providing units, rather than miles. Further, please note that there are units associated with circuit segments that are not present in the requested list of circuit segments, therefore that data is not included in this response. a. Explain why circuit segments that include units of a mitigation presented in the 2026-2028 Base WMP are not included in the requested list of circuit segments. b. Provide an updated version of WMP-Discovery2026-2028_DR_SPD_004-Q005Supp03Atch01.xlsx or any subsequent version of this dataset that includes all of the circuit segments referenced in Question 1a. | a.The circuit segments in the provided template are from WDRM v4. There are circuit segments that include units of mitigation in the 2026-2028 Base WMP that are only in WDRM versions preceding v4. As stated in Supplemental 01 response to Question 5 of SPD-PGE-WMP2026-004 (May 30, 2025), PG&E only reported units for those circuit segments in the provided template: The information reported in the provided template may not fully represent System Hardening and Rebuild work in its entirety because the provided circuit segment list is based on WDRM v4. There are miles and costs associated to circuit segments that are not present in the provided template, therefore that data is not included in this response. b. Circuit segments that were not in the provided template but have forecasted units of mitigation in the 2026-2028 Base WMP are listed below in Table 1. This table also shows which of the preceding WDRM versions each of these circuit segments are part of, and that they are not included in v4. Table 1: 2026-2028 Base WMP Circuit Segments not in WDRM v4 Circuit Segment In WDRM v2 In WDRM v3 In WDRM v4 CURTIS 170356972 Yes Yes No MARIPOSA 210135244 Yes No No UPPER LAKE 11011276 Yes Yes No DUNBAR 1103534 Yes No No PARADISE 110636042 Yes Yes No PARADISE 110443008 Yes No No All analysis that supports the previous responses to Question 5 of SPD-PGE-WMP2026-004 were performed specifically for the circuit segments in the provided template, and therefore are not available for the circuit segments listed in Table 1. However, data regarding units and expenditures is independent of WDRM version and is readily available, so PG&E is providing the units and expenditures for these circuit segments as they relate to our System Hardening and Undergrounding programs in attachment “WMP-Discovery2026-2028_DR_SPD_009-Q001Atch01.xlsx.xlsx.”Q001Atch01.xlsx.” The notes regarding this data in Supplemental 01 response to Question 5 of SPD-PGE-WMP2026-004 (May 30, 2025) are applicable to the data provided in this attachment. | Edwin Schmitt | 2025-07-03 | 2025-07-10 | 2025-07-10 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_009.zip | 1 | No |  | Risk Methodology & Assessment | 5.4 | Summary of Risk Models
27 | 274 | SPD | 009 | SPD_009 | 2 | No | SPD_009_Q2 | PG&E’s third supplemental response to Question 5 of SPD-PGE-WMP2026-004 included the dataset labeled WMP-Discovery2026-2028_DR_SPD_004-Q005Supp03Atch01.xlsx. In the “Primary” spreadsheet under the WDRM v.4 portion of the dataset all of the “Post-Mitigated” fields (Columns AB-AF) have now been given N/A or “See written response” values. a. Explain why PG&E has included an N/A for some circuit segments. b. Explain why PG&E has included “See written response” for some circuit segments. c. Explain why PG&E’s third supplemental response to Question 5 of SPD-PGE-WMP2026-004 did not inform SPD that it would fill in these fields with N/A or “See written response”. d. Explain why PG&E is able to present Wildfire Risk Reduction for Undergrounding and Overhead Hardening according to WDRM v.4, v. 3 and v.2 in response to Question 1 of TURN-PG&E-3, but PG&E is unable to provide the “Post-Mitigated” fields from Question 5 of SPD-PGE-WMP2026-004.1 i. PG&E’s original response to Question of SPD-PGE-WMP2026-004 stated that WDRM v.4 “cannot be used to quantify mitigation effectiveness”. Explain how PG&E used WDRM v.4, v.3 and v.2 to calculate Wildfire Risk Reduction in response to Question 1 of TURN-PG&E-3. ii. Provide the datasets and workpapers used to calculate the fields “Est. Wildfire Risk Reduction (V4)” “Est. Wildfire Risk Reduction (V3)” and “Est. Wildfire Risk Reduction (V2)” in the workpapers titled WMP-Discovery2026-2028_DR_TURN_003-Q001Atch02CONF.xlsx and WMP-Discovery2026-2028_DR_TURN_003-Q001Atch03CONF.xlsx. Include all excel formulas within the dataset and workpapers to ensure Staff can follow how PG&E arrived at the final calculation for these three fields for each circuit segment. e. In response to Question 1g. of SPD- PGE-WMP2026-SPD-006 about the “Post-Mitigated” fields, PG&E stated the following: “PG&E believes we can provide the requested values through use of the preliminary version of the WBCA tool, dependent on completion of mapping of mitigation activities to the given list of circuit segments.” Explain when PG&E will provide SPD with the data for the “Post-Mitigated” fields using a preliminary version of the WBCA tool. i. If PG&E has determined that it cannot provide SPD with the data for the “Post-Mitigated” fields using a preliminary version of the WBCA tool, explain why it cannot. ii. If PG&E has determined that it cannot provide SPD with the data for the “Post-Mitigated” fields using a preliminary version of the WBCA tool, explain when PG&E made this determination. iii. If PG&E has determined that it cannot provide SPD with the data for the “Post-Mitigated” fields using a preliminary version of the WBCA tool, then as was already requested in Question 1.g.ii. of SPD- PGE-WMP2026-SPD-006 describe a solution for providing SPD with the “Post-Mitigated” fields for each circuit segment. | a. For these columns, “N/A” and “See written response” are meant to convey the same information and should be considered synonymous. As described in PG&E’s third supplemental response to Question 5 of SPD-PGE-WMP2026-004 (pages 11-12), the reason that these fields are impossible to report as requested is because “WDRM v4 model was developed as a predictive model and cannot be used to quantify mitigation effectiveness”. b. See response to subpart a. c. PG&E’s third supplemental response to Question 5 of SPD-PGE-WMP2026-004 intended to describe the values in these fields in the table on pages 11-12. d. Please see the following responses for clarification on Wildfire Risk Reduction and the “Post-Mitigated” fields: i. PG&E did not use WDRM v2, v3, or v4 to calculate Wildfire Risk Reductions in response to Question 1 of TURN-PG&E-3. As previously described in PG&E’s response to WMP-Discovery2026-2028_DR_SPD_007-Q001, “The primary objective of the WDRM v4 is to predict wildfire risk associated with the distribution system. The WDRM does not calculate mitigation effectiveness. Further, the WDRM v4 is a set of machine learning (ML) models, and it is not appropriate to extract causal information from the predictive models. The models predict future values based on historical event data.” The same is true for WDRM v2 and WDRM v3. ii. Calculations were completed in an internal code repository (Risk Reduction Model) and cannot be provided in excel format. e. The ability to calculate post-mitigated values in the WBCA tool is not yet finalized This capability is expected to be available by August 4th. However, the tool is being developed to allow for detailed scoping of a single project at a time, rather than bulk entry of thousands of historic sub-projects. To provide the requested post-mitigated values for these historic projects would require additional weeks of manual entry. i. PG&E has not determined that this analysis cannot be done, but that it is unduly burdensome. The tool is being developed to allow for detailed scoping of a single project at a time, rather than bulk entry of thousands of historic sub-projects. To provide the requested post-mitigated values for these historic projects would require weeks of manual entry. ii. PG&E has not determined that this analysis cannot be done, but that it is unduly burdensome. With the data currently available, PG&E is able to perform individual circuit segment analysis. iii. See response to subparts ei and eii. PG&E welcomes a meeting with SPD staff to discuss this issue in greater detail and to provide information in a timely manner to SPD. | Edwin Schmitt | 2025-07-03 | 2025-07-10 | 2025-07-10 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_009.zip |  | No |  | Risk Methodology & Assessment | 5.4 | Summary of Risk Models
27 | 275 | SPD | 009 | SPD_009 | 3 | No | SPD_009_Q3 | In PG&E’s first supplemental response to Question 5 of SPD-PGE-WMP2026-004 it included a table of forecasted 2026-2028 costs for system hardening mitigations. PG&E also stated that comparing the reported expenditures and the reported miles will not yield an accurate unit cost because a project’s costs may be spread across multiple years. a. Explain how PG&E estimated the forecasted 2026-2028 costs for the three system hardening mitigations. b. Provide all workpapers PG&E used to estimate the forecasted 2026-2028 costs for the three system hardening mitigations c. Provide the unit cost for each of the three system hardening mitigations that PG&E used to estimate this forecast. d. Provide all workpapers that PG&E uses to generate a unit cost for each of the three system hardening mitigations that PG&E used to estimate this forecast. i. Provide all historical datasets used to estimate the unit cost of each of the three system hardening mitigations. e. In its response to Question 4a. of SPD-PGE-WMP2026-006, PG&E provided SPD with a list of cost adders and constraints and their associated amounts.2 In response to Question 4b., PG&E stated: “PG&E’s project management team established these estimated values based on a review of historical project costs, which are captured and maintained upon project completion.” Provide the most recent dataset(s) of historical data that PG&E used to generate the values for each cost adder or constraint listed in WMP-Discovery2026-2028_DR_SPD_006-Q004Atch01CONF.xlsx. i. All formulas should be kept within the dataset so that staff can trace how PG&E arrived at the final values for each cost adder or constraint. | a. Forecasted capital costs are a function of forecasted miles and estimated unit costs. The forecasted miles for a given mitigation type and given year are multiplied by the estimated unit cost for that same mitigation type and year (see response to subpart b for an example). For example, in “WMP-Discovery2026- 2028_DR_SPD_009-Q003Atch01.xlsx” PG&E planned to complete 214 miles of undergrounding (Cell D4) at the unit cost of $3.26 million/mile (Cell D11) for the total estimated cost of $697 million (Cell D17): 214 miles x $3.26 million/mile = $697 million total estimated cost. The capital costs for a system hardening subproject (overhead hardening, undergrounding, and line removal) are incurred over its full lifecycle (e.g., approximately three to four years for undergrounding). Therefore, the costs associated to a single subproject are spread across multiple years as it progresses through preconstruction, construction, and post-construction. This is illustrated in the Multi-Year Capital Cost section of “WMP-Discovery2026- 2028_DR_SPD_009-Q003Atch01.xlsx” (C26:I46). b. Please see attachment “WMP-Discovery2026-2028_DR_SPD_009-Q003Atch01.xlsx”: • Miles for each mitigation type is provided by year in section A (C3:I8) • Unit cost for each mitigation type is provided by year in section B (C10:I14) • Annual Capital Cost for each mitigation type is calculated by year in section AxB (C16:I21) c. Please see attachment “WMP-Discovery2026-2028_DR_SPD_009-Q003Atch01.xlsx”: • Unit cost for each mitigation type is provided by year in section B (C10:I14) d. Worksheet ‘Subpart A and B’ of attachment “WMP-Discovery2026-2028_DR_SPD_009-Q003Atch02.xlsx”2 shows the historic average unit costs for undergrounding (2019-2024) and overhead hardening (2018-2024). These historic unit costs are the basis for the 2026-2028 WMP unit costs we used to generate the forecast costs for the undergrounding and overhead hardening unit costs. The 2024 unit cost for undergrounding was $3.2 million/mile and is comparable to the $3.26 million/mile WMP unit cost. The details of Undergrounding subprojects completed from 2018 to 2024 can be found on worksheet ‘Subpart C’ of the attachment. The 2024 unit cost for overhead hardening was $0.9 million/mile and is comparable to the $1.09 million/mile WMP unit cost. The details of Overhead Hardening subprojects completed from 2018 to 2024 can be found on worksheet ‘Subpart D’ of the attachment. For line removal, PG&E uses estimates for line removal mileage per project and cost per remote grid informed by project costs from 2021-2024. (see PG&E’s 2027 GRC Exhibit PG&E-4, Chapter 7, WP 7-14 and WP 7-11, line 4) The unit costs for Butte undergrounding are based on the projects planned for 2026 and 2027 as opposed to historic unit costs. PG&E uses project specific forecasts for Butte undergrounding work because there are very few planned projects and miles of work. The estimated projects, units and unit costs are provided on attachment “WMP-Discovery2026-2028_DR_SPD_009-Q003Atch03.xlsx.” e. The data provided in response to Question 4a of SPD-PGE-WMP2026-006 was based on a snapshot of recorded actual project cost elements for all completed projects through 2021 to inform approximate values for the various cost categories. PG&E is unable to locate the dataset that supports said analysis and it cannot be provided. PG&E would like to reiterate that these reported values are considered a Class 5 estimate in accordance with Association for the Advancement of Cost Engineering (AACE) that is used during the scoping stage. As a subproject progresses towards design and estimating and more subproject details are available, the cost estimates are refined. | Edwin Schmitt | 2025-07-03 | 2025-07-10 | 2025-07-10 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_009.zip | 2 | No | 5 | Risk Methodology & Assessment | 5.5.2 | Top Risk-Contributing Circuits/Segments/Spans
27 | 276 | SPD | 009 | SPD_009 | 4 | No | SPD_009_Q4 | In response to Question 23 of SPD-PGE-WMP2026-004, PG&E stated that the Decision-Trees in Figures PG&E-8.2.1-1, PG&E-8.2.1-2, and PG&E-8.2.1-3 in the 2026-2028 Base WMP are in fact one single decision-tree connected together and that there are five results from the decision tree: (1) do not implement system hardening; (2) implement a 100% overhead hardening solution; (3) implement a 100% undergrounding solution; (4) implement a hybrid hardening solution where portions of a line are undergrounded and other portions are overhead hardened; and (5) implement a line removal with remote grid solution. a. Provide an example circuit segment from each of the five results. For each of the five circuit segments, provide a step-by-step explanation of each decision that PG&E needed to make and each analysis PG&E needed to conduct in order to arrive at the final result for said circuit segment. i. At each step in the explanation of the five circuit segments, provide the level of accuracy of the cost estimate at that point in the process. PG&E should reference the Association for the Advancement of Cost Engineering (AACE) scale for understanding the accuracy of the cost estimate at a given point within the decision tree. b. Explain PG&E’s rational for allowing the decision-tree to include result #1, which is to not implement system hardening. c. For result #4, explain what is meant by “portions of a line”. i. Explain how the “portions of a line” are determined by PG&E. d. Is there another decision tree for determining whether the line removal with remote grid solution would be an economical solution? i. If so, provide that decision tree and a narrative of how it operates. ii. If not, explain why not and explain how PG&E determines that line removal with remote grid solution is an economical solution. | Please see the below responses that provide an example circuit segment from each of the five decision-tree results. (1) Do not implement System Hardening Example CPZ: Tassajara 21123202 (V4 rank 9) – Determined to be privately owned line. Decision Tree Steps: 1. Confirmed CPZ is less than 1 mile, proceed with identifying scope due to end of line. 2. Confirmed that this segment is partially complete and what is remaining is determined to be privately owned line. End scope. (2) Implement a 100% Overhead Hardening solution with EPSS Example CPZ: Pit NO 5 11011614 (V4 rank 63) – 100% OH Decision Tree Steps: 1. Confirmed CPZ is not less than 1 mile. 2. Confirmed that this segment does not have a current workplan or is already hardened. 3. Confirmed that this segment does not have HFRA adjustment. 4. Confirmed segment does have adjacent high risk and adjacent circuit segment is large enough to warrant its own project. 5. Confirmed segment is not near the HFTD border for PSPS/EPSS benefit. 6. Confirmed remote grid or Line Elimination Incentive Program (LEIP) are not a potentially economical solution. 7. Confirmed there are no idle lines or redundant circuit ties that can be removed. 8. AACE Class 5 cost estimate. UG CBR >1 and not within 50% of OH + EPSS CBR and UG NB < OH NB. Proceed to review Hybrid alternative to meet CBR and NB requirement. 9. Confirmed there are areas identified with high tree strike potential. 10.Confirmed there are no ingress/egress issues. 11.It is confirmed there is no PSPS polygon affecting this zone. 12.N/A - No UG for PSPS required. 13.N/A - No UG for Ingress/Egress Required. 14.AACE Class 4/5 cost estimate. Hybrid (Tree) CBR >1, not within 50% of OH + EPSS CBR and Hybrid NB < OH NB. Proceed with OH + EPSS Scope. 15.There are no significant dependency or constructability limitations related to OH scope proposed. 16.AACE Class 5 cost estimate. The preferred alternative is OH + EPSS scope. 17.Engineer approved Key Sketch. (3) Implement a 100% undergrounding solution Example CPZ: Monte Rio 1113320 (V4 rank 79) – 100% UG Decision Tree Steps: 1. Confirmed CPZ is not less than 1 mile 2. Confirmed that this segment does not have a current workplan or is already hardened. 3. Confirmed this segment does not have HFRA adjustment 4. Confirmed segment does have adjacent high risk and adjacent circuit segment is large enough to warrant its own project 5. Confirmed this segment is not near HFTD border for PSPS/EPSS benefit 6. Confirmed remote grid or LEIP is not a potentially economical solution 7. Confirmed there are no idle lines or redundant circuit ties that can be removed 8. AACE Class 5 cost estimate. UG CBR > 1, UG CBR within 50% of OH + EPSS CBR, and UG NB > OH + EPSS NB (skip to 15) 9. N/A – Confirmed there are areas identified with high tree strike potential 10.N/A – Confirmed there are ingress/egress issues 11.N/A – Confirmed there is no PSPS polygon affecting this zone 12.N/A – No PSPS identified. 13.N/A – UG for ingress/egress included in UG scope 14.N/A – UG for tree strike risk included in UG scope 15.Two locations identified by construction were adjusted to accommodate their constructability concerns. Scope updated. 16.AACE Class 4/5 cost estimate. UG CBR > 1 and UG CBR is within 50% of OH CBR and the UG NB > OH NB so the preferred alternative is ALL UG scope 17.Engineer approved Key Sketch (4) Implement a hybrid hardening solution where portions of a line are undergrounded and other portions are overhead hardened Example CPZ: Oro Fino 11022236 (V4 rank 44) – Hybrid Decision Tree Steps: 1. Confirmed CPZ is not less than 1 mile. 2. Confirmed that this segment does not have a current workplan or is already hardened. 3. Confirmed that this segment does not have HFRA adjustment 4. Confirmed segment does have adjacent high risk and adjacent circuit segment is large enough to warrant its own project. 5. Confirmed segment is not near the HFTD border for PSPS/EPSS benefit. 6. Confirmed remote grid or LEIP is not a potentially economical solution. 7. Confirmed there are no idle lines or redundant circuit ties that can be removed. 8. AACE Class 5 cost estimate. UG CBR < 1, not within 50% of OH + EPSS CBR and UG NB < OH NB. Proceed to review Hybrid alternative to meet CBR and NB requirement. 9. Confirmed there is tree strike potential. 10.Confirmed there is no ingress/egress concerns. 11.Confirmed there is one PSPS polygon affecting this zone. 12.AACE Class 5 cost estimate. Hybrid (Tree/PSPS/PSS)1 CBR >1, Hybrid (Tree/PSPS/PSS) CBR > OH + EPSS CBR and Hybrid NB > OH NB. Proceed with Hybrid alternative. 13.N/A – No UG for ingress/egress required. (skip to 15) 14.N/A – Tree strike risk is addressed in Proposed Hybrid Scope. 15.There is no significant dependency or constructability limitations in the areas of impact. Construction Management team identified a shorter alternative UG route to minimize cost. 16.AACE Class 4/5 cost estimate. The preferred scope is Hybrid (Tree/PSPS/PSS) CBR >1, Hybrid (Tree/PSPS/PSS) CBR > OH + EPSS CBR and Hybrid NB > OH NB. Proceed with Hybrid alternative. 17.Engineer approved Key Sketch. (5) Implement a Line Removal with Remote Grid solution Example CPZ: Coalinga No 2 11059260 (V4 rank 121) Note that we will continue to review 100% UG, 100% OH, or Hybrid where we need an alternative hardening solution in the case that the remote grid project fails to proceed due to feasibility and/or re-analysis of remote grid cost. Decision Tree Steps: 1. Confirmed CPZ is not less than 1 mile. 2. Confirmed that this segment does not have a current workplan or is already hardened. 3. Confirmed that this segment does not have HFRA adjustment. 4. Confirmed segment does not have adjacent high risk. 5. Confirmed segment is not near the HFTD border for PSPS/EPSS benefit. 6. Confirmed remote grid or LEIP would be a potentially feasible and economical solution using AACE Class 5 cost estimate accuracy • Remote Grid CBR >1, greater than 50% of OH + EPSS CBR and RG NB > OH NB. 7. Even if remote grid or LEIP is preferred solution, proceed with steps 7 – 16 to prepare alternative solution if remote grid fails. Confirmed there are no idle lines or redundant circuit ties that can be removed. 8. AACE Class 5 cost estimate. UG CBR >1, not within 50% of OH + EPSS CBR and UG NB < OH NB. Proceed to review Hybrid (Tree/PSPS/PSS) alternative to meet CBR and NB requirement. 9. Confirmed there is no tree strike potential. 10.Confirmed there is no ingress/egress concerns. 11.Confirmed there is one PSPS polygon affecting this zone. 12.AACE Class 5 cost estimate. Hybrid (Tree/PSPS/PSS) CBR >1, not within 50% of OH + EPSS CBR and Hybrid NB < OH NB. Proceed with OH + EPSS as alternative if Remote Grid fails. 13.N/A – No ingress/egress risk identified requiring UG. 14.N/A – No tree strike risk identified requiring UG. 15.Confirmed there is no significant dependency or constructability limitations in the areas of impact. 16.AACE Class 4/5 cost estimate. Given results from steps 8-15, the alternative scope if remote grid fails determined to be OH + EPSS scope. 17.Engineer approved Key Sketch incorporating preferred and alternative scopes. b. There are multiple scenarios that are reviewed by the team during the Grid Design team’s high-level feasibility review that can result in the decision to not implement system hardening. These scenarios include: • CPZ is 100% privately/customer owned lines • CPZ is 100% included in the previous year’s workplan • CPZ is 100% hardened • CPZ is less than 1 mile and adjacent zones are not included in the expected 2027-2030 CPZ list. c. When the decision is made that a complete UG Primary solution does not meet the economic criteria, PG&E’s Grid Design team begins the Hybrid analysis (result #4). This analysis results in a span-by-span analysis of each of the scenarios listed in the decision tree: • Are there areas identified with high tree strike potential within the circuit segment? • Are there ingress/egress concerns expressed by the PSS team? • Does a PSPS polygon affect only part of the CPZ? High-Tree Strike Potential Example An example of a portion of a line that may be considered to have high tree strike potential is a single span or series of spans with high tree strike risk (shown as red lines in the figure below) where underground is the most effective solution. The undergrounding required to mitigate the span(s) may require additional adjacent spans to be included due to required relocation of the underground line compared to the existing overhead alignment. There is also a field visit by the vegetation management team to validate the high risk spans due to the potential of coincidental vegetation work conducted to mitigate the tree fall-in risk. This is reviewed by the Grid Design team as part of our Field Scoping Desktop meeting. Ingress/ Egress Risk Example For ingress/egress risk, the portions of a line include those poles and spans near enough the road or crossing the road where the ingress/egress risk was identified by the Public Safety Specialist (PSS) and only those spans and poles would be considered for an underground solution. Some of the overhead crossings can result in a significant re-route which then would include the mitigation of additional areas to support the underground in that location PSPS Risk Example For PSPS risk, the UG primary solution would result in reducing 100% of the risk due to PSPS. But not all PSPS events are the same and some events only impact portions of the segment. In these cases, we would consider implementing underground on portions of the CPZ to mitigate the PSPS impact d. For line removal with remote grid, there is not a separate decision tree for determining whether the solution would be economical. Rather, PG&E categorizes line removal with remote grid as a “Hybrid” solution in the cost benefit analysis portion of the decision tree shown in Figure PG&E-8.2.1-2 in the 2026-2028 Base WMP. Since remote grids are typically suited to address only a portion of a circuit segment (such as a location at the end of a long radial distribution line), another system hardening method is used for any remaining portion of the circuit segment and the overall solution is considered a hybrid hardening solution. Because the feasibility and cost of a remote grid can vary significantly due to sitespecific factors, PG&E performs a detailed feasibility study for the remote grid after scoping approval. The detailed feasibility study includes onsite evaluation, preliminary engineering designs (e.g. 10% engineering design), and a price quote from a vendor for the installation and maintenance of the remote grid. PG&E uses this updated cost estimate at the 10% engineering design stage (which can be considered AACE Class WMP-Discovery 2026-2028_DR_SPD_009-Q004 Page 11 3) to re-confirm that the remote grid remains economical versus the preferred alternative as determined by the System Hardening project scoping decision tree. Note: Where a remote grid is infeasible due to site or customer factors, PG&E may achieve wildfire risk reduction by mutual agreement with a property owner to remove PG&E electric service, known as the Line Elimination Incentive Program (LEIP). The agreement is tied to financial incentives for the property owner. The LEIP screening process is downstream of the remote grid feasibility analysis, which PG&E initiates for sites that are prioritized as candidates for line elimination via remote grid or LEIP. Please refer to “WMP-Discovery2026-2028_DR_SPD_003-Q001CONF.pdf” sent on April 29, 2025 for a thorough explanation of LEIP | Edwin Schmitt | 2025-07-03 | 2025-07-21 | 2025-07-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_009.zip | 0 | No | 5 | Risk Methodology & Assessment | 5.2.2.2 | Consequence of Risk Event
28 | 277 | OEIS | 016 | OEIS_016 | Q001 | No | OEIS_016_QQ001 | Q01. Regarding unplanned distribution system outages from Jan 1, 2023, to Dec 31, 2024 a. Provide a list and description of each distinct cause code attributed to an unplanned distribution outage1 from Jan 1, 2023, to Dec 31, 2024. b. Provide the average number of distribution poles in PG&E’s High, Severe, and Extreme plat maps (as defined in section 8.1.3 of its 2023-2025 WMP) from Jan 1, 2023, to Dec 31, 2024. c. Provide the total number of unplanned distribution outages in PG&E’s High, Severe, and Extreme plat maps from Jan 1, 2023, to Dec 31, 2024. d. Provide the number of unplanned distribution outages in PG&E’s High, Severe, and Extreme plat maps caused by vegetation contact from Jan 1, 2023, to Dec 31, 2024. i. As a subset, provide the number of unplanned distribution outages caused by vegetation contact during major event days. e. Provide the number of unplanned distribution outages in PG&E’s High, Severe, and Extreme plat maps caused by equipment failure from Jan 1, 2023, to Dec 31, 2024. i. As a subset, provide the number of unplanned distribution outages caused by equipment failure during major event days. f. In an Excel file attachment(s), provide the data PG&E used to determine the number of outages in tabular form. | a. Please see attachment “WMP-Discovery2026-2028_DR_OEIS_016- Q001Atch01.xlsx” for the requested information. b. Pursuant to our correspondence, we are working on providing the requested information and will respond to this subpart no later than July 18, 2025. c. Pursuant to our correspondence, we are working on providing the requested information and will respond to this subpart no later than July 18, 2025. d. Pursuant to our correspondence, we are working on providing the requested information and will respond to this subpart no later than July 18, 2025. i. Please see Worksheet “SO Counts by Basic Cause” in attachment “WMPDiscovery2026- 2028_DR_OEIS_016-Q001Atch01.xlsx” for the number of unplanned distribution outages caused by vegetation contact during major event days. e. Pursuant to our correspondence, we are working on providing the requested information and will respond to this subpart no later than July 18, 2025. i. Please see Worksheet “SO Counts by Basic Cause” in attachment “WMPDiscovery2026- 2028_DR_OEIS_016-Q001Atch01.xlsx.” for the number of unplanned distribution outages caused by equipment failure during major event days. f. Please see attachment “WMP-Discovery2026-2028_DR_OEIS_016- Q001Atch01.xlsx” for the requested information. | Nathan Poon | 2025-07-08 | 2025-07-11 | 2025-07-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_016.zip | 0 | No | 8 |  | 8.1.3
29 | 278 | OEIS | 017 | OEIS_017 | 1 | No | OEIS_017_Q1 | a. Complete the table below regarding PG&E’s pole clearing work in State Resource Areas (SRAs) located within the HFTD from 2022 to 2024: b. Complete the table below regarding PG&E’s pole clearing work in Local Resource Areas (LRAs) located within the HFTD from 2022 to 2024: c. Complete the table below regarding PG&E’s pole clearing work in Federal Responsibility Areas (FRAs) located within the HFTD from 2022 to 2024: | a. SRA within the HFTD PRC 4292 Exempt/Non-Exempt Pole Statistics. b. LRA within the HFTD PRC 4292 Exempt/Non-Exempt Pole Statistics. c. FRA within the HFTD PRC 4292 Exempt/Non-Exempt Pole Statistics. | Nathan Poon | 2025-07-15 | 2025-07-18 | 2025-07-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_017.zip | 0 | No
30 | 279 | SPD | 010 | SPD_010 | 1 | No | SPD_010_Q1 | In PG&E’s fourth supplemental response to Question 5 of SPD-PGE-WMP2026-004, PG&E provided SPD with WMP-Discovery2026-2028_DR_SPD_004-Q005Supp05Atch01.xlsx. On July 14 2025, SPD met with PG&E to discuss various topics. PG&E agreed that it could associate each CPZ with the EPSS and PSPS tranches. On July 19 2025, SPD met with PG&E to discuss the WDRM v.4 model. PG&E agreed that it would be able to complete the post-mitigated fields found within the WDRM v.4 topic of WMP-Discovery2026-2028_DR_SPD_004-Q005Supp05Atch01.xlsx. a. Fill in the data requested in the attached workbook titled “Decision Tree Results by Circuit Segment 2.0.xlsx”. The dataset is based on WMP-Discovery2026-2028_DR_SPD_004-Q005Supp05Atch01.xlsx. b. In the “Instruction” spreadsheet, fields have been added in the Circuit Segment Description and Tranches topics. These must be completed for this data request. c. The Post-Mitigated fields found in the WDRM v.4 topic in the “Instructions” spreadsheet should be filled out according to the method PG&E discussed with SPD on July 19 2025. d. Follow the Field Descriptions in the “Instruction” spreadsheet to complete the corresponding cells in the “Primary”, “S&S” and “DistTotal” spreadsheets. e. Responses in the “Primary” spreadsheet must be limited to the primary lines found on the corresponding “Circuit Segment Name” listed in Column A. f. Responses in the “S&S” spreadsheet must be limited to the secondary and service lines found on the corresponding “Circuit Segment Name” listed in Column A. g. Responses in the “DistTotal” spreadsheet must include both the primary, secondary and service lines found on the corresponding “Circuit Segment Name” listed in Column A. h. PG&E may complete its response to this question in tranches if it so desires. PG&E must complete the first tranche by July 25 2025. The first tranche must include the added fields in the Circuit Segment Description and Tranches topics as mentioned in Question 1b. If PG&E determines additional tranches are necessary to complete Question 1, it must reach out to SPD with a timeline by July 23 2025. | Please see attachment “WMP-Discovery2026-2028_DR_SPD_010-Q001Atch01.xlsx” for the requested information. Please note that the fields in columns AR through AT on the “Primary” tab have been modified to show EPSS and not WLDFR tranches1. PG&E believes this was a copy and paste error and has corrected it to reflect the list of fields in the “Instructions” tab. It should also be noted that the “S&S” tab only applies to 2024 RAMP WLDFR HFRA/Non-HFRA and 2027 GRC HFRA/Non-HFRA tranches. Secondary and service lines are not considered separate tranches for EPSS and PSPS. For clarity, circuit segments are not a fixed location on PG&E’s grid. A circuit segment is defined as a portion of a circuit that is directly protected by a protection device. As PG&E regularly reconfigures its circuits, (e.g., transferring load), a circuit segment that was identified at one point of time might be either larger or smaller at a different point of time. To that end, there are 630 circuit segments that did not map to a tranche for 2024 RAMP WLDFR HFRA/Non-HFRA Tranches and 2024 RAMP EPSS HFRA/Non-HFRA Tranches. As explained in Answer 3 to SPD004 Q5 Supplemental 5, 2024, RAMP uses WDRM v3 and 2027 GRC uses WDRM v4, which could cause circuit segments to drop or change. For PSPS tranches, “No” was provided if the circuit segment that had been originally identified no longer exists (i.e., the reconfiguration of the circuit led it to be absorbed or combined into another circuit segment). The pre-mitigated values in the WDRM V4 section of attached spreadsheet are the CoRE, LoRE, and wildfire risk from WDRM V4. These are used as the baseline distribution wildfire risk value for the 2026-2028 WMP. To determine the post-mitigated values, the percent risk reduction was obtained by calculating the percent difference in risk from 2026 and the risk at the end of 2028, which accounts for the projected reduction in distribution wildfire risk from planned system hardening work between 2026 and 2028. Post-mitigated risk values are one minus 2026 – 2028 percent risk reduction from system hardening multiplied by the pre-mitigated risk value. Wildfire risk mitigations do not reduce CoRE; therefore, CoRE is the same pre and post mitigation. Post-mitigated LoRE is determined by dividing post-mitigated risk by CoRE. We are continuing to evaluate which additional information is available for the Secondary and Service Lines and will provide that information in a future submittal. | Edwin Schmitt | 2025-07-21 | 2025-07-25 | 2025-07-25 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_010.zip | 0 | No
30 | 280 | SPD | 010 | SPD_010 | 2 | No | SPD_010_Q2 | On July 19 2025, SPD met with PG&E to discuss the WDRM v.4 model. PG&E informed SPD that it is developing a means of mapping CPZ across WDRM v.2, v.3 and v.4. This was a clarification upon PG&E’s third supplemental response to SPD-PGE-WMP2026-006 where in response to Question 1a. it stated “The methodology and tooling for relating circuit segments between model versions and explaining the change is in the process of being matured.” a. Provide SPD with an update to WMP-Discovery2026-2028_DR_SPD_006-Q001Supp03Atch01.xlsx. This updated dataset must include every circuit segment listed in the Circuit Segment Name field in the Primary spreadsheet. b. PG&E must provide the updated dataset by filling out Circuit Segment Change Tracker.xlsx workbook that is attached to this data request. i. If Explanation for Change v3-v4 or Explanation for Change v2-v3 lists "merge" or "split/merge", and PG&E merged more than two circuit segments to create a “new” circuit segment, then PG&E should expand the number of fields in order for SPD to properly track the changes that were made across the risk models. c. Provide SPD with the GIS datasets associated with WDRM v.2 and WDRM v.3 that at a minimum include the circuit segment names, coordinates, shapefiles and any other spatial data that was included in previous WMP submissions to Energy Safety that used these two risk models. This should be equivalent to PG&E’s response to CalAdvocates_041-Q003 for WDRM v.4 | As discussed via email, PG&E will be providing: c. Please see attachment “WMP-Discovery2026-2028_DR_SPD_010- Q002Atch01CONF.zip” for the requested WDRM v3 risk GIS dataset. We are in the process of transforming the WDRM v2 risk dataset into a GIS file format and will provide the dataset in a future response. | Edwin Schmitt | 2025-07-21 | 2025-07-25 | 2025-07-25 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_010.zip | 1 | No | N/A
31 | 281 | SPD | 011 | SPD_011 | 1 | No | SPD_011_Q1 | a. Complete the attached Excel workbook ICE 2.0 Inputs.xlsx. Follow the Instructions spreadsheet to complete the By HFTD and With EPSS spreadsheets. | Please refer to the attached file, “WMP-Discovery2026-2028_DR_SPD_011- Q001Atch01.xlsx” for the requested information. Kindly note that the values for the following categories remain consistent across HFTD and Non-HFTD classifications, including HFTD Tier 2 and 3, Non-HFTD with EPSS, and Non-HFTD without EPSS: • Residential BUG; • Residential Work From Home; • Non-Residential Manufacturing; • Non-Residential Health and Social; • Non-Residential Advanced Warning; • SAIDI; and • SAIFI. This approach ensures that PG&E utilizes system-level estimates with greater statistical reliability, as opposed to granular segments that lack sufficient sample sizes. It also WMP-Discovery 2026-2028_DR_SPD_011-Q001 Page 2 aligns with the methodology used in the 2027 GRC and maintains consistency with ICE 1.0 | Edwin Schmitt | 2025-07-28 | 2025-08-11 | 2025-08-07 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_011.zip |  | No
31 | 282 | SPD | 011 | SPD_011 | 2a | No | SPD_011_Q2a | Provide SPD with a dataset of actual recorded consumption data spanning 2022 through 2024 that informs the percentage of health care customers that PG&E used in its ICE 2.0 Calculation. This should be equivalent to the Manufacturing spreadsheet within WP 1- 05_PG&E Data for ICE Calculator 2025. | Please refer to the worksheet titled “HealthCare” in the attachment “WMPDiscovery2026-2028_DR_SPD_011-Q002Atch02.xlsx.” | Edwin Schmitt | 2025-07-28 | 2025-08-11 | 2025-08-07 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_011.zip |  | No
31 | 283 | SPD | 011 | SPD_011 | 2b | No | SPD_011_Q2b | Explain why for percentages of manufacturing and health care customers PG&E used the actual recorded consumption data for 2022 through 2024. i. Explain why it is reasonable to use a single year (2024 customer data) to estimate customer counts and customer usage and a three year average for percentages of manufacturing and health care customers. ii. Provide a side-by-side comparison of the percentages of manufacturing and health care customers using the actual recorded consumption data for 2022 through 2024 and just 2024. | Our customer database includes a North American Industry Classification System (NAICS) code that enables us to designate manufacturing and healthcare customers. However, the classification labels come from a third-party data source with reasonable uncertainties. We use a three-year average for percentages of manufacturing and health care customers to improve the consistency and stability of the data to avoid single year fluctuation. i. Customer count and consumption information are based on our internal billing data. Therefore, we use the last year of recorded data. Ultimately, 2024 % consumption values compared to 2022-2024 averages has a small deviation and an immaterial impact on the overall inputs used in the ICE tool. ii. The manufacturing and healthcare percentages for 2022-2024 vs just 2024 don’t change significantly. Manufacturing percent would change WMP-Discovery 2026-2028_DR_SPD_011-Q002 Page 3 from 12.4% (2022-2024) to 12.3% (2024) and healthcare percent would change from 5.4% (2022-2024) to 5.5% (2024). Please refer to the sheet “Comparison” in the in the attachment “WMP-Discovery2026- 2028_DR_SPD_011-Q002Atch02.xlsx.” | Edwin Schmitt | 2025-07-28 | 2025-08-11 | 2025-08-07 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_011.zip |  | No
31 | 284 | SPD | 011 | SPD_011 | 2c | No | SPD_011_Q2c | Confirm that the Electric Operations Unplanned Outage Data from 2016-2022 (ilis_fnl_local), which was used to estimate Temporal Outage Distributions inputs, was drawn from the same data source that informs the outage dataset used in WDRM v4 (see WMP-Discovery2026-2028_DR_SPD_001-Q010Atch02.xlsx). i. If so, explain why PG&E only used the data from 2016-2022 and not the complete dataset of outages from 2015-2024. ii. If not, provide SPD with the Electric Operations Unplanned Outage Data from 2016-2022 (ilis_fnl_local) referenced in Temporal Outage Distributions spreadsheet of WP 1-05_PG&E Data for ICE Calculator 2025.xlsx. | The Electric Operations Unplanned Outage Data from 2016-2022 used in our ICE 1.0 calculations was not drawn from the same data source and includes all unplanned outages system-wide. WMP-Discovery2026-2028_DR_SPD_001- Q010Atch02.xlsx uses unplanned HFTD outages only to inform effectiveness calculations for grid hardening programs. i. Not applicable. The outage dataset used in WDRM v4 (see WMPDiscovery2026-2028_DR_SPD_001-Q010Atch02.xlsx tab “Outages_HFTD”) includes outages occurring in HFTD only. The outage dataset used to estimate Temporal Outage Distributions includes outages in both HFTD and non-HFTD. ii. Please see “WMP-Discovery2026-2028_DR_SPD_011- Q002Atch01.xlsx” for the dataset of Electric Operations Unplanned Outage Data from 2016-2022 (ilis_fnl_local) referenced in Temporal Outage Distributions spreadsheet of WP 1-05_PG&E Data for ICE Calculator 2025.xlsx. | Edwin Schmitt | 2025-07-28 | 2025-08-11 | 2025-08-07 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_011.zip |  | No
31 | 285 | SPD | 011 | SPD_011 | 2d | No | SPD_011_Q2d | Explain why PG&E did not include the 2024 SAIDI data in the SAIFI and SAIDI spreadsheet in WP 1-05_PG&E Data for ICE Calculator 2025.xlsx. i. Explain why PG&E did not update the 2024 SAIDI data when it completed the Compliance Filing on June 20 2025 in the GRC. | To finalize risk modeling for its 2027 GRC Application, PG&E updated the ICE 1.0 Calculator using full-year SAIDI and SAIFI data from its most recent Safety and Operational Metrics (SOMs) Report filed to the CPUC, namely PG&E’s 2023 SOMs Report that was filed at the CPUC on April 1, 2024. PG&E’s 2024 SOMs Report was not filed at the CPUC until April 1, 2025, which was too late to use for risk modeling in PG&E’s 2027 GRC Application. i. When PG&E finalized the Compliance Filing on June 20, 2025 in the GRC, it didn’t try to update the data used in the ICE 1.0 Calculator for the May 15, 2025 GRC filing for consistency. | Edwin Schmitt | 2025-07-28 | 2025-08-11 | 2025-08-07 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_011.zip |  | No
31 | 285 | SPD | 011 | SPD_011 | 2e | No | SPD_011_Q2e | Explain why PG&E rounds SAIFI to the nearest whole number in WP 1-05_PG&E Data for ICE Calculator 2025.xlsx to prepare the Reliability Inputs for the ICE Calculator. i. If the actual SAIFI value was 1.455, what would be the SAIFI value that PG&E would use for the ICE Calculator? Explain how this would impact the $/CMI valuation from the ICE 2.0 Calculator. | In preparing the Reliability Inputs for the ICE 1.0 Calculator, PG&E set the value of SAIFI to “1” to get a “per outage reliability value” as described in PG&E’s 2024 RAMP Report2. In PG&E’s 2023 SOMS Report, annual SAIFI values over the 10- year period from 2014 to 2023 ranged from 0.879 to 1.470 resulting in an average SAIFI of 1.057, which rounds to a value of 1 i. PG&E is unclear on what the data source for an “actual SAIFI value of 1.455” would be. However, if PG&E were to update the ICE Calculator with currently available data it would use the same method used in its 2024 RAMP Report and 2027 GRC Application. This would involve calculating average SAIFI and SAIDI values from the annual SAIFI and SAIDI values reported in PG&E’s 2024 SOMs Report over the 10-year period from 2015 to 2024. The resulting average SAIFI and SAIDI values would then be used as inputs to the ICE 2.0 Calculator. | Edwin Schmitt | 2025-07-28 | 2025-08-11 | 2025-08-07 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_011.zip |  | No
31 | 285 | SPD | 011 | SPD_011 | 3 | No | SPD_011_Q3 | Provide SPD with the dataset and results of the PG&E-specific customer surveys developed and administered by LBNL and Resource Innovations (LBNL’s subcontractor) for the ICE 2.0 calculator. | In response to this question, PG&E is providing as attachment “WMPDiscovery2026-2028_DR_SPD_011-Q003Atch01CONF.pdf” the report titled “ICE Calculator 2.0 Initiative. Customer Interruption Cost Survey Findings for Pacific Gas & Electric”, prepared by Resource Innovations, Inc. and Lawrence Berkeley National Laboratory. We are working with Resource Innovations to obtain the underlying survey responses by August 20th . | Edwin Schmitt | 2025-07-28 | 2025-08-11 | 2025-08-07 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_011.zip |  | No
31 | 285 | SPD | 011 | SPD_011 | 4 | No | SPD_011_Q4 | Provide SPD with an update to WMP-Discovery2026-2028_DR_SPD_010- Q001Atch01.xlsx, that includes the Residential and Non-Residential customer count for each circuit segment name. These two fields must be the exact customer count; they must not be presented as a percentage. These two variables must be added after the Nominal Voltage field (Column D). i. Explain which customers PG&E classifies as Non-Residential. SPD understands that “streetlights,” or something similar, is a customer class – but is unclear how PG&E is classifying streetlights (and other customer classes) into residential versus non-residential. | a. Please refer to columns “Res_CustCount” and “NonRes_CustCount” added in column E and F of worksheet “Primary” in the attachment “WMP-Discovery2026- 2028_DR_SPD_011-Q004Atch01.xlsx All PG&E customers classified under the "Residential" customer class code in our billing data are designated as Residential customers. All others are considered Non-Residential. Premises identified as street lights or with an industry classification of road-highway are excluded from customer counts | Edwin Schmitt | 2025-07-28 | 2025-08-11 | 2025-08-07 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_011.zip |  | No
31 | 285 | SPD | 011 | SPD_011 | 5a | No | SPD_011_Q5a | Explain why the SPD Calculated Pre-Mitigated Ignition Risk per tranche is different than the Unscaled Pre-Mitigated Ignition Risk provided by PG&E in first supplemental response Question 5 of SPD-PGE-WMP2026-004. | PG&E confirms SPD’s understanding of risk being calculated as the product of CoRE*LoRE*Circuit Miles. a. Based on PG&E’s review, it appears that the tranche mileage in the two distribution tranche tables created by SPD are based on the "2024 RAMP WLDFR HFRA Tranche" and "2024 RAMP WLDFR Non-HFRA Tranche" in columns AM and AN of the “Primary” tab in PG&E’s submission WMPDiscovery2026-2028_DR_SPD_010-Q001Atch01.xlsx. As footnoted in PG&E’s first supplemental response to Question 5 of SPD-PGE-WMP2026-004, the provided EORM values are from the February 2025 vintage, which utilizes WDRM v4. This is an update from WDRM 3, previously used in the 2024 RAMP. The transition to WDRM v4 has resulted in revised circuit segment assignments to tranches, and thereby altering the HFRA/non-HFRA mileage allocations for each tranche. To calculate the Pre-Mitigated Ignition Risk per tranche, as provided in PG&E’s first supplemental response to Question 5 of SPD-PGE-WMP2026-004, the following updates are necessary: 1. Tranche Reference Update Replace the use of “2024 RAMP WLDFR HFRA Tranche” and “2024 RAMP WLDFR Non-HFRA Tranche” in columns AM and AN with the “2027 GRC WLDFR HFRA Tranche” and “2027 GRC WLDFR Non-HFRA Tranche” in columns AO and AP of the “Primary” worksheet in attachment WMPDiscovery2026-2028_DR_SPD_010-Q001Atch01.xlsx. 2. Mileage Source Update Replace the use of “Length of Circuit Segment HFRA” and “Length of Circuit Segment Non-HFRA” values in columns H and I with the “Length of Circuit Segment HFTD/HFRA” and “Length of Circuit Segment Non-HFTD/HFRA” values in columns J and K of the “Primary” worksheet in the attachment “WMPDiscovery2026-2028_DR_SPD_011-Q004Atch01.xlsx”.1 For clarity, PG&E’s 2026–2028 Wildfire Mitigation Plan defines HFTD and HFRA collectively as “HFTD/HFRA”2 and uses this combined designation as a dimension for tranche assignment.3 Accordingly, the tranche labels “HFRA” and “Non-HFRA” in columns AM through AT of attachment WMP-Discovery2026- 2028_DR_SPD_010-Q001Atch01.xlsx are shorthand for “HFTD/HFRA” and “Non-HFTD/HFRA,” respectively. | Edwin Schmitt | 2025-07-28 | 2025-08-11 | 2025-08-07 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_011.zip |  | No
31 | 285 | SPD | 011 | SPD_011 | 5b | No | SPD_011_Q5b | If any errors are discovered in the EORM tranche level values, explain if those errors impact the tranche level values for EPSS and PSPS. | An error prevented some circuit segments from being mapped to tranches in the WEPSS model, as noted in the footnote of WMP-Discovery 2026- 2028_DR_SPD_010_Q001. This was corrected in WMP-Discovery2026- 2028_DR_SPD_010_Q001Atch01.xlsx and does not significantly affect the overall risk profile. There are no errors in the EORM tranche level values provided on tabs “EORM WLDFR Values,” “EORM EPSS Values,” and “EORM PSPS Values” of attachment “WMP-Discovery2026-2028_DR_SPD_004- Q005Supp01Atch01.xlsx”. Please note the most recent tranche exposures for EPSS and PSPS can be found in the respective bowtie files in the GRC workpaper filing in Exhibit PGE-2, Chapter 1 | Edwin Schmitt | 2025-07-28 | 2025-08-11 | 2025-08-07 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_011.zip |  | No
31 | 285 | SPD | 011 | SPD_011 | 5c | No | SPD_011_Q5c | If there are any errors discovered in the EORM tranche level values, provide SPD with an update to WMP-Discovery2026-2028_DR_SPD_010-Q001Atch01.xlsx with corrected EORM risk values for each tranche. | There are no errors that warrant an update to attachment “WMP-Discovery2026- 2028_DR_SPD_010-Q001Atch01.xlsx” | Edwin Schmitt | 2025-07-28 | 2025-08-11 | 2025-08-07 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_011.zip |  | No
31 | 285 | SPD | 011 | SPD_011 | Q003Supp01 | 1 | SPD_011_QQ003Supp01 | In its response to Question 2a. of SPD-PGE-WMP2026-008, PG&E states that the inputs labeled Residential BUGs1 and Residential Work from Home within AppendixB_ICE10 to ICE20 Input Comparison.xlsx are based on PG&E-specific customer surveys developed and administered by Lawerence Berkeley National Labs (LBNL) and Resource Innovations (LBNL’s subcontractor) for the ICE 2.0 calculator. Provide SPD with the dataset and results of the PG&E-specific customer surveys developed and administered by LBNL and Resource Innovations (LBNL’s subcontractor) for the ICE 2.0 calculator. | a. Please see the following attachments for the underlying survey responses provided by Resource Innovations (LBNL’s subcontractor) for the ICE 2.0 calculator. “WMP-Discovery2026-2028_DR_SPD_011-Q003Supp01Atch01.xlsx” “WMP-Discovery2026-2028_DR_SPD_011-Q003Supp01Atch02.xlsx” “WMP-Discovery2026-2028_DR_SPD_011-Q003Supp01Atch03.xlsx” ANSWER 003 a. In response to this question, PG&E is providing as attachment “WMPDiscovery2026-2028_DR_SPD_011_Q003Atch01CONF.pdf” the report titled “ICE Calculator 2.0 Initiative. Customer Interruption Cost Survey Findings for Pacific Gas & Electric”, prepared by Resource Innovations, Inc. and Lawrence Berkeley National Laboratory. PG&E also requested that Resource Innovations, Inc. provide the underlying survey responses. This will be made available as soon as the vendor is able to, which is no sooner than August 20th, 2025. | Edwin Schmitt | 2025-07-28 | 2025-08-20 | 2025-08-20 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_011.zip |  | No
32 |  | SPD | 012 | SPD_012 | Q001 | No | SPD_012_QQ001 | 1. In its response to Question 2 of SPD-PGE-WMP2026-008, PG&E stated that it cannot provide SPD with the offline ICE 2.0 model it used to generate values in the Compliance Filing submitted to A.25-05-009 on June 20 2025. PG&E states in its response that the $/CMI values may also be generated through the online ICE 2.0 calculator using the inputs provided in AppendixB_ICE10 to ICE20 Input Comparison.xlsx file of the Compliance Filing. SPD understands that these inputs from AppendixB_ICE10 to ICE20 Input Comparison.xlsx represent PG&E’s entire service territory. In its response to Question 1 of SPD-PGE-WMP2026-011, PG&E stated the following: “Kindly note that the values for the following categories remain consistent across HFTD and NonHFTD classifications, including HFTD Tier 2 and 3, Non-HFTD with EPSS, and Non-HFTD without EPSS: • Residential BUG; • Residential Work From Home; • Non-Residential Manufacturing; • Non-Residential Health and Social; • Non-Residential Advanced Warning; • SAIDI; and • SAIFI. This approach ensures that PG&E utilizes system-level estimates with greater statistical reliability, as opposed to granular segments that lack sufficient sample sizes. It also aligns with the methodology used in the 2027 GRC and maintains consistency with ICE 1.0.” This is not what SPD was requesting, and so SPD is sending another data request. a. Complete the attached Excel workbook ICE 2.0 Inputs.xlsx. Follow the Instructions spreadsheet to complete the By HFTD and With EPSS spreadsheets. b. In the By HFTD spreadsheet, PG&E must comply with the following requirement: the fields in the spreadsheet must be filled out with information relevant to the HFTD or NonHFTD, respectively. c. In the With EPSS spreadsheet, PG&E must comply with the following requirement: the spreadsheet must be filled out with information relevant to Tier 3, Tier 2, Non-HFTD with EPSS and Non-HFTD without EPSS, respectivel | For clarity, PG&E is submitting the fully completed ICE 2.0 Inputs that are consistent with PG&E use of the model. As discussed, we have requested and expect to receive additional granular data from LBNL, which we will provide as available. Please see attachment “WMP-Discovery2026-2028_DR_SPD_012-Q001Atch01 (ICE 2.0 Inputs 8.8) V2.xlsx |  | 2025-08-08 |  | 2025-08-13 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_012.zip
33 |  | SPD | 013 | SPD_013 | Q001 | No | SPD_013_QQ001 | The following questions relate to “WMP-Discovery2026-2028_DR_SPD_001-Q019Atch01.xlsx”: a. Outage ID (column Q) has values in Row 40776 to 40783 as “1.” Correct if necessary. b. There are many blanks in Column B. Of 106,425 values, 71,1151 are blank. Explain why the values are blank. Correct if necessary. c. Explain why 6680 rows in Column O are blank, “false” or “1” – correct if necessary. d. Add a new column to the data set which includes the Facility Damage Action (FDA) for each tag. If the tag has more than one FDA, each additional FDA should be added in a second column. e. Create a data set with the same data as the “WMP-Discovery2026-2028_DR_SPD_001- Q019Atch01.xlsx” (including the FDA information as requested in question 1d) but with Priority X data, including the FDAs. | a. To be delivered on Thursday, August 28, 2025. b. The Asset Type column has been corrected. This omission was the result of inadvertent error and all notifications now have their asset type filled. Please see “WMP-Discovery2026-2028_DR_SPD_013-Q001Atch01.xlsx.” c. The Circuit ID column has been corrected. There are still 298 notifications with an unknown Circuit ID. This can occur when: (1) the equipment information for a notification is incorrect or missing; or (2) the circuit information for an equipment is missing. Please see “WMP-Discovery2026-2028_DR_SPD_013-Q001Atch01.xlsx.” d. The FDA information is in columns [Primary_FDA] and [Additional_FDAs_If_Applicable]. Please see “WMP-Discovery2026-2028_DR_SPD_013-Q001Atch01.xlsx e. To be delivered on Thursday, August 28, 2025. |  | 2025-08-11 | 2025-08-14 | 2025-08-14 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_013.zip
33 |  | SPD | 013 | SPD_013 | 002 | No | SPD_013_Q002 | “WMP-Discovery2026-2028_DR_SPD_001-Q019Atch01.xlsx” reports 5185 Priority As associated with “patrol inspections” or “detailed inspections” in 2023. However, PG&E’s response titled “WMP-Discovery2023-2025_DR_SPD_014-Q005Rev02Supp01.pdf” reports 1,419 Priority As created from patrols and detailed inspections. Additionally, “WildfireMitigationPlansDiscovery2023_DR_OEIS_023-Q001” appears to show a separate set of value of Level 1 (Priority As) from inspections. Explain the differences between the documents and correct as necessary. | PG&E’s response regarding patrol inspection A-priority (Level 1) findings is consistent across the three documents. Table 2 and its footnotes below demonstrate this consistency. PG&E’s response regarding detailed inspection A-priority (Level 1) findings in Document 2 (WMP-Discovery2023-2025_DR_SPD_014-Q005Rev02Supp01.pdf) is incorrect. The correct value as of August 20, 2025 is 4,817, not 1,3191. Document 2 provided an incorrect value with regard to detailed inspection A-priority (Level 1) findings because of the methodology used to identify overhead tags. The value provided above uses the correct methodology used in Documents 1 and 3. PG&E plans to resubmit Document 2 (WMP-Discovery2023-2025_DR_SPD_014-Q005Rev02Supp01.pdf) with corrected values by September 1, 2025. Full 2024 values will be provided rather than the year-to-date values provided in the July 2024 data response. Table Notes: 1. A-priority (Level 1) notifications that match QDR Methodology used for Document 1. Value includes notifications cancelled subsequently as part of work planning and execution processes. 2. Detailed inspection refers to detailed inspections conducted by PG&E’s ground inspection plan. Any values reported exclude the aerial pilot program and aerial inspection programs. 3. Patrol inspection information was not provided in Document 2. 4. Document 3 presents data as find rates, which are the number of findings divided by the number of inspections. For patrol, the 0.04% find rate in the data response was derived from dividing 368 findings by 917,767 patrols. For inspections, the 0.88% find rate in the data response was derived from dividing 4,817 findings by 544,492 inspections. “Refer to table in data request response” as public versions of DR responses will have the initial question and response tables |  | 2025-08-11 | 2025-08-21 | 2025-08-21 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_013.zip
33 |  | SPD | 013 | SPD_013 | 003 | No | SPD_013_Q003 | Provide a table (see table below) with the number of work orders resolved for each priority type from 2020 through 2024 for the HFTD and the entire territory for both (1) distribution (primary & secondary) and (2) transmission. “Refer to table in data request response” as public versions of DR responses will have the initial question and response tables. | The table below is populated from the data pull used to generate Table 2 tag data for the 2025 Q2 Quarterly Data Report. “Refer to table in data request response” as public versions of DR responses will have the initial question and response tables. |  | 2025-08-11 | 2025-08-14 | 2025-08-14 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_013.zip
33 |  | SPD | 013 | SPD_013 | 004 | No | SPD_013_Q004 | Provide a table (see table below) of the number of tags created for each priority type from 2020 through 2024 for the HFTD and the entire territory for both (1) distribution (primary & secondary) and (2) transmission. “Refer to table in data request response” as public versions of DR responses will have the initial question and response tables. | The table below is populated from the data pull used to generate Table 2 tag data for the 2025 Q2 Quarterly Data Report |  | 2025-08-11 | 2025-08-14 | 2025-08-14 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_013.zip
33 |  | SPD | 013 | SPD_013 | 005 | No | SPD_013_Q005 | Identify any ignitions from 2014-2024 associated with assets where PG&E had an existing corrective notification at the time of the ignition which PG&E attributes as causally connected to the ignition in the same format as “WMP-Discovery2026-2028_DR_SPD_001-Q014Atch01.xlsx” a. Include one additional column that includes the existing corrective notification b. Include one additional column which identifies the FDA associated with the ignition. c. Include one additional column which identifies the priority of the tag. d. Include one additional column which identifies the creation date of the tag. | Please note that PG&E did not collect data regarding tags related to ignitions prior to 2020. Accordingly, PG&E is providing the requested data from 2020-2024. PG&E has identified 19 CPUC-reportable ignitions where the failure mode associated with the fire was specifically captured in the scope of an EC or LC corrective notification created prior to, and still open at, the ignition event. Please see “WMP-Discovery2026-2028_DR_SPD_013-Q005Atch01.xlsx.” Please note that PG&E has determined that the conditions identified by the provided corrective notifications are likely related to the failure mode of an ignition event but cannot definitively determine causality. |  | 2025-08-11 | 2025-08-14 | 2025-08-14 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_013.zip
33 |  | SPD | 013 | SPD_013 | 006 | No | SPD_013_Q006 | Provide an updated version of “WMP-Discovery2026-2028_DR_SPD_001-Q016Atch01.xlsx” which includes data from 2020-2024. a. Include one additional column which includes the creation date of original tag. b. Include one additional column which includes the FDA of the original tag. If the tag has additional FDAs, include these FDAs in a second additional column. i. If in all cases, the FDAs matches the FDA in Question 1e, confirm this in the response, and this column may be omitted. | Please see attachment “WMP-Discovery2026-2028_DR_SPD_013-Q006Atch01.xlsx” for 2020-2024 Level 1 corrective notifications associated with overhead distribution assets where PG&E had an existing corrective notification at the time of failure. The following 4 columns of data have been added per request and to match the data presented in response to Question 007: corrective notification date, corrective notification primary FDA, correction notification other FDAs, and Level 1 (A-tag) date. Due to the volume of data, the method used to derive this data defines “causally connected” as having a Level 1 (emergency) tag, attributed to an equipment failure associated with the primary indicator on the same electric facility as a non-compliance (primary or otherwise) in the open maintenance tag. As this is a data pull and each event has not been desktop reviewed, there may be cases where the associated notification was not causal—for example, an instance in which a pole with two crossarms and an open tag on crossarm 1 experiences a failure of crossarm 2. Similarly, there may be cases where causally connected notifications are excluded—for example, an instance in which a pole fails due to a broken/damaged guy which had an existing notification. Details on the filtering procedure are included in “WMPDiscovery2026-2028_DR_SPD_013-Q006Atch01.xlsx” |  | 2025-08-11 | 2025-08-21 | 2025-08-21 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_013.zip
33 |  | SPD | 013 | SPD_013 | 007 | No | SPD_013_Q007 | Provide an updated version of “WMP-Discovery2026-2028_DR_SPD_001-Q015Atch01.xlsx” which includes data from 2020-2024, matching the same format as Question 5. | Please see “WMP-Discovery2026-2028_DR_SPD_013-Q007Atch01.xlsx” for 2020- 2024 distribution outages associated with overhead assets where PG&E had an existing corrective notification at the time of the outage. Due to the similarity of the request and data for to that in Question 6, the data has been presented in the same format with additional columns: corrective notification date, corrective notification primary FDA, and correction notification other FDAs. Due to the volume of data, the method used to derive this data defines “causally connected” as having a Level 1 (emergency) tag, linked to an unplanned outage, attributed to an equipment failure associated with the primary indicator on the same electric facility as a non-compliance (primary or otherwise) in the open maintenance tag. As this is a data pull and each event has not been desktop reviewed, there may be cases where the associated notification was not causal—for example, an instance in which a pole with two crossarms and an open tag on crossarm 1 experiences an outage caused by a failure of crossarm 2. Similarly, there may be cases where causally connected notifications are excluded—for example, an instance in which a pole fails due to a broken/damaged guy which had an existing notification. Details on the filtering procedure are included in attachment “WMP-Discovery2026-2028_DR_SPD_013- Q007Atch01.xlsx.” |  | 2025-08-11 | 2025-08-21 | 2025-08-21 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_013.zip
33 |  | SPD | 013 | SPD_013 | 008 | No | SPD_013_Q008 | Provide an updated version of “WMP-Discovery2026-2028_DR_SPD_001-Q016Atch02.xlsx” which includes data from 2020-2024. a. Include one additional column which includes the creation date of original tag. b. Include one additional column which includes the due date of the original tag. c. Include one additional column which includes the priority of the original tag. d. Include one additional column which includes the FDA of the original tag. If the tag has additional FDAs, include these FDAs in a second additional column. i. If in all cases, the FDAs matches the FDA in “WMP-Discovery2026- 2028_DR_SPD_001-Q019Atch01.xlsx” confirm this in the response, and this column may be omitted. | Please see attachment “WMP-Discovery2026-2028_DR_SPD_013-Q08Atch01.xlsx”, which includes the requested data for subparts (a) through (d) for the years 2020-2024. |  | 2025-08-11 | 2025-08-28 | 2025-08-28 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_013.zip
33 |  | SPD | 013 | SPD_013 | 009 | No | SPD_013_Q009 | Provide an updated version of “WMP-Discovery2026-2028_DR_SPD_001-Q015Atch02.xlsx” which includes data from 2020-2024, matching the same format as Question 7. | Please see “WMP-Discovery2026-2028_DR_SPD_013-Q009Atch01.xlsx” containing 2020-2024 data that was generated using the same review process as “WMPDiscovery2026-2028_DR_SPD_001-Q015Atch02.xlsx”, with a greater reliance on manual review. Additional columns provided are: • Notification date (date the condition was identified). • Required end date (due date). • Priority. • Facility/Damage/Action |  | 2025-08-11 | 2025-08-28 | 2025-08-28 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_013.zip
33 |  | SPD | 013 | SPD_013 | 010 | No | SPD_013_Q010 | Provide an updated response to “WMP-Discovery2023-2025_DR_SPD_016-Q010” which includes the full year data for 2024, and January 1, 2025 through July 31, 2025. a. Provide the workpaper that is used to respond to this request in .xlsx format. | a. For Priorities B, E, F, and H, please see our response to part (a) of “WMPDiscovery2023-2025_DR_SPD_016-Q010.pdf”. Please note Priorities B/E/F/H have an additional cancel reason: “NCOA: All work found completed/resolved upon arrival in the field.” “Refer to table in data request response” as public versions of DR responses will have the initial question and response tables. |  | 2025-08-11 | 2025-08-28 | 2025-08-28 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_013.zip
33 |  | SPD | 013 | SPD_013 | 011 | No | SPD_013_Q011 | Provide copies and a list of all Priority X tags which were either reprioritized from the original assignment in the field or canceled in 2024 and in 2025 through July 31, 2025. The format should match the list and work orders from PG&E’s response to “WMPDiscovery2023- 2025_DR_SPD_014-Q006Atcho02CONF” and “WMP-Discovery2023- 2025_DR_SPD_014- Q006Atch03.xlsx.” In lieu of providing the list and copies of the work orders, PG&E may add columns to the submission of question 1e, which include the current priority (if applicable), reason for cancelation (if applicable), and the work order’s comments. | Please see attachment “WMP-Discovery2026-2028_DR_SPD_013-Q011Atch01CONF.xlsx” for the requested information.” Please note that this following data represents overhead Priority X notifications generated by inspections, consistent with the scope of PG&E’s response to “WMP-Discovery2023-2025_DR_SPD_016-Q010.pdf” PG&E will supplement this response to include all Priority X tags that were either reprioritized from the original assignment in the field or canceled in 2024 and in 2025 through July 31, 2025. |  | 2025-08-11 | 2025-08-28 | 2025-08-28 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_013.zip
33 |  | OEIS | 018 | OEIS_018 | 001 | No | OEIS_018_Q001 | In Data Request OEIS-P-WMP_2025-PG&E-001 Question 18, Energy Safety requested information on PG&E’s idle transmission lines. a. Provide the definition of “idle transmission lines” PG&E used to respond to this request. b. Explain what criteria differentiates “deenergized transmission lines,” “idle transmission lines,” and “abandoned transmission lines.” | a. We define “idle transmission lines” as sections of transmission circuits that are currently not serving transmission load or generation facilities. These can be either de-energized transmission line facilities or energized facilities at distribution voltages. Please note that the idle transmission lines discussed in Data Request OEIS-P-WMP_2025-PG&E-001 Question 18 did not include idle transmission lines that are energized at distribution voltage. b. The criteria are as follows: • Deenergized transmission lines are circuit sections that are intentionally out of service for operational reasons; • Idle transmission lines are circuit sections that are currently not serving transmission load or generation facilities, these can be either de-energized transmission line facilities or energized facilities at distribution voltages.; and • Abandoned transmission lines are idle transmission lines that have no foreseeable future use for load or generation. |  | 2025-08-12 | 2025-08-15 | 2025-08-15 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_018.zip |  |  |  | Grid Design, Operations, and Maintenance | 8.2.9.1
34 |  | OEIS | 019 | OEIS_019 | 001 | No | OEIS_019_Q001 | Regarding incorporating the FTI program into distribution routine patrol On page 38 of the 2026-2028 Response to Revision Notice, PG&E states “Elevated inspections in those identified high-risk areas, such as what was previously performed in FTI, will continue through the Distribution Routine and Distribution Hazard Patrol programs.” a. Provide PG&E’s definition of “elevated inspections.” b. What will the minimum qualifications be for an arborist performing “elevated inspections”? (e.g., Tree Risk Assessment Qualified [TRAQ]) c. Will “elevated inspections” under the Distribution Routine and Distribution Hazard Patrol programs include Level 2, 360-degree inspections of all strike trees in identified high-risk areas? i. If not, does PG&E plan to provide guidance to inspectors on when to perform Level 2, 360-degree inspections? d. Describe the differences between the procedure for non-elevated Distribution Routine inspections and the minimum level of elevated inspections PG&E is considering for Distribution Routine Patrol. e. Describe the differences between the procedure for non-elevated Distribution Hazard inspections and the minimum level of elevated inspections PG&E is considering for Distribution Hazard Patrol. | PG&E is still in Phase 1 of the process of incorporating FTI work in our Routine and Hazard Patrols; we are gathering data and conducting analyses to inform the scope of the Routine Patrol inspections, including defining the scope and implementation of “elevated inspections.” Per Table PG&E-RN-PGE-26-09-01 “Program Consolidation Timeline and Milestones,” PG&E plans to finalize the scope of the Distribution Routine Patrol program by October 30, 2025. At that time, we will answer the above questions regarding “elevated inspections". |  | 2025-08-19 |  | 2025-08-22 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_019.zip
34 |  | OEIS | 020 | OEIS_020 | 001 | No | OEIS_020_Q001 | Regarding objective verification that hazard trees or tree parts will strike infrastructure Across the industry, utility vegetation management pre-inspectors may only perform an “eyeball” estimate of strike potential and then prescribe hazard tree mitigation work. Laser rangefinders and other digital and analog tools provide potentially more accurate and precise objective measures of tree distance and height.1 a. Describe how PG&E uses measurement tools (e.g., rangefinders) to assess whether a tree or tree part will strike infrastructure. In doing so, discuss: i. Tools that pre-inspectors use to measure tree or tree part height, and distance from infrastructure. ii. Tools that auditors use to measure tree or tree part height, and distance from infrastructure. iii. Tools that tree crew workers use to measure tree or tree part height, and distance from infrastructure. iv. Onboarding and refresher training PG&E or PG&E contractors provide on best management practices for using height and distance measurement tools. b. Prior to hazard tree mitigation, do quality assurance (QA) auditors, quality control (QC) auditors, and/or tree crews use measurement tools to verify that a pre-inspector’s measurements are correct (i.e., a tree or tree part will likely strike electrical infrastructure if it fails)? i. If yes, indicate which worker type performs the measurement verification: QA auditors, QC auditors, or tree crews. ii. If yes, does measurement verification occur for all trees or tree parts with fall-in potential that a pre-inspector lists for work? 1. If no, provide examples of: a) When verification will occur. b) When verification will not occur. iii. If no, indicate how PG&E ensures it only mitigates trees and tree parts whose height or length is such that the tree or tree part would contact electrical infrastructure if it failed.1 Martin, A.J.F., Accuracy and Precision in Urban Forestry Tools for Estimating Total Tree Height, Published November 2022, URL: (https://auf.isa-arbor.com/content/48/6/319). | a. i. Vegetation Management Inspectors (VMI) and Senior Vegetation Management Inspectors (SVMI) use rangefinders to measure the height of the tree, length of tree part and the distance to facility. They also may use the stick method to estimate the height of the tree using basic geometry as a backup method if a rangefinder is unavailable or unable to be used. ii. Vegetation Management Quality Control/Auditors (VMQC/VMQA) use rangefinders to measure tree or tree part height, and distance from infrastructure. iii. Tree crews are not required to use rangefinders or analog measuring tools before conducting their work. iv. As part of the onboarding, VMI and SVMI must take VEGM-180 WBT which provides a brief overview of how to utilize the stick method when a rangefinder is unavailable or unable to be used. Additionally, the VEGM-0500 Instructor-Led Training course provides in-field training on how to utilize rangefinders to identify if a tree or tree part has potential to reach a facility. These methods are then reinforced in the VEGM-0510 Instructor-Led Training refresher course. These PG&E training resources are made available to external VMIs for delivery by the contract company if they choose to use them. b. No, quality assurance (QA) auditors, quality control (QC) auditors, and/or tree crews do not use measurement tools to verify that a pre-inspector’s measurements are correct. i. N/A ii. N/A iii. Quality Auditors (VMQC/VMQA) do not verify whether inspectors’ measurements are correct. Quality Auditors verify that all fall-in trees requiring mitigation within the annual maintenance cycle are mitigated and/or prescribed for work. During the quality assessment, auditors will use the aforementioned measurement tools to identify fall-in trees requiring mitigation within the annual maintenance cycle that were not previously prescribed/and or mitigated by VM operations. Tree crews do not use measurement tools to verify whether inspectors’ measurements are correct prior to hazard tree mitigation. PG&E ensures it only mitigates trees and tree parts whose height or length is such that the tree or tree part would contact electrical infrastructure if it failed, via its inspection process. All inspectors are provided with rangefinders to capture tree heights and distances to infrastructure. They also use the stick method when a rangefinder is unavailable or unable to be used. In addition to available tools, inspectors follow a set scope of work which outlines conditions which constitute prescribing work (i.e. dead, dying or diseased trees which can impact the facilities). PG&E ensures the quality of its inspections through various means, including local auditing of work prescribed and the use of a structured QA/QC program. |  | 2025-08-22 |  | 2025-08-27 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_020.zip
34 |  | OEIS | 020 | OEIS_020 | 002 | No | OEIS_020_Q002 | Regarding PG&E’s Pole Clearing Program targets On page 368 of its 2026-2028 Base WMP R1, PG&E provides quantitative targets for its vegetation inspection and vegetation management programs in Table 9-1. For targets “Pole Clearing Program – Compliance” and “Pole Clearing Program – Risk Reduction”, column “% HFTD Covered in 2026,” in Table 9-1 shows a value of 4%. a. Provide the equation PG&E used to calculate the “% HFTD Covered in 2026” column for its Pole Clearing Program – Compliance target. i. If PG&E used a different equation than dividing the number of poles in the HFTD that are required to be cleared under PRC 4292 that PG&E projects to clear in 2026 by the total number of poles in the HFTD that are required to be cleared under PRC 4292, provide an updated value for the “% HFTD Covered in 2026” column using this equation. b. Provide the equation PG&E used to calculate the “% HFTD Covered in 2026” column for its Pole Clearing Program – Risk Reduction target. ii. If PG&E used a different equation than dividing the number of poles exempt from PRC 4292 in HFTD that PG&E projects to clear in 2026 by the total number of poles in HFTD that are exempt from PRC 4292, provide an updated value for the “% HFTD Covered in 2026” column using this equation. | Please note that the responses below are in reference to Table 9-2 and not Table 9-1. a. The equation used to calculate the “% HFTD Covered in 2026” for Pole Clearing Program – Compliance target is as follows: The quantity of subject poles for the Pole Clearing Program – Compliance in HFTD in 2025 divided by the total inventory of HFTD poles in 2025. These numbers fluctuate and numbers used were a snapshot as of April 2025. i. If PG&E were to recalculate this percentage using the suggested equation (number of poles in the HFTD that are required to be cleared under PRC 4292 that PG&E projects to clear in 2026 divided by the total number of poles in the HFTD that are required to be cleared under PRC 4292), the % HFTD Covered in 2026 is 100%. Please note, PG&E’s WMP target for VM-02C Pole Clearing - Compliance includes PRC 4292 poles inside and outside of HFTD. This definition in the above question represents only HFTD, which is a subset of the WMP target. Further, please note that the 2026 targets reported in Table 9-2 are estimates based on the 2025 pole population. b. The equation used to calculate the “% HFTD Covered in 2026” for Pole Clearing Program – Risk Reduction target is as follows: The quantity of subject poles for the Pole Clearing Program – Risk Reduction in HFTD in 2025 divided by the total inventory of HFTD poles in 2025. These numbers fluctuate and numbers used were a snapshot as of April 2025. i. If PG&E were to recalculate this percentage using the suggested equation (number of poles exempt from PRC 4292 in HFTD that PG&E projects to clear in 2026 divided by the total number of poles in HFTD that are exempt from PRC 4292), the % HFTD Covered in 2026 is ~4%. “Total number of poles in HFTD that are exempt from PRC 4292” was interpreted as the total inventory of HFTD poles less the total number of poles in the HFTD that are required to be cleared under PRC 4292. Please note, PG&E’s WMP target for VM-02R Pole Clearing – Risk Reduction includes poles inside and outside of HFTD. The definition in the above question represents only HFTD, which is a subset of the WMP target. Further, please note that the 2026 targets reported in Table 9-2 are estimates based on the 2025 pole population. |  | 2025-08-22 |  | 2025-08-29 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_020.zip
34 |  | OEIS | 019 | OEIS_019 | 002 | No | OEIS_019_Q002 | Regarding 2024 aerial inspection findings In response to OEIS_005-Q001, PG&E stated that it performed 216,796 aerial inspections in 2024. a. Provide the number of level 1 work orders and the number of level 2 work orders in the HFRA/HFTD that resulted from distribution aerial inspections in 2024. | Table 1: Number of Work Orders from 2024 Distribution Aerial Inspections6 in HFTD-HFRA Notes: 1. Level 1 work orders are A priority notifications including notifications identified in the field. 2. Level 2 work orders are X, B, E, or H priority notifications. 3. Excludes work orders created to document an inspection access issue (“CGI” notifications). These work orders do not document maintenance activity. 4. Includes work order categories reported in QDR responses (major work categories 17, BH, 95, IF) 5. Includes work order categories reported in QDR responses (major work categories 07, 2A, KA, GA). 6. Aerial Inspections are understood to be inspections planned and executed in HFTD-HFRA to meet commitments described in WMP 2023-2025 Section 8.1.3.2.7 in 2024. “Refer to table in data request response” as public versions of DR responses will have the initial question and response tables. |  | 2025-08-19 |  | 2025-08-27 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_019.zip
31 |  | SPD | 010 | SPD_010 | 002Supp01 |  | SPD_010_Q002Supp01 | On July 19 2025, SPD met with PG&E to discuss the WDRM v.4 model. PG&E informed SPD that it is developing a means of mapping CPZ across WDRM v.2, v.3 and v.4. This was a clarification upon PG&E’s third supplemental response to SPD-PGE-WMP2026-006 where in response to Question 1a. it stated “The methodology and tooling for relating circuit segments between model versions and explaining the change is in the process of being matured.” a. Provide SPD with an update to WMP-Discovery2026-2028_DR_SPD_006-Q001Supp03Atch01.xlsx. This updated dataset must include every circuit segment listed in the Circuit Segment Name field in the Primary spreadsheet. b. PG&E must provide the updated dataset by filling out Circuit Segment Change Tracker.xlsx workbook that is attached to this data request. i. If Explanation for Change v3-v4 or Explanation for Change v2-v3 lists "merge" or "split/merge", and PG&E merged more than two circuit segments to create a “new” circuit segment, then PG&E should expand the number of fields in order for SPD to properly track the changes that were made across the risk models. c. Provide SPD with the GIS datasets associated with WDRM v.2 and WDRM v.3 that at a minimum include the circuit segment names, coordinates, shapefiles and any other spatial data that was included in previous WMP submissions to Energy Safety that used these two risk models. This should be equivalent to PG&E’s response to CalAdvocates_041-Q003 for WDRM v.4 | ANSWER 002 SUPPLEMENTAL 01 SENT – , 2025 c. Please see attachment “WMP-Discovery2026-2028_DR_SPD_010- Q002Supp01Atch01CONF.zip” for the WDRM v2 GIS dataset. There are two small discrepancies to be aware of in the WDRM v2 GDB file. i. CPZ DIABLO CANYON 1101CB is not present in the GIS dataset even though it was an HFTD CPZ. This CPZ had only underground conductors, no overhead conductor risk value, and was ranked 3,635 out of 3,635 CPZs. Hence, it was filtered out and was not included in the gdb file. ii. CPZ ALLEGHENY 11011101/2 appears twice in the original WDRM v2 dataset as two switchable configurations existed, and both were modeled for risk. However, when the GIS dataset was built only the higher ranked configuration was included. This is a very minor discrepancy as both configurations were less than 150 ft in length, and they were ranked 2,977 and 3,124 out of 3,635 CPZs. Therefore, neither configuration was under any consideration for Undergrounding nor System Hardening projects. ANSWER 002 As discussed via email, PG&E will be providing: c. Please see attachment “WMP-Discovery2026-2028_DR_SPD_010-Q002Atch01CONF.zip” for the requested WDRM v3 risk GIS dataset. We are in the process of transforming the WDRM v2 risk dataset into a GIS file format and will provide the dataset in a future response. |  | 2025-07-30 |  | 2025-07-30 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_010.zip
33 |  | SPD | 012 | SPD_012 | 001Supp01 |  | SPD_012_Q001Supp01 | In its response to Question 2 of SPD-PGE-WMP2026-008, PG&E stated that it cannot provide SPD with the offline ICE 2.0 model it used to generate values in the Compliance Filing submitted to A.25-05-009 on June 20 2025. PG&E states in its response that the $/CMI values may also be generated through the online ICE 2.0 calculator using the inputs provided in AppendixB_ICE10 to ICE20 Input Comparison.xlsx file of the Compliance Filing. SPD understands that these inputs from AppendixB_ICE10 to ICE20 Input Comparison.xlsx represent PG&E’s entire service territory. In its response to Question 1 of SPD-PGE-WMP2026-011, PG&E stated the following: “Kindly note that the values for the following categories remain consistent across HFTD and NonHFTD classifications, including HFTD Tier 2 and 3, Non-HFTD with EPSS, and Non-HFTD without EPSS: • Residential BUG; • Residential Work From Home; • Non-Residential Manufacturing; • Non-Residential Health and Social; • Non-Residential Advanced Warning; • SAIDI; and • SAIFI. This approach ensures that PG&E utilizes system-level estimates with greater statistical reliability, as opposed to granular segments that lack sufficient sample sizes. It also aligns with the methodology used in the 2027 GRC and maintains consistency with ICE 1.0.” This is not what SPD was requesting, and so SPD is sending another data request. a. Complete the attached Excel workbook ICE 2.0 Inputs.xlsx. Follow the Instructions spreadsheet to complete the By HFTD and With EPSS spreadsheets. b. In the By HFTD spreadsheet, PG&E must comply with the following requirement: the fields in the spreadsheet must be filled out with information relevant to the HFTD or Non-HFTD, respectively. c. In the With EPSS spreadsheet, PG&E must comply with the following requirement: the spreadsheet must be filled out with information relevant to Tier 3, Tier 2, Non-HFTD with EPSS and Non-HFTD without EPSS, respectively. | PG&E objects to this request because it is not related to the WMP proceeding and exceeds the scope of that proceeding. This request would be more appropriately served as non-case discovery or in a different regulatory proceeding. Notwithstanding and without waiving this objection, PG&E responds as follows. Please see attachment “WMP-Discovery2026-2028_DR_SPD_012-Q001Supp01Atch01 (ICE 2.0 Inputs 8.19).xlsx”. Please note, the data that is being provided in this response is not inclusive of the data utilized to calculate Cost-Benefit Ratios in our 2026-2028 Base Wildfire Mitigation Plan. We are providing this information as requested; however, we do not utilize this data to inform our WMP or RAMP filings. Notwithstanding the information provided with this response, PG&E continues to have concerns about estimating the reliability benefits on a granular geographic basis using the ICE calculator. For example, doing so could lead to underestimating the reliability benefits from improving service to disadvantaged and vulnerable communities. Additionally, the data and percentages presented in the attached workbook are compiled from multiple sources with contextual details provided in the footnotes. Due to the evolving nature of risk and ongoing data collection efforts—including for granular customer-level information used by ICE 2.0 as well as expected updates to the ICE 2.0 Calculator—all results should be interpreted with caution. ANSWER 001 Please see attachment “WMP-Discovery2026-2028_DR_SPD_012-Q001Atch01 (ICE 2.0 Inputs 8.8).xlsx”. |  | 2025-08-13 |  | 2025-08-22 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_012.zip
33 |  | SPD | 013 | SPD_013 | 001Supp01 |  | SPD_013_Q001Supp01 | The following questions relate to “WMP-Discovery2026-2028_DR_SPD_001-Q019Atch01.xlsx”: a. Outage ID (column Q) has values in Row 40776 to 40783 as “1.” Correct if necessary. b. There are many blanks in Column B. Of 106,425 values, 71,1151 are blank. Explain why the values are blank. Correct if necessary. c. Explain why 6680 rows in Column O are blank, “false” or “1” – correct if necessary. d. Add a new column to the data set which includes the Facility Damage Action (FDA) for each tag. If the tag has more than one FDA, each additional FDA should be added in a second column. e. Create a data set with the same data as the “WMP-Discovery2026-2028_DR_SPD_001- Q019Atch01.xlsx” (including the FDA information as requested in question 1d) but with Priority X data, including the FDAs. | e. Please see attachment “WMP-Discovery2026-2028_DR_SPD_013-Q001Supp01Atch01.xlsx” for Priority X tag data in the same format as that provided in “WMP-Discovery2026-2028_DR_SPD_001- Q019Atch01.xlsx”. ANSWER 001 a. To be delivered on Thursday, August 28, 2025. b. The Asset Type column has been corrected. This omission was the result of inadvertent error and all notifications now have their asset type filled. Please see “WMP-Discovery2026-2028_DR_SPD_013-Q001Atch01.xlsx.” c. The Circuit ID column has been corrected. There are still 298 notifications with an unknown Circuit ID. This can occur when: (1) the equipment information for a notification is incorrect or missing; or (2) the circuit information for an equipment is missing. Please see “WMP-Discovery2026-2028_DR_SPD_013-Q001Atch01.xlsx.” d. The FDA information is in columns [Primary_FDA] and [Additional_FDAs_If_ Applicable]. Please see “WMP-Discovery2026-2028_DR_SPD_013-Q001Atch01.xlsx.” e. To be delivered on Thursday, August 28, 2025. |  | 2025-08-14 |  | 2025-08-21 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_013.zip
33 |  | SPD |  | SPD_013 | 001Supp02 |  | SPD_013_Q001Supp02 | The following questions relate to “WMP-Discovery2026-2028_DR_SPD_001- Q019Atch01.xlsx”: a. Outage ID (column Q) has values in Row 40776 to 40783 as “1.” Correct if necessary. b. There are many blanks in Column B. Of 106,425 values, 71,1151 are blank. Explain why the values are blank. Correct if necessary. c. Explain why 6680 rows in Column O are blank, “false” or “1” – correct if necessary. d. Add a new column to the data set which includes the Facility Damage Action (FDA) for each tag. If the tag has more than one FDA, each additional FDA should be added in a second column. e. Create a data set with the same data as the “WMP-Discovery2026- 2028_DR_SPD_001- Q019Atch01.xlsx” (including the FDA information as requested in question 1d) but with Priority X data, including the FDAs. | ANSWER 001 SUPPLEMENTAL 02 SENT – AUGUST 28, 2025 a. PG&E believes the “1” entries to be data entry errors made in the field. The “1” entry is not associated with an outage or other condition in PG&E’s systems. PG&E will supplement this response when the values in our system are updated. ANSWER 001 SUPPLEMENTAL 01 SENT – AUGUST 21, 2025 e. Please see attachment “WMP-Discovery2026-2028_DR_SPD_013-Q001Supp01Atch01.xlsx” for Priority X tag data in the same format as that provided in “WMP-Discovery2026-2028_DR_SPD_001- Q019Atch01.xlsx”. ANSWER 001 a. To be delivered on Thursday, August 28, 2025. b. The Asset Type column has been corrected. This omission was the result of inadvertent error and all notifications now have their asset type filled. Please see “WMP-Discovery2026-2028_DR_SPD_013-Q001Atch01.xlsx.” c. The Circuit ID column has been corrected. There are still 298 notifications with an unknown Circuit ID. This can occur when: (1) the equipment information for a notification is incorrect or missing; or (2) the circuit information for an equipment is missing. Please see “WMP-Discovery2026-2028_DR_SPD_013-Q001Atch01.xlsx.” d. The FDA information is in columns [Primary_FDA] and [Additional_FDAs_If_ Applicable]. Please see “WMP-Discovery2026-2028_DR_SPD_013- Q001Atch01.xlsx.” e. To be delivered on Thursday, August 28, 2025. |  | 2025-08-14 |  | 2025-08-28 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_013.zip
31 |  | SPD | 010 | SPD_010 | 002Supp02 |  | SPD_010_Q002Supp02 | On July 19 2025, SPD met with PG&E to discuss the WDRM v.4 model. PG&E informed SPD that it is developing a means of mapping CPZ across WDRM v.2, v.3 and v.4. This was a clarification upon PG&E’s third supplemental response to SPD-PGE-WMP2026- 006 where in response to Question 1a. it stated “The methodology and tooling for relating circuit segments between model versions and explaining the change is in the process of being matured.” a. Provide SPD with an update to WMP-Discovery2026-2028_DR_SPD_006- Q001Supp03Atch01.xlsx. This updated dataset must include every circuit segment listed in the Circuit Segment Name field in the Primary spreadsheet. b. PG&E must provide the updated dataset by filling out Circuit Segment Change Tracker.xlsx workbook that is attached to this data request. i. If Explanation for Change v3-v4 or Explanation for Change v2-v3 lists "merge" or "split/merge", and PG&E merged more than two circuit segments to create a “new” circuit segment, then PG&E should expand the number of fields in order for SPD to properly track the changes that were made across the risk models. c. Provide SPD with the GIS datasets associated with WDRM v.2 and WDRM v.3 that at a minimum include the circuit segment names, coordinates, shapefiles and any other spatial data that was included in previous WMP submissions to Energy Safety that used these two risk models. This should be equivalent to PG&E’s response to CalAdvocates_041-Q003 for WDRM v.4 | ANSWER 002 SUPPLEMENTAL 02 SENT – AUGUST 28, 2025 b. Please see attachment “WMP-Discovery2026-2028_DR_SPD_010- Q002Supp02Atch01.xlsx” for the WDRM v3 to WDRM v4 circuit segment change mapping. Please note that in the case of a “merge” or a “split”, where more than one circuit segment is contributing to a change, the rows have been expanded to include a row for each circuit segment involved in the change. Column definitions are provided in the first sheet in the attachment. WDRM v2 to WDRM v3 mapping is not provided as part of this response, which was agreed to by SPD during a meeting on August 6, 2025. The Risk and Data Analytics team will discuss the need for v2 to v3 mapping with SPD at a future meeting. ANSWER 002 SUPPLEMENTAL 01 SENT – JULY 30, 2025 c. Please see attachment “WMP-Discovery2026-2028_DR_SPD_010-Q002Supp01Atch01CONF.zip” for the WDRM v2 GIS dataset. There are two small discrepancies to be aware of in the WDRM v2 GDB file. i. CPZ DIABLO CANYON 1101CB is not present in the GIS dataset even though it was an HFTD CPZ. This CPZ had only underground conductors, no overhead conductor risk value, and was ranked 3,635 out of 3,635 CPZs. Hence, it was filtered out and was not included in the gdb file. ii. CPZ ALLEGHENY 11011101/2 appears twice in the original WDRM v2 dataset as two switchable configurations existed, and both were modeled for risk. However, when the GIS dataset was built only the higher ranked configuration was included. This is a very minor discrepancy as both configurations were less than 150 ft in length, and they were ranked 2,977 and 3,124 out of 3,635 CPZs. Therefore, neither configuration was under any consideration for Undergrounding nor System Hardening projects. ANSWER 002 As discussed via email, PG&E will be providing: c. Please see attachment “WMP-Discovery2026-2028_DR_SPD_010-Q002Atch01CONF.zip” for the requested WDRM v3 risk GIS dataset. We are in the process of transforming the WDRM v2 risk dataset into a GIS file format and will provide the dataset in a future response. |  | 2025-07-30 | 2025-08-28 | 2025-08-28 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_010.zip
36 |  | OEIS | 021 | OEIS_021 | 001 | No | OEIS_021_Q001 | Regarding Transmission Work Orders a. Provide the number of level 1 and 2 work orders created on PG&E’s transmission system in 2020, 2021, 2022, 2023 and 2024. b. Provide the number of level 1 and 2 work orders closed on PG&E’s transmission system in 2020, 2021, 2022, 2023, and 2024. c. Provide the number of transmission work orders that had due dates extended later than Dec 31, 2024, when PG&E aligned its internal required end dates of A, E, and F tags with the maximum allowable Rule 18 remediation timeframes for Level 1, 2 and 3 conditions in early 2023. | a. Level 1 and Level 2 findings are provided for 2020-2024 below, using the supporting dataset for 2025 Q2 QDR Table 2, Question 14. “Refer to table in data request response” as public versions of DR responses will have the initial question and response tables. |  | 2025-09-02 |  | 2025-09-08 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_021.zip
33 |  | SPD | SPD | SPD_013 | 002Rev01 |  | SPD_013_Q002Rev01 | “WMP-Discovery2026-2028_DR_SPD_001-Q019Atch01.xlsx” reports 5185 Priority As associated with “patrol inspections” or “detailed inspections” in 2023. However, PG&E’s response titled “WMP-Discovery2023-2025_DR_SPD_014-Q005Rev02Supp01.pdf” reports 1,419 Priority As created from patrols and detailed inspections. Additionally, “WildfireMitigationPlansDiscovery2023_DR_OEIS_023-Q001” appears to show a separate set of value of Level 1 (Priority As) from inspections. Explain the differences between the documents and correct as necessary. | “Refer to table in data request response” as public versions of DR responses will have the initial question and response tables. |  | 2025-08-11 |  | 2025-09-08 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_013.zip
31 |  | SPD | SPD | SPD_010 | 002Supp03 |  | SPD_010_Q002Supp03 | SUBJECT: DECISION TREE RESULTS BY CIRCUIT SEGMENT 2.0 (SPD-PGE-WMP2026-010) QUESTION 002 On July 19 2025, SPD met with PG&E to discuss the WDRM v.4 model. PG&E informed SPD that it is developing a means of mapping CPZ across WDRM v.2, v.3 and v.4. This was a clarification upon PG&E’s third supplemental response to SPD-PGE-WMP2026- 006 where in response to Question 1a. it stated “The methodology and tooling for relating circuit segments between model versions and explaining the change is in the process of being matured.” a. Provide SPD with an update to WMP-Discovery2026-2028_DR_SPD_006- Q001Supp03Atch01.xlsx. This updated dataset must include every circuit segment listed in the Circuit Segment Name field in the Primary spreadsheet. b. PG&E must provide the updated dataset by filling out Circuit Segment Change Tracker.xlsx workbook that is attached to this data request. i. If Explanation for Change v3-v4 or Explanation for Change v2-v3 lists "merge" or "split/merge", and PG&E merged more than two circuit segments to create a “new” circuit segment, then PG&E should expand the number of fields in order for SPD to properly track the changes that were made across the risk models. c. Provide SPD with the GIS datasets associated with WDRM v.2 and WDRM v.3 that at a minimum include the circuit segment names, coordinates, shapefiles and any other spatial data that was included in previous WMP submissions to Energy Safety that used these two risk models. This should be equivalent to PG&E’s response to CalAdvocates_041-Q003 for WDRM v.4 | ANSWER 002 SUPPLEMENTAL 03 SENT – SEPTEMBER 5, 2025 a. “WMP-Discovery2026-2028_DR_SPD_010_Q002Supp03Atch01.xlsx” contains all circuit segments in the snapshot for WDRM v4, the circuit segment from WDRM v3 from which they originate, the cause of the circuit segment name change, and the length of the WDRM v3 and WDRM v4 circuit segments. This file is an expansion of “WMP-Discovery2026-2028_DR_SPD_010_Q002Supp02Atch01.xlsx”. The only difference between “WMP-Discovery20262028_DR_SPD_010_Q002Supp03Atch01.xlsx” and “WMP-Discovery2026-2028_DR_SPD_010_Q002Supp02Atch01.xlsx” is the addition of 12 circuit segments which contained no assets that were present in the WDRM v3 circuit segment snapshot. These 12 circuit segments have an “Explanation for Change v3-v4” of “new construction”. ANSWER 002 SUPPLEMENTAL 02 SENT – AUGUST 28, 2025 b. Please see attachment “WMP-Discovery2026-2028_DR_SPD_010-Q002Supp02Atch01.xlsx” for the WDRM v3 to WDRM v4 circuit segment change mapping. Please note that in the case of a “merge” or a “split”, where more than one circuit segment is contributing to a change, the rows have been expanded to include a row for each circuit segment involved in the change. Column definitions are provided in the first sheet in the attachment. WDRM v2 to WDRM v3 mapping is not provided as part of this response, which was agreed to by SPD during a meeting on August 6, 2025. The Risk and Data Analytics team will discuss the need for v2 to v3 mapping with SPD at a future meeting. ANSWER 002 SUPPLEMENTAL 01 SENT – JULY 30, 2025 c. Please see attachment “WMP-Discovery2026-2028_DR_SPD_010- Q002Supp01Atch01CONF.zip” for the WDRM v2 GIS dataset. There are two small discrepancies to be aware of in the WDRM v2 GDB file. a. CPZ DIABLO CANYON 1101CB is not present in the GIS dataset even though it was an HFTD CPZ. This CPZ had only underground conductors, no overhead conductor risk value, and was ranked 3,635 out of 3,635 CPZs. Hence, it was filtered out and was not included in the gdb file. b. CPZ ALLEGHENY 11011101/2 appears twice in the original WDRM v2 dataset as two switchable configurations existed, and both were modeled for risk. However, when the GIS dataset was built only the higher ranked configuration was included. This is a very minor discrepancy as both configurations were less than 150 ft in length, and they were ranked 2,977 and 3,124 out of 3,635 CPZs. Therefore, neither configuration was under any consideration for Undergrounding nor System Hardening projects. ANSWER 002 As discussed via email, PG&E will be providing:c. Please see attachment “WMP-Discovery2026-2028_DR_SPD_010- Q002Atch01CONF.zip” for the requested WDRM v3 risk GIS dataset. We are in the process of transforming the WDRM v2 risk dataset into a GIS file format and will provide the dataset in a future response |  | 2025-07-30 | 2025-07-30 | 2025-09-05 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_010.zip
#N/A |  | SPD | SPD | SPD_014 | 001 | No | SPD_014_Q001 | In PG&E’s third supplemental response to Question 2 of SPD-PGE-WMP2026-010, PG&E provided SPD with WMP-Discovery2026-2028_DR_SPD_010_Q002Atch01Supp03.xlsx. On September 9, 2025, SPD met with PG&E to discuss various topics related to the mapping of CPZs from v3 to v4 of the WDRM model associated with the SPD-PGE-WMP2026-010 data request. PG&E explained that it used Conductor Asset ID to map the relationship between v3 CPZ and v4 CPZ. a. Provide a detailed explanation of what the Conductor Asset ID is. b. Provide a detailed explanation of how PG&E used the Conductor Asset ID to map the relationship between v3 CPZs and v4 CPZs. c. Provide an explanation for why PG&E decided to use the Conductor Asset ID to map the relationship between v3 CPZs and v4 CPZs. d. Could PG&E have used other spatial data to map the relationship between v3 CPZs and v4 CPZs? Explain what other spatial data could have achieved this result. i. If so, explain why PG&E did not chose to use those methods. ii. If not, explain why not. e. List which spatial datasets in PG&E’s possession currently include the Conductor Asset IDas a field. f. List which tabular datasets in PG&E’s possession currently include the Conductor Asset IDas a field. | a. Every asset in PG&E’s network is given a Global Unique Identifier, also referred to as a GUID or Global ID, in PG&E’s Electric Distribution Geographic Information System (EDGIS). These Global IDs serve as the primary identifiers for assets within PG&E’s network trace tables, which are structured datasets used to represent the connectivity and relationships between assets in EDGIS. Network trace tables help define network groups, such as circuit segments, by showing how assets are positioned relative to dynamic protection devices. Conductor Asset ID is this Global ID for each conductor in PG&E’s network. It represents a length of conductor with homogenous asset information. A Global ID is given to each length of conductor between two network nodes. A network node is any equipment that create a separation point along the conductor, for example, switches, transformers, and fuses. b. When comparing the circuit segment snapshots between WDRM v3 and WDRM v4, if a conductor global ID on one circuit segment in the WDRM v3 snapshot is on a different circuit segment in the WDRM v4 snapshot, we know one of the following is true: (1) the circuit segment in WDRM v4 was split from the circuit segment in WDRM v3, or (2) the circuit segment in WDRM v3 was merged into a circuit segment in WDRM v4. c. The conductor Global ID is how conductors are identified in PG&E’s network trace tables, which are fundamental to how circuit segments are defined. These network trace tables are dynamic datasets that are kept up to date by PG&E’s Asset Knowledge Management (AKM). The WDRM v3 and WDRM v4 circuit segments, were defined by taking a snapshot of the network trace tables on January 1, 2022, and January 1, 2023, respectively. This makes the conductor Global ID uniquely qualified at identifying where each conductor is in relation to its nearest upstream dynamic protection device when compared between the two snapshots. d. Network trace tables use an R-Tree structure to store asset connectivity information from EDGIS in tabular format. The tree level, order number, and branch concepts of R-Tree allow for the upstream and downstream relationship information between electric distribution assets to be determined from a relational query. Because conductor Global IDs are in these table, the mapping between circuit segment snapshots can be completed using relational comparisons as opposed to spatial comparisons. This approach yields greater accuracy and is less impacted by spatialmapping improvements. e. PG&E’s Electric Distribution Geographic Information System (EDGIS) is the source of Global IDs for all assets in PG&E’s distribution network. f. Conductor Global IDs are how conductors are identified in PG&Es electric network trace tables, which are fundamental to how network groups are defined and thus the unique identifiers in these tables are pervasive throughout PG&E electric distribution datasets. |  | 9/16/2025 |  | 2025-09-26 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_014.zip
38 |  | SPD | SPD | SPD_014 | 002 | No | SPD_014_Q002 | SPD pointed out some of the “merge” and “split” explanations for how a CPZ changed from WDRM v3 to WDRM v4 may be exhibiting odd results. For instance, ATASCADERO 1103A14, which was approximately 25.83 circuit miles long, was merged with a portion of ATASCADERO 1103A16, which was approximately 20.39. This resulted in a new CPZ name “ATASCADERO 1103635958”, which is approximately 25.70 circuit miles long, and the new length for ATASCADERO 1103A16, which is approximately 20.12 circuit miles long. In this example this means that the v3 CPZs accounted for 46.22 circuit miles but the v4 CPZs only accounted for 45.82 circuit miles. a. Explain the .40 circuit mile discrepancy between v3 and v4 in the relationship between the three CPZs discussed above. b. Provide a tabular dataset that shows how the circuit miles of each Conductor Asset IDaggregate up to the CPZs in WDRM v3 and WDRM v4. i. The dataset must show the length of each Conductor Asset ID. ii. The dataset must show how each Conductor Asset ID is associated with either ATASCADERO 1103A14 or ATASCADERO 1103A16 in WDRM v3. iii. The dataset must show how each Conductor Asset ID is associated with either ATASCADERO 1103635958 or ATASCADERO 1103A16 in WDRM v4. c. Provide a set of map screenshots that shows how the circuit miles of each ConductorAsset ID aggregate up to the CPZs in WDRM v3 and WDRM v4. i. The screenshots must show how each Conductor Asset ID is associated with either ATASCADERO 1103A14 or ATASCADERO 1103A16 in WDRM v3. ii. The screenshots must show how each Conductor Asset ID is associated with either ATASCADERO 1103635958 or ATASCADERO 1103A16 in WDRM v4. d. Provide a copy of the spatial dataset that PG&E used to generate the screenshots in answer Question 2c. i. Include any spatial tools that PG&E used to generate the screenshots in answer Question 2c. | a. The following is an explanation of the changes in conductor length between ATASCADERO 1103A14 and ATASCADERO 1103A16 in WDRM v3 and ATASCADERO 1103A16 and ATASCADERO 1103635958 in WDRM v4. All conductor data related to WDRM v3 and WDRM v4 circuit segments is based on the measured straight-line geometry of conductors in EDGIS as they were on January 1, 2022 (WDRM v3) and January 1, 2023 (WDRM v4). The length of a conductor may be increased or reduced for various reasons. One reason is to accommodate changes in field equipment, such as switches, support structures, or transformers. Another is to reflect updates of the equipment’s location within EDGIS. When device locations are revised, the conductor geometry in EDGIS is adjusted to better reflect the updated placement, improving alignment between field conditions and system records. • Five primary overhead conductors, accounting for 0.269 miles, were removed from ATASCADERO 1103A14 between WDRM v3 and WDRM v4. The Global ID of these conductors are as follows: o {3DC2C429-71BD-4654-AC1B-1B71DCE04210} o {42A1AF79-EEED-41C0-B61B-F4D14631B0C4} o {84430C0D-1AA5-4AEC-849E-285B9512C41E} o {DB2A672D-DAE9-467B-8D28-9C388EC3126E} o {DBB412F1-243F-4392-A569-42F442ABD525} • Three secondary conductors, accounting for 0.068 miles, were removed from ATASCADERO 1103A14, between WDRM v3 and WDRM v4. The Global ID of these conductors are as follows: o {511E15ED-0526-40B6-BB21-2CB0C5F1E06D} o {BF18C905-CCE7-4774-AC80-752BE9DFEABC} o {CF65B065-4D20-4DC5-9663-54B5325FFA7C} • Three primary overhead conductors, accounting for 0.131 miles, were removed from ATASCADERO 1103A16 between WDRM v3 and WDRM v4. The Global ID of these conductors are as follows: o {5FF72B2F-1CE8-49FB-888A-85DBDEAF7756} o {B1123E4F-1AFE-4190-AE5C-1A234EC9CE7A} o {B335AB9D-F02D-4699-B509-4AA1670BFEEB} • Seven primary overhead conductors, accounting for 0.030 miles, were newly created on ATASCADERO 1103A16 between WDRM v3 and WDRM v4. The Global ID of these conductors are as follows: o {D750FC0A-9E95-468F-A6CA-7A034B325BEA o {B3A806BA-10E6-4590-934A-BCA3470E8DE5} o {2C99633D-0CDF-4A1E-9D1C-92112A642FC0} o {1E2464C3-5DBB-4421-9059-9D30A59727F7} o {21F12B7B-8AF2-42BB-833A-9E9EF16BB5FD} o {02303DC2-1341-4777-8EA8-6F5D6F66DD9A} o {49BBAEBE-D13F-479F-8EE5-149A7522E288} • Five primary overhead conductors, accounting for 0.013 miles, were newly created on ATASCADERO 1103635958 between WDRM v3 and WDRM v4. The Global ID of these conductors are as follows: o {6AF3F919-3ED4-4744-9D98-B2C3C675A1EF} o {E07CC6D3-80C3-4176-BB38-91F837828A6B} o {94EBAE7B-AC59-499B-9606-3E1221ECB1D0} o {DE96172E-29A6-477D-99C3-FAAC9480A555} o {14511975-E23B-4BB7-8B45-479E06B1E351} • Four primary overhead conductors that remained on ATASCADERO 1103A16 between WDRM v3 and WDRM v4 had a combined reduction in length of 0.021 miles. The Global ID of these conductors are as follows: o {3A7205C7-BAAE-4ED3-B65D-10637B6DA480} o {69833F1D-9AFE-4B49-A583-FDE2B07DA989} o {C20E99B1-54E5-422E-B826-C6CB1C672484} o {60B7C08D-DB37-49FD-94EE-5EA8F1E60EE8} • Two primary overhead conductors that remained on ATASCADERO 1103A16 between WDRM v3 and WDRM v4 had a combined increase in length of 0.004 miles. The Global ID of these conductors are as follows: o {611DB825-5983-41CF-9C1D-23C9C425103A} o {A375A45D-5662-44DA-B7D2-EE7046344AA5} • Eight primary overhead conductors that moved from ATASCADERO 1103A14 to ATASCADERO 1103635958 between WDRM v3 and WDRM v4 had a combined reduction in length of 0.028 miles. The Global ID of these conductors are as follows: o {A480E556-FFB1-478E-B0C8-24E27BC49708} o {94B541F4-AA5B-4D89-BE54-9B2893CBA474} o {3EE50327-658A-42D1-BE9B-FCC986EEA99E} o {013EE909-8EFE-485A-86F5-5D26AAFAC508} o {35737FDE-CA94-47E3-87FC-463533D110EC} o {15B59632-CCF8-4ECF-BC55-9CE25180BDEB} o {D7F10146-F208-4F51-A58E-57595B8408B5} o {1BC1C169-9B16-4CE3-A9AE-4493A07A3BD4} • Five primary overhead conductors that moved from ATASCADERO 1103A14 to ATASCADERO 1103635958 between WDRM v3 and WDRM v4 had a combined increase in length of 0.068 miles. The Global ID of these conductors are as follows: o {AEB4C189-3B67-4A2A-BCA7-34C3EAB62B9F} o {FE360D22-C8E7-4A80-86BC-DAAEB0203EED} o {EA918A81-7C9B-49FA-9857-6B1121437271} o {7607CBAD-71D0-45F6-8307-E8F1F28DC714} o {DBBCDC89-BBEC-488E-B555-5CABD51E3895} • One secondary overhead conductor that moved from ATASCADERO 1103A14 to ATASCADERO 1103635958 between WDRM v3 and WDRM v4 had an increase in length of 0.002 miles. The Global ID of this conductor is as follows: o {40FDEF55-7133-44B9-9882-913F54F2FA7B} b. Please see attachment “WMP-Discovery2026-2028_DR_SPD_014-Q002Atch01.xlsx” for the requested information. If the v3_conductor_global_id is blank, then the conductor did not exist in the WDRM v3 circuit segments. If the v4_conductor_global_id is blank, then the conductor did not exist in the WDRM v4 circuit segments. |  | 2025-09-16 |  | 2025-09-26 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_014.zip
38 |  | SPD | SPD | SPD_014 | 003 | No | SPD_014_Q003 | In each Quarterly Data Report (QDR), PG&E provides a geodatabase labeled PGE_Year_QX.gdb. Within these quarterly submitted geodatabases, there is a File Geodatabase Feature Dataset labeled PGE_Initiative. a. Provide a geodatabase that combines all of the PGE_Initiative File Geodatabase Feature Datasets from 2020-2025. i. The resulting File Geodatabase Feature Dataset should be labeled PGE_Initiative_All. ii. PGE_Initiative_All must allow for a user to be able to map all WMP mitigations that were implemented between 2020-2025. iii. PGE_Initiative_All must retain the same data fields that are found within a PGE_Initiative File Geodatabase Feature Dataset. | PG&E met with SPD on October 1, 2025, where it was agreed that SPD could internally review the Spatial Quarterly Data Report data available to perform analysis against. PG&E has agreed to answer additional questions that may arise and to meet with SPD for their analysis. |  | 2025-09-16 |  | 2025-10-08 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_014.zip
38 |  | SPD | SPD | SPD_014 | 004 | No | SPD_014_Q004 | Regarding SPD-PGE-WMP2026-010 Question 2(b) that requests the mapping of v2 to v3 circuit segments, SPD understands that it is PG&E's position that it does not have all the data necessary to automate this mapping process. PG&E has stated to SPD that it would require a manual approach that is different from what PG&E did to complete the mapping of v3 to v4 circuit segments. According to PG&E this manual approach would require additional SME resources. a. Clearly explain each step taken to complete the mapping of v3 to v4 circuit segments that was submitted as PG&E’s third supplemental response to SPD-PGEWMP2026-010 Question 2(b). i. What datasets were used to complete each step in Question 4a. b. What step(s) from Question 4a. is PG&E unable to complete in the mapping of v2 to v3 CPZs i. What datasets are not available for PG&E to complete the mapping of v2 to v3CPZs. ii. Explain why those datasets do not exist. iii. Explain the steps PG&E is taking to make sure those datasets are available for mapping CPZ across future risk model transitions. iv. What SME resources would be needed to recreate the datasets that are needed to complete the mapping of v2 to v3 CPZs. | a. The mapping tool uses several Circuit Segment (CS) attributes to determine how a WDRM v3 CS maps to a WDRM v4 CS, including: • CS Name • Circuit Feeder Name • Interrupting Device Global ID • CS Total Length (Primary & Secondary, Overhead & Underground) • CS Total Overhead Conductor Length (Primary & Secondary Overhead) • CS to Conductor Assets assignments. The mapping tool uses various logical checks on these attributes to determine if a CS is the same in both versions and, if not, what type of change has occurred. For instance, a CS is determined to be the same in both versions if: • CS Names are identical • Circuit Feeder Names are identical • Interrupting Device IDs are identical • CS Total Length has changed by less than 1% • All Conductor Asset IDs are identical. i. The input datasets to the mapping tool are the: • WDRM v3 Circuit Segment Statistics table o circuit_segment_statistics_20220101 • WDRM v3 Circuit Segment to Conductor Mapping o 20220101_conductor_to_cs_mapping • WDRM v4 Circuit Segment Statistics table o circuit_segment_statistics_20230101 • WDRM v4 Circuit Segment to Conductor Mapping o all_assets_to_circuit_segment_lookup_snapshot_2023_01_18_00_46 _30.parquet b. The WDRM v2 to WDRM v3 cannot use the mapping tool i. Data missing for WDRM v2: • WDRM v2 was built only for CS within HFTD, not the entire service territory like WDRM v3. Any non-HFTD WDRM v3 CS would therefore be classified as new using the tool. • WDRM v2 was only modeled against primary overhead conductors. o No secondary overhead conductor data was collected or archived. o No primary or secondary underground data was collected or archived. ii. WDRM v2 was PG&E’s first internal iteration of the WDRM. The model was developed in 2020 for the purpose of guiding the Enhanced Vegetation Management (EVM) and overhead System Hardening mitigation programs to the highest wildfire risk locations in HFTD. The decision to use circuit segments arose during the development process to address limitations in the historical event data and was not understood at that time to be a requirement for future model versions. Thus, the missing data was not required for the simple single event probability model approach used for producing WDRM v2 risk values. Therefore, the data was not collected at that time. iii. All collected CS attribute data used for WDRM v3 and v4 development havebeen archived. In addition, just prior to WDRM v4 final development began, a process was implemented to collect and archive snapshots of the current CS attribute data on our Foundry platform on the first of each month. iv. To create a WDRM v2 to v3 mapping, it is anticipated that much of the mapping work would require manual visual comparison of v2 and v3 (HFTD only) CS primary overhead conductor configurations. A gross comparison could be built to programmatically verify that identical v2 and v3 CS names have the same primary overhead conductor lengths to create an initial list of CS that most likely remained the same. All other CS would require a manual visual comparison to determine v3 CS configuration(s) against v2 CS configuration(s). A limited number of these comparisons were performed during WDRM v3 validation and proved to be very time consuming to perform. Given this experience we estimate that a complete WDRM v2 to v3 mapping would consume 2 full-time SMEs for at least 2 to 3 months. |  | 2025-09-16 |  | 2025-09-26 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_014.zip
#N/A |  | SPD | SPD | SPD_014 | 002Supp01 | No | SPD_014_Q002Supp01 | SPD pointed out some of the “merge” and “split” explanations for how a CPZ changed from WDRM v3 to WDRM v4 may be exhibiting odd results. For instance, ATASCADERO 1103A14, which was approximately 25.83 circuit miles long, was merged with a portion of ATASCADERO 1103A16, which was approximately 20.39. This resulted in a new CPZ name “ATASCADERO 1103635958”, which is approximately 25.70 circuit miles long, and the new length for ATASCADERO 1103A16, which is approximately 20.12 circuit miles long. In this example this means that the v3 CPZs accounted for 46.22 circuit miles but the v4 CPZs only accounted for 45.82 circuit miles. a. Explain the .40 circuit mile discrepancy between v3 and v4 in the relationship between the three CPZs discussed above. b. Provide a tabular dataset that shows how the circuit miles of each Conductor Asset IDaggregate up to the CPZs in WDRM v3 and WDRM v4. i. The dataset must show the length of each Conductor Asset ID. ii. The dataset must show how each Conductor Asset ID is associated with either ATASCADERO 1103A14 or ATASCADERO 1103A16 in WDRM v3. iii. The dataset must show how each Conductor Asset ID is associated with either ATASCADERO 1103635958 or ATASCADERO 1103A16 in WDRM v4. c. Provide a set of map screenshots that shows how the circuit miles of each ConductorAsset ID aggregate up to the CPZs in WDRM v3 and WDRM v4. i. The screenshots must show how each Conductor Asset ID is associated with either ATASCADERO 1103A14 or ATASCADERO 1103A16 in WDRM v3. ii. The screenshots must show how each Conductor Asset ID is associated with either ATASCADERO 1103635958 or ATASCADERO 1103A16 in WDRM v4. d. Provide a copy of the spatial dataset that PG&E used to generate the screenshots in answer Question 2c. i. Include any spatial tools that PG&E used to generate the screenshots in answer Question 2c. | Please see “WMP-Discovery2026-2028_DR_SPD_014-Q002Supp01Atch01.zip” for a spatial dataset depicting the overhead conductors for ATASCADERO 1103A14 and ATASCADERO 1103A16 in WDRM v3 and ATASCADERO 1103635958 and ATASCADERO 1103A16 in WDRM v4. |  | 9/16/2025 | 2025-09-30 | 2025-09-30 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_014.zip
38 |  | SPD | SPD | SPD_014 | 002Supp02 | No | SPD_014_Q002Supp02 | SPD pointed out some of the “merge” and “split” explanations for how a CPZ changed from WDRM v3 to WDRM v4 may be exhibiting odd results. For instance, ATASCADERO 1103A14, which was approximately 25.83 circuit miles long, was merged with a portion of ATASCADERO 1103A16, which was approximately 20.39. This resulted in a new CPZ name “ATASCADERO 1103635958”, which is approximately 25.70 circuit miles long, and the new length for ATASCADERO 1103A16, which is approximately 20.12 circuit miles long. In this example this means that the v3 CPZs accounted for 46.22 circuit miles but the v4 CPZs only accounted for 45.82 circuit miles. a. Explain the .40 circuit mile discrepancy between v3 and v4 in the relationship between the three CPZs discussed above. b. Provide a tabular dataset that shows how the circuit miles of each Conductor Asset ID aggregate up to the CPZs in WDRM v3 and WDRM v4. i. The dataset must show the length of each Conductor Asset ID. ii. The dataset must show how each Conductor Asset ID is associated with either ATASCADERO 1103A14 or ATASCADERO 1103A16 in WDRM v3. iii. The dataset must show how each Conductor Asset ID is associated with either ATASCADERO 1103635958 or ATASCADERO 1103A16 in WDRM v4. c. Provide a set of map screenshots that shows how the circuit miles of each Conductor Asset ID aggregate up to the CPZs in WDRM v3 and WDRM v4. i. The screenshots must show how each Conductor Asset ID is associated with either ATASCADERO 1103A14 or ATASCADERO 1103A16 in WDRM v3. ii. The screenshots must show how each Conductor Asset ID is associated with either ATASCADERO 1103635958 or ATASCADERO 1103A16 in WDRM v4. d. Provide a copy of the spatial dataset that PG&E used to generate the screenshots in answer Question 2c. i. Include any spatial tools that PG&E used to generate the screenshots in answer Question 2c. | c). Pursuant to PG&E’s discussion with SPD on Wednesday, October 1, 2025, we are providing a KMZ file including ATASCADERO 1103A14 and ATASCADERO 1103A16 in WDRM v3 and ATASCADERO 1103635958 and ATASCADERO 1103A16 in WDRM v4. Please see WMP-Discovery2026-2028_DR_SPD_014-Q002Supp02Atch01.kmz for the requested information. Further, please see below for a screenshot showing the removal of two conductors on ATASCADERO 1103A14 between the snapshots for WDRM v3 (January 1, 2022) and WDRM v4 (January 1, 2023): {3DC2C429-71BD-4654-AC1B-1B71DCE04210} which accounts for 0.127 miles of primary overhead conductor, and {42A1AF79-EEED-41C0-B61B-F4D14631B0C4} which accounts for 0.079 miles of primary overhead conductor. “Refer to screenshot in data request response” as public versions of DR responses will have the initial question and response tables. |  | 2025-09-16 | 2025-10-03 | 2025-10-03 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_014.zip
41 |  | SPD | SPD | SPD_015 | 001 |  | SPD_015_Q001 | Provide an update to Data Request SPD_WSPS_PG&E_2024_011 that was submitted to Safety Policy Division on January 10 2025. This would be an update to PGE-WMP Cost Reporting Template 20250110.xlsx. This update to the WMP Cost Reporting Template should represent values associated with the 2023-2025 Base WMP. a. Complete tabs 2 through 4 of the attached spreadsheet IOU WMP Cost Reporting and Account Tracking Template 2025_09.xlsx. b. For tabs 2 and 4, complete a data row corresponding for each of the utility mitigation tracking IDs in Table 1 of the QDRs, according to the directions in the spreadsheet and the two attached guidance documents listed below: i. Guidance for WMP Cost Reporting 2025.docx (applicable to tabs 2 and 3) ii. Guidance for Account Tracking 2025.docx (applicable to tab 4) c. For each entry in Tab 2, 4 entries will automatically populate into Tab 3, which break out the mitigation initiative by HFTD/non-HFTD, CapEx/OpEx expenditures. | Please see attachment “WMP-Discovery2026-2028_DR_SPD_015-Q001Atch01.xlsx” for our response to this request. PG&E’s QDR Table 1 only has numbered initiatives for specific commitments (i.e. AI-02 and GH-05), Using just this population will not tie back to the financials in the QDR Table 11 which has the complete WMP initiative costs. PG&E’s QDR Table 11 shows some costs at the level of a specific commitment, such as VM-02 or GH-07, while it shows others at the level of an Initiative Activity. Within the latter group, Table 11 shows that some Initiative Activities have associated commitments, while others do not. In this data request response, PG&E listed each commitment in its own row and for each MAT code the initiative has, and, for those Initiative Activities with no associated commitments, listed each remaining Initiative Activity (‘Emergency Preparedness Plan’, ‘Fire Potential Index’) as its own row and by MAT code. Please note that certain initiatives are not tracked at an HFTD and non-HFTD level. We provide HFTD and non-HFTD allocations of recorded costs for such initiatives by allocating values based on the percentage of our distribution line-miles in HFTD and non-HFTD, respectively. Please note that we provide recorded cost and unit data for 2023 and 2024 and unit data mostly consistent with our QDR submissions however we did find an error in one initiative for the 2023 amounts of approximately $15.6 million that we removed from this data set. For 2025 we have provided our Projected amounts. Regarding “Section A: WMP Cost and Unit Data” In the Expenses tab, please note that we do not provide unit data for unnamed initiatives (e.g.“VM-Emergency response vegetation management,” WMP Section 8.2.3.8) because these categories include variously unitized activities or non-unitized activities. Regarding “Section B Costs and Units Authorized in Last GRC,” in the Expenses tab, please note that the 2023 GRC did not provide HFTD and non-HFTD forecasts for many programs, so we are reporting all authorized dollars and units for those programs in Section B in the “HFTD, CapEx” and “HFTD, OpEx” cells of the worksheet. Regarding “Section C: Costs and Units Forecast to be Requested in the Next GRC” in the Expenses tab, we understand that this section is requesting any 2023-2025 WMP costs requested in the 2027 GRC, which are years prior to the 2027 GRC time period. Please refer to our upcoming response to Question 2 of this data request that will have 2026-2028 WMP projected costs in the 2027 GRC. Regarding “Section D: Costs Recorded via Application (Memo or Balancing Account)” in the Expenses tab, we understand “Application (Memo or Balancing Account” to include the following memo or balancing accounts where costs are recorded, including those authorized and funded in the GRC. This population consists of the MicroGrid Memorandum Account (MGMA); MicroGrid Balancing Account (MGBA); Elect Program Invest Charge BA (EPIC); Wildfire Mitigation Plan Memorandum Account (WMPMA)/Fire Risk Mitigation Memorandum Account (FRMMA); Catastrophic Emergency Memorandum Account (CEMA). Regarding “Section E: EUP” in the Expenses tab, we have not submitted PG&E’s Electric Undergrounding Plan. Therefore, there are no forecast units or forecast costs for the EUP Section. Regarding “Section F: FERC or Other” in the Expenses tab, we understand this to mean costs related to the Transmission Owner case. Please note that certain initiatives (e.g. RM - Risk Methodology and Assessment) include the full 2024 and 2025 WMP forecast amount in this section. Those values do not represent the expected actual allocation of cost to the Transmission Owner case. Additionally, please note that we did not forecast our work under the Community Outreach and Engagement category by WMP Initiative ID in our 2023 GRC. As such, we report all GRC forecasts under this category in the section titled “CO-Public outreach and education awareness program.” Further, please note that we have updated our data to re-categorize 2023 recorded costs related to the Community Outreach and Engagement from initiatives, CO-01, CO-02, CO-04 and CO-05 into: CO-Public outreach and education awareness program; CO-Best practice sharing with other utilities; CO-Engagement with access and functional needs populations, and COCollaboration on local wildfire mitigation planning. Upon review, we determined that recorded costs for 2023 could not be allocated on an initiative level and were more properly allocated as presented here. Please note that our 2024 and 2025 forecasts remain allocated by numbered initiative, but that these forecasts are inclusive of activities beyond those described in the initiatives. Further, please note that we did not forecast our work in our 2023 GRC under the Emergency Preparedness category by WMP Initiative ID. As such, we report our GRC forecasts under this category in the sections titled “EP-External Collaboration and Coordination,” and “EP-Emergency Preparedness Plan.” Further, please note that we have updated our data to re-categorize 2023 recorded costs related to Emergency Preparedness into: EP-Customer support in wildfire and PSPS emergencies; EPEmergency preparedness plan; EP-External collaboration and coordination, and; EPPublic emergency communication strategy. Upon review, we determined that recorded costs for 2023 could not be allocated on an initiative level and were more properly allocated as presented here. Please note that portions of our 2024 and 2025 forecasts remain allocated by numbered initiative, but that these forecasts are inclusive of activities beyond those described in the initiatives. Some of the initiatives being provided include blank cells for costs in the worksheets. These initiatives have costs; however, the costs are in a Provider Cost Center (PCC) for the WMP objective, and line-item costs are not able to be extracted. Some initiatives being provided reflect (0) for costs in the worksheets. These initiatives have costs related to the WMP, however, their recorded or forecasted costs are currently $0. Regarding the “General Info” tab, PG&E is providing the Risk Spend Efficiency (RSE) from the 2023 GRC application as available, as Cost-Benefit Ratios (CBR)s were not calculated when the 2023 GRC was filed. The Column labeled “Cost requested in original GRC Application ($000s)” has been completed based on PG&E’s 2023 GRC Reply Brief (December 9, 2022) with the non-labor escalation update. The Column labeled “GRC Activity Section and Page Number” refers to the sections as filed in the 2023 GRC February 25, 2022, update and the page number is as reported in the table of contents for the Exhibit and Chapter for the referenced section. Note that some MAT codes provided in the GRC Activity Unique Code column may apply to multiple WMP initiatives. PG&E is meeting with SPD on November 7, 2025, to discuss progress and the final deadline for the Account Tracking tab and Question 2 of this data request. | Edwin Schmitt | 2025-10-06 | 2025-11-06 | 2025-11-06 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_015.zip
41 |  | SPD | SPD | SPD_015 | 002 |  | SPD_015_Q002 | Complete the WMP Cost Reporting Template with values associated with the 2026-2028 Base WMP. a. Complete tabs 2 through 4 of the attached spreadsheet IOU WMP Cost Reporting and Account Tracking Template 2026_09.xlsx. b. For tabs 2 and 4, complete a data row corresponding for each of the utility mitigation tracking IDs in Table 1 of the QDRs according to the directions in the spreadsheet and the two attached guidance documents listed below: i. Guidance for WMP Cost Reporting 2026.docx (applicable to tabs 2 and 3) ii. Guidance for Account Tracking 2025.docx (applicable to tab 7) c. For each entry in Tab 2, 4 entries will automatically populate into Tab 3, which break out the mitigation initiative by HFTD/non-HFTD, CapEx/OpEx expenditures. d. The response to tab 4 should be identical to the response to tab 4 found in the completion of Question 1 of this data request. | Please see attachment “WMP-Discovery2026-2028_DR_SPD_015-Q002Atch01.xlsx” for our response to this request. Please note that the values provided therein represent our available data at the time of this data request response and may be subject to change. PG&E’s Quarterly Data Report (QDR) Table 1 only has numbered initiatives for specific commitments (i.e. AI-02 and GH-05). Using just this population will not tie back to the financials in the QDR, Table 11, which has the complete WMP initiative costs. PG&E’s QDR, Table 11, shows some costs at the level of a specific commitment, such as VM-02 or GH-07, while it shows others at the level of an Initiative Activity. Within the latter group, Table 11 shows that some Initiative Activities have associated commitments, while others do not. In this data request response, PG&E listed each commitment in its own row and for each MAT code the initiative has. Additionally, for those Initiative Activities with no associated commitments, PG&E listed each remaining Initiative Activity (‘Emergency Preparedness Plan’, ‘Fire Potential Index’) as its own row and by MAT code. Regarding “Section A: WMP Cost and Unit Data”, in the Expenses tab, please note that we do not provide unit data for unnamed initiatives (e.g.“VM-Emergency response vegetation management,” WMP Section 8.2.3.8) because these categories include variously unitized activities or non-unitized activities. Regarding “Section B: Costs and Units Authorized in Last GRC,” in the Expenses tab, we understand that this section is requesting any 2026-2028 WMP costs requested in the 2023 GRC. Please note that the 2023 GRC did not provide HFTD and non-HFTD forecasts for many programs, so we are reporting all authorized dollars and units for those programs in Section B in the “HFTD, CapEx” and “HFTD, OpEx” cells of the worksheet. Regarding “Section C: Costs and Units Forecast to be Requested in the Next GRC” in the Expenses tab, we understand that this section is requesting any 2026-2028 WMP costs requested in the 2027 GRC. Please note that the 2027 GRC did not provide HFTD and non-HFTD forecasts for many programs, so we are reporting all requested dollars and units for those programs in Section C in the “HFTD, CapEx” and “HFTD, OpEx” cells of the worksheet. Regarding “Section E: EUP”, in the Expenses tab, we have not submitted PG&E’s Electric Undergrounding Plan (EUP). Therefore, there are no forecast units or forecast costs for the EUP Section. Regarding “Section F: FERC or Other”, in the Expenses tab, we understand this to mean costs related to the Transmission Owner case. As described in our narrative response to Question 1, PG&E does not track costs for all WMP activities separately. In Question 2, PG&E identified these areas by noting “costs not tracked separately” in the General Info tab, column “GRC Activity Unique Code”. Regarding the “General Info” tab, PG&E is providing the Risk Spend Efficiency (RSE) as “Not Applicable” because there were no RSE in the 2024 RAMP and 2027 GRC. Benefit-Cost Ratios (BCR) are filled in based on the 2027 GRC. The column labeled “Cost requested in original GRC Application ($000s)” has been completed based on PG&E’s 2023 GRC Reply Brief (December 9, 2022) with the non-labor escalation update. The column labeled “GRC Activity Section and Page Number” refers to the sections as filed in the 2023 GRC February 25, 2022. Note that some MAT codes provided in the GRC Activity Unique Code column may apply to multiple WMP initiatives. For the column “Recorded Costs Above GRC Authorization”, PG&E entered $0 because there are no recorded costs for 2026-2028. | Edwin Schmitt | 2025-10-06 | 2025-11-26 | 2025-11-26 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_015.zip
41 |  | SPD | SPD | SPD_015 | 003 |  | SPD_015_Q003 | When submitting the response to Questions 1 and 2 in this data request, do not manipulate the template provided in the attached Excel files in anyway. This includes, but is not limited to, the following: a. Within the Excel files do not hide any rows or make the data in any way difficult for the user to access, view or otherwise utilize. b. Do not adjust the formatting. c. Do not remove formulas. d. Unless otherwise specified above, where information is not available the cell must be left blank and the utility must provide an explanation for the blank in the narrative response to this data request; do not fill in with N/A or any other figure to designate that the information is not available. |  | Edwin Schmitt | 2025-10-06 |  |  | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_015.zip
41 |  | SPD | SPD | SPD_015 | 004 |  | SPD_015_Q004 | Provide the following summarized WMP cost data for each calendar year from 2020 through 2025. This should be based on logic used in Table 11 of the OEIS Tabular Quarterly Data Report (QDR), and should include any adjustments as reported in the final OEIS annual report on compliance. If a calendar year is not yet reconciled, provide estimates as they would have been provided in Table 11 of the OEIS QDR. Column Names listed below: WMP Year WMP Category2 Territory Type (HFTD/non-HFTD) Expense Type (CapEx/OpEx) Total Expense Type (Actual/Projected) | Please see attachment “WMP-Discovery2026-2028_DR_SPD_015-Q004Atch01.xlsx“ for the PG&E WMP cost data for each calendar year (2020-2024) provided in Table 11 of the QDR, summarized by the column attributes requested. For 2025, we provided the projected amounts under column F (Total Expense (in thousands)) and column G (Type (Actual/Projected)). | Edwin Schmitt | 2025-10-06 | 2025-10-30 | 2025-10-30 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_015.zip
33 |  | SPD | SPD | SPD_013 | Q001Supp03 |  | SPD_013_QQ001Supp03 | The following questions relate to “WMP-Discovery2026-2028_DR_SPD_001-Q019Atch01.xlsx”: a. Outage ID (column Q) has values in Row 40776 to 40783 as “1.” Correct if necessary. b. There are many blanks in Column B. Of 106,425 values, 71,1151 are blank. Explain why the values are blank. Correct if necessary. c. Explain why 6680 rows in Column O are blank, “false” or “1” – correct if necessary. d. Add a new column to the data set which includes the Facility Damage Action (FDA) for each tag. If the tag has more than one FDA, each additional FDA should be added in a second column. e. Create a data set with the same data as the “WMP-Discovery2026-2028_DR_SPD_001- Q019Atch01.xlsx” (including the FDA information as requested in question 1d) but with Priority X data, including the FDAs. | a. Upon review, we have been unable to determine correct OIS numbers, or lack thereof, for the “1” entries as these values are manually entered in the field and, therefore, could not be traced back. We have opened a corrective action to determine how to ensure correct and consistent data entry for this field going forward. |  | 2025-08-14 | 2025-10-10 | 2025-10-10 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_013.zip
16 |  | SPD | 001 | SPD_001 | Q019Supp01 |  | SPD_001_QQ019Supp01 | Provide all Priority A work orders PG&E created between 2020 and 2024 in the same format as “WMP-Discovery2023-2025_DR_SPD_019-Q002Atch01CONF,” with the exception that column T and U need not be filled out. Include Priority As for both distribution and transmission. a. For the purposes of this response to the data request, use column J (“Completion Data (if applicable)” for the date the work order was closed and column R (“Last Maintenance Date”) as the date the field work was finished. b. Correct Column P so the values are either Y (for yes, a wire down occurred) or N (for no, a wire down did not occur), unless there is a unique identifier for the wires down that does not match the Outage ID. Add a new column with the Outage Event ID that matches the unique outage ID identifier for the QDR data set. For instance, in the current data set, the column Q outage ID 1910360 appears to refer to an event in 2023, but in the QDR spatial data set, outage ID 1910360 appears to refer to an event in 2024. Continue to use the same methodology for creating outage event IDs for column Q. i. Explain why the QDR spatial data appears to have a different outage event IDs than those specified in column Q. | As noted in our revised response to “WMP-Discovery2026-2028_DR_SPD_013-Q002Rev01.pdf”, provided on September 8, 2025, we are amending our response to this request. Please see “WMP-Discovery2026-2028_DR_SPD_001-Q019Supp01Atch01.xlsx”. Upon review, we have performed the following corrections: The “Method Found” field for notifications 126647411, 126646908, 126646746, 126366769, 125867147 has been corrected from “Detailed Inspection” to “Aerial Inspection.” The “Method Found” field for notifications 128198022, 126176622, 126600516, 126600517, 126599397, 126176620, 127332067, 126993965, 128418688, 126715552, 126206452 has been corrected from “Other Inspections” to “Detailed Inspection.” |  | 2025-04-15 | 2025-10-23 | 2025-10-23 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-SPD_001.zip
|  | OEIS | 022 | OEIS_022 | OEIS_022-Q001 |  | OEIS_022_QOEIS_022-Q001 | On page 85 of the draft Decision for the PG&E 2026-2028 Base WMP, PGE-26B-18 requires PG&E in its next WMP Update to include “[t]he number of outages caused by each [tree] species per 1,000 trees in PG&E’s records of that species.” In PG&E’s Opening Comments on the draft Decision, it requested that Energy Safety modify PGE-26B-18 to require PG&E calculate “[t]he Number of outages caused by each species per 1,000 trees in its Strike Tree Species Model Prediction.” PG&E indicated that this modification would improve the specificity of the requirement. a. Regarding PG&E’s Strike Tree Species Model: i. Describe the model’s history (e.g., when it was created, who created it, and what dataset(s) informs its predictions) and purpose (i.e., how PG&E currently uses the model and plans to use the model). ii. List and describe the model’s inputs (e.g., environmental factors, plant species, plant age, plant height, etc.) iii. List and describe the model’s outputs (e.g., probability of outage by plant species or genus, probability of ignition by plant species or genus, etc.) iv. Is the model able to predict the species- or genus-specific probability of an outage due to both grow-in and fall-in events? 1. If yes, is PG&E able to divide this prediction into separate grow-in and fall-in outage probabilities? 2. If no, what types of vegetation failure modes does the model’s output take into account to calculate the species- or genus-specific outage probability? v. What are the advantages and disadvantage of using PG&E’s Strike Tree Species Model Prediction in place of “PG&E’s records” to calculate the number of outages by each tree species or genus per 1,000 trees? | a. Responses Below: i. The Tree Species Model, developed jointly by PG&E’s Vegetation Management and Risk Management organizations, was initiated in 2023 and continued through 2024. The purpose was to create a machine learningbased tree species identification system to support wildfire mitigation strategies. The model identifies how vegetation types across different ecoregions in High Fire-Threat Districts (HFTDs) impact mitigation planning. This per‑tree model provides an updateable baseline of species variation across PG&E’s service territory, providing input to future risk models (e.g., Wildfire Distribution Risk Model (WDRM), in addition to supporting future program development and planning. ii. The initial model inputs include: • LiDAR point cloud data — HFTD collection of ~5 million data points for tree geometry and proximity mapping. • EVM Inspection data — species-level details from PG&E’s vegetation management program, used as labels for training the model. • Satellite Data — surface reflectance imagery for canopy height, cover, and mortality indicators. 8 bands, 4.7m resolution. • Internal Wildfire Risk Models — various wildfire risk covariates. iii. The initial raw model outputs include: 1. Predicted tree species label: • One of 20+ possible species classes. 2. Sensitivity/Confidence scores: • Probability or confidence of the tree belonging to each class. Tree features like canopy height are also extracted through LiDAR point cloud data and each tree is represented as a cluster of points rather than a single pixel. iv. This model is not intended to predict the species- or genus-specific probability of an outage due to grow-in and fall-in events. 1. N/A 2. This model could feed other models that account for vegetation failure to develop a species- or genus-specific probability of outage model. Currently, it includes outages caused by vegetation contact events, without the explicit separation of grow‑in and fall‑in categories. Instead, PG&E uses other models (like OPW/IPW and WDRM vegetation sub-models) to handle failure-mode differentiation, by 1) breaking down vegetation-caused outages into branch, trunk, and other categories, 2) incorporating LiDAR and satellite-derived metrics to estimate fall‑in risk, and 3) using weather covariates (i.e., wind speed, soil moisture) for dynamic failure probability modeling. Additionally, this data is better suited for fall‑in outage probabilities, as its prediction is associated with strike tree species determination. Any estimate of grow‑in outage probabilities would be inferred from the strike tree species output. v. The main advantage of using PG&E’s Tree Species Model is that it provides comprehensive and consistent species identification at single‑tree level across HFTDs. This level of granularity could be used as the “denominator” of a probability‑of‑outage estimate, as outage probabilities can be severely skewed by counting only trees recorded in PG&E records. The disadvantage of using only PG&E records is that they predominantly rely on trees identified as needing maintenance or mitigation. Other than the subset of miles inspected and documented in our 2023–2025 Focused Tree Inspection (FTI) program and our continuing 2026–2028 Elevated Inspections in areas of high risk, all other miles are largely based on recording trees that require work. |  | 2026-12-22 | 2026-12-26 |  | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/2026-2028-OEIS_022.zip
|  | SPD | 015 | SPD_015 | Q001Supp01 |  | SPD_015_QQ001Supp01 | Provide an update to Data Request SPD_WSPS_PG&E_2024_011 that was submitted to Safety Policy Division on January 10 2025.1 This would be an update to PGE-WMP Cost Reporting Template 20250110.xlsx. This update to the WMP Cost Reporting Template should represent values associated with the 2023-2025 Base WMP. a. Complete tabs 2 through 4 of the attached spreadsheet IOU WMP Cost Reporting and Account Tracking Template 2025_09.xlsx. b. For tabs 2 and 4, complete a data row corresponding for each of the utility mitigation tracking IDs in Table 1 of the QDRs, according to the directions in the spreadsheet and the two attached guidance documents listed below: i. Guidance for WMP Cost Reporting 2025.docx (applicable to tabs 2 and 3) ii. Guidance for Account Tracking 2025.docx (applicable to tab 4) c. For each entry in Tab 2, 4 entries will automatically populate into Tab 3, which break out the mitigation initiative by HFTD/non-HFTD, CapEx/OpEx expenditures. | Please see attachment “WMP-Discovery2026-2028_DR_SPD_015-Q001Supp01Atch01.xlsx” for our response to this request. Regarding the Account Tracking tab, please note the following: - Blank entries in the “Wildfire Mitigation Initiative” columns indicate mitigation programs that are not named initiatives in our Wildfire Mitigation Plan. - The CPUC Proceeding Number, CPUC Decision Number, and Any Other ID Number columns have been updated to reflect the proceedings and decisions related to the most recent authorization of revenue associated with the relevant memorandum or balancing account. - Blank entries in the “Unit” columns indicate non-unitized initiatives. - We understand “GRC Authorized Expenditures” columns to refer to expenditures authorized in the 2023 GRC, which includes years 2023 through 2026. - Mitigations for which the "Authorized Amount, Balancing or Memorandum Account Name" is "No GRC Imputed", the columns "CPUC Proceeding Number" and "CPUC Decision Number" are blank because the mitigation is not directly forecasted or recovered in any PG&E proceeding at the granular level of that mitigation. - We understand “GRC Authorized Revenue Requirement (Entered Rates)” to refer to the revenue requirement of expenditures authorized in our 2023 GRC for years 2023, 2024 and 2025. - We determined that expenditures under the CEMA account have yet to enter rates. This update is reflected in our data and in the explanations of the sections including “Entered Rates” and “Yet to Enter Rates,” below. - We understand “Recorded Cost Expenditures” to refer to 2023-2024 Recorded costs regardless of memorandum or balancing account. - We understand “Recorded Cost Revenue Requirement (Entered Rates)” to refer to 2023 and 2024 Recorded costs regardless of memorandum or balancing account. Operational expenditures for 2023 and 2024 have entered rates, with the exception of Transmission Base, CEMA, WMPMA, and FRMMA, and capital expenditures for 2023 and 2024, with the exception of Transmission Base, CEMA, MGMA, EPIC, WMPMA, and FRMMA, have entered rates. - We understand “Recorded Cost Revenue Requirement (Yet to Enter Rates)” to refer to 2023 and 2024 Recorded costs regardless of memorandum or balancing account. Operational expenditures for 2023 and 2024 for Transmission Base, CEMA, WMPMA, and FRMMA, and capital expenditures for 2023 through 2026 for Transmission Base, CEMA, MGMA, WMPMA, and FRMMA, have yet to enter rates. - We understand “Non-GRC Authorized Expenditures” to refer to non-GRC balancing and memorandum accounts. We include Transmission Owner case costs here for CapEx and OpEx for 2023 and 2024. - We understand “Non-GRC Authorized Revenue Requirements (Entered Rates)” to refer to non-GRC balancing and memorandum accounts. No operational or capital expenditures for 2023 and 2024 have entered rates. - We understand “Non-GRC Recorded Cost Expenditures” to refer to non-GRC balancing and memorandum accounts. We include Transmission Owner case costs here for 2023 and 2024. - We understand “Non-GRC Recorded Costs Revenue Requirements (Entered Rates)” to refer to non-GRC balancing and memorandum accounts. Operational expenditures for 2023 have entered rates, with the exception of CEMA, WMPMA, and FRMMA. Operational expenditures for 2024 have entered rates, with the exception of Transmission Base, CEMA, WMPMA, and FRMMA. No capital expenditures have entered rates with the exception of Transmission Base for the year 2023. - We understand “Non-GRC Recorded Costs Revenue Requirement (Yet to Enter Rates)” to refer to non-GRC balancing and memorandum accounts. Operational expenditures for 2023 for CEMA, WMPMA, and FRMMA, and Operational expenditures for 2024 for Transmission Base, CEMA, WMPMA, and FRMMA have yet to enter rates. Capital expenditures for 2023 for CEMA, MGMA, WMPMA, and FRMMA, and Capital expenditures for 2024 through 2026 for Transmission Base, CEMA, MGMA, WMPMA, and FRMMA, have yet to enter rates. - We understand the “Pending Non-GRC Expenditures” columns to refer to all costs in non-GRC balancing and memorandum accounts that have not been authorized which include costs in the following accounts: MBMA/MGBA/CEMA/EPIC/FRMMA/WMPMA/TRRRMA recorded in 2023 and 2024. At this time, we do not have pending GRC decisions for 2023-2026; “Pending GRC Expenditures” and therefore are left blank. Some of the initiatives being provided include blank cells for costs in the worksheets. These initiatives have costs; however, the costs are in a Provider Cost Center (PCC) for the WMP objective, and line-item costs are not able to be extracted. Some initiatives being provided reflect (0) for costs in the worksheets. These initiatives have costs related to the WMP, however, are qualitative and therefore we are not tracking reportable costs. We did not update the Account Total and Wildfire Mitigation Program Total columns as they contain formulas for SPD to conduct their calculations. ` | Henry Sweat | 2025-11-06 | 2026-01-22 | 2026-01-22

## Steering Committee Chart 3 (hidden)
Date Rec'd | (Multiple Items) |  |  |  | Date Sent | (Multiple Items)
Supp/Rev | No |  |  |  | Supp/Rev | No
Row Labels | Count of Question ID | Sum of Subparts | Count of Question ID2 | Sum of Extension Count | Row Labels | Count of Question ID | Sum of Subparts | Count of Question ID2 | Sum of Extension Count
MGRA | 34 | 52 | 12.55% | 16 | GPI | 2 | 7 | 0.7067%
MGRA_002 | 5 | 4 | 1.845% | 0 | GPI_001 | 2 | 7 | 0.7067%
MGRA_003 | 11 | 8 | 4.059% | 7 | MGRA | 42 | 53 | 14.84% | 16
MGRA_004 | 3 | 1 | 1.107% | 0 | MGRA_001 | 8 | 1 | 2.827% | 0
MGRA_005 | 5 | 17 | 1.845% | 1 | MGRA_002 | 5 | 4 | 1.767% | 0
MGRA_006 | 9 | 22 | 3.321% | 8 | MGRA_003 | 11 | 8 | 3.887% | 7
MGRA_007 | 1 | 0 | 0.369% |  | MGRA_004 | 3 | 1 | 1.06% | 0
OEIS | 87 | 464 | 32.1% | 26 | MGRA_005 | 5 | 17 | 1.767% | 1
OEIS_001 | 28 | 131 | 10.33% | 7 | MGRA_006 | 9 | 22 | 3.18% | 8
OEIS_002 | 18 | 95 | 6.642% | 4 | MGRA_007 | 1 | 0 | 0.3534%
OEIS_003 | 7 | 24 | 2.583% | 2 | OEIS | 87 | 464 | 30.74% | 26
OEIS_004 | 4 | 76 | 1.476% | 3 | OEIS_001 | 28 | 131 | 9.894% | 7
OEIS_005 | 9 | 38 | 3.321% | 4 | OEIS_002 | 18 | 95 | 6.36% | 4
OEIS_006 | 4 | 19 | 1.476% | 1 | OEIS_003 | 7 | 24 | 2.473% | 2
OEIS_007 | 3 | 15 | 1.107% | 1 | OEIS_004 | 4 | 76 | 1.413% | 3
OEIS_008 | 2 | 2 | 0.738% |  | OEIS_005 | 9 | 38 | 3.18% | 4
OEIS_009 | 1 | 5 | 0.369% | 1 | OEIS_006 | 4 | 19 | 1.413% | 1
OEIS_010 | 2 | 5 | 0.738% |  | OEIS_007 | 3 | 15 | 1.06% | 1
OEIS_011 | 1 | 6 | 0.369% | 2 | OEIS_008 | 2 | 2 | 0.7067%
OEIS_012 | 3 | 21 | 1.107% | 1 | OEIS_009 | 1 | 5 | 0.3534% | 1
OEIS_013 | 1 | 7 | 0.369% |  | OEIS_010 | 2 | 5 | 0.7067%
OEIS_014 | 1 | 2 | 0.369% |  | OEIS_011 | 1 | 6 | 0.3534% | 2
OEIS_015 | 1 | 7 | 0.369% | 0 | OEIS_012 | 3 | 21 | 1.06% | 1
OEIS_016 | 1 | 8 | 0.369% |  | OEIS_013 | 1 | 7 | 0.3534%
OEIS_017 | 1 | 3 | 0.369% |  | OEIS_014 | 1 | 2 | 0.3534%
SPD | 117 | 371 | 43.17% | 56 | OEIS_015 | 1 | 7 | 0.3534% | 0
SPD_001 | 28 | 59 | 10.33% | 14 | OEIS_016 | 1 | 8 | 0.3534%
SPD_002 | 4 | 5 | 1.476% | 0 | OEIS_017 | 1 | 3 | 0.3534%
SPD_003 | 15 | 31 | 5.535% | 5 | SPD | 119 | 371 | 42.05% | 56
SPD_004 | 42 | 151 | 15.5% | 29 | SPD_001 | 28 | 59 | 9.894% | 14
SPD_005 | 6 | 8 | 2.214% |  | SPD_002 | 4 | 5 | 1.413% | 0
SPD_006 | 7 | 54 | 2.583% | 5 | SPD_003 | 15 | 31 | 5.3% | 5
SPD_007 | 7 | 35 | 2.583% | 1 | SPD_004 | 42 | 151 | 14.84% | 29
SPD_008 | 4 | 1 | 1.476% | 1 | SPD_005 | 6 | 8 | 2.12%
SPD_009 | 4 | 27 | 1.476% | 1 | SPD_006 | 7 | 54 | 2.473% | 5
TURN | 33 | 85 | 12.18% | 12 | SPD_007 | 7 | 35 | 2.473% | 1
TURN_002 | 10 | 17 | 3.69% | 1 | SPD_008 | 4 | 1 | 1.413% | 1
TURN_003 | 10 | 37 | 3.69% | 7 | SPD_009 | 4 | 27 | 1.413% | 1
TURN_004 | 10 | 22 | 3.69% | 4 | SPD_010 | 2 |  | 0.7067%
TURN_005 | 3 | 9 | 1.107% |  | TURN | 33 | 85 | 11.66% | 12
Grand Total | 271 | 972 | 100% | 110 | TURN_002 | 10 | 17 | 3.534% | 1
[5 empty] | TURN_003 | 10 | 37 | 3.534% | 7
Supp/Rev | No |  |  |  | TURN_004 | 10 | 22 | 3.534% | 4
[5 empty] | TURN_005 | 3 | 9 | 1.06%
Row Labels | Count of Question ID | Sum of Subparts |  |  | Grand Total | 283 | 980 | 100% | 110
Wildfire Mitigation Strategy Development | 33 | 141
Vegetation Management & Inspections | 23 | 83
Situational Awareness and Forecasting | 6 | 20
ACI PG&E-23B-15 | 1 | 4
Supporting Documentation for Risk Methodology | 1 | 4
Outage-to-Ignition Risk Analyses | 1 | 2
ES-02/AI-11 | 1 | 3
Grid Design, Operations, and Maintenance | 47 | 157
Areas of Continued Improvement | 8 | 16
Vegetation Management and Inspections | 15 | 50
GH-04 | 4 | 20 | [6 empty] | Supp/Rev | No
Appendix D: Areas of Continued Improvement | 5 | 21 | [6 empty] | Date Received | (Multiple Items)
VM-02 | 1 | 1
Risk Methodology and Assessment | 1 | 12 | [6 empty] | Row Labels | Count of Question ID | Sum of Subparts
(blank) | 9 | 12 | [6 empty] | Risk Methodology & Assessment | 80 | 353
Risk Methodology & Assessment | 80 | 353 | [6 empty] | Grid Design, Operations, and Maintenance | 47 | 157
Public Safety Power Shutoff | 5 | 17 | [6 empty] | Wildfire Mitigation Strategy Development | 33 | 141
N/A | 9 | 5 | [6 empty] | Vegetation Management & Inspections | 22 | 78
GIS | 16 | 6 | [6 empty] | Overview of WMP | 17 | 34
Enterprise Systems | 1 | 3 | [6 empty] | Vegetation Management and Inspections | 16 | 55
Emergency Preparedness, Collaboration, and Public Awareness | 1 | 5 | [6 empty] | Areas of Continued Improvement | 8 | 16
ACI PG&E-25U-04 | 1 | 9 | [6 empty] | GIS | 8 | 5
Overview of WMP | 17 | 34 | [6 empty] | (blank) | 8 | 12
Evaluation and Reporting of Safety Impacts Relating to EPSS | 1 | 2 | [6 empty] | Situational Awareness and Forecasting | 6 | 20
Grand Total | 287 | 980 | [6 empty] | N/A | 6 | 5
[9 empty] | Appendix D: Areas of Continued Improvement | 5 | 21
Supp/Rev | No | [7 empty] | Public Safety Power Shutoff | 5 | 17
[9 empty] | GH-04 | 4 | 20
Row Labels | Count of Question ID | [7 empty] | Enterprise Systems | 1 | 3
ACI PG&E-25U-04 | 1 | [7 empty] | VM-02 | 1 | 1
Emergency Preparedness, Collaboration, and Public Awareness | 1 | [7 empty] | Outage-to-Ignition Risk Analyses | 1 | 2
Enterprise Systems | 1 | [7 empty] | Emergency Preparedness, Collaboration, and Public Awareness | 1 | 5
GIS | 5 | [7 empty] | ES-02/AI-11 | 1 | 3
N/A | 2 | [7 empty] | Supporting Documentation for Risk Methodology | 1 | 4
Public Safety Power Shutoff | 3 | [7 empty] | ACI PG&E-25U-04 | 1 | 9
Risk Methodology & Assessment | 13 | [7 empty] | Risk Methodology and Assessment | 1 | 12
Situational Awareness and Forecasting | 2 | [7 empty] | ACI PG&E-23B-15 | 1 | 4
Vegetation Management & Inspections | 20 | [7 empty] | Evaluation and Reporting of Safety Impacts Relating to EPSS | 1 | 2
Wildfire Mitigation Strategy Development | 8 | [7 empty] | Grand Total | 275 | 979
Overview of WMP | 1
Evaluation and Reporting of Safety Impacts Relating to EPSS | 1
ACI PG&E-23B-15 | 1
Supporting Documentation for Risk Methodology | 1
Outage-to-Ignition Risk Analyses | 1
ES-02/AI-11 | 1
Grid Design, Operations, and Maintenance | 13
Grand Total | 75

## Steering Committee Chart 2 (hidden)
Supp/Rev | No |  |  |  | Supp/Rev | No
Date Received | (Multiple Items) |  |  |  | Date Received | (Multiple Items)
Row Labels | Count of Question ID | Sum of Subparts | Count of Question ID2 | Sum of Extension Count | Row Labels | Count of Question ID | Sum of Subparts | Count of Question ID2 | Sum of Extension Count
GPI | 2 | 7 | 0.7273% |  | GPI | 2 | 7 | 0.7273%
GPI_001 | 2 | 7 | 0.7273% |  | MGRA | 34 | 52 | 12.36% | 16
MGRA | 34 | 52 | 12.36% | 16 | OEIS | 87 | 464 | 31.64% | 26
MGRA_002 | 5 | 4 | 1.818% | 0 | SPD | 119 | 371 | 43.27% | 56
MGRA_003 | 11 | 8 | 4% | 7 | TURN | 33 | 85 | 12% | 12
MGRA_004 | 3 | 1 | 1.091% | 0 | Grand Total | 275 | 979 | 100% | 110
MGRA_005 | 5 | 17 | 1.818% | 1
MGRA_006 | 9 | 22 | 3.273% | 8
MGRA_007 | 1 | 0 | 0.3636%
OEIS | 87 | 464 | 31.64% | 26
OEIS_001 | 28 | 131 | 10.18% | 7
OEIS_002 | 18 | 95 | 6.545% | 4
OEIS_003 | 7 | 24 | 2.545% | 2
OEIS_004 | 4 | 76 | 1.455% | 3
OEIS_005 | 9 | 38 | 3.273% | 4
OEIS_006 | 4 | 19 | 1.455% | 1
OEIS_007 | 3 | 15 | 1.091% | 1
OEIS_008 | 2 | 2 | 0.7273%
OEIS_009 | 1 | 5 | 0.3636% | 1
OEIS_010 | 2 | 5 | 0.7273%
OEIS_011 | 1 | 6 | 0.3636% | 2
OEIS_012 | 3 | 21 | 1.091% | 1
OEIS_013 | 1 | 7 | 0.3636%
OEIS_014 | 1 | 2 | 0.3636%
OEIS_015 | 1 | 7 | 0.3636% | 0
OEIS_016 | 1 | 8 | 0.3636%
OEIS_017 | 1 | 3 | 0.3636%
SPD | 119 | 371 | 43.27% | 56
SPD_001 | 28 | 59 | 10.18% | 14
SPD_002 | 4 | 5 | 1.455% | 0
SPD_003 | 15 | 31 | 5.455% | 5
SPD_004 | 42 | 151 | 15.27% | 29
SPD_005 | 6 | 8 | 2.182%
SPD_006 | 7 | 54 | 2.545% | 5
SPD_007 | 7 | 35 | 2.545% | 1
SPD_008 | 4 | 1 | 1.455% | 1
SPD_009 | 4 | 27 | 1.455% | 1
SPD_010 | 2 |  | 0.7273%
TURN | 33 | 85 | 12% | 12
TURN_002 | 10 | 17 | 3.636% | 1
TURN_003 | 10 | 37 | 3.636% | 7
TURN_004 | 10 | 22 | 3.636% | 4
TURN_005 | 3 | 9 | 1.091%
Grand Total | 275 | 979 | 100% | 110

## Steering Committee Chart 1 (hidden)
Date Sent | (Multiple Items) |  |  |  | Date Sent | (Multiple Items)
Row Labels | Count of Question ID | Sum of Subparts | Count of Question ID2 | Sum of Extension Count | Row Labels | Count of Question ID | Sum of Subparts | Count of Question ID2 | Sum of Extension Count
GPI | 3 | 12 | 0.8982% |  | GPI | 3 | 12 | 0.9346%
GPI_001 | 3 | 12 | 0.8982% |  | MGRA | 50 | 60 | 15.58% | 16
MGRA | 50 | 60 | 14.97% | 16 | OEIS | 92 | 483 | 28.66% | 27
MGRA_001 | 8 | 1 | 2.395% | 0 | SPD | 140 | 573 | 43.61% | 61
MGRA_002 | 10 | 8 | 2.994% | 0 | TURN | 36 | 105 | 11.21% | 12
MGRA_003 | 13 | 8 | 3.892% | 7 | Grand Total | 321 | 1233 | 100% | 116
MGRA_004 | 3 | 1 | 0.8982% | 0
MGRA_005 | 5 | 17 | 1.497% | 1
MGRA_006 | 10 | 25 | 2.994% | 8
MGRA_007 | 1 | 0 | 0.2994%
OEIS | 92 | 483 | 27.54% | 27
OEIS_001 | 29 | 137 | 8.683% | 7
OEIS_002 | 19 | 97 | 5.689% | 4
OEIS_003 | 7 | 24 | 2.096% | 2
OEIS_004 | 4 | 76 | 1.198% | 3
OEIS_005 | 9 | 38 | 2.695% | 4
OEIS_006 | 4 | 19 | 1.198% | 1
OEIS_007 | 3 | 15 | 0.8982% | 1
OEIS_008 | 3 | 3 | 0.8982%
OEIS_009 | 3 | 15 | 0.8982% | 2
OEIS_010 | 2 | 5 | 0.5988%
OEIS_011 | 1 | 6 | 0.2994% | 2
OEIS_012 | 3 | 21 | 0.8982% | 1
OEIS_013 | 1 | 7 | 0.2994%
OEIS_014 | 1 | 2 | 0.2994%
OEIS_015 | 1 | 7 | 0.2994% | 0
OEIS_016 | 1 | 8 | 0.2994%
OEIS_017 | 1 | 3 | 0.2994%
SPD | 153 | 578 | 45.81% | 61
SPD_001 | 31 | 70 | 9.281% | 14
SPD_002 | 4 | 5 | 1.198% | 0
SPD_003 | 15 | 31 | 4.491% | 5
SPD_004 | 55 | 203 | 16.47% | 33
SPD_005 | 6 | 8 | 1.796%
SPD_006 | 12 | 193 | 3.593% | 6
SPD_007 | 7 | 35 | 2.096% | 1
SPD_008 | 4 | 1 | 1.198% | 1
SPD_009 | 4 | 27 | 1.198% | 1
SPD_010 | 2 |  | 0.5988%
SPD_011 | 12 | 5 | 3.593%
SPD_012 | 1 |  | 0.2994%
TURN | 36 | 105 | 10.78% | 12
TURN_002 | 11 | 23 | 3.293% | 1
TURN_003 | 10 | 37 | 2.994% | 7
TURN_004 | 12 | 36 | 3.593% | 4
TURN_005 | 3 | 9 | 0.8982%
Grand Total | 334 | 1238 | 100% | 116

## Sheet1 (hidden)
Count | Party Name | Data Set | Data Request | Question No. | Question ID | Question Text | Responses | Requestor | Date Rec'd | Final Due Date | Date Sent | Links | Number of Atchs | NDA Required | 2023 WMP Section | Category | Subcategory | 2025 WMP Section | URL to Response | Party | Data Set2 | Q# | # of Sub-Parts | DRU | WM PMO | SME | RD | Legal | Chief Sponsor | Draft Sent For Review | RD Review Complete | Legal Review Complete | Confidential Review Complete | WM PMO Complete | QC Review Complete | Reg Review Complete | Peer Review | Due Date | Confidential? | Extension? And Reason | Notes | 2022 WMP Prior Review | 2021 WMP Prior Review | 2020 WMP Prior Review | 2023 GRC Prior Review | 2020 GRC Prior Review | 2017 GRC Prior Review | Additional Priors/Documents | Objections w/in 5 Bus. Days | Delayed Response Notice w/in 3 Bus. Days | "Verified Responses" | Clarifications | Email/Phone of Employees | Bates-Stamped Response | Question # | SME2 | Responsible Director | DRU Lead | WM PMO2 | Legal Lead | # Subparts | Priors | Web Docs | DRU Number | DRU Notes | Status | Due Today | Due in 1 Business Day | Due in 2 Business Days | Due Later | Other Situations
642 | OEIS | 021 | OEIS_021 | 1 | OEIS_021_Q1 | Regarding PG&E’s 2025 Distribution Hardening GH-01 Risk Impact: a. In table 8-3 of PG&E’s 2023-2025 WMP, PG&E targets a 4.7% risk impact in 2025 for initiative GH-01.1 PG&E also states that it is redeveloping its undergrounding workplan.2 Please explain how PG&E calculated the 4.7% risk impact for GH-01 given the 2025 workplan was not finalized at the time of WMP submission. Provide all supporting documentation necessary to justify the 4.7% risk impact for initiative GH-01 in 2025. | a. Please see attachment WMPWMP-Discovery2023-2025_DR_OEIS_021- Q001Atch01.xlsx for the requested information. The projected GH-01 risk reduction estimates leveraged the System Hardening workplan as of February 22, 2024, and was normalized to be proportionate to the mileage targets for 2025 (520 System Hardening miles). To normalize the risk reduction estimates based on the target miles, PG&E selected for projects that were marked to move forward post-GRC decision and their corresponding project status (SAP status). The steps taken are further described in the attachment (see worksheet “2025 Risk Reduction Estimate”) referencing summary information and formulas to calculate the reported 4.7% risk reduction. The 2025 workplan data, including project status, hardening miles, and risk reduction values, is provided in the attachment (see worksheet “2025 GH-01 Workplan”). When taking the snapshot of the workplan on February 22, 2024, PG&E provided the best data available at the time, recognizing that PG&E’s 2025 and 2026 workplan was still evolving to account for the risk reduction and funding requirements from GRC D.23-11-069. | Brad Hill | 2024-05-20 | 2024-05-23 | 2024-05-23 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/OEIS_021.zip | 1 | N/A | 8 | Section 8.1.2 - Grid Design and System Hardening | 8.1.2.2 Undergrounding of electric lines and/or equipment | 2.1.1.2 GH-04 Undergrounding |  | OEIS | 021 | 1 | 0 | Mona Hedin | Deanna Maraccini | Brad Koelling Benson Wong Underground Data Requests Julie Cerio Jerry Santos Lucy Morris Francis Massad James Ash Jr. Paayal Murti Justin Sadler Merih Tekeste | Megan Ardell Jim Gill | Aaron Shapiro | Matt Pender | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | 2024-05-23 | [16 empty] | 1 | Brad Koelling Benson Wong Underground Data Requests Julie Cerio Jerry Santos Lucy Morris Francis Massad James Ash Jr. Paayal Murti Justin Sadler Merih Tekeste | Megan Ardell Jim Gill | Mona Hedin | Deanna Maraccini | Aaron Shapiro | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
631 | OEIS | 020 | OEIS_020 | 1 | OEIS_020_Q1 | Regarding PG&E’s 2025 Workplan: a. In table 8.1.2-2 of PG&E’s 2023-2025 WMP, PG&E provides a table detailing the number of miles it plans to underground in 2023-2026 in the top 20% Risk ranked circuits, other high-risk circuits, and for all other undergrounding programs.1 i. Please provide this table with the 2025 column updated to reflect PG&E’s 2025 workplan. If the 2025 workplan has not been finalized, please update the table with the current 2025 workplan as of receipt of this data request. ii. Please provide a table outlining PG&E’s 2025 covered conductor workplan including the number of miles in the top 20% risk ranked circuit segments, other high-risk (if applicable), and other covered conductor programs. If the 2025 workplan has not been finalized, please update the table with the current 2025 workplan as of receipt of this data request. b. In table RN-PG&E-05-2 of PG&E’s 2023-2025 WMP, PG&E provides the number of undergrounding miles planned and percentage of portfolio in the top 20% WFE, WDRM v2, WDRM v3, and WDRM v2 + WDRM v3.2 i. Please provide this table with the 2025 row updated to reflect PG&E’s 2025 workplan. If the 2025 workplan has not been finalized, please update the table with the current 2025 workplan as of receipt of this data request. ii. Please provide this table for PG&E’s 2025 covered conductor workplan. If the 2025 workplan has not been finalized, please update the table with the current 2025 workplan as of receipt of this data request. | a. Based on the context of the question, PG&E believes the cited table in this request (8.1.2-2) is a typo, and the intended referenced table is PG&E-8.1.2-3: PG&E Undergrounding Workplan 2023-2026. For transparency, PG&E is providing an updated table 8.1.2-3 for 2023-2026 of our system hardening and undergrounding workplan data from our system of record, Distribution Operations Tool (DOT), as of May 21, 2024. Note, the total miles in 2025 is currently showing as oversubscribed compared to the target. PG&E is finalizing the planned end dates -- many of which will shift their end date into 2026, which is currently showing as undersubscribed in our system of record. For the requested updates to this table, please see the following tables below: i. Table 1: PG&E Undergrounding Workplan 2023-2026. This table incorporates updated miles for 2023 through 2026 from PG&E’s GH–04 undergrounding portfolio as of May 21, 2024. ii. Table 2: PG&E Overhead Hardening Workplan 2023-2026. This table incorporates overhead hardening miles which contribute to PG&E’s GH-01 system hardening portfolio as of May 21, 2024. b. For the requested updates to RN-PG&E-05-02 see the following tables below: i. Table 3: PG&E Undergrounding Workplan Top 20% Risk Comparison. This table incorporates updated miles for 2023 through 2026 from PG&E’s GH-04 undergrounding portfolio as of May 21, 2024. ii. Table 4: PG&E Overhead Hardening Workplan Top 20% Risk Comparison. This table summarizes overhead hardening miles from PG&E’s GH-01 system hardening portfolio as of May 21, 2024. | Brad Hill | 2024-05-17 | 2024-05-24 | 2024-05-24 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/OEIS_020.zip | 0 | N/A | 9 | Section 8.1.2 - Grid Design and System Hardening | 8.1.2.2 Undergrounding of electric lines and/or equipment | 2.1.1.2 GH-04 Undergrounding |  | OEIS | 020 | 3 | 2 | Mona Hedin | Deanna Maraccini | Underground Data Requests Julie Cerio Jerry Santos Lucy Morris | Megan Ardell Justin Sadler | Aaron Shapiro | Matt Pender | Yes | Yes | Yes |  | Yes | Yes | Yes |  | 2024-05-24 |  | 5/21 - extension requested to 5/24 due to SMEs needing more time. kxfk | 5/21 - extension requested to 5/24 due to SMEs needing more time. kxfk | [13 empty] | 1 | Underground Data Requests Julie Cerio Jerry Santos Lucy Morris | Megan Ardell Justin Sadler | Mona Hedin | Deanna Maraccini | Aaron Shapiro | 2 |  |  |  |  | completed | 0 | 0 | 0 | 0
566 | MGRA | Data Request No. 10 | MGRA_Data Request No. 10 | 2 | MGRA_Data Request No. 10_Q2 | Please provide a spreadsheet listing (as rows) of every planned undergrounding projected to be fully or partially completed by the end of 2025. This includes work currently underway, completed in 2024, or to be performed in 2024. a) Order number b) Program c) Circuit ID number d) Circuit-segment name or ID number (if the project affects more than one circuitsegment, please identify each one) e) Relevant wildfire risk score(s) from the wildfire risk model that you are using to estimate distribution risk in your 2025 WMP Update filing f) The expected or actual start date of the project g) The expected completion date of the project h) Length (in circuit miles) of underground conductor to be installed prior to the end of 2025 j) Length (in circuit miles) of overhead conductor to be permanently removed prior to the end 2025 and replaced by underground conductor (note that this may differ slightly from the previous section due to differing overhead and underground routes) k) Length (in circuit miles) of overhead conductor to be permanently removed in 2025 and not replaced with covered conductor or undergrounded) l) Total number of customers served by the project m) Total number of minutes of PSPS experienced by the project circuit segments since 2019. | Please see attachment “WMP-Discovery2023-2025_DR_MGRA_010-Q002Atch01.xlsx”, worksheet “Q2 a-k” for a list of PG&E’s forecasted undergrounding projects for 2024-2026. Please note that the forecasted miles for 2025 and 2026 have been combined in this report as the projects associated with each of these years are still being finalized. A description of the included fields is as follows: a) In worksheet “Q2 a-k”, please see column A (Order). b) In worksheet “Q2 a-k”, please see column B (Category). c) In worksheet “Q2 a-k”, please see column C (Circuit ID) and column D (Circuit Name). d) In worksheet “Q2 a-k”, please see column E (Circuit Protection Zone (CPZ)). e) In worksheet “Q2 a-k”, please see column H (Applicable Risk Score) and column G (Applicable Risk Model). f) In worksheet “Q2 a-k”, please see column I (Est. Construction Start Date). This date represents the estimated date construction will be initiated on the project, recognizing there are additional phases prior to the construction start (e.g., planning, design, estimating, permitting). g) In worksheet “Q2 a-k”, please see column J (Est. Project End Date). The year included represents when the newly installed undergrounded lines are planned for electrification and the project is considered complete. Since the key criteria for reporting miles as complete is not the construction end date, but the fire risk safety audit completion and electric energization, please note that a project can have a construction end dates at the end of year, but may be associated with the following year given they passed the fire risk safety audit in the later year. This dynamic is common within the year as well. h) In worksheet “Q2 a-k”, please see column M (Total Planned UG Miles). The sum of all undergrounding miles planned for the project for 2024-2026. As noted above the, forecasted miles for 2025 and 2026 have been combined in this report. i) [Noting that this Data Request skipped subpart (i) and, therefore, no response is included.] j) PG&E interprets the data requested as the distance of existing overhead infrastructure that was replaced with underground infrastructure in an undergrounding project. This information is not provided in this response because PG&E currently does not have complete tabular data to provide the total overhead circuit-miles removed relating to the undergrounding project. k) In worksheet “Q2 a-k”, please see column N (Total Planned Removal Miles). This includes the sum of all Line Removal miles planned for the project for 2024-2026. WMP-Discovery2023-2025_DR_MGRA_010-Q002 Page 3 As noted above, the, forecasted miles for 2025 and 2026 have been combined in this report. l) In worksheet “Q2 l-m,” please see column B for data, and see the response to MGRA 010-Question 001 subpart i of this data request for an explanation. m) In worksheet “Q2 l-m,” please see columns C and D for data. Additionally, please see the response to Request No. 1, subpart (j) of this data request for a further explanation. | Joseph Mitchell | 2024-04-12 | 2024-04-17 | 2024-04-17 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_010.zip | 1 | N/A | 8 | Section 8.1.2 - Grid Design and System Hardening | 8.1.2.2 Undergrounding of electric lines and/or equipment | 2.1.1.2 GH-04 Undergrounding |  | MGRA | Data Request No. 10 | 2 | 13 | Mona Hedin | Andrew Trombley | UG Team Jerry Santos Julie Cerio Lucy Morris PSPS Team | Megan Ardell Shawn Holder | Kenny Lee | Matt Pender Mark Quinlan | Yes | Yes | Yes |  | Yes | Yes |  |  | 2024-04-17 | [16 empty] | 2 | UG Team Jerry Santos Julie Cerio Lucy Morris PSPS Team | Megan Ardell Shawn Holder | Mona Hedin | Andrew Trombley | Kenny Lee | 13 |  |  |  |  | completed | 0 | 0 | 0 | 0
565 | MGRA | Data Request No. 10 | MGRA_Data Request No. 10 | 1 | MGRA_Data Request No. 10_Q1 | Please provide a spreadsheet listing (as rows) of every undergrounding project completed during the period of January 1, 2023, through December 31, 2023, including non-WMP projects. For each project, please provide the following information (as columns): a) Project ID number or other identifier b) Circuit ID c) ID of each circuit segment that was entirely undergrounded in the project d) ID of each circuit segment that was partially undergrounded in the project e) Total overhead circuit-miles removed f) Total circuit-miles of underground conductor installed g) Total miles of trenching required h) Total electric costs of the project (i.e., costs attributed to your electric facilities), including costs for planning, design, permitting, and construction i) Total number of customers served by the project j) Total number of minutes of PSPS experienced by the project circuit segments since 2019. | Please see attachment “WMP-Discovery2023-2025_DR_MGRA_010-Q001Atch01.xlsx,” worksheet “Q1 a-h”, for a list of PG&E’s system hardening projects with undergrounding miles—as well as the Community Rebuild undergrounding miles— completed in 2023. Descriptions of the included fields are as follows: a) In worksheet “Q1 a-h”, please see column A (Order). b) In worksheet “Q1 a-h”, please see column B (Circuit ID), also included are the following related fields: • Column C (Circuit Name); • Column D (Circuit Protection Zone (CPZ)). c) Not applicable. To date, no circuit segment (referred to as a CPZ in this response) has been fully undergrounded. When PG&E undergrounds a CPZ, 100% of the pre-existing overhead circuitry is not replaced because one or more of the following reasons may be applicable: • Hardening applied to a CPZ can be a hybrid of mitigation methods (overhead hardening, undergrounding, line removal). • There are portions of the CPZ in locations that are infeasible to replace with underground circuitry (e.g. water crossings). • Hardening a CPZ may be split into multiple sub-projects, each focused on different portions of the CPZ. Various project specific constraints (e.g. permits) lead to multi-year hardening of a whole CPZ. d) Please see the response to subpart (c). All circuit segments (referred to as a CPZ in this response) identified in this response are considered partially undergrounded; therefore, that field is not included in the attachment. e) PG&E interprets the request for “Total overhead circuit-miles removed” as the distance of existing overhead infrastructure that was replaced with underground infrastructure in an undergrounding project. This information is not provided in this response because PG&E currently does not have complete tabular data to provide the total overhead circuit-miles removed relating to the undergrounding project. This information is actively being consolidated and will be available in PG&E’s System Hardening Accountability Report in accordance with the requirements of GRC 23-11-069 (OP 20–23). f) In worksheet “Q1 a-h”, please see column T (UG – 2023 Complete). This includes the undergrounding miles completed in 2023. In worksheet “Q1 a-h”, please see column L (Total Planned UG Miles). This includes the sum of all undergrounding miles planned for the project for all years, including 2023 miles completed and pre- and post-2023, where applicable. Also provided is mileage for our other system hardening methods (overhead hardening and line removal). g) Trenching length data is not currently captured; therefore, that field is not provided in the attachment. h) In worksheet “Q1 a-h”, please see column AA (Total Estimated Actual Cost). PG&E interprets “electric costs” as project costs associated with starting and completing an electric undergrounding project; therefore, both incurred and forecasted costs for the project are included. i) In worksheet “Q1 i-j,” please see column B (Customer Count – April 2024). PG&E does not currently have a complete mapping of customer counts by undergrounding order (job). PG&E is proving the number of customers associated with a CPZ as of April 2024 where undergrounding work has taken place in 2023. Note, the customers reported by CPZ are not representative of the customers impacted by a specific undergrounding project. j) In worksheet “Q1 i-j,” please see columns C and D. PSPS minutes are measured at the customer level, but PG&E does not currently have a completed mapping of customers to undergrounding orders (jobs). PG&E is providing two measures associated with total number of minutes of PSPS experienced by the project CPZs since 2019 where undergrounding work has taken place in 2023: 1. The minutes reported in column C (Sum of PSPS Minutes for Average Customer Outage on CPZ) is a total of the average customer outage duration from events in 2019-2023. 2. The minutes reported in column D (Sum of PSPS Minutes for Maximum Event Duration on CPZ) is a total from events in 2019-2023, measuring the duration from the beginning of the first outage start and concluding with the last outage end. PG&E points out that the minutes reported in column C may be less than the minutes reported in column D for the following reasons: • Some customers may experience multiple short-duration outages within the same PSPS event, such as microgrid switching. Column C reports the duration as the sum of these multiple outage durations, while column D calculates the time period between the earliest outage start (among these multiple outages) and the last outage end. • Customers located on the same CPZ may be restored at different times. This results in the average outage duration reported, in column C, being lower than the duration reported in column D (which uses the restoration time of the last customer as the end time). Note, the PSPS minutes reported by CPZ is not representative of the outages on a specific portion of that CPZ that is in scope of a specific undergrounding project. | Joseph Mitchell | 2024-04-12 | 2024-04-17 | 2024-04-17 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_010.zip | 1 | N/A | 8 | Section 8.1.2 - Grid Design and System Hardening | 8.1.2.2 Undergrounding of electric lines and/or equipment | 2.1.1.2 GH-04 Undergrounding |  | MGRA | Data Request No. 10 | 1 | 10 | Mona Hedin | Andrew Trombley | UG Team Jerry Santos Julie Cerio Lucy Morris PSPS Team | Megan Ardell Shawn Holder | Kenny Lee | Matt Pender Mark Quinlan | Yes | Yes | Yes |  | Yes | Yes |  |  | 2024-04-17 | [16 empty] | 1 | UG Team Jerry Santos Julie Cerio Lucy Morris PSPS Team | Megan Ardell Shawn Holder | Mona Hedin | Andrew Trombley | Kenny Lee | 10 |  |  |  |  | completed | 0 | 0 | 0 | 0
508 | CalPA | Set WMP-40 | CalPA_Set WMP-40 | 2 | CalPA_Set WMP-40_Q2 | PG&E states on page 23 of its 2025 WMP Update regarding its workplan for undergrounding projects: PG&E is currently refining our workplans for both overhead hardening and undergrounding projects through the end of the GRC period (2026) to account for the direction provided in D.23-11-069. Additionally, PG&E’s Base 2023-2025 WMP R5 at page 408 states annual undergrounding mileage targets or forecasts: 350 miles in 2023, 250 miles in 2024, 330 miles in 2025, and 440 miles in 2026. With respect to undergrounding projects specifically: a) D.23-11-069 sets annual risk reduction targets to be achieved by undergrounding.4 In the 2023-2025 WMP period as a whole, does PG&E currently expect to fall short of, meet, or exceed the risk reduction target established in the GRC proceeding? b) According to PG&E’s current workplan, what is the amount of risk reduction that PG&E expects to achieve in 2024 due to undergrounding projects? c) How does your answer to part (b) compare to the risk reduction target established in D.23-11-069? d) According to PG&E’s current workplan, what is the amount of risk reduction that PG&E expects to achieve in 2025 due to undergrounding projects? e) How does your answer to part (d) compare to the risk reduction target established in D.23-11-069? f) Does PG&E anticipate completing additional undergrounding mileage in 2023-2026 beyond the GRC-authorized 1,230 undergrounding miles? g) If yes, please state the number of miles and PG&E’s intended cost recovery venue for said miles. | a. PG&E intends to meet the cumulative system hardening risk reduction requirement of 18% by 2026, using the risk reduction methodology described in Advice Letter 7150-E-A. b. Based on the workplan as of February 22, 2024, and using the GRC risk reduction methodology described in Advice Letter 7150-E-A, the 2024 target-informed risk reduction for undergrounding projects is currently forecasted to be approximately 1.6%. Using the WMP risk reduction method (risk reduction based on WDRM v3 only), the target-informed anticipated risk reduction for undergrounding projects currently forecasted for completion in 2024 is approximately 1.5%. Note: these values only include projects in Maintenance Activity Type (MAT) codes 08W and 3UG. c. Annual risk reduction forecasts established in D.23-11-069 are cumulative for the GRC period (2023-2026). Risk reduction forecasts for specific mitigation types were not established. The response to subpart (b) includes the undergrounding contribution to the GRC System Hardening cumulative risk reduction target (to be achieved by 2026) noted above and shown in the table below. System Hardening GRC Risk Reduction Targets (per D.23-11-069, OP 23) Date 12/31/2023 12/31/2024 12/31/2025 12/31/2026 Overall Target: 2023-2026 Cumulative Risk Reduction Target 2% 5% 10% 18% 18% For all system hardening work, including overhead covered conductor, underground and line removal, the 2024 cumulative risk reduction target established in D.23-11- 069 is 5% for 2023-2024. Based on the system hardening workplan as of February 22, 2024 and using the GRC risk reduction methodology described in Advice Letter 7150-E-A, PG&E’s current forecasted cumulative risk reduction for system hardening in 2023-2024 is 4.7% (MAT codes 3UG and 08W only). The actual risk reduction values of completed system hardening work are expected to meet the overall cumulative target of 18% by 2026. Note, as described in the 2023 WMP ACI 22-16, the workplans purposefully build in additional miles compared to the proposed targets at that time to account for the fact that project dependencies and construction issues may arise and delay some projects. Therefore, the cumulative mileage and risk reduction associated with the workplan are currently overstated as compared to what would be accomplished in accordance with the target. To account for this, the risk reduction reported in this response has been proportionately adjusted to align the anticipated risk reduction with the target miles. d. The system hardening workplan associated with years 2025 and 2026 is currently combined, as the projects associated with each year are still being finalized. Based on the workplan as of February 22, 2024 and using the GRC risk reduction methodology described in Advice Letter 7150-E-A, the 2025-2026 target-informed risk reduction for undergrounding projects is currently forecasted to be approximately 8.3%. Using the WMP risk reduction method (risk reduction based on WDRM v3 only), the target-informed anticipated risk reduction for undergrounding projects currently forecasted for completion in 2025-2026 is approximately 8.4%. Note: these values only include projects in MAT codes 08W and 3UG. e. As mentioned in subpart (c), risk reduction targets established in D.23-11-069 are cumulative for the GRC period (2023-2026). Risk reduction targets for specific mitigation types were not established. The response to sub-part d includes the undergrounding contribution to the GRC System Hardening cumulative risk reduction target noted above and shown in the table below. System Hardening GRC Risk Reduction Targets (per D.23-11-069, OP 23) Date 12/31/2023 12/31/2024 12/31/2025 12/31/2026 Overall Target: 2023-2026 Cumulative Risk Reduction Target 2% 5% 10% 18% 18% For all system hardening work, including overhead covered conductor, underground and line removal, the 2025 cumulative risk reduction target established in D-23-11- 069 is 10% for 2023-2025, and 18% for 2023-2026. Based on the system hardening workplan as of February 22, 2024 and using the GRC risk reduction methodology described in Advice Letter 7150-E-A, PG&E’s current forecasted cumulative risk reduction for system hardening in 2025-2026 and 2023-2026 is 13.7% and 18.4%, respectively (MAT codes 3UG and 08W only). Note, as described in the 2023 WMP ACI 22-16, the workplans purposefully build in additional miles compared to the proposed targets at that time to account for the fact that project dependencies and construction issues may arise and delay some projects. Therefore, the cumulative mileage and risk reduction associated with the workplan are currently overstated as compared to what would be accomplished in accordance with the target. To account for this, the risk reduction reported in this response has been proportionately adjusted to align the anticipated risk reduction with the target miles. f. PG&E does not currently anticipate materially exceeding the 1,230 miles of undergrounding targeted in the 2023 GRC decision. PG&E intends to align with the authorized 2023 GRC system hardening cost cap of $4.723 billion and 18% cumulative risk reduction target. PG&E may continue to complete undergrounding work beyond the 1,230 miles if those miles are within authorized costs. PG&E would count those miles as contributing to the four-year cumulative risk reduction requirement. g. If undergrounding miles are completed beyond the 1,230 estimated miles but are within the authorized costs and contribute to the risk reduction requirements, PG&E will recover costs in the GRC Wildfire Mitigation Balancing Account (WMBA). | Miles Gordon | 2024-04-05 | 2024-04-10 | 2024-04-10 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_040.zip | 0 | N/A | 8 | Section 8.1.2 - Grid Design and System Hardening | 8.1.2.2 Undergrounding of electric lines and/or equipment | 2.1.1.2 GH-04 Undergrounding |  | CalPA | Set WMP-40 | 2 | 7 | Mona Hedin | Andrew Trombley Alex Quintana | System Hardening Merih Tekeste Brad Koelling Heidi Ramos UG Data Requests Jerry Santos Julie Cerio Lucy Morris | Megan Ardell | Aaron Shapiro | Matt Pender | Yes | Yes | Yes |  | Yes |  | Yes |  | 2024-04-10 | [16 empty] | 2 | System Hardening Merih Tekeste Brad Koelling Heidi Ramos UG Data Requests Jerry Santos Julie Cerio Lucy Morris | Megan Ardell | Mona Hedin | Andrew Trombley Alex Quintana | Aaron Shapiro | 7 |  |  | DRU13430 |  | completed | 0 | 0 | 0 | 0
507 | CalPA | Set WMP-40 | CalPA_Set WMP-40 | 1 | CalPA_Set WMP-40_Q1 | PG&E states on page 23 of its 2025 WMP Update regarding its workplan for undergrounding and covered conductor projects: PG&E is currently refining our workplans for both overhead hardening and undergrounding projects through the end of the GRC period (2026) to account for the direction provided in D.23-11-069. As we update the workplan, we continue the approach described in the Base 2023-2025 WMP of intentionally building additional miles into the workplan to account for unforeseen delays to individual projects such as property access, weather, permitting, land rights acquisition, materials, or other constraints. Thus, some of the projects included in this workplan may not be completed in the 2023 to 2026 timeframe. Generally, PG&E will continue working on these projects until they can be completed. Finally, additional projects may be identified and added to the workplan going forward for potential completion between 2023 and 2026. a) Please identify PG&E’s intended cost recovery venue for the abovementioned undergrounding projects not completed in the 2023-26 timeframe. b) Please identify PG&E’s intended cost recovery venue for the abovementioned overhead hardening projects not completed in the 2023-26 timeframe. c) Please identify PG&E’s intended cost recovery venue for the abovementioned “additional projects” that may be identified and added to the workplan. | a. The cost recovery venue for undergrounding projects depends on the year in which the project becomes operational (i.e. is electrified). Any undergrounding project made operational in 2023-2026 will be recovered through PG&E’s 2023 General Rate Case (GRC) via the Wildfire Mitigation Balancing Account (WMBA). PG&E plans to submit its SB 884 10-Year Undergrounding Plan with a currently anticipated program launch date of January 1, 2027 and proposes that any undergrounding project that is operational on or after January 1, 2027 would be recovered through PG&E’s SB 884 10-Year Undergrounding Plan. While PG&E’s intent is to launch the SB 884 undergrounding program in 2027, PG&E is currently awaiting the SB 884 10-Year Plan guidelines from Energy Safety. Based on the review timeline of the legislation (i.e., nine-month review by Energy Safety, two months for electric utilities to submit to the CPUC, and nine-month review by CPUC), if final guidelines are issued mid-year 2024, the earliest we could possibly receive approval for our SB 884 Plan and cost recovery would be in mid2026. Thus, PG&E anticipates our Plan period would begin January 1, 2027 – meaning that projects included in our SB 884 Plan would begin to be electrified in 2027. The Plan launch in January 2027 assumes Energy Safety and the CPUC approve our Plan and cost recovery without requiring significant changes to our planned program. Furthermore, given the typical undergrounding project lifecycle of approximately two or more years, electrifying projects in 2027 will require project readiness work in 2025 and 2026. Thus, PG&E would begin incurring costs in 2025 and 2026 for projects that will become used and useful in the SB 884 Plan period of 2027 and beyond. PG&E’s cost recovery application will include these costs for readiness work for projects that become operative during the SB 884 Plan period. b. Any overhead hardening projects not fully completed in the 2023-2026 GRC timeframe will continue to be recovered through PG&E’s next GRC period via the WMBA. c. Please see the responses to subparts (a) and (b) for the requested information. | Miles Gordon | 2024-04-05 | 2024-04-10 | 2024-04-10 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_040.zip | 0 | N/A | 8.1.2 | Section 8.1.2 - Grid Design and System Hardening | 8.1.2.2 Undergrounding of electric lines and/or equipment | 2.1.1.2 GH-04 Undergrounding |  | CalPA | Set WMP-40 | 1 | 3 | Mona Hedin | Andrew Trombley Alex Quintana | System Hardening Merih Tekeste Brad Koelling Heidi Ramos UG Data Requests Jerry Santos Julie Cerio Lucy Morris | Megan Ardell | Aaron Shapiro | Matt Pender | Yes | Yes | Yes |  | Yes |  | Yrd |  | 2024-04-10 | [16 empty] | 1 | System Hardening Merih Tekeste Brad Koelling Heidi Ramos UG Data Requests Jerry Santos Julie Cerio Lucy Morris | Megan Ardell | Mona Hedin | Andrew Trombley Alex Quintana | Aaron Shapiro | 3 |  |  | DRU13430 |  | completed | 0 | 0 | 0 | 0
530 | MGRA | Data Request No. 9 | MGRA_Data Request No. 9 | 8 | MGRA_Data Request No. 9_Q8 | If not, is EPSS enabled based on weather conditions and if so how? | Yes, EPSS is enabled and disabled based on forecasted weather conditions. EPSS settings are enabled or disabled based on criteria approved by our Wildfire Risk Governance Steering Committee. This criteria is based on 2km-by-2km model outputs from our Fire Potential Index (FPI) model. PG&E’s FPI model is trained to identify localized wildfire risk based on a variety of key risk indicators derived from fire science as well as lessons learned from previous catastrophic wildfires. | Joseph Mitchell | 2024-04-08 | 2024-04-11 | 2024-04-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_009.zip | 0 | N/A | 8.1.8.1.1 | 8.1.8 Grid Operations and Procedures | 8.1.8.1.1 Protective Equipment and Device Settings | 2.1.1.3 PS-07: Reduce PSPS Impacts to Customers |  | MGRA | Data Request No. 9 | 8 | 0 | Mona Hedin | Saritha Basani | Katherine Hee | Eric Lamoureux | Kenny Lee | Mark Quinlan Martin Wyspianski | Yes | Yes | Yes |  | Yes | Yes | Yes |  | 2024-04-11 | [16 empty] | 8 | PSPS PMO/UG Team | Shawn Holder/Megan Ardel | Mona Hedin | Alex Quintana | Kenny Lee | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
529 | MGRA | Data Request No. 9 | MGRA_Data Request No. 9 | 7 | MGRA_Data Request No. 9_Q7 | Does MSO also allow for EPSS to be enabled as a function of weather conditions? | Motor Switch Operator (MSO) devices are not capable of fault protection and therefore are not part of EPSS. As part of the MSO initiative in the WMP, these units are being replaced with either a line recloser, an automated switch, or a manual switch. If the line recloser option is selected, those replaced devices will have EPSS capability and be enabled during EPSS weather conditions. | Joseph Mitchell | 2024-04-08 | 2024-04-11 | 2024-04-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_009.zip | 0 | N/A | 8.1.8.1.1 | 8.1.8 Grid Operations and Procedures | 8.1.8.1.1 Protective Equipment and Device Settings | 2.1.1.3 PS-07: Reduce PSPS Impacts to Customers |  | MGRA | Data Request No. 9 | 7 | 0 | Mona Hedin | Saritha Basani | Katherine Hee James Tuccillo | Eric Lamoureux | Kenny Lee | Mark Quinlan Martin Wyspianski | Yes | Yes | Yes |  | Yes | Yes | Yes |  | 2024-04-11 | [16 empty] | 7 | Katherine Hee | Eric Lamoureux | Mona Hedin | Saritha Basani | Kenny Lee | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
528 | MGRA | Data Request No. 9 | MGRA_Data Request No. 9 | 6 | MGRA_Data Request No. 9_Q6 | Explain how MSO reduces PSPS incidence. | For clarification, Motorized Switch Operator (MSO) devices do not reduce “PSPS incidence,” but rather the scope of customer impact during a PSPS event. While MSO devices were intended to serve as a sectionalizing device, PG&E identified MSO devices as an ignition risk when operated while energized due to the chance of arc flashes. As a result, MSO devices are not operated while energized, but must first be de-energized before they can be operated. If an MSO device is selected for a PSPS event, the next upstream non-MSO device must first be used to temporarily de-energize the MSO device, so that the MSO device can be operated while de-energized. The non-MSO device is closed to energize up to the now-open MSO device. This procedure eliminates the ignition risk from the MSO device but results in a short duration PSPS outage for the customers located between the MSO device and the upstream device. If the MSO device is replaced with a non-MSO device such as reclosers, subsurface equipment, and other vacuum switch equipment approved for current usage, these short duration outage customers will no longer experience any outage during the PSPS event because the replacement devices can be opened directly without needing to utilize an upstream device. | Joseph Mitchell | 2024-04-08 | 2024-04-11 | 2024-04-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_009.zip | 0 | N/A | 9.1.5 | 9.0 Public Safety Power Shutoff | 9.1.5 Performance Metrics Identified by the Electrical Corporation | 2.1.1.3 PS-07: Reduce PSPS Impacts to Customers |  | MGRA | Data Request No. 9 | 6 | 0 | Mona Hedin | Wilson Wong | PSPS PMO UG Team Jerry Santos Julie Cerio Lucy Morris | Shawn Holder | Kenny Lee | Matt Pender Mark Quinlan | Yes | Yes | Yes |  | Yes | Yes | Yes |  | 2024-04-11 | [16 empty] | 6 | PSPS PMO UG Team Jerry Santos Julie Cerio Lucy Morris | Shawn Holder | Mona Hedin | Wilson Wong | Kenny Lee | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
527 | MGRA | Data Request No. 9 | MGRA_Data Request No. 9 | 5 | MGRA_Data Request No. 9_Q5 | PS-07: Reduce PSPS Impacts to Customers (Section 9.1.5) For the 22k to 13k reduction in customers exposed to PSPS events, how much of the reduction is due to 1) undergrounding 2) Motorized Switch Operations (MSOs), and 3) other factors. | All of the reduction from 22k to 13k is attributed to undergrounding. As mentioned in section B.2.1.1.3 of the 2025 WMP, the number of undergrounding miles for 2025 was adjusted from 550 miles to 330 miles, therefore the reduction in customer events mitigated corresponds proportionally to the decrease in undergrounding miles completed. No customer events mitigated from Motorized Switch Operations (MSO) replacements are expected in 2025 as the program is expected to be completed in 2024. | Joseph Mitchell | 2024-04-08 | 2024-04-11 | 2024-04-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_009.zip | 0 | N/A | 9.1.5 | 9.0 Public Safety Power Shutoff | 9.1.5 Performance Metrics Identified by the Electrical Corporation | 2.1.1.3 PS-07: Reduce PSPS Impacts to Customers |  | MGRA | Data Request No. 9 | 5 | 0 | Mona Hedin | Wilson Wong | PSPS PMO UG Team Jerry Santos Julie Cerio Lucy Morris | Shawn Holder Megan Ardell | Kenny Lee | Matt Pender/Mark Quinlan | Yes | Yes | Yes |  | Yes | Yes | Yes |  | 2024-04-11 | [16 empty] | 5 | PSPS PMO UG Team Jerry Santos Julie Cerio Lucy Morris | Shawn Holder Megan Ardell | Mona Hedin | Wilson Wong | Kenny Lee | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
648 | CPUC - SPD (Safety Policy Division) | 016 | CPUC - SPD (Safety Policy Division)_016 | 5 | CPUC - SPD (Safety Policy Division)_016_Q5 | Provide GIS Data that show progressive sectionalization of PSPS-enabled circuits: a. Data snapshot of circuits from January 1, 2020 b. Data snapshot of circuits from January 1, 2021 c. Data snapshot of circuits from January 1, 2022 d. Data snapshot of circuits from January 1, 2023 e. Data snapshot of circuits from January 1, 2024 | PG&E is still compiling data and will provide the requested information as soon as possible. | Henry Sweat | 2024-05-30 | 2024-06-04 | 2024-06-04 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_016.zip | 0 | N/A | 9 | Section 9 - Public Safety Power Shutoff | 9.1.5 Performance Metrics Identified by the Electrical Corporation | 2.1.1.3 PS-07: Reduce PSPS Impacts to Customers |  | CPUC - SPD (Safety Policy Division) | 016 | 5 | 5 | Mona Hedin | Wilson Wong | PSPS Team; GIS | Shawn Holder | Kenny Lee | Mark Quinlan | Yes |  | Yes |  | Yes |  | Yes |  | 2024-06-04 | [16 empty] | 5 | PSPS Team; GIS | Shawn Holder | Mona Hedin | Wilson Wong | Kenny Lee | 5 |  |  |  |  | completed | 0 | 0 | 0 | 0
610 | CalPA | Set WMP-47 | CalPA_Set WMP-47 | 1 | CalPA_Set WMP-47_Q1 | The attached spreadsheet (filename “CalAdvocates-PGE-2025WMP-11Q1ATTCH_CONF.xlsx”) contains a subset of PG&E’s 2024-2026 system hardening workplan as provided in response to Cal Advocates data request CalAdvocates-PGE-2025WMP-01 Question 8. Specifically it contains 30 undergrounding projects that were scoped using Wildfire Distribution Risk Model (WDRM) v2, 30 undergrounding projects that were scoped using Wildfire Distribution Risk Model v3, and 51 projects in locations with a mix of v2 and v3 basis. a) For all projects scoped using WDRM v2 (in the tab labeled “v2 projects”), please provide the total risk reduction percentage (similar to Column AN) for these projects using WDRM v4 in a working Excel spreadsheet (i.e., with links, formulae, source data, etc.). b) For all projects scoped using WDRM v3 (in the tab labeled “v3 projects”), please provide the total risk reduction percentage (similar to Column AN) for these projects using WDRM v4 in a working Excel spreadsheet (i.e., with links, formulae, source data, etc.). c) For all projects in the tab “v2 and v3 mix”, please provide the total risk reduction percentage (similar to Column AN) for these projects using WDRM v4 in a working Excel spreadsheet (i.e., with links, formulae, source data, etc.). | PG&E objects to each of the three subparts of this request on the grounds that they are overly burdensome because it would involve multiple months of work to obtain the requested analysis. Given that the model was only recently released, work in implementing the model is ongoing and still in the early stages. PG&E cannot provide the requested information as PG&E does not currently have WDRM v4 risk reduction calculations available for the 2023-2026 System Hardening workplan specific to the job level. WMP-Discovery2023-2025_DR_CalAdvocates_047-Q001 Page 2 PG&E notes that each version of the WDRM has statistical validity and each iteration does not invalidate the results of preceding models. In other words, retroactively applying a newer model to a portfolio scoped with prior models does not impact the viability of the previously derived results. Please do not hesitate to reach out if you would like to meet and confer about this request as we would be happy to further discuss this issue with you. | Miles Gordon | 2024-04-20 | 2024-05-03 | 2024-05-03 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_047.zip | 0 | N/A | 8.1.2.5 | System Hardening | N/A | 2.1.4.1 GH-11 Traditional Overhead Hardening Conductor |  | CalPA | Set WMP-47 | 1 |  | Mona Hedin | Mandy Knockaert/Kaet Bulkowski | Underground Data Requests Julie Cerio Jerry Santos Lucy Morris SH Risk | Justin Sadler Jon Eric Thalman Paul McGregor Megan Ardell | Aaron Shapiro | Matt Pender Martin Wyspianski Andy Abranches | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | 2024-05-03 | [16 empty] | 1 | Underground Data Requests Julie Cerio Jerry Santos Lucy Morris SH Risk | Justin Sadler Jon Eric Thalman Paul McGregor Megan Ardell | Mona Hedin | Mandy Knockaert/Kaet Bulkowski | Aaron Shapiro | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
510 | CalPA | Set WMP-40 | CalPA_Set WMP-40 | 4 | CalPA_Set WMP-40_Q4 | PG&E states on page 25 of its 2025 WMP Update: “PG&E proposes to add a 2025 target (System Hardening – Transmission Conductor Segment Replacement (GH-11)) to perform conductor segment replacement on two transmission lines.” a) Was the abovementioned work requested and authorized in PG&E’s Test Year 2023 GRC? b) If yes, please provide the exhibit and page number in PG&E’s Test Year 2023 GRC testimony that discusses this work, as well as the relevant Major Activity Type (MAT) code or codes. c) If yes, please provide the final authorized funding amount for this program as set forth in D.23-11-069, with a citation to the relevant pages of that decision.5 | a) No. System Hardening - Transmission Conductor Segment Replacement was not forecast or authorized in the 2023 General Rate Case (GRC). b) Not applicable, please see the response to subpart (a). c) Not applicable, please see the response to subpart (a). | Miles Gordon | 2024-04-05 | 2024-04-10 | 2024-04-10 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_040.zip | 0 | N/A | 8 | Section 8.1.2 - Grid Design and System Hardening | 8.1.2.5.1 Traditional Overhead Hardening – Transmission Conductor | 2.1.4.1 GH-11 Traditional Overhead Hardening Conductor |  | CalPA | Set WMP-40 | 4 | 3 | Mona Hedin | Andrew Trombley Alex Quintana | Kathy Wade (GRC) System Hardening Merih Tekeste Brad Koelling Heidi Ramos UG Data Requests Jerry Santos Julie Cerio Lucy Morris | Vincent Tanguay (GRC) Megan Ardell | Aaron Shapiro | Matt Pender | Yes | Yes | Yes |  | Yes |  |  |  | 2024-04-10 | [16 empty] | 4 | Kathy Wade (GRC) System Hardening Merih Tekeste Brad Koelling Heidi Ramos UG Data Requests Jerry Santos Julie Cerio Lucy Morris | Vincent Tanguay (GRC) Megan Ardell | Mona Hedin | Andrew Trombley Alex Quintana | Aaron Shapiro | 3 |  |  | DRU13430 |  | completed | 0 | 0 | 0 | 0
509 | CalPA | Set WMP-40 | CalPA_Set WMP-40 | 3 | CalPA_Set WMP-40_Q3 | PG&E states on page 23 of its 2025 WMP Update regarding its workplan for covered conductor projects: PG&E is currently refining our workplans for both overhead hardening and undergrounding projects through the end of the GRC period (2026) to account for the direction provided in D.23-11-069. With respect to covered conductor projects specifically: a) D.23-11-069 sets annual risk reduction targets to be achieved by installing covered conductor. In the 2023-2025 WMP period as a whole, does PG&E currently expect to fall short of, meet, or exceed the risk reduction target established in the GRC proceeding? b) According to PG&E’s current workplan, what is the amount of risk reduction that PG&E expects to achieve in 2024 due to covered conductor projects? c) How does your answer to part (b) compare to the risk reduction target established in D.23-11-069? d) According to PG&E’s current workplan, what is the amount of risk reduction that PG&E expects to achieve in 2025 due to covered conductor projects? e) How does your answer to part (d) compare to the risk reduction target established in D.23-11-069? f) Does PG&E anticipate completing additional covered conductor mileage in 2023-2026 beyond the GRC-authorized 778 covered conductor miles? g) If yes, please state the number of miles and PG&E’s intended cost recovery venue for said miles. | a. PG&E intends to meet the cumulative system hardening risk reduction requirement of 18% by 2026 using the risk reduction methodology described in Advice Letter 7150-E-A. b. Based on the workplan as of February 22, 2024 and referencing the GRC risk reduction methodology described in Advice Letter 7150-E-A, the 2024 targetinformed risk reduction for overhead hardening projects is currently forecasted to be approximately 0.6%. Using the WMP risk reduction method (risk reduction based on WDRM v3 only), the target-informed anticipated risk reduction for overhead hardening projects currently forecasted for completion in 2024 is approximately 0.1%. Note: these values only include projects in Maintenance Activity Type (MAT) codes 08W and 3UG. c. Annual risk reduction forecasts established in D.23-11-069 are cumulative for the GRC period (2023-2026). Risk reduction forecasts for specific mitigation types were not established. The response to subpart (b) includes the overhead hardening contribution to the GRC System Hardening cumulative risk reduction target noted above and shown in the table below. System Hardening GRC Risk Reduction Targets (per D.23-11-069, OP 23) Date 12/31/2023 12/31/2024 12/31/2025 12/31/2026 Overall Target: 2023-2026 Cumulative Risk Reduction Target 2% 5% 10% 18% 18% For all system hardening work, including overhead covered conductor, underground and line removal, the 2024 cumulative risk reduction target established in D.23-11- 069 is 5% for 2023-2024. Based on the system hardening workplan as of February 22, 2024 and using the GRC risk reduction methodology described in Advice Letter 7150-E-A, PG&E’s current forecasted cumulative risk reduction for system hardening in 2023-2024 is 4.7% (MAT codes 3UG and 08W only). The actual risk reduction values of completed system hardening work is expected to meet the overall cumulative target of 18% by 2026. Note, as described in the 2023 WMP ACI 22-16, the workplans purposefully build in additional miles compared to the proposed targets at that time to account for the fact that project dependencies and construction issues may arise and delay some projects. Therefore, the cumulative mileage and risk reduction associated with the workplan are currently overstated as compared to what would be accomplished in accordance with the target. To account for this, the risk reduction reported in this response has been proportionately adjusted to align the anticipated risk reduction with the target miles. d. The system hardening workplan associated with years 2025 and 2026 is currently combined, as the projects associated with each year are still being finalized. Based on the workplan as of February 22, 2024 and referencing the GRC risk reduction methodology described in Advice Letter 7150-E-A, the 2025-2026 target-informed risk reduction for overhead hardening projects is currently forecasted to be approximately 5.0% Using the WMP risk reduction method (risk reduction based on WDRM v3 only), the target-informed anticipated risk reduction for overhead hardening projects currently forecasted for completion in 2025-2026 is approximately 4.3%. Note: these values only include projects in MAT codes 08W and 3UG. e. As mentioned in subpart (c), risk reduction targets established in D.23-11-069 are cumulative for the GRC period (2023-2026). Risk reduction targets for specific mitigation types were not established. The response to subpart (d) includes the overhead hardening contribution to the GRC System Hardening cumulative risk reduction target noted above and shown in the table below. System Hardening GRC Risk Reduction Targets (per D.23-11-069, OP 23) Date 12/31/2023 12/31/2024 12/31/2025 12/31/2026 Overall Target: 2023-2026 Cumulative Risk Reduction Target 2% 5% 10% 18% 18% For all system hardening work, including overhead covered conductor, underground and line removal, the 2025 cumulative risk reduction target established in D.23-11- 069 is 10% for 2023-2025, and 18% for 2023-2026. Based on the system hardening workplan as of February 22, 2024 and using the GRC risk reduction methodology described in Advice Letter 7150-E-A, PG&E’s current forecasted cumulative risk reduction for system hardening in 2025-2026 and 2023-2026 is 13.7% and 18.4%, respectively (MAT codes 3UG and 08W only). Note, as described in the 2023 WMP ACI 22-16, the workplans purposefully build in additional miles compared to the proposed targets at that time to account for the fact that project dependencies and construction issues may arise and delay some projects. Therefore, the cumulative mileage and risk reduction associated with the workplan are currently overstated as compared to what would be accomplished in accordance with the target. To account for this, the risk reduction reported in this response has been proportionately adjusted to align the anticipated risk reduction with the target miles. f. Please see the response to CalAdvocates_040_Q002, subpart (f), PG&E has the same position as it relates to Overhead Hardening target miles as articulated in the response to Q2 (f) for undergrounding. g. Please see the response to CalAdvocates_040_Q002, subpart (g) PG&E has the same position as it relates to Overhead Hardening target miles as articulated in the response to Q2 (g) for undergrounding. | Miles Gordon | 2024-04-05 | 2024-04-10 | 2024-04-10 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_040.zip | 0 | N/A | 8 | Section 8.1.2 - Grid Design and System Hardening | 8.1.2.1 Covered Conductor Installation – Distribution | 2.1.4.1 GH-11 Traditional Overhead Hardening Conductor |  | CalPA | Set WMP-40 | 3 | 7 | Mona Hedin | Andrew Trombley Alex Quintana | System Hardening Merih Tekeste Brad Koelling Heidi Ramos UG Data Requests Jerry Santos Julie Cerio Lucy Morris | Megan Ardell | Aaron Shapiro | Matt Pender | Yes | Yes | Yes |  | Yes |  | Yes |  | 2024-04-10 | [16 empty] | 3 | System Hardening Merih Tekeste Brad Koelling Heidi Ramos UG Data Requests Jerry Santos Julie Cerio Lucy Morris | Megan Ardell | Mona Hedin | Andrew Trombley Alex Quintana | Aaron Shapiro | 7 |  |  | DRU13430 |  | completed | 0 | 0 | 0 | 0
708 | CPUC - SPD (Safety Policy Division) | 021 | CPUC - SPD (Safety Policy Division)_021 | 1(s4) | CPUC - SPD (Safety Policy Division)_021_Q1(s4) | 1. Complete tabs 2 through 6 of the attached spreadsheet. For tabs 2 through 5, complete a corresponding data row for each of the 114 mitigation initiatives in the most recent QDR, Table 11 according to the directions in the spreadsheet and the two attached guidance documents listed below: • Guidance for WMP Cost Reporting (applicable to tab 2 through 5) • Guidance for Account Tracking (applicable to tab 6) |  | Kevin Miller | 2024-09-10 | 2024-12-27 |  |  |  | N/A | 4.3 | 4.0 Overview of WMP | 4.3 Proposed Expenditures | 2.3 Expenditures |  | CPUC - SPD (Safety Policy Division) | 021
708 | CPUC - SPD (Safety Policy Division) | 021 | CPUC - SPD (Safety Policy Division)_021 | 1 | CPUC - SPD (Safety Policy Division)_021_Q1 | 1. Complete tabs 2 through 6 of the attached spreadsheet. For tabs 2 through 5, complete a corresponding data row for each of the 114 mitigation initiatives in the most recent QDR, Table 11 according to the directions in the spreadsheet and the two attached guidance documents listed below: • Guidance for WMP Cost Reporting (applicable to tab 2 through 5) • Guidance for Account Tracking (applicable to tab 6) | PG&E and SPD met on September 27, 2024, to discuss clarifications within this request as well as a tranche schedule for production. Per this meeting, and follow up correspondence from SPD received October 1, 2024, PG&E will submit data on a weekly basis in tranches to SPD, with all data being submitted by November 1, 2024. PG&E would like to clarify that there are 109 activities with costs related to the Wildfire Mitigation Plan (WMP). PG&E is providing Columns A-G of the “General Info (1 of 5)” worksheet in Tranche 1, as well as information regarding SB 884. Please see attachment “WMP-Discovery2023-2025_DR_SPD_021-Q001Atch01.zip” for Tranche 1 of this request. Please see the following explanations per the instructions to report on the Utility Tracking ID included in Table 11 from the most recent Quarterly Data Report (QDR). Table 11 of the QDR includes: • WMP Initiative Categories (Column B); • WMP Initiative Activities (Column C), which are a subset of initiative categories; and • Utility Initiative Tracking IDs (UITID) (Column D) for WMP commitments. Table 11 shows some costs at the level of a specific commitment, such as CO-05 or GH-07, while it shows others at the level of an Initiative Activity. Within the latter group, Table 11 shows that some Initiative Activities have associated commitments, while others do not. In this data request response, PG&E listed each commitment in its own row, and, for those Initiative Activities with no associated commitments, listed each remaining Initiative Activity (‘Emergency Preparedness Plan’, ‘Fire Potential Index’) as its own row. PG&E used naming and unique keys consistent with both the QDR and the WMP to identify each row. For commitments, PG&E used the UITIDs, which can be found in Table 1 of the QDR, and for Initiative Activities with no commitments, PG&E used Table PG&E-A-2: Definitions of Initiatives – By Category in the WMP (version R6 pp. 990-996), located at the following link: https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/pge-wmp-r6-07052024.pdf. Please see the following clarifications regarding “Section E” of the attachment included in this request: Regarding “Section E: SB 884 Activity,” PG&E anticipates submitting its SB 884 Electric Undergrounding Plan in 2025. Work forecast in the SB 884 Electric Undergrounding Plan will begin in 2027. Therefore, there are no forecast units and no forecast costs for SB 884 in 2023, 2024, or 2025. | Kevin Miller | 2024-09-10 | 2024-10-04 | 2024-10-04 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_021.zip | 1 | N/A | 4.3 | 4.0 Overview of WMP | 4.3 Proposed Expenditures | 2.3 Expenditures |  | CPUC - SPD (Safety Policy Division) | 021 | 1 | 0 | Mona Hedin | Kevin Bateman Smith/Nelson Lau & Andrew Trombley QC | Dan Blair/Julie Cerio/Cynthia Lorie/Justin Sadler | Maria Ly/Matt Whorton/Megan Ardell/Jay Leyno | Nick Karkazis | Martin Wyspianski | Yes |  | Yes | Yes |  | Yes | Yes |  | 2024-10-04 |  |  | QDR Tranche request - first delivery on 10/4 10/10 - General Info tab – WMP data; SB 884 | [13 empty] | 1 | Dan Blair/Julie Cerio/Cynthia Lorie/Justin Sadler | Maria Ly/Matt Whorton/Megan Ardell/Jay Leyno | Mona Hedin | Kevin Bateman Smith/Nelson Lau & Andrew Trombley QC | Nick Karkazis | [5 empty] | completed | 0 | 0 | 0 | 0
707 | CPUC - SPD (Safety Policy Division) | 020 | CPUC - SPD (Safety Policy Division)_020 | 1 | CPUC - SPD (Safety Policy Division)_020_Q1 | Please provide a copy of the example spreadsheet with data discussed and presented in the meeting of 8/26/2025 at 9am-10am between PG&E and CPUC/SPD with the agenda as follows: a. Provide and discuss additional example(s) in the WMP Cost Reporting Template with a goal of providing all mitigation initiatives by end of September (when Final Decision on WMP is expected). | PG&E includes the following attachment of the WMP Cost Reporting Template in draft version that we reviewed with SPD on August 26: Attachment “WMP-Discovery2023- 2025_DR_SPD_020-Q001Atch01.xlsx.” This file contains the sample initiatives discussed with SPD on August 5 (System Hardening Distribution and 10k Undergrounding) and the initiatives discussed on August 26 (HFTD/HFRA Open Tag Reduction – Transmission; HFTD/HFRA Open Tag Reduction – Distribution Backlog; and Eliminate HFTD HFRA Distribution Backlog). The information provided is a sample of the level of detail PG&E proposes to provide in response to the template provided by SPD. We have referenced prior filings to populate this sample draft version; however, open questions remain as indicated in the template. “WMP-Discovery2023-2025_DR_SPD_020-Q001Atch01.xlsx” is the original template sent out by SPD and does not reflect any template changes discussed on August 26. | Edwin Schmitt | 2024-08-27 | 2024-09-04 | 2024-09-04 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_020.zip | 1 | N/A | 4.3 | 4.0 Overview of WMP | 4.3 Proposed Expenditures | 2.3 Expenditures |  | CPUC - SPD (Safety Policy Division) | 020 | 1 | 1 | Kenya Owens | Hema Sukumar | Dan Blair/Julie Cerio/Cynthia Lorie/Kevin Bateman Smith | Megan Ardell/Justin Sadler/Matt WhortonKathy Wade/Ken Arnold | N/A | Kristin Manz | Yes | Yes | N/A | Yes | Yes | Yes | Yes | Yes | 2024-09-04 | [16 empty] | 1 | Dan Blair/Julie Cerio/Cynthia Lorie/Kevin Bateman Smith | Megan Ardell/Justin Sadler/Matt WhortonKathy Wade/Ken Arnold | Kenya Owens | Hema Sukumar | N/A | 1
646 | CPUC - SPD (Safety Policy Division) | 016 | CPUC - SPD (Safety Policy Division)_016 | 3 | CPUC - SPD (Safety Policy Division)_016_Q3 | Provide a list of all memorandum (memo) and balancing accounts where WMP costs are currently being recorded as of May 31, 2024. a. In each of the memorandum and balancing accounts where WMP costs are being recorded provide the current WMP cost balances as follows (if future years [e.g., 2025] are expected to use memo accounts, add columns and data for them as well): Year 2020 2021 2022 2023 2024 Recorded Account Capital Expenditure ($) Recorded Account O&M Expenditure ($) Authorized GRC Capital Expenditure ($) Authorized GRC O&M Expenditure ($) b. Regarding planning for work with budgeting for future years, how does PG&E use its memo and balancing accounts with regard to projecting expenditures, projects, and workplans? | a. Please see “WMP-Discovery2023-2025_DR_SPD_016-Q003Atch01.xlsx” which represents the total spend recorded to each identified wildfire balancing or memorandum account in SAP, at the time the respective costs were extracted and prepared for the Commission's reasonableness review process. Please note, these costs are not adjusted for the WF OII Disallowance amount ordered by the Commission. For 2024, PG&E is providing Year to Date through Quarter 1. PG&E does not have an approved 2025 Investment Plan at this time. b. Through PG&E’s planning process, PG&E forecasts the work for future years within known memo and balancing accounts. When future year plans have been approved, plans are broken out by memo and balancing account. | Henry Sweat | 2024-05-30 | 2024-06-10 | 2024-06-10 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_016.zip | 1 | N/A | 4.3 | 4.0 Overview of WMP | 4.3 Proposed Expenditures | 2.3 Expenditures |  | CPUC - SPD (Safety Policy Division) | 016 | 3 | 2 | Mona Hedin | Nelson Lau | Kamran Bhatti | Matthew Whorton | Aaron Shapiro | Kristin Manz | Yes | Yes | Yes |  | Yes |  | Yes |  | 2024-06-10 |  | 6/4/2024 - Extension to 6/10 approved by Wade Greenacre. Kxfk | 6/4/2024 - Extension to 6/10 approved by Wade Greenacre. Kxfk | [13 empty] | 3 | Kamran Bhatti | Matthew Whorton | Mona Hedin | Nelson Lau | Aaron Shapiro | 2 |  |  |  |  | completed | 0 | 0 | 0 | 0
546 | CalPA | Set WMP-42 | CalPA_Set WMP-42 | 8 | CalPA_Set WMP-42_Q8 | Page 29 of PG&E’s 2025 WMP Update states that PG&E’s 2025 forecast capital expenditure associated with covered conductor installation will increase by a factor of 5.8, from $41.4 million to $241.6 million. The updated Table PG&E-8.1.2-1 on page 402 of PG&E’s 2023-2025 WMP R5 redline indicates that, in 2025, the mileage associated with covered conductor installation will increase by a factor of 4, from 50 miles to 200 miles. Please explain why PG&E’s capital forecast for 2025 will increase by a factor of 5.8 while the mileage will increase by a factor of 4. | The primary driver for the capital expenditure increase ratio being larger than the mileage increase ratio is the allocation of future year readiness costs. For any given year, the budget allocation includes costs for the current year construction costs and readiness/planning costs (Scoping, Design, Permitting, Pre-Construction activities) for future year projects. For the original 2025 capital forecast in the 2023 WMP, approximately $35.7 million was allocated for 2025 construction costs and $5.7 million for future year readiness. For the updated 2025 capital forecast, approximately $184.6 million was allocated for 2025 construction costs and $57.1 million for future year readiness. The significant increase in future year readiness cost between the original and updated forecast is due to the 2026 mileage differences (50 miles in the original 2023 WMP and 348 miles in the update). The secondary driver for the capital expenditure increase ratio being larger than the mileage increase ratio is the change in the unit cost assumption. In the 2023 WMP, the OH unit costs used in the capital forecast model was $0.83 million/mile which was based on completed 2021 and 2022 projects. For the update, the unit cost was updated to $1.00 million/mile based on completed 2023 projects. | Holly Wehrman | 2024-04-09 | 2024-04-12 | 2024-04-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_042.zip | 0 | N/A | 4.3 | 4.0 Overview of WMP | 4.3 Proposed Expenditures | 2.3 Expenditures |  | CalPA | Set WMP-42 | 8 | 0 | Mona Hedin | Andrew Trombley | Jack Liu Chris Wong UG Team Julie Cerio Jerry Santos Lucy Morris Merih Tekeste | Matt Whorton Megan Ardell | Aaron Shapiro | Andy Abranches Matt Pender | Yes | Yes | Yes |  | Yes | Yes |  |  | 2024-04-12 | [16 empty] | 8 | Jack Liu Chris Wong UG Team Julie Cerio Jerry Santos Lucy Morris Merih Tekeste | Matt Whorton Megan Ardell | Mona Hedin | Andrew Trombley | Aaron Shapiro | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
724 | OEIS | Mitigation Selection 001 | OEIS_Mitigation Selection 001 | 3 | OEIS_Mitigation Selection 001_Q3 | Regarding mitigation compatibility a. For each mitigation activity listed in Q01. a. i-xxii: i. List the constraints associated with each activity (e.g., cannot be deployed on 3 wire systems, in areas with frequent freeze/thaw cycles, requires communication network to function). ii. Provide a completed compatibility table. Each cell must identify one of the following: (1) Mitigations are compatible and the combination will further reduce wildfire risk. (2) Mitigations are compatible, but combination will not further reduce wildfire risk. (3) Mitigations are compatible, but it is unknown if combination will further reduce wildfire risk. (4) Mitigations are not compatible/combination is impractical. The utility must submit two separate tables, one for transmission specific initiatives and one for distribution specific initiatives, if the transmission and distribution tables are not identical. Example Mitigation Initiative Compatibility Table: Mitigation Activity Covered Conductor Installation Undergrounding Distribution Pole Replacements and Reinforcements (Mitigation Activities continued…) Covered Conductor Installation Mitigations are not compatible/ combination is impractical Mitigations are compatible and combination will reduce additional wildfire risk Undergrounding Mitigations are not compatible/ combination is impractical Mitigations are not compatible/ combination is impractical Distribution Pole Replacements and Reinforcements Mitigations are compatible and combination will reduce additional wildfire risk Mitigations are not compatible/ combination is impractical (Mitigation Activities continued…) END OF | Please see “WMP-Discovery2023-2025_DR_OEIS_026-Q003Atch01.xlsx” for our response to this request. Please note that we have answered “N/A” for mitigations we are not executing. Please refer to the worksheet titled “Compatibility Table Notes” for further details regarding certain entries in the table. With regard to subpart (i), please note that we have provided general constraints associated with each mitigation and that this list is non-exhaustive of all possible constraints. | Will Dundon | 2024-11-07 | 2024-12-20 | 2024-12-20 | TBD | 1 | N/A | N/A | N/A | N/A | N/A |  | OEIS | Mitigation Selection 001 | 3 | 6 | Kevin Laxalt-Nomura | Kevin Bateman Smith | [12 empty] | 2024-12-20 | [16 empty] | 3
723 | OEIS | Mitigation Selection 001 | OEIS_Mitigation Selection 001 | 2 | OEIS_Mitigation Selection 001_Q2 | Q02. Regarding the deployment time of mitigation initiatives: a. For each mitigation activity listed in Q01. a. i-xxii, provide: i. The projected project duration (days/circuit mile)6 for projects expected to be completed in 2025. ii. The average project duration (days/circuit mile) of projects completed from Jan 1, 2021, to Jun 30, 2024. iii. A discussion of factors that have resulted in projects completed from Jan 1, 2021, to Jun 30, 2024, with a project duration (days/circuit mile) 20 percent more than the average project duration from Jan 1, 2021, to Jun 30, 2024, for that given activity. List the factors and discuss how each impacted the project duration. iv. A discussion of factors that have resulted in projects completed from Jan 1, 2021, to Jun 30, 2024, with a project duration (days/circuit mile) 20 percent less than the average project duration from Jan 1, 2021, to Jun 30, 2024, for that given activity. List the factors and discuss how each impacted the project duration. v. Complete the following table for the 10 projects with the longest duration per circuit mile and 10 projects with the lowest duration per circuit mile completed in 2023. If less than 20 projects were completed in 2023, complete the table for all projects completed in 2023. Mitigation Activity Project ID Location Project length (circuit miles) Project Capital Cost Project Duration (days) Duration per circuit mile | Please see “WMP-Discovery2023-2025_DR_OEIS_026-Q002Atch01.xlsx” for data responsive to subparts 1 through 5 of this request. Please note that, of the 22 mitigations listed here, only the following are unitized by circuit mile: Covered Conductor, Undergrounding, Transmission Traditional Hardening,2 and Remote Grids.3 We are unable to provide the information requested with respect to the other mitigations on a circuit mile basis. With regard to our response to subpart 5 for Covered Conductor, Undergrounding, and Remote Grids, please note that work under our Base System Hardening (Base SH) program and work under our Fire Rebuild (FRRB) program are separated to provide visibility to the differences between the two programs. Please also note that there are fewer projects listed in our response to subpart 5 for System Hardening Remote Grid compared to the System Hardening Remote Grid table in response to Q1 subpart 6, because orders that do not currently have the necessary data in our system of record to calculate the project duration are omitted in this response. With regard to our response to subpart 5 for Covered Conductor and Undergrounding, please note that projects with very low milage may result in unrepresentatively high duration per circuit mile metrics. | Will Dundon | 2024-11-07 | 2024-12-20 | 2024-12-20 | TBD | 1 | N/A | N/A | N/A | N/A | N/A |  | OEIS | Mitigation Selection 001 | 2 | 5 | Kevin Laxalt-Nomura | Kevin Bateman Smith | [12 empty] | 2024-12-20 | [16 empty] | 2
722 | OEIS | Mitigation Selection 001 | OEIS_Mitigation Selection 001 | 1 | OEIS_Mitigation Selection 001_Q1 | Q01. Regarding the cost of mitigations: a. PG&E discusses the following mitigation activities in its 2023-2025 Base WMP: i. Covered Conductor Installation ii. Undergrounding iii. Distribution Pole Replacements and Reinforcements iv. Distribution Traditional Hardening v. Transmission Pole/Tower Protections and Reinforcements vi. Transmission Traditional Hardening vii. Transmission Shunt Splices viii. Distribution Protective Devices ix. Breakaway Connector x. Surge Arrestor Removal/Replacement xi. Distribution Motorized Switch Operator (MSO) Replacements xii. Non-Exempt Expulsion Fuse Removal/Replacement xiii. Microgrids, including remote grids xiv. Avian/animal protection plan xv. Enhanced Powerline Safety Settings (EPSS) xvi. Distribution, Transmission, and Substation: Fire Action Schemes and Technology (DTS-FAST) xvii. Downed Conductor Detection (DCD) xviii. Rapid Earth Fault Current Limiter (REFCL) xix. Pole Mounted Sensors xx. Early Fault Detection (EFD) xxi. Distribution Fault Anticipation (DFA) xxii. Smart Tape For each of the above activities, provide: (1) The projected average capital cost per circuit mile1 of projects2 expected to be completed3 in 2025. (2) The average capital cost per circuit mile of projects completed from Jan 1, 2021, to Jun 30, 2024. (3) The average operation and maintenance cost per circuit mile per year4 of projects completed from Jan 1, 2021, to Jun 30, 2024. (4) A discussion of factors that have resulted in projects completed from Jan 1, 2021, to Jun 30, 2024, with a capital cost per circuit mile 20 percent more than the average cost per circuit mile from Jan 1, 2021, to Jun 30, 2024, for that given activity. List the factors and discuss how each impacts the cost. (5) A discussion of factors that have resulted in projects completed from Jan 1, 2021, to Jun 30, 2024, with a capital cost per circuit mile 20 percent less than the average cost per circuit mile from Jan 1, 2021, to Jun 30, 2024, for that given activity. List the factors and discuss how each impacts the cost. (6) Complete the following table for the 10 projects with the highest capital cost per circuit mile and 10 projects with the lowest capital cost per circuit mile completed in 2023. If less than 20 projects were completed in 2023, complete the table for all projects completed in 2023. Mitigation Activity Project ID Location Project length (circuit miles) Project Capital Cost Project Duration5 (days) Capital Cost per circuit mile | Please see “WMP-Discovery2023-2025_DR_OEIS_026-Q001Atch01.xlsx” for data responsive to subparts 1 through 6 of this request. Please note that, of the 22 mitigations listed here, only the following are unitized by circuit mile: Covered Conductor, Undergrounding, Transmission Traditional Hardening,5 and Remote Grids.6 We are unable to provide the information requested with respect to the other mitigations on a circuit mile basis. Please note that operation and maintenance costs after mitigation work is complete are not traceable to a specific mitigation. With regard to our response to subpart 6 for Covered Conductor and Undergrounding, please note that projects with very low milage may result in unrepresentatively high cost per circuit mile metrics. With regard to our response to subpart 6 for Remote Grid, please note that some projects do not currently have the necessary data in our system of record to calculate the project duration and are represented as "N/A.” With regard to our response to subpart 5 for Covered Conductor, Undergrounding, and Remote Grids, please note that work under our Base System Hardening (Base SH) program and work under our Fire Rebuild (FRRB) program are separated to provide visibility to the differences between the two programs. | Will Dundon | 2024-11-07 | 2024-12-20 | 2024-12-20 | TBD | 1 | N/A | N/A | N/A | N/A | N/A |  | OEIS | Mitigation Selection 001 | 1 | 6 | Kevin Laxalt-Nomura | Kevin Bateman Smith | [12 empty] | 2024-12-20 | [16 empty] | 1 |  |  | Kevin Laxalt-Nomura
717 | OEIS | 025 | OEIS_025 | 2 | OEIS_025_Q2 | Specific to VMP ID: VP_BC125-H01_1633087_2020, VP_BC125-H01_1632351_2020, VP_BC125-H01_1633192_2020, VP_BC125-H01_1632349_2020 a. Confirm if the GPS point 37.52410, -120.00378 is the location of the log, chips, and slash for the associated VMP ID VP_BC125-H01_1633087_2020 b. Confirm if the GPS point 37.52359, -120.00448 is the general location of the various log, chips, and slash for the associated VMP IDs: VP_BC125- H01_1632351_2020, VP_BC125-H01_1633192_2020, VP_BC125- H01_1632349_2020 c. Confirm the wood, chips, and slash destination for the trees in question. d. Confirm if the logs, chips, and slash in the attached photographs match the trees in question on Gold Creek Lane, Mariposa, CA e. If these are not the same trees, please supply photographs of the tree or tree stump, chips, and slash. | PG&E completed clean up and disposal of wood and slash at the Gold Creek Lane location as of September 25, 2024. Please see the table below for before and after photos. Gold Creek Lane Pre-Clean-Up WMP-Discovery2023-2025_DR_OEIS_025-Q002Atch01.pdf Pre-Clean-Up WMP-Discovery2023-2025_DR_OEIS_025-Q002Atch02.pdf Pre-Clean-Up WMP-Discovery2023-2025_DR_OEIS_025-Q002Atch03.pdf Pre-Clean-Up WMP-Discovery2023-2025_DR_OEIS_025-Q002Atch04.pdf Pre-Clean-Up WMP-Discovery2023-2025_DR_OEIS_025-Q002Atch05.pdf Gold Creek Lane Pre-Clean-Up WMP-Discovery2023-2025_DR_OEIS_025-Q002Atch06.pdf Pre-Clean-Up WMP-Discovery2023-2025_DR_OEIS_025-Q002Atch07.pdf Post-Clean-Up WMP-Discovery2023-2025_DR_OEIS_025-Q002Atch08.pdf Post-Clean-Up WMP-Discovery2023-2025_DR_OEIS_025-Q002Atch09.pdf Post-Clean-Up WMP-Discovery2023-2025_DR_OEIS_025-Q002Atch10.pdf Post-Clean-Up WMP-Discovery2023-2025_DR_OEIS_025-Q002Atch11.pdf Post-Clean-Up WMP-Discovery2023-2025_DR_OEIS_025-Q002Atch12.pdf Post-Clean-Up WMP-Discovery2023-2025_DR_OEIS_025-Q002Atch13.pdf Post-Clean-Up WMP-Discovery2023-2025_DR_OEIS_025-Q002Atch14.pdf a. PG&E performed a field visit to the coordinates listed above on September 23, 2024, and confirms that the log and slash for VMP ID VP_BC125- H01_1633087_2020 are located at these GPS coordinates. b. PG&E performed a field visit to the coordinates listed above on September 23, 2024, and confirms that the log and slash for the following VPs are located at these GPS coordinates: o VP_BC125- H01_1632351_2020 o VP_BC125-H01_1633192_2020 o VP_BC125- H01_1632349_2020. c. PG&E confirms the original destination for the wood in question for the following was located at the following coordinates: 37.52359, -120.00448: o VP_BC125- H01_1632351_2020 o VP_BC125-H01_1633192_2020 o VP_BC125- H01_1632349_2020. Please note, a clean-up was facilitated at this location and the wood and slash have been removed. d. Yes, the log and slash photographs provided by Energy Safety in the DR-268 data request matches the tree in question. e. Not applicable, please see the response to subpart (d) above. | Ramzi Ibrahim | 2024-09-17 | 2024-09-27 | 2024-09-27 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/OEIS_025.zip | 14 | N/A | QDR | N/A | N/A | N/A |  | OEIS | 025 | 2 | 5 | [17 empty] | QDR
716 | OEIS | 025 | OEIS_025 | 1 | OEIS_025_Q1 | Specific to VMP ID VP_BC125-D06_1674177_2020, please confirm the following: a. Confirm if the GPS point 37.56086076985676, -120.00231237377247 is the location of the log and slash for the associated VMP ID b. Confirm the wood destination for the tree in question. c. Confirm if the log and slash in the attached photographs matches the tree in question (Pinus sabiniana, sixty feet height with 24-inch dbh off Sherlock Road, Mariposa, CA) d. If this is not the same tree, please supply photographs of the tree or tree stump and slash. | PG&E completed a clean-up and disposal of wood and slash at the Sherlock Road location as of September 25, 2024. Please see the following before and after photos: • Pre-disposal: “WMP-Discovery2023-2025_DR_OEIS_025-Q001Atch01.pdf;” and • Post-disposal: “WMP-Discovery2023-2025_DR_OEIS_025-Q001Atch02.pdf.” a. PG&E performed a field visit to the coordinates listed above on September 23, 2024, and confirms that the log and slash for VMP ID VP_BC125-D06_1674177_2020 are located these GPS coordinates. b. PG&E confirms the original destination for the wood in question was located at the following coordinates: 37.56086076985676, -120.00231237377247. Please note, a clean-up was facilitated at this location and the wood and slash have been removed. c. Yes, the log and slash photographs provided by Energy Safety in this request match the tree in question. d. Not applicable, please see the response to subpart (c) above. | Ramzi Ibrahim | 2024-09-17 | 2024-09-27 | 2024-09-27 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/OEIS_025.zip | 2 | N/A | QDR | N/A | N/A | N/A |  | OEIS | 025 | 1 | 4 | [17 empty] | QDR
670 | OEIS | 023 | OEIS_023 | 2 | OEIS_023_Q2 | Regarding PG&E’s transmission asset inspection programs and pilots: a. Provide the find rate of level 1 and 2 conditions and number of inspections performed from January 1, 2020, to December 31, 2023, for the following inspection initiatives and pilot programs. If the inspection initiative or pilot began after January 1, 2020, please specify the start date of the initiative in the response. i. Aerial detailed inspections ii. Infrared inspections iii. Conductor measurement iv. Below grade foundation assessment v. Corona inspections vi. Ultrasonic pole inspections vii. Corrosion climbing assessment viii. Proactive sampling and testing ix. LiDAR assessment x. Climbing detailed inspections xi. Intrusive Pole inspections xii. Patrol inspections | a. The three tables below provide the number of completed inspection units, Level 1 and Level 2 finds (count of notifications) and the Level 1 and Level 2 find rates (notifications per inspection unit). The counts of notifications for aerial and climbing detailed inspections, LiDAR assessment, intrusive pole inspections, and patrols are derived from the dataset used to generate Table 2 in the 2024 Q1 WMP QDR. The counts of aerial inspections from 2021-2023 also are taken from Table 2 of the QDR. The counts of climbing detailed inspections and patrols are derived from data in SAP. The inspection units and counts of notifications for the remaining programs are based on data collected by the program managers. Table 1: Completed inspection units. 2020 2021 2022 2023 Inspection units # Inspections # Inspections # Inspections # Inspections i. Aerial detailed inspections Structures 52,834 66,645 59,022 50,491 ii. Infrared inspections Miles 5,355 7,500 9,474 8,011 iii. Conductor measurement Spans 3 13 13 0 iv. Below grade foundation assessment Structures (started in 2021) N/A 99 545 352 v. Corona inspections Miles 5,355 7,500 9,474 8,011 vi. Ultrasonic pole inspections Structures (started in 2022) N/A N/A 157 8 vii. Corrosion climbing assessment Structures (started in 2023) N/A N/A N/A 172 viii. Proactive sampling and testing Samples 3 17 25 17 ix. LiDAR assessment Spans (started in 2023) N/A N/A N/A 27,147 2020 2021 2022 2023 Inspection units # Inspections # Inspections # Inspections # Inspections x. Climbing detailed inspections Structures 2,911 3,317 3,607 4,180 xi. Intrusive Pole inspections Structures 14,841 17,512 12,645 10,376 xii. Patrol inspections Structures 142,660 130,677 111,206 105,480 Table 2: Level 1 and Level 2 finds (count of notifications) 2020 2021 2022 2023 2020 2021 2022 2023 Level 1 Finds Level 1 Finds Level 1 Finds Level 1 Finds Level 2 Finds Level 2 Finds Level 2 Finds Level 2 Finds i. Aerial detailed inspections 178 103 88 234 17,159 22,666 21,508 15,289 ii. Infrared inspections 0 1 2 2 3 15 12 16 iii. Conductor measurement 0 0 0 0 0 0 0 0 iv. Below grade foundation assessment N/A – started in 2021 0 0 0 N/A – started in 2021 9 3 0 v. Corona inspections 0 0 0 0 0 0 1 0 vi. Ultrasonic pole inspections N/A – started in 2022 N/A 0 0 N/A – started in 2022 N/A 0 0 vii. Corrosion climbing assessment N/A – started in 2023 N/A N/A 0 N/A – started in 2023 N/A N/A 62 viii. Proactive sampling and testing N/A - sampling drives proactive repair/replace decisions ix. LiDAR assessment N/A N/A N/A 1 N/A N/A N/A 727 x. Climbing detailed inspections 1 0 0 0 335 251 616 512 xi. Intrusive Pole inspections 0 0 1 4 221 191 1,637 1,242 xii. Patrol inspections 456 420 226 497 1,047 1,267 715 508 Table 3: Level 1 and Level 2 find rates (count of notifications per inspection unit) 2020 2021 2022 2023 2020 2021 2022 2023 Level 1 Find Rate Level 1 Find Rate Level 1 Find Rate Level 1 Find Rate Level 2 Find Rate Level 2 Find Rate Level 2 Find Rate Leve l 2 Find Rate i. Aerial detailed inspections 0.00337 0.00155 0.00149 0.00463 0.32477 0.34010 0.36441 0.302 81 ii. Infrared inspections 0.00000 0.00013 0.00021 0.00025 0.00056 0.00200 0.00127 0.002 00 iii. Conductor measurement 0.00000 0.00000 0.00000 0.00000 0.00000 0.00000 0.00000 0.000 00 iv. Below grade foundation assessment N/A – started in 2021 0.00000 0.00000 0.00000 N/A – started in 2021 0.09091 0.0550 0.000 00 v. Corona inspections 0.00000 0.00000 0.00000 0.00000 0.00000 0.00000 0.00011 0.000 00 vi. Ultrasonic pole inspections N/A – started in 2022 N/A 0.0000 0 0.00000 N/A – started in 2022 N/A 0.0000 0 0.00000 vii. Corrosion climbing assessment N/A – started in 2023 N/A N/A 0.00000 N/A – started in 2023 N/A N/A 0.36047 viii. Proactive sampling and testing N/A - sampling drives proactive repair/replace decisions ix. LiDAR assessment N/A N/A N/A 0.00004 N/A N/A N/A 0.02678 x. Climbing detailed inspections 0.00034 0.00000 0.00000 0.00000 0.11508 0.07567 0.17078 0.12249 xi. Intrusive Pole inspections 0.00000 0.00000 0.00008 0.00039 0.01489 0.01091 0.12946 0.11970 xii. Patrol inspections 0.00320 0.00321 0.00203 0.00471 0.00734 0.00970 0.00643 0.00482 b. i. Aerial detailed inspections PG&E estimates roughly >2/3 of Aerial finds would not have been identified through Ground inspections based on an analysis of tags found on structures receiving Ground and Aerial inspections in the same year. Note this is due to the difference in vantage point and the aerial review process allowing for additional data sources during desktop review. ii. Infrared inspections PG&E estimates the majority of infrared findings would not be identified through other inspection methods due to the failure mode being internal electrical connection degradation not visible externally. iii. Conductor measurement PG&E estimates the majority of LineVue findings would not be identified through other inspection methods due to the failure mode being internal steel core conductor corrosion not visible externally. iv. Below grade foundation assessment PG&E estimates the majority of below grade foundation findings would not be identified through other inspection methods due to the failure mode being foundation integrity degradation not visible to the above ground inspection methods. v. Corona inspections PG&E does not have an estimate at this time due to the small number of finds. vi. Ultrasonic pole inspections PG&E does not have an estimate at this time due to the lack of findings. vii. Corrosion climbing assessment PG&E estimates that the majority of findings could be identified through a detailed Climbing, Aerial, or Ground inspection due to the visual assessment tower members during the pilot. This pilot includes quantitative measurement of material loss due to corrosion which provides input into calibration of our asset degradation model and informs asset repair vs replace decisions. viii. Proactive sampling and testing PG&E does not have an estimate at this time. The findings of this pilot mainly inform proactive repair/replace decisions. ix. LiDAR assessment PG&E estimates the majority of LiDAR findings would not be identified through other inspection methods due to the quantitative spatial nature which is difficult for other inspection methods to provide. | Nathan Poon | 2024-06-20 | 2024-07-01 | 2024-07-01 | https://preview.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/OEIS_023.zip | 0 | N/A | 8 | Section 8.1.3 - Asset Inspection | Section 8.1.3 - Asset Inspection | N/A |  | OEIS | 023 | 2 | 2 | Mona Hedin | Nelson Lau | Natalie Dawley/Matt Horowitz | Maria Ly | Aaron Shapiro | Martin Wyspianski | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | 2024-07-01 |  | j1oz - extension requested - 6/21 - extension granted per CPUC engineer | [14 empty] | 2 | Natalie Dawley/Matt Horowitz | Maria Ly | Mona Hedin | Nelson Lau | Aaron Shapiro | 2 |  |  |  |  | completed | 0 | 0 | 0 | 0
669 | OEIS | 023 | OEIS_023 | 1 | OEIS_023_Q1 | Regarding PG&E’s distribution asset inspection initiatives and pilots: a. Provide the number of inspections performed and find rate of level 1 and 2 conditions from January 1, 2020, to December 31, 2023, for the following inspection initiative or pilot programs. If the inspection initiative or pilot program began after January 1, 2020, please specify the start date of the initiative in the response. i. Infrared inspections ii. LiDAR based pole loading assessments iii. Aerial inspections iv. Detailed ground inspections v. Intrusive pole inspections vi. Patrol inspections b. For each inspection initiative or pilot below, please provide the estimated percentage of conditions that PG&E would likely not have identified through detailed ground, patrol, or intrusive pole inspections. Describe how PG&E calculated the estimated percentage. i. Infrared inspections ii. LiDAR based pole loading assessments iii. Aerial inspections | Please see the tables below for the requested information. | Nathan Poon | 2024-06-20 | 2024-07-10 | 2024-07-10 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/OEIS_023.zip | 0 | N/A | 8 | Section 8.1.3 - Asset Inspection | Section 8.1.3 - Asset Inspection | N/A |  | OEIS | 023 | 1 | 2 | Mona Hedin | Nelson Lau | Jared Leong/Mina Amir/Michael Lee/Josh Riffle | Jim Gill/John Klavdianos | Aaron Shapiro/Nick Karkazis | Martin Wyspianski | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | 2024-07-10 |  | j1oz - extension requested - 6/21 - extension granted per CPUC engineer j1oz - 7/1/24 - extension granted to 7/10 from engineer | [14 empty] | 1 | Jared Leong/Mina Amir/Michael Lee/Josh Riffle | Jim Gill/John Klavdianos | Mona Hedin | Nelson Lau | Aaron Shapiro/Nick Karkazis | 2 |  |  |  |  | completed | 0 | 0 | 0 | 0
604 | Green Power Institute (GPI) | 003 | Green Power Institute (GPI)_003 | 3 | Green Power Institute (GPI)_003_Q3 | Please provide a summary of any developments since the 2023 meeting and working sessions towards initiating a Joint IOU scoping study on best practices and efficacy of fuels management, including but not limited to planned topics for inclusion in the scoping study. | Please see response to Question 002 for supporting communications, meeting invites and draft research project proposal attachments for the requested information from April 2024. | Zoe Harrold | 2024-04-26 | 2024-05-01 | 2024-05-01 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/GPI_003.zip | 0 | N/A | 8 | Section 8.2 - Vegetation Management and Inspections | 8.2.3 Vegetation and Fuels Management | N/A |  | Green Power Institute (GPI) | 003 | 3 | 0 | Mona Hedin | Cherimae Vail | VMDR April Schneider | John Fiske | Lauren Ruby | Angela Sanford | Yes |  | Yes |  | Yes |  | Yes |  | 2024-05-01 | [16 empty] | 3 | VMDR April Schneider | John Fiske | Mona Hedin | Cherimae Vail | Lauren Ruby | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
603 | Green Power Institute (GPI) | 003 | Green Power Institute (GPI)_003 | 2 | Green Power Institute (GPI)_003_Q2 | Please provide any PG&E slides, meeting materials, and meeting minutes generated for and/or presented at the Joint IOU meeting held in 2023 to “discuss each utility’s respective fuels management programs and began initial collaboration on a possible scoping study on best practices and efficacy of fuels management [2].” [2] SDG&E 2025 WMP Update, April 2, 2024, pp. 52-53 | Attachments to this response contain CONFIDENTIAL information provided pursuant to the acaccompanying confidentiality declaration. Joint IOU discussions to review and evaluate utility fuel management programs were coordinated within a working group that had already been established to support ongoing efforts to develop and establish the Cal Poly San Luis Obispo Wildland-Urban Interface (WUI) Fire Institute. The WUI Fire Institute conducts research, training and education geared towards creating more fire-resistant communities. In October 2023, the utility stakeholders began collaboration on fuel management programs analysis. Each utility contributed to the development of an initial survey, drafting questions, soliciting responses and conducting reviews. Please see attached emails and meeting invites from October 2023 through December 2023 outlined in the table below. Attachment Name Description WMP-Discovery2023-2025_DR_GPI_003- Q002Atch01CONF.pdf Emails re: IOU Engagement with the WUI FIRE Institute WMP-Discovery2023-2025_DR_GPI_003- Q002Atch02CONF.pdf Meeting invite and Agenda re: IOU WUI Research Coordination - Fuel Clearing and Modification Study WMP-Discovery2023-2025_DR_GPI_003- Q002Atch03CONF.pdf Emails re: IOU Meeting Notes/Survey Responses WMP-Discovery2023-2025_DR_GPI_003- Q002Atch04CONF.pdf Emails re: IOU Meeting Notes/Survey Responses WMP-Discovery2023-2025_DR_GPI_003- Q002Atch05CONF.pdf Problem Statement Drafts re: IOU WUI Research Coordination - Fuel Clearing and Modification Study While the IOUs continued to work together to develop a research project request, the Cal Poly WUI Fire Institute formalized and hired a director. The IOUs requested a meeting with the WUI Fire Institute in March 2024, but the meeting did not take place until April 29, 2024, due to scheduling conflicts. The meeting with SCE, SDG&E, PG&E and Cal Poly WUI Fire Institute leadership was intended to finalize the research project request and initiate WUI Fire Institute evaluation. Efforts will continue to refine the research project proposal through 2024 to define a phased scope and delivery schedule. Please see attached emails and meeting invites from April 2024 outlined in the table below. Attachment Name Description WMP-Discovery2023-2025_DR_GPI_003- Q002Atch06CONF.pdf Meeting invite re: WUI Research Request for Fuels Management WMP-Discovery2023-2025_DR_GPI_003- Q002Atch07CONF.pdf Emails re: IOU Questionnaire Follow-Up WMP-Discovery2023-2025_DR_GPI_003- Q002Atch08CONF.pdf Meeting follow-up re: Fuels Management References | Zoe Harrold | 2024-04-26 | 2024-05-01 | 2024-05-01 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/GPI_003.zip | 8 | N/A | 8 | Section 8.2 - Vegetation Management and Inspections | 8.2.3 Vegetation and Fuels Management | N/A |  | Green Power Institute (GPI) | 003 | 2 | 0 | Mona Hedin | Cherimae Vail | VMDR April Schneider | John Fiske | Lauren Ruby | Angela Sanford | Yes |  |  |  | Yes |  | Yes |  | 2024-05-01 | [16 empty] | 2 | VMDR April Schneider | John Fiske | Mona Hedin | Cherimae Vail | Lauren Ruby | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
602 | Green Power Institute (GPI) | 003 | Green Power Institute (GPI)_003 | 1 | Green Power Institute (GPI)_003_Q1 | Please provide any PG&E slides, meeting materials, and meeting minutes generated for and/or presented at the two Joint IOU working sessions held in 2023 to “discuss the different types of programs and practices each IOU has in place for disposing and recycling woody debris and vegetation [1].” [1] SDG&E 2025 WMP Update, April 2, 2024, pp. 52-53 | Attachments to this response contain CONFIDENTIAL information provided pursuant to the acaccompanying confidentiality declaration. Please see the following meeting invitations with agendas/questions and meeting notes for the two joint IOU working sessions held in 2023 regarding wood management. Please note, there were no other materials used by PG&E during these meetings. • June 2023 Joint IOU Working Session Attachment Name Description WMP-Discovery2023-2025_DR_GPI_003- Q001Atch01CONF.pdf June 2023_Joint IOU Fuel Management Recycling Practices Meeting Invitation WMP-Discovery2023-2025_DR_GPI_003- Q001Atch02CONF.pdf June 2023_Follow up Email “RE Meeting Notes Joint IOU Fuel Management Recycling Practices” WMP-Discovery2023-2025_DR_GPI_003- Q001Atch03CONF.pdf June 2023_Attachment to Follow up Email – “SCE Meeting Minutes FM Recycling Disposal_2023-06-20” • August 2023 Joint IOU Working Session Attachment Name Description WMP-Discovery2023-2025_DR_GPI_003- Q001Atch04CONF.pdf July 2023_Joint IOU Wood Management Practices Follow-Up Meeting Invitation WMP-Discovery2023-2025_DR_GPI_003- Q001Atch05CONF.pdf August 2023_Follow up Email “FW Joint IOU Wood Management Practices Follow-Up” WMP-Discovery2023-2025_DR_GPI_003- Q001Atch06CONF.pdf August 2023_Attachment to Follow up Email – “Joint IOU Wood Management Meeting Notes” | Zoe Harrold | 2024-04-26 | 2024-05-01 | 2024-05-01 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/GPI_003.zip | 6 | N/A | 8 | Section 8.2 - Vegetation Management and Inspections | 8.2.3 Vegetation and Fuels Management | N/A |  | Green Power Institute (GPI) | 003 | 1 | 0 | Mona Hedin | Cherimae Vail | VMDR April Schneider | John Fiske | Lauren Ruby | Angela Sanford | Yes |  | Yes |  | Yes |  | Yes |  | 2024-05-01 | [16 empty] | 1 | VMDR April Schneider | John Fiske | Mona Hedin | Cherimae Vail | Lauren Ruby | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
715 | CPUC - SPD (Safety Policy Division) | 022 | CPUC - SPD (Safety Policy Division)_022 | 1 | CPUC - SPD (Safety Policy Division)_022_Q1 | 2. We looked at QDR metric 15.b from Q1 and Q2 (metric name – Level 2 Findings Fixed) to try to see if we could correlate the number of Level 2 findings fixed with the number of findings fixed reported by PG&E in the last meeting. We got ~55k compared to 69k reported in the last meeting. We wanted to double check why the numbers are not the same. I attached my spreadsheet so your team can see exactly what I did. | PG&E believes there may have been a misunderstanding regarding the Level 2 Findings discussed during the meeting on September 12, 2024. During the September 12 meeting with SPD, PG&E reported the year-to-date Safety and Operational Metrics (SOM) as of June 2024 for Level 2 findings were 69% on time. PG&E did not report on the number of tags completed. It is difficult to compare the SOM with the Quarterly Data Report (QDR). SOMs measure the timeliness of Tier 2 and Tier 3 HFTD Level 2 tags by their maximum allowable timeframes per GO 95 compared to QDR which reports on the total number of tags completed each quarter regardless of their compliance due dates. Furthermore, SOMs includes vegetation management tags whereas the QDR does not and the QDR also includes non-HFTD tags. PG&E would be happy to further discuss or clarify this item at future meetings, if it would be helpful. | Henry Sweat | 2024-09-18 | 2024-10-11 | 2024-10-07 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_022.zip | 0 | N/A | QDR | N/A | N/A | N/A |  | CPUC - SPD (Safety Policy Division) | 022 | 2 | 0 | Mona Hedin | Nelson Lau | Hannah Keller/Tom Huynh/Mina Amir/Matthew Horowitz | Satvir Nagra/Jim Gill/Bryon Winget | Aaron Shapiro | Martin Wyspianski | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | 2024-10-11 |  |  | QDR | [14 empty] | Hannah Keller/Tom Huynh/Mina Amir/Matthew Horowitz | Satvir Nagra/Jim Gill/Bryon Winget | Mona Hedin | Nelson Lau | Aaron Shapiro
706 | CPUC - SPD (Safety Policy Division) | 019 | CPUC - SPD (Safety Policy Division)_019 | 14 | CPUC - SPD (Safety Policy Division)_019_Q14 | Provide Ignition reports (also known as PIIRs) for CPUC reportable ignitions that occurred on days when EPSS was enabled in 2024. Reports already provided in response to Question 13 need not be resubmitted in response to Question 14. | PG&E interprets this request as asking for ignition reports for CPUC reportable ignitions which occurred on primary lines on EPSS enabled circuits in 2024. PG&E is still undergoing investigations for some ignitions that occurred on days when EPSS was enabled in 2024. PG&E has provided reports for ignitions where the investigations have concluded. Please see the table below for PIIRs for CPUC reportable ignitions which occurred on primary lines on EPSS enabled circuits in 2024 that were not provided in Question 13. CPUC Reportable Ignition Date of Ignition Attachment Name 20240434 May 18, 2024 WMP-Discovery2023-2025_DR_SPD_019- Q014Atch01CONF.pdf 20240605 June 7, 2024 WMP-Discovery2023-2025_DR_SPD_019- Q014Atch02CONF.pdf Please note, these reports are preliminary and are based on available information at the time they were drafted. Event data is subject to change based upon subsequently discovered information. | Henry Sweat | 2024-08-29 | 2024-09-12 | 2024-09-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_019.zip | 2 | N/A | Appendix D | Appendix D - Areas for Continued Improvement | ACI PG&E-22-06 – Addressing Increase in Risk Events | N/A |  | CPUC - SPD (Safety Policy Division) | 019 | 14 | 0 | Mona Hedin | Nelson Lau | Rhys McMenamin | Andy Abranches | Aaron Shapiro | Mark Quinlan | Yes | Yes | Yes |  | Yes |  | Yes |  | 2024-09-12 | [16 empty] | 14 | Rhys McMenamin | Andy Abranches | Mona Hedin | Nelson Lau | Aaron Shapiro
705 | CPUC - SPD (Safety Policy Division) | 019 | CPUC - SPD (Safety Policy Division)_019 | 13 | CPUC - SPD (Safety Policy Division)_019_Q13 | Provide Ignition reports (also known as PIIRs) for CPUC reportable ignitions that occurred on R3+ days in 2024. | PG&E is still preforming investigations for some ignitions that occurred on R3+ days in 2024. PG&E has provided reports for ignitions where its investigations have concluded. Please see the table below for the Preliminary Ignition Investigation Report (PIIR) for CPUC reportable ignitions that occurred on R3+ days in 2024. CPUC Reportable Ignition Date of Ignition Attachment Name 20240455 May 21, 2024 WMP-Discovery2023-2025_DR_SPD_019- Q013Atch01CONF.pdf 20240610 June 8, 2024 WMP-Discovery2023-2025_DR_SPD_019- Q013Atch02CONF.pdf 20240655 June 15, 2024 WMP-Discovery2023-2025_DR_SPD_019- Q013Atch03CONF.pdf 20240753 June 25, 2024 WMP-Discovery2023-2025_DR_SPD_019- Q013Atch04CONF.pdf 20240770N June 27, 2024 WMP-Discovery2023-2025_DR_SPD_019- Q013Atch05CONF.pdf 20240909N July 9, 2024 WMP-Discovery2023-2025_DR_SPD_019- Q013Atch06CONF.pdf 20240949 July 14, 2024 WMP-Discovery2023-2025_DR_SPD_019- Q013Atch07CONF.pdf Please note, these reports are preliminary and are based on available information at the time they were drafted. Event data is subject to change based upon subsequently discovered information. | Henry Sweat | 2024-08-29 | 2024-09-12 | 2024-09-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_019.zip | 7 | N/A | Appendix D | Appendix D - Areas for Continued Improvement | ACI PG&E-22-06 – Addressing Increase in Risk Events | N/A |  | CPUC - SPD (Safety Policy Division) | 019 | 13 | 0 | Mona Hedin | Nelson Lau | Rhys McMenamin | Andy Abranches | Aaron Shapiro | Mark Quinlan | Yes | Yes | Yes |  | Yes |  | Yes |  | 2024-09-12 | [16 empty] | 13 | Rhys McMenamin | Andy Abranches | Mona Hedin | Nelson Lau | Aaron Shapiro
704 | CPUC - SPD (Safety Policy Division) | 019 | CPUC - SPD (Safety Policy Division)_019 | 12 | CPUC - SPD (Safety Policy Division)_019_Q12 | Describe Focus Tree Inspection progress thus far in 2024 (provide the date at which the data is current through in the response). Include the following: • Number of total trees prescribed to be worked • Number of total trees worked thus far • Number of total trees prescribed for removal • Number of total trees removed thus far • Number of miles inspected • Number of strike trees inspected • Number of strike trees per mile of lines inspected before removals • Number of strike trees per mile after removals • Number of trees inspected • Confirm the number of strike trees inspected, number of miles inspected and number of trees removed in the pilot program in 2023. • The Q2 2023 QDR seems to state $0 dollars were spent, please explain (see row 49 and Table 11). Provide an update comparing costs estimated as part of the Revision Notice compared to forecasted costs for the rest of the year and the costs currently incurred. Explain any variance. | Please see the following data for the requested information through September 6, 2024: • Number of trees prescribed to be worked: 51,374 • Number of total trees worked thus far: 2,116 • Number of total trees prescribed for removal: 42,101 • Number of total trees removed thus far: 1,750 • Number of miles inspected: 1,122.6 • Number of strike trees per mile of lines inspected before removals: 45.76 • Number of strike trees per mile after removals: 8.26 • Number of trees inspected: 760,893 • Number of strike trees inspected in 2023: 7,393 • Number of miles inspected in 2023: 273.93 • Number of trees removed in 2023: 5,030 • PG&E believes this question is referring to the Quarter 2 2024 QDR where in row 49 in Table 11 there is $0 for Vegetation Management Activity ‘Clearance’. PG&E is capturing VM-03 under Fall-In Mitigation Activity in row 51. The costs for VM-03 specifically are as follows: o 2023 Recorded: $27.3M which was a portion of the total of $75.5M for Fall-In Mitigation. o 2024 Forecast: $216.4M which was a portion of the total of $309M for FallIn Mitigation. o 2025 Forecast: PG&E will provide an update for this year in the next QDR. | Henry Sweat | 2024-08-29 | 2024-09-12 | 2024-09-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_019.zip | 0 | N/A | 8.2.2.2.5 | Vegetation Management and Inspections | Focused Tree Inspections | N/A |  | CPUC - SPD (Safety Policy Division) | 019 | 12 | 11 | Mona Hedin | Cherimae Vail | VMDR | Eva Miller | Lauren Ruby | Peter Kenny | Yes | Yes | Yes |  | Yes |  |  |  | 2024-09-12 | [16 empty] | 12 | VMDR | Eva Miller | Mona Hedin | Cherimae Vail | Lauren Ruby
703 | CPUC - SPD (Safety Policy Division) | 019 | CPUC - SPD (Safety Policy Division)_019 | 11 | CPUC - SPD (Safety Policy Division)_019_Q11 | For inspectors for PG&E’s distribution overhead inspection programs, (1) how are future weather conditions profiled to inspectors, (2) when would and how would an inspector consider weather conditions when prioritizing a work order as Priority A, X, B, E or F (such as an inspector seeing a vulnerable asset and also having knowledge of high winds incoming)? | 1) PG&E Inspector Training advises inspectors to check the weather reports each morning before they report to the field. This can be done in multiple ways, including checking the weather application on their cell phone and/or reviewing daily emails from PG&E’s meteorology department. 2) Inspectors take into consideration the weather conditions in recommending a priority level when creating Electric Corrective (EC) notifications for compelling abnormal conditions. Per the formal inspector training, inspectors learn they can assign default priorities for many scenarios, including weather conditions. | Henry Sweat | 2024-08-29 | 2024-09-12 | 2024-09-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_019.zip | 0 | N/A | 8 | Section 8.1.3 - Asset Inspection | 8.1.3 Asset Inspections | N/A |  | CPUC - SPD (Safety Policy Division) | 019 | 11 | 0 | Mona Hedin | Nelson Lau | SIDR | Stacie Doyle/Heather Duncan | Aaron Shapiro | Jason Regan | [8 empty] | 2024-09-12 | [16 empty] | 11 | SIDR | Stacie Doyle/Heather Duncan | Mona Hedin | Nelson Lau | Aaron Shapiro
702 | CPUC - SPD (Safety Policy Division) | 019 | CPUC - SPD (Safety Policy Division)_019 | 10 | CPUC - SPD (Safety Policy Division)_019_Q10 | When will the further engineering assessment be completed? | G&E currently plans to risk prioritize the locations that require engineering assessment and complete all the subject engineering analysis by end of Quarter 2 of 2026. | Henry Sweat | 2024-08-29 | 2024-09-12 | 2024-09-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_019.zip | 0 | N/A | 8 | Section 8.1.3 - Asset Inspection | 8.1.3.2.4 LiDAR based Pole Loading Assessments | N/A |  | CPUC - SPD (Safety Policy Division) | 019 | 10 | 0 | Mona Hedin | Nelson Lau | Arvind Simhadri/Tiffany Pazdan | Jim Gill | Aaron Shapiro | Martin Wyspianski | Yes | Yes | Yes |  | Yes |  | Yes |  | 2024-09-12 | [16 empty] | 10 | Arvind Simhadri/Tiffany Pazdan | Jim Gill | Mona Hedin | Nelson Lau | Aaron Shapiro
701 | CPUC - SPD (Safety Policy Division) | 019 | CPUC - SPD (Safety Policy Division)_019 | 9 | CPUC - SPD (Safety Policy Division)_019_Q9 | Submit one example of a one desktop-based assessment pole loading calculation for an unguyed tangent pole and highlight where the criteria submitted in the spreadsheet as part of question 8 may be obtained from the calculation. | Please reference attachments “WMP-Discovery2023-2025_DR_SPD_019- Q009Atch01.pdf” and “WMP-Discovery2023-2025_DR_SPD_019-Q009Atch02.pdf” for one desktop-based assessment Pole Loading Calculation (PLC) for an un-guyed tangent pole with the criteria submitted as part of Question 008, also listed below, highlighted for reference. • Pole SAP ID • Horizontal Loading Criteria • Loading Type • Safety Factor • Grade of Construction • Maximum Capacity Utilization Attachment “WMP-Discovery2023-2025_DR_SPD_019-Q009Atch01.pdf” is the PLC that resulted from the Desktop-Based Assessment. This PLC utilized the conductors from our EDGIS system of record, which indicated that the pole had #4CU conductor on one side and 2ACSR on the other side. Please see Figure 1 on “WMP-Discovery2023- 2025_DR_SPD_019-Q009Atch03CONF.pdf”. These conductors resulted in the pole being imbalanced, and presumed to be overloaded, as both sets of conductors are at full tension and double dead-ended at the subject pole. “WMP-Discovery2023-2025_DR_SPD_019-Q009Atch02CONF.pdf” is the PLC that resulted from the Further Engineering Assessment. This PLC utilized enhanced imagery and work management records from SAP to recognize that the #4CU conductor is actually 2ACSR conductor in the field. Please see Figure 2 on “WMP-Discovery2023- 2025_DR_SPD_019-Q009Atch03CONF.pdf”. The correction that the pole is not double dead ended and has 2ACSR on both sides balanced the subject pole and validated that it is not in an overloaded condition. | Henry Sweat | 2024-08-29 | 2024-09-12 | 2024-09-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_019.zip | 3 | N/A | 8 | Section 8.1.3 - Asset Inspection | 8.1.3.2.4 LiDAR based Pole Loading Assessments | N/A |  | CPUC - SPD (Safety Policy Division) | 019 | 9 | 0 | Mona Hedin | Nelson Lau | Arvind Simhadri/Tiffany Pazdan | Jim Gill | Aaron Shapiro | Martin Wyspianski | Yes | Yes | Yes |  | Yes |  | Yes |  | 2024-09-12 | [16 empty] | 9 | Arvind Simhadri/Tiffany Pazdan | Jim Gill | Mona Hedin | Nelson Lau | Aaron Shapiro
700 | CPUC - SPD (Safety Policy Division) | 019 | CPUC - SPD (Safety Policy Division)_019 | 8 | CPUC - SPD (Safety Policy Division)_019_Q8 | In response to SPD_016-Q15, PG&E stated it completed pole loading desktopbased assessments for 530,000 poles in the HFTD area. SPD understands a subset of these poles are undergoing further engineering analysis. Submit the following for each of the 530,000 poles in the HFTD area that was assessed as part of the desktop-based assessment (see the attached spreadsheet for the template): • SAP ID, • Horizontal Loading Criteria (for cylindrical shapes), • Loading Type (Heavy or Light), • Safety Factor Calculated by Desktop-based assessment, • Yes/No for Undergoing Further Engineering Assessment. | Please see “WMP-Discovery2023-2025_DR_SPD_019-Q002Ath01CONF.xlsx” for the requested data for the approximately 530,000 poles in HFTD areas that have completed pole loading desktop-based assessments, plus an additional approximately 16,000 poles that are in the buffer areas surrounding the HFTD areas. These poles have also received a desktop-based pole loading assessment. In addition to Pole SAP Equipment ID, Horizontal Loading Criteria, Loading Type, Safety Factor (SF), and Yes/No for Undergoing Further Engineering Assessment, we have included Grade of Construction (GOC) and Maximum Capacity Utilization (MCU). PG&E has included GOC because it is a critical data element when assessing the poles loading capability. In addition, MCU is included because it is an easier to compare data point, as it is essentially a SF percentage that incorporates the GOC. Therefore, with MCU, it is possible to understand the loading capacity of the pole with just the one data point. Please understand that for all poles that are undergoing further engineering assessment, PG&E has not reported SF or MCU, as these are currently in-progress. We would be happy to meet to review this data with you to discuss the program more in-depth if it would be helpful. | Henry Sweat | 2024-08-29 | 2024-09-12 | 2024-09-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_019.zip | 0 | N/A | 8 | Section 8.1.3 - Asset Inspection | 8.1.3.2.4 LiDAR based Pole Loading Assessments | N/A |  | CPUC - SPD (Safety Policy Division) | 019 | 8 | 5 | Mona Hedin | Nelson Lau | Arvind Simhadri/Tiffany Pazdan | Jim Gill | Aaron Shapiro | Martin Wyspianski | Yes |  | Yes |  | Yes |  |  |  | 2024-09-12 | [16 empty] | 8 | Arvind Simhadri/Tiffany Pazdan | Jim Gill | Mona Hedin | Nelson Lau | Aaron Shapiro
699 | CPUC - SPD (Safety Policy Division) | 019 | CPUC - SPD (Safety Policy Division)_019 | 7 | CPUC - SPD (Safety Policy Division)_019_Q7 | Submit the following documents for a pole which (1) has a pole loading calculation and (2) was identified by the pole test and treat inspection program to have 40% or less remaining strength: • Pole test and treat inspection report • The procedures used to perform and pole test and treat • Work order for the pole • The calculation (in spreadsheet form) for the remaining strength. The spreadsheet submitted should be able to modifiable so that SPD can recalculate parameters depending on different properties. • Papers or testing data which justifies the methodology used to calculate the remaining strength. • The pole loading calculation. • A description of actions taken by PG&E after the inspection. | PG&E has identified Pole 100884900 (subject pole), which has both a Pole Loading Calculation (PLC) and was identified by the Pole Test and Treat (PTT) program to have less than 40% Remaining Strength (RS). Please see explanations below and referenced attachments for each of the bullets from the original question. • PTT inspected the subject pole on December 5, 2023. Please see attachment “WMP-Discovery2023-2025_DR_SPD_019-Q007Atch01CONF.pdf” for the PTT inspection report. • PTT utilized Utility Procedure, TD-2325P-01, Revision 3 to inspect the subject pole. Please see attachment “WMP-Discovery2023-2025_DR_SPD_019- Q007Atch02CONF.pdf” for the Utility Procedure. • PTT rejected the subject pole on December 5, 2023, recommending replacement. PTT generated Electric Corrective (EC) Notification 127543038 to replace the subject pole. Please see attachment “WMP-Discovery2023-2025_DR_SPD_019- Q007Atch03CONF.pdf” for the EC notification. • PG&E intrusive inspectors utilize our Inspect Application to document their inspections. The Inspect Application has a strength calculator (D-Calc) built into the intrusive inspection checklist, which is used to document the decay observed and results in a remaining strength. PG&E welcomes the opportunity to demonstrate the Inspect Application and embedded strength calculator to SPD. • PG&E purchased D-Calc from EDM and integrated the strength calculator into the Inspect Application. Please see attachment “WMP-Discovery2023- 2025_DR_SPD_019-Q007Atch04.pdf” for EDM’s D-Calc software manual from July 2015. • PG&E Estimating team performed a PLC for Pole 100884900. Please see attachment “WMP-Discovery2023-2025_DR_SPD_019-Q007Atch05CONF.pdf” for the PLC. • PTT inspected this pole on December 5, 2023. PG&E’s Estimating team performed a PLC for this pole in February 2024, which indicated a Bending Safety Factor (SF) of 1.33. Due to the low SF, the Asset Strategy team upgraded the EC Notification to a Priority-B replacement, due within 6-Months. The EC Notification was estimated, permitted and provided to construction for execution. Pole 100884900 was replaced on June 19, 2024. | Henry Sweat | 2024-08-29 | 2024-09-12 | 2024-09-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_019.zip | 3 | N/A | 8 | Section 8.1.3 - Asset Inspection | 8.1.3.2.4 LiDAR based Pole Loading Assessments | N/A |  | CPUC - SPD (Safety Policy Division) | 019 | 7 | 7 | Mona Hedin | Nelson Lau | Arvind Simhadri/Tiffany Pazdan | Jim Gill | Aaron Shapiro | Martin Wyspianski | Yes | Yes | Yes |  | Yes |  | Yes |  | 2024-09-12 | [16 empty] | 7 | Arvind Simhadri/Tiffany Pazdan | Jim Gill | Mona Hedin | Nelson Lau | Aaron Shapiro
698 | CPUC - SPD (Safety Policy Division) | 019 | CPUC - SPD (Safety Policy Division)_019 | 6 | CPUC - SPD (Safety Policy Division)_019_Q6 | SPD observed discrepancies in table 2 regarding the reporting unit used for the category 3 - Time between level 1 asset inspection finding and resulting maintenance activity. The 2023 QDRs designate this time in days, while the first two quarters of the 2024 QDR list hours as their unit of measure. There is also a note on the 2024 QDRs listing the following: “Please note that PGE is reporting this metric in Days as the duration of correcting these infractions are typically in months.” Please confirm if this metric has been reported in days and why the 2024 QDRs is listing the measurement in hours. | The fields in PG&E’s System of Record, SAP, are recorded in days. As such, PG&E is reporting the referenced metric in days in the QDR. In 2023, PG&E modified the QDR template to change the metric from days to hours. PG&E was asked by Energy Safety not to modify the QDR template metrics going forward. In 2024, PG&E added a note to the referenced table in the QDR reports to note that even though the metric column reflects hours, the units of measurement are still reflective of days due to system limitations. | Henry Sweat | 2024-08-29 | 2024-09-12 | 2024-09-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_019.zip | 0 | N/A | QDR | N/A | N/A | N/A |  | CPUC - SPD (Safety Policy Division) | 019 | 6 | 0 | Mona Hedin | Nelson Lau | Matt Horowitz/Ashely Lamb/Issam El Ayadi | Brittany Beston/Maria Ly | Aaron Shapiro | Martin Wyspianski | Yes | Yes | Yes |  | Yes |  | Yes |  | 2024-09-12 | [16 empty] | 6 | Matt Horowitz/Ashely Lamb/Issam El Ayadi | Brittany Beston/Maria Ly | Mona Hedin | Nelson Lau | Aaron Shapiro
697 | CPUC - SPD (Safety Policy Division) | 019 | CPUC - SPD (Safety Policy Division)_019 | 5 | CPUC - SPD (Safety Policy Division)_019_Q5 | Table 13 in the Q2 2024 QDR lists Work Order numbers 128769192 and 129125787 as open as of 6/30/2024. Provide the work orders and discuss why these work orders remained open as of 6/30/2024. | Please see attachment “WMP-Discovery2023-2025_DR_SPD_019- Q005Atch01CONF.pdf” for Electric Corrective (EC) tag 128769192 and attachment “WMP-Discovery2023-2025_DR_SPD_019-Q005Atch02CONF.pdf” for Line Corrective (LC) tag 129125787. PG&E is still researching Notification 128769192 and will follow up with additional details as to why the work order stayed open as of June 30, 2024, as soon as possible. July 3, 2024. Once created, PG&E needed to wait until the customer could repair their weather head to coordinate the service installation. The notification was also pending clerical processing to close out the completed paperwork, however, is now closed in SAP. Notification 129125787 was not closed in SAP until July 1, 2024; however, the work was completed in the field on June 26, 2024, per the long text comment generated by the Construct application. | Henry Sweat | 2024-08-29 | 2024-09-12 | 2024-09-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_019.zip | 2 | N/A | QDR | N/A | N/A | N/A |  | CPUC - SPD (Safety Policy Division) | 019 | 5 | 0 | Mona Hedin | Nelson Lau | Emily Ketcherside/Lakshmi Kumar | Angie Gibson | Aaron Shapiro | Martin Wyspianski | Yes | Yes | Yes |  | Yes |  | Yes |  | 2024-09-12 | [16 empty] | 5 | Emily Ketcherside/Lakshmi Kumar | Angie Gibson | Mona Hedin | Nelson Lau | Aaron Shapiro
696 | CPUC - SPD (Safety Policy Division) | 019 | CPUC - SPD (Safety Policy Division)_019 | 4 | CPUC - SPD (Safety Policy Division)_019_Q4 | Table 13 in the Q2 2024 QDR lists Work Order number 121706053 as an open level 1 work order originating on July 9th 2021. Provide the work order and background information regarding this asset including why this work order remained open as of 6/30/2024. | Please see attachment “WMP-Discovery2023-2025_DR_SPD_019- Q004Atch01CONF.pdf” for the requested work order. Tag 121706053 was reopened on August 1, 2024, for correction of closure. Originally the tag was closed out as COMP (completed) but when it was reopened, it was corrected to CNCL (canceled) due to being a duplicate location to a lower priority tag, where the work was completed. Please see the comments included on the work order for additional information. | Henry Sweat | 2024-08-29 | 2024-09-12 | 2024-09-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_019.zip | 1 | N/A | QDR | N/A | N/A | N/A |  | CPUC - SPD (Safety Policy Division) | 019 | 4 | 0 | Mona Hedin | Nelson Lau | Emily Ketcherside/Lakshmi Kumar | Angie Gibson | Aaron Shapiro | Martin Wyspianski | Yes | Yes | Yes |  | Yes |  | Yes |  | 2024-09-12 | [16 empty] | 4 | Emily Ketcherside/Lakshmi Kumar | Angie Gibson | Mona Hedin | Nelson Lau | Aaron Shapiro
695 | CPUC - SPD (Safety Policy Division) | 019 | CPUC - SPD (Safety Policy Division)_019 | 3 | CPUC - SPD (Safety Policy Division)_019_Q3 | Explain if a same day repair would be designated as 0 or 1 day in table 2. | PG&E designates same day repairs as “0” in table 2. | Henry Sweat | 2024-08-29 | 2024-09-12 | 2024-09-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_019.zip | 0 | N/A | QDR | N/A | N/A | N/A |  | CPUC - SPD (Safety Policy Division) | 019 | 3 | 0 | Mona Hedin | Nelson Lau | Matt Horowitz/Ashely Lamb/Issam El Ayadi | Brittany Beston/Maria Ly | Aaron Shapiro | Martin Wyspianski | Yes | Yes | Yes |  | Yes |  | Yes |  | 2024-09-12 | [16 empty] | 3 | Matt Horowitz/Ashely Lamb/Issam El Ayadi | Brittany Beston/Maria Ly | Mona Hedin | Nelson Lau | Aaron Shapiro
694 | CPUC - SPD (Safety Policy Division) | 019 | CPUC - SPD (Safety Policy Division)_019 | 2 | CPUC - SPD (Safety Policy Division)_019_Q2 | Provide a breakdown of all of the level 1 asset findings or corrective actions (per GO 95 Priority Level) that made up the results of table 2. SPD requests a table containing the following columns with each level 1 asset inspection for years 2020 Q1 through present listed on the Y axis. Follow the attached excel formatting: 1. Work Order Number 2. Asset Type (overhead, underground) 3. Line Type (Transmission, Distribution-Primary, Distribution-Secondary) 4. PG&E Tag Priority 5. Longitude 6. Latitude 7. Location (Division) 8. Date created / found 9. Completion date (If applicable) 10. Method found (inspection, normal order of work, storm work) 11. GO 95 Required Compliance Date, 12. Location (HFTD Tier 2, HFTD Tier 3, HFTD Zone 1, HFRA (Non-HFTD), Non HFTD/Non HFRA)), 13. Segment ID 14. Circuit ID 15. Wire down Event ID (If Applicable) 16. Outage event ID (If Applicable) 17. Facility Damage Action (FDA) 18. Cause / Notes 19. Explanation for a non-immediate repair. If repair took longer than 1 day to complete, explain reason why. | Please see attachment “WMP-Discovery2023-2025_DR_SPD_019- Q002Ath01CONF.xlsx” for the requested information. Please note, the last maintenance date for each asset was included in the provided template (Column R), however, it was not included in the narrative of the data request. Since providing the last maintenance date requires a substantial amount of manual data gathering, please let us know if this information is being requested. If so, we would greatly appreciate some additional time to provide this information. We would be happy to meet and confer on this issue if it would be helpful. Notes: • “Location (Division)” (#7): Transmission maintenance work is organized by work center and not division. Work center is provided in response to this question. • “Method found” (#10): Method is tracked through manually added statuses for different inspection and patrol types. These are the same statuses used to derive the QDR Table 2 inspection type and method. • “Wire down event ID” (#15): Wire down event IDs are outage event IDs for which a wire down was noted. • “Outage event ID” (#16): Outage events are not directly associated with tags and were matched to tags using the circuit and date. If the same circuit experienced multiple outages on the same date, all outage IDs from that date are listed. • “Cause/notes” (#18) and “explanation for non-immediate repair” (#19): The long text comments are provided and are the only readily queried source of information related to the cause and available explanations for non-immediate repair. | Henry Sweat | 2024-08-29 | 2024-09-12 | 2024-09-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_019.zip | 1 | N/A | QDR | N/A | N/A | N/A |  | CPUC - SPD (Safety Policy Division) | 019 | 2 | 19 | Mona Hedin | Nelson Lau | Emily Ketcherside/Lakshmi Kumar | Jim Gill | Aaron Shapiro | Martin Wyspianski | Yes | Yes | Yes |  | Yes |  | Yes |  | 2024-09-12 | [16 empty] | 2 | Emily Ketcherside/Lakshmi Kumar | Jim Gill | Mona Hedin | Nelson Lau | Aaron Shapiro
693 | CPUC - SPD (Safety Policy Division) | 019 | CPUC - SPD (Safety Policy Division)_019 | 1 | CPUC - SPD (Safety Policy Division)_019_Q1 | Explain why the median corrective action time for a level 1 finding exceeded 1 day in table 2 of the 2024 Q2 QDR. [See metric “Time between level 1 asset inspection finding and resulting maintenance activity” which includes – metric numbers 3.d.2.a through 3.t.4.a). | There are several reasons why a median corrective action time for a Level 1 finding could exceed one day. Some examples of delays are discussed below. PG&E will immediately respond to all Level 1 (A priority) notifications and immediately repair the condition (fully or temporarily), not to exceed the next day. In situations where immediate resolution is not possible, PG&E will continuously monitor the nonconformance until it is mitigated. The associated notification will be closed as soon as possible following infield mitigation. Closure of a notification will take place after the work has been verified with applicable documentation and photo evidence uploaded into SAP. Additionally, night emergency work will occasionally stay open until the next day when higher quality pictures that verify mitigation can be taken to document the work completion. Also, if the Level 1 condition was temporarily mitigated but more repairs were needed, this could exceed one day for ongoing work still needing to be addressed. Finally, some notifications reported in the Quarterly Data Report (QDR) originated as Level 2 or 3 and later were escalated to Level 1, for example, through a field safety reassessment. Since the timelines for the original priority levels were longer, the time between the finding and closure of these notifications will exceed one day. | Henry Sweat | 2024-08-29 | 2024-09-12 | 2024-09-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_019.zip | 0 | N/A | QDR | N/A | N/A | N/A |  | CPUC - SPD (Safety Policy Division) | 019 | 1 | 0 | Mona Hedin | Nelson Lau | Emily Ketcherside/Lakshmi Kumar | Angie Gibson | Aaron Shapiro | Martin Wyspianski | Yes | Yes | Yes |  | Yes |  | Yes |  | 2024-09-12 | [16 empty] | 1 | Emily Ketcherside/Lakshmi Kumar | Angie Gibson | Mona Hedin | Nelson Lau | Aaron Shapiro
682 | CPUC - SPD (Safety Policy Division) | 018 | CPUC - SPD (Safety Policy Division)_018 | 1 | CPUC - SPD (Safety Policy Division)_018_Q1 | Submit the 2024 Q2 QDR Confidential and non-Confidential versions (including both spatial and non-spatial) via Kiteworks to SPD’s Wildfire and Safety Performance Section. | Please find the requested 2024 Q2 QDR Spatial and Non-Spatial files attached to this response: • OEIS Cover letter Q2 2024 Submission.pdf • PG&E_2024_Q2_Tables1-15_R0.xlsx • PG&E_2024_Q2_SpatialDataStatusReport.xlsx • PG&E_2024_Q2_CONF.zip • PG&E_2024_Q2_Risk Event Photos - Ignitions_CONF.zip • PG&E_2024_Q2_Initiative Photo Log - Asset Inspections_CONF_1.zip • PG&E_2024_Q2_Initiative Photo Log - Asset Inspections_CONF_2.zip • PG&E_2024_Q2_Initiative Photo Log - Asset Inspections_CONF_3.zip • PG&E_2024_Q2_Initiative Photo Log - Asset Inspections_CONF_4.zip | Henry Sweat | 2024-08-02 | 2024-08-06 | 2024-08-02 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_018.zip | 9 | N/A | QDR | N/A | N/A | N/A |  | CPUC - SPD (Safety Policy Division) | 018 | 1 | 0 | Mona Hedin | Nelson Lau | Chris Wong | Matt Whorton | Aaron Shapiro | Kristin Manz | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | 2024-08-06 | [16 empty] | 1 | Chris Wong | Matt Whorton | Mona Hedin | Nelson Lau | Aaron Shapiro | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
658 | CPUC - SPD (Safety Policy Division) | 016 | CPUC - SPD (Safety Policy Division)_016 | 15 | CPUC - SPD (Safety Policy Division)_016_Q15 | These questions are based off the Pole Loading Assessment work described in Section 8.1.3.2.4 of “TN13804_20240402T112956_PGE's_20232025_Wildfire_Mitigation_Plan_Revision_5.pdf” a. Provide summary statistics for the pole calculations already performed including: i. Number of pole calculations performed in the HFTD ii. Number of pole calculations remaining in the HFTD iii. Number of poles where the calculated safety factor was less than the safety factor specified by GO-95, Rule 44.1, Table 4 in the HFTD iv. Number of poles where the calculated safety factor was less than the safety factor specified by GO-95, Rule 44.3 in the HFTD v. Number of poles where the calculated safety factor was less than the safety factor specified by GO-95, Rule 44.1, Table 4 in the HFTD despite no strength deterioration being incorporated into the calculation. vi. Number of poles where the calculated safety factor was less than the safety factor specified by GO-95, Rule 44.3 in the HFTD despite no strength deterioration being incorporated into the calculation. vii. Provide the same information for poles not located in the HFTD. b. Provide an updated completion date for the program for both HFTD and non-HFTD areas. c. When the calculated safety factor is less than the safety factor specified by GO-95, Rule 44.1, Table 4 or GO-95, Rule 44.3, discuss typical root causes. d. Describe how this information related to the pole loading assessment is profiled to inspectors performing inspections. e. Provide the loading criteria used for the pole loading assessments. f. Describe how the pole loading assessments incorporate the intrusive inspection data from the Pole Test and Treat program, and how the Pole Test and Treat program will incorporate the pole loading data when performing inspections. g. Describe how the pole loading assessments incorporate observations from system inspections, such as leaning or damaged poles. h. Describe PG&E’s actions when the calculated safety factor for a pole is less than the safety factor specified by GO-95, Rule 44.1, Table 4 and separately when the calculated safety factor for a pole is less than the safety factor specified by GO-95, Rule 44.3. i. Discuss calculations performed on crossarms and conductors, and provide similar data as requested in part (a). j. Provide “WMP-Discovery2023_DR_CalAdvocates_032-Q008Atch01CONF.zip.” If one of these poles calculations does not include a pole calculation with a down guy, provide a randomly chosen pole calculation with a down guy. k. Explain how the tensions from both vertical and horizontal loads in the conductors are calculated, especially when adjacent spans are not the same length, do not have the same sag, or are not at the same elevation. l. Discuss which measurements used in the pole loading assessments are provided by LIDAR, and what other sources of measurements are used in the assessments. i. What is the accuracy of the LIDAR being used? ii. What is the max range of the LIDAR? iii. What does PG&E use for measurements for assessments where LIDAR cannot obtain suitable measurements? m. Describe any calculations performed related to deflections, pole foundations, clearances between conductors, and aeolian vibrations. | a. The Pole Loading Assessment (PLA) Program began in 2020 and conducted a desktop-based assessment of the pole loading by utilizing the pole attributes from EDGIS and LiDAR data. The PLA Program is above and beyond the requirements in GO 95, Rule 44, because no work is occurring at the poles as part of the PLA Program, so no new installation or reconstruction requires Pole Loading Calculations (PLCs). PG&E is performing proactive pole loading assessments to risk-prioritize maintenance and remediation of in-service poles. The PLA desktop-based assessments are performed by a team of data analysts. These assessments highlighted higher risk poles that need further engineering analysis. The higher risk poles are currently being prioritized for a comprehensive engineering analysis (which includes field validation, where needed). Once this analysis is completed, we will have the Safety Factor (SF) for the poles. i. The PLA Program completed desktop-based assessments on approximately 530,000 poles in HFTD areas. The pole loading for the remaining poles in HFTD areas has been assessed through other programs, such as system hardening. ii. No poles are remaining in HFTD areas for the PLA Program. iii. PG&E is currently prioritizing the higher risk poles for a comprehensive engineering analysis (which includes field validation, where needed). thus, the requested SFs are not yet available but will be available after this analysis is complete. iv. Please see the response to subpart a(iii) above which explains our process and why the requested information is not yet available. v. Please see the response to subpart a(iii) above which explains our process and why the requested information is not yet available. vi. Please see the response to subpart a(iii) above which explains our process and why the requested information is not yet available. vii. PG&E has not started assessing poles in non-HFTD areas. b. Please see the response to subpart (a) above for the status of poles in HFTD areas. As stated in subpart a(vii), PG&E has not yet started assessing poles in non-HFTD areas. c. Please see the response to subpart (a) above for an explanation of the status of this work. PG&E is in the beginning stages of understanding the causes and influences of overload conditions through the comprehensive engineering analysis of higher risk poles. d. Once the comprehensive engineering analysis is complete, the pole will either be determined to be overloaded or not overloaded. If the pole is determined to be overloaded and in need of remediation, an Electric Corrective (EC) notification will be created to perform the remediation activities through the maintenance program. Inspectors have visibility of the open EC notifications for the inspection locations. e. Please see the response to subpart a(iii) above. PG&E is in the beginning stages of performing comprehensive engineering analysis of the higher risk poles. f. The pole loading assessments incorporate the remaining strength captured during the most recent intrusive inspection. g. Minor physical damage on the pole does not significantly impact the pole loading. In addition, pole leaning is typically indicative of a pole foundation issue or improper guying. As such, these types of conditions are entered directly into the maintenance program for remediation via an EC notification. h. Please see the response to subpart a(iii) above. PG&E is in the beginning stages of performing comprehensive engineering analysis of the higher risk poles. i. PG&E does not perform such calculations as part of the PLA Program. j. Please see attachment “WMP-Discovery2023_DR_CalAdvocates_032-Q008Atch01CONF.zip” for the requested information. Multiple poles included in this zip file have down guys. k. O-Calc Pro considers both vertical and horizontal loading of all components modeled on the pole, which includes conductors, framing equipment, OH equipment, etc. In addition, the span lengths, angles, height of attachments and elevations are calculated leveraging EDGIS positions, which are derived from the LiDAR data. Further, O-Calc Pro’s conductor tensions are configured based on PG&E’s Standards, which are based on new installations and do not account for relaxation while in-service. l. The position of the pole is derived from EDGIS, which is based on LiDAR data. As discussed in subpart k, the span lengths, angles, heights of attachments and elevations are calculated leveraging EDGIS position, which are derived from the LiDAR data as well. Additional data, such as framing and OH equipment are observed from recently collected field inspection photographs. i. PG&E uses multiple types of LiDAR (aerial: rotary (helicopter) and fixed wing, and ground: vehicle). The accuracy of the LiDAR is dependent on the vintage (year collected), as well as the method of collection. The expectation is that the position of the pole is +/- 3 feet in EDGIS, as derived from the LiDAR data. ii. Please see the response to subpart l(i) above for the requested information. iii. The PLA Program leverages pole positions from EDGIS, which is based on LiDAR data. Additional data, such as framing and OH equipment are observed from recently collected field inspection photographs. If there is crucial data missing, the team can send someone to the field to gather the required information for performing the PLC. m. PG&E does not perform these calculations as part of the PLA Program. | Henry Sweat | 2024-05-30 | 2024-06-19 | 2024-06-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_016.zip | 1 | N/A | 8 | Section 8.1.3 - Asset Inspection | 8.1.3.2.4 LiDAR based Pole Loading Assessments | N/A |  | CPUC - SPD (Safety Policy Division) | 016 | 15 | 23 | Mona Hedin | Nelson Lau | Tiffany Pazdan/Jamie Salazar/Arvind Simhardi | Jim Gill | Aaron Shapiro | Martin Wyspianski | Yes | Yes | Yes | Yes | Yes | Yes |  |  | 2024-06-19 |  | extension - asking for significant amount of data that will take time to pull | [14 empty] | 15 | Tiffany Pazdan/Jamie Salazar/Arvind Simhardi | Jim Gill | Mona Hedin | Nelson Lau | Aaron Shapiro | 23 |  |  |  |  | completed | 0 | 0 | 0 | 0
657 | CPUC - SPD (Safety Policy Division) | 016 | CPUC - SPD (Safety Policy Division)_016 | 14 | CPUC - SPD (Safety Policy Division)_016_Q14 | SPD understands PG&E recently attended the 2024 Annual Conference ¦ International Wildfire Risk Mitigation Consortium (umsgroup.com). Provide all presentations from that conference and provide the Conference program/schedule. | The International Wildfire Risk Mitigation Consortium 2024 Annual Conference agenda is provided here: https://iwrmcannualconference.umsgroup.com/iwrmc-2024-annual-conference-agenda/ . Please see table below for presentations made by PG&E employees and which are attached to this response. Agenda Item Title Attachment Name Leveraging LiDAR to Identify & Mitigate Risk Associated with Low Hanging Communication Lines WMP-Discovery2023-2025_DR_SPD_016-Q014Atch01CONF.pdf Panel Discussion & Roundtable Q&A: PSPS Execution WMP-Discovery2023-2025_DR_SPD_016-Q014Atch02CONF.pdf PG&E Wildfire Risk Models - Overview & Incorporation of Egress, Suppression, and Internal Resources WMP-Discovery2023-2025_DR_SPD_016-Q014Atch03CONF.pdf Reducing Customer Vulnerability WMP-Discovery2023-2025_DR_SPD_016-Q014Atch04CONF.pdf Measuring Risk & Mitigation Effectiveness WMP-Discovery2023-2025_DR_SPD_016-Q014Atch05CONF.pdf PG&E's 2024 Vegetation Management WMP-Discovery2023-2025_DR_SPD_016-Q014Atch06CONF.pdf | Henry Sweat | 2024-05-30 | 2024-06-04 | 2024-06-04 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_016.zip | 6 | N/A | Appendix D | Appendix D - Areas for Continued Improvement | ACI PG&E-22-06 – Addressing Increase in Risk Events | N/A |  | CPUC - SPD (Safety Policy Division) | 016 | 14 | 0 | Mona Hedin | Nelson Lau | Paige Light | Andy Abranches | Aaron Shapiro | Andy Abranches | Yes |  | Yes |  | Yes | Yes | Yes |  | 2024-06-04 | [16 empty] | 14 | Paige Light | Andy Abranches | Mona Hedin | Nelson Lau | Aaron Shapiro | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
656 | CPUC - SPD (Safety Policy Division) | 016 | CPUC - SPD (Safety Policy Division)_016 | 13 | CPUC - SPD (Safety Policy Division)_016_Q13 | The following questions reference information from the provided in response the previous Data Request CPUC – SPD (Safety Policy Division)_004. a. Provide an updated version of “WMP-Discovery2023_DR_SPD_004-Q001Atch01.xlsx” that includes the data from 2023 and any adjustments since the previous submission made to ignition data in previous years by PG&E. b. “WMP-Discovery2023_DR_SPD_004-Q001Atch01.xlsx” indicates 49 CPUC-reportable ignitions occurred during R3, R4, or R5 (R3+) conditions in 2022. The spreadsheet also states in 2022 that there were 3,479,209 Overhead Circuit Mile Days (CMDs) in R3, R4 or R5 conditions. Dividing 49 ignitions by 3,479,209 CMDs * 100,000 returns an ignition rate of 1.41 ignitions per 100k CMD in R3+ conditions. The ISM submitted a separate graph which indicates the ignition rate was 1.03 which SPD understands was produced by PG&E (see Figure 3 on page 6 of the Q1 2024 ISM report, available at: PG&E Independent Safety Monitor Report (ca.gov)). The two ignition rates differ (the rate also appears to differ from other ignition rates computed in the following table) but appear to have similar units and presumably the same methodology and same data. i. Explain the discrepancy, and if there was a different methodology or data source. ii. Discuss the differences and the advantages of one methodology or data source over the other. Data supplied to SPD in CPUC-SPD (Safety Policy Division)_004 FPI Ignition Rate R3 R4 R5 R5+ Total (R3+) 2022 Ignitions Total 26 21 2 0 49 1.41 Ignitions in HFTD/HFRA 21 17 2 0 40 1.15 Ignitions in HFTD/HFRA Distribution 20 15 2 37 1.06 CMDs 2015280 1351493 112436 0 3479209 | a. Please see “WMP-Discovery2023-2025_DR_SPD_016-Q013Atch01CONF.xlsx” which includes the requested data from 2023 and any adjustments since the previous submission made to ignition data in previous years by PG&E. b. i. Per the Independent Safety Monitor’s Status Update Report, published on March 29, 2024, the graph in figure 3 represents the count of R3+ CPUC reportable ignitions in HFTD and/or HFRA normalized by the cumulative R3+ circuit mile days for that same period. There are ignitions included on WMP-Discovery2023_DR_SPD_004-Q001Atch01.xlsx that had an FPI rating of R3 or above but are not in HFTD nor HFRA and would have been excluded from the analysis conducted by the ISM. PG&E’s internal methodology for calculating the results of this metric from 2022 yield 0.95 R3+ ignitions per circuit mile day. This differs slightly from the ISM’s analysis where the cumulative circuit mile day total used as the denominator represented the total number of circuit miles in R3+ conditions calculated at the Fire Index Area (FIA) level; PG&E’s internal methodology uses the cumulative circuit mileage associated with an FPI value calculated for each unique circuit, a more granular approach. The circuit-specific circuit mileage data was unavailable at the time of the ISM’s analysis. ii. PG&E’s internal approach of calculating the ignitions and cumulative circuit miles associated with the FPI calculated for each independent circuit is more granular and a better representation of the risk actualized (in terms of high FPI ignitions in risky places) versus the exposure for that risk in that period. In addition, the circuit level values better align with our operational mitigations (for example: when we would enable EPSS protection). | Henry Sweat | 2024-05-30 | 2024-06-04 | 2024-06-04 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_016.zip | 0 | N/A | Appendix D | Appendix D - Areas for Continued Improvement | ACI PG&E-22-06 – Addressing Increase in Risk Events | N/A |  | CPUC - SPD (Safety Policy Division) | 016 | 13 | 4 | Mona Hedin | Nelson Lau | Nick Babb | Andy Abranches | Aaron Shapiro | Andy Abranches | Yes | Yes | Yes |  | Yes | Yes | Yes |  | 2024-06-04 | [16 empty] | 13 | Nick Babb | Andy Abranches | Mona Hedin | Nelson Lau | Aaron Shapiro | 4 |  |  |  |  | completed | 0 | 0 | 0 | 0
655 | CPUC - SPD (Safety Policy Division) | 016 | CPUC - SPD (Safety Policy Division)_016 | 12 | CPUC - SPD (Safety Policy Division)_016_Q12 | What is PG&E’s False Start rate for addressing work orders? a. What factors are the most common for a false start? | PG&E is completing this response per clarification from the Safety Policy Division that “false start” are situations when job crews arrive at a job site and are unable to complete the job as scheduled. For Planned Electric Distribution Maintenance work, Major Work Categories 07, 2A, and KA, PG&E’s schedule adherence rate for January 2024 to June 04, 2024, is 68%. 22,997 units were completed, and 10,875 units were not completed. Of the 10,875 units not completed, 1,075 units (10%) is the rate of the units that would be considered not completed due to false start. a. From this year’s data, the most common factors for a false start are: i. Additional time required (unforeseen field conditions) (2.5%) ii. Clearance not set (1.1%) iii. Field conditions changed (4.8%) iv. Miscalculated hours of effort (0.2%) v. No USA (0.1%) vi. Field decision not to work (0.9%) vii. Contractor field decision not to work (0.5%) Overall, the three highest factors for not meeting schedule adherence are Emergency, Inclement Weather, and Rest Period. These factors for not completing against schedule are typically determined prior to a crew arriving at a job site and not being able to complete the work as scheduled. | Henry Sweat | 2024-05-30 | 2024-06-10 | 2024-06-10 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_016.zip | 0 | N/A | 8 | Section 8.1.7 - Open Work Orders | 8.1.7.2 Open Work Orders - Distribution Tags | N/A |  | CPUC - SPD (Safety Policy Division) | 016 | 12 | 1 | Mona Hedin | Nelson Lau | John Jones, Mina Amir, Jared Leong Systems Inspections/Emergency/Restoration/CIRT | Byron Winget Jim Gill | Aaron Shapiro | Martin Wyspianski | Yes | Yes |  |  | Yes |  |  |  | 2024-06-10 | [16 empty] | 12 | John Jones, Mina Amir, Jared Leong Systems Inspections/Emergency/Restoration/CIRT | Byron Winget Jim Gill | Mona Hedin | Nelson Lau | Aaron Shapiro | 1 |  |  |  |  | completed | 0 | 0 | 0 | 0
654 | CPUC - SPD (Safety Policy Division) | 016 | CPUC - SPD (Safety Policy Division)_016 | 11 | CPUC - SPD (Safety Policy Division)_016_Q11 | Discuss how work orders are bundled. a. When an area is selected for bundling, explain whether all or only a partial list of work orders is addressed in a bundling project. iii. How would the remaining work orders not addressed by the bundled project be addressed? b. Are there different types of bundling projects? a. How does the project type affect the bundling? c. How are work orders near their correction deadline handled when bundled? a. Are these work orders (especially Priority A, B and X work orders) allowed to exceed their due date if they are part of a bundling project in process which has a later overall due date? b. Would such individual work orders be recorded as being completed on time? d. Are new work orders created for bundling projects, or are the existing work orders used? e. How would a situation be addressed where a contractor hired to do a bundling project finds multiple work orders already completed due to past work, such as emergency storm work, but were erroneously included in the bid? iv. Would PG&E still pay for the work, or would the contractor refund payment, or be would the contractor not charge for the work orders erroneously included in the bid? | a. PG&E is prioritizing bundling pole and non-pole priority E and F overhead HFTD/HFRA EC notifications when bundling an area, as well as when possible with other notification types. If an area consists of both HFTD and non-HFTD notifications, the non-HFTD notifications may not be addressed within the bundling project. In addition, a bundled notification may not be executed with the bundle if there are external constraints, for instance customer access or permitting requirements that are unique to only a small portion of the bundle some of the notifications maybe removed from the bundle to allow execution of the rest of the notifications. i. The remaining notifications will be addressed during the annual work planning cycle. b. There are two main types of planned bundling projects when it comes to bundling pole and non-pole priority E and F overhead HFTD/HFRA EC notifications. The first type consists of single isolation zone bundles and the second type consists of multiple isolation zones bundled by circuit. i. The main differences between these two types of bundling projects consist of the following: 1. Circuit level bundles are usually much larger consisting of over 100 notifications and take multiple weeks to execute while isolation zone bundles are smaller and are executed in one to a few days typically. 2. Circuit-level bundles are project managed while single isolation zone bundles are managed within the divisions and individual work centers. 3. The majority of the circuit-level bundles are resourced by contract partners while single isolation zone bundles are resourced through the normal work and resource planning process. 4. Circuit level bundles are forecasted to be more efficient to execute as PG&E can bundle more activities increasing throughput with the same amount of resources. c. Bundles are developed through PG&E’s annual planning process and are prioritized based on risk reduction and executability with an emphasis on bundling pole and non-pole priority E and F overhead HFTD/HFRA EC notifications. With the current HFTD maintenance tag backlog, bundling and working tags by isolation zone instead of working newly created tags to meet current GO95 time requirements, described as Steady State previously, will allow us to accelerate our program to be in compliance in HFTD by 2029. Bundling by isolation zone provides us the flexibility to address the most risk first through a risk spend efficiency (RSE) approach. i. Priority A and X EC notifications are strictly out of scope for these types of bundling projects due to the risk they pose on the public and our system. Priority B EC notifications are typically excluded from bundling projects as they are emergent, however, if work is able to be bundled at the operational level by crews executing a priority B EC notification, then they are encouraged to do so. ii. We do not change the required end date (compliance to GO95 Rule 18 timeline) when bundling EC notifications and bundles are not given a separate compliance date. If an EC notification is completed past its due date it will continue to be recorded as being completed late no matter if it is in a bundle or not. d. Currently, the existing work orders are used for bundling projects. e. The contractor would notify the contract manager to modify the work authorization in the bid to remove the work already completed and adjust the overall value of those projects. i. Each vendor has agreed on pricing in their contractors for COA (Completed on Arrival) projects. ii. PG&E is also looking for ways to minimize this scenario, for instance on circuit bundles we performed aerial inspections on all assets months before construction to verify the current status of the assets to increase the quality of our work plan and contractor bids. | Henry Sweat | 2024-05-30 | 2024-06-04 | 2024-06-04 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_016.zip | 0 | N/A | 8 | Section 8.1.7 - Open Work Orders | 8.1.7.2 Open Work Orders - Distribution Tags | N/A |  | CPUC - SPD (Safety Policy Division) | 016 | 11 | 10 | Mona Hedin | Nelson Lau | John Jones Mina Amir Jared Leong Systems Inspections/Emergency/Restoration/CIRT | Byron Winget Jim Gill Kristine Kent | Aaron Shapiro | Martin Wyspianski | Yes | Yes | Yes |  | Yes | Yes |  |  | 2024-06-04 | [16 empty] | 11 | John Jones Mina Amir Jared Leong Systems Inspections/Emergency/Restoration/CIRT | Byron Winget Jim Gill Kristine Kent | Mona Hedin | Nelson Lau | Aaron Shapiro | 10 |  |  |  |  | completed | 0 | 0 | 0 | 0
653 | CPUC - SPD (Safety Policy Division) | 016 | CPUC - SPD (Safety Policy Division)_016 | 10 | CPUC - SPD (Safety Policy Division)_016_Q10 | For each year from 2020 through 2023, and January 1, 2024, through April 30, 2024, and for each work order priority level: a. Provide a list and examples of all cause categories used when canceling work orders. b. Provide the number of cancelled work orders for each priority work under each cause category. c. Provide the number of cancelled work orders for each priority work order under each cause category that was cancelled after the due date. d. Provide the number of cancelled work orders for each priority work order under each cause category that was cancelled within ten days before the due date. e. Provide the number of cancelled work orders for each priority that were replaced by another work order under each cause category and the priority to which it was assigned. f. Provide the number of cancelled work orders for each priority which were cancelled because the work order was no longer considered necessary (for instance, PG&E has referenced the criteria for splices adjacent to insulators may have changed). ii. For this case, explain how PG&E is actively attempting to identify these work orders and streamline the process for assessing them. How many does PG&E anticipate remain in the backlog? |  | Henry Sweat | 2024-05-30 | 2024-06-10 | 2024-06-10 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_016.zip | 1 | N/A | 8 | Section 8.1.7 - Open Work Orders | 8.1.7.2 Open Work Orders - Distribution Tags | N/A |  | CPUC - SPD (Safety Policy Division) | 016 | 10 | 7 | Mona Hedin | Nelson Lau | John Jones, Mina Amir, Jared Leong Systems Inspections/Emergency/Restoration/CIRT | Byron Winget Jim Gill Craig Kurtz | Aaron Shapiro | Martin Wyspianski | Yes |  | Yes |  | Yes |  |  |  | 2024-06-10 |  | 6/4/2024 - Extension to 6/10 approved by Wade Greenacre. Kxfk | 6/4/2024 - Extension to 6/10 approved by Wade Greenacre. Kxfk | [13 empty] | 10 | John Jones, Mina Amir, Jared Leong Systems Inspections/Emergency/Restoration/CIRT | Byron Winget Jim Gill Craig Kurtz | Mona Hedin | Nelson Lau | Aaron Shapiro | 7 |  |  |  |  | completed | 0 | 0 | 0 | 0
652 | CPUC - SPD (Safety Policy Division) | 016 | CPUC - SPD (Safety Policy Division)_016 | 9 | CPUC - SPD (Safety Policy Division)_016_Q9 | Answer the following with regards to QA/QC for system inspections. a. Provide the procedures for QA and QC for all System Inspections for transmission and distribution assets. b. Provide the procedures for detailed inspections (aerial and ground) of distribution and transmission assets. c. Describe what is in a Critical Pass Rate, and how that differs from other types of findings – for Distribution QA the “other” findings appear to be classified as “High,” “Medium,” and “Low” as seen in “WMP-Discovery2023-2025_DR_CalAdvocates_039-Q001Atch01.xlsx.” Provide examples. d. Explain when QC or QA would have different criteria for evaluation and discuss how this manifests in the pass rate. For instance, when would an inspection pass QA but not QC and vice versa. e. Explain why a CritAtt would not result in a new EC tag. Provide examples. See column P of “WMP-Discovery2023-2025_DR_CalAdvocates_039-Q001Atch01.xlsx” for reference. f. Define “STIP” in Column N of “WMP-Discovery2023-2025_DR_CalAdvocates_039-Q001Atch01.xlsx”. g. Explain why some findings identified during QA/QC inspections classified as “High” are considered “Critical Attributes” and others are not? i. Referencing ““WMP-Discovery2023-2025_DR_CalAdvocates_039-Q001Atch05.xlsx,” justify why the finding in Row 4 is not considered a Critical Attribute, whereas the finding in Row 148 is considered a Critical Attribute. Discuss why the finding in Row 4 is not a Critical Attribute considering (1) the two rows have the same identified description “Molding missing, broken, damaged, or loose,” (2) the risk rank and HFTD risk tier is the same (see Columns L through N), but (3) the finding in Row 4 is a Priority E whereas the finding in Row 148 is a Priority F, especially since (3) implies that Row 4 was more risky and thus a more critical miss. | a. Please see attachment “WMP-Discovery2023-2025_DR_SPD_016-Q009Atch01CONF.pdf” for PG&E’s Quality Assurance System Inspections Business Process Document and attachment “WMP-Discovery2023-2025_DR_SPD_016-Q009Atch02CONF.pdf” for PG&E’s procedure for System Inspections Quality Control. b. PG&E uses the guidance set forth in its Electric Distribution Preventative Maintenance (EDPM) Manual for detailed distribution inspections and the Electric Transmission Preventative Maintenance (ETPM) Manual for detailed transmission inspections. Please see attachment “WMP-Discovery2023-2025_DR_SPD_016-Q009Atch03CONF.pdf” for the EDPM and the following link for PG&E’s ETPM: https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/td-1001m-etpmm.pdf. Please see attachments “WMP-Discovery2023-2025_DR_SPD_016-Q009Atch04CONF.pdf” and “WMP-Discovery2023-2025_DR_SPD_016-Q009Atch05CONF.pdf” for aerial inspections. c. Critical Pass Rate is the number of unique SAP Equipment IDs with zero Critical Attribute Findings divided by total number of unique SAP Equipment IDs reviewed. Critical Attribute findings differ from “other” findings in that they are the highest priority condition, as defined by Asset Strategy. The “other” findings that are categorized as “High”, “Medium”, or “Low” risk are not used in calculating the Critical Pass Rate. See SAP Equipment ID 104088798 for an example of a Critical Attribute finding. See SAP Equipment ID 104138705 for an example of a “High” finding. See SAP Equipment ID 104060532 for an example of a “Low” finding. There were no “Medium” findings in document “WMP-Discovery2023-2025_DR_CalAdvocates_039-Q001Atch01.xlsx.” d. QC and QA utilize the same critical miss criteria that is set by Asset Strategy. Current QC and QA audits do not have a pass/fail acceptance criteria for completed inspections. QC and QA audits review inspection checklist attributes and pass/fail the attribute. e. All Critical Attribute findings as defined by Asset Strategy would result in either the creation of a new EC tag or the updating of an existing EC tag. Any Critical Attribute in column P that does not correspond to a Critical Attribute in column N (totalSTIP) is a data entry error that does not adversely affect the pass rate because the pass rate is calculated per column N. f. “STIP” in column N refers to the number of Critical Attribute findings for the corresponding SAP Equipment ID. g. The QA/QC discrepancy rankings include Critical, High, Medium, and Low. PG&E identified attributes/conditions in the system inspection checklist that posed the potential for wildfire risk if the condition existed in the field. Critical Attribute ranked findings are directly related to wildfire risk and represent the highest-level concerns. High, Medium, and Low findings represent non-wildfire risk concerns related to administrative errors, documentation issues, equipment reliability, public safety, etc. h. When referencing “WMP-Discovery2023-2025_DR_CalAdvocates_039- Q001Atch05.xlsx," it appears that Row 4 and Row 148 both identify the finding Description in column “H” as “Molding missing, broken, damaged, or loose,” additionally, both have the same assigned Risk Rank of “High” in column “L”. PG&E is unclear regarding the “Critical Attribute” Risk Rank that was cited in the original question and will require addition information to provide an appropriate response. | Henry Sweat | 2024-05-30 | 2024-06-04 | 2024-06-04 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_016.zip | 5 | N/A | 8 | Section 8.1.3 - Asset Inspection | 8.1.3 Asset Inspections | N/A |  | CPUC - SPD (Safety Policy Division) | 016 | 9 | 8 | Mona Hedin | Hitesh Bhatt | Teresa Tusch SIDR Josh Houston Jared Leong Sean Vanier (Part B) | Josh Keene Stacie Doyle (Part B) Joshua Fredriksson | Aaron Shapiro | Jason Regan | Yes | Yes |  |  | Yes | Yes | Yes |  | 2024-06-04 | [16 empty] | 9 | Teresa Tusch SIDR Josh Houston Jared Leong Sean Vanier (Part B) | Josh Keene Stacie Doyle (Part B) Joshua Fredriksson | Mona Hedin | Hitesh Bhatt | Aaron Shapiro | 8 |  |  |  |  | completed | 0 | 0 | 0 | 0
649 | CPUC - SPD (Safety Policy Division) | 016 | CPUC - SPD (Safety Policy Division)_016 | 6 | CPUC - SPD (Safety Policy Division)_016_Q6 | PG&E describes in “WMP-Discovery2023_DR_CalAdvocates_015-Q018Atch01.docx” a brief description of “Critical attributes” and “Conformance attributes” used to define pass rate. For the following questions, Vegetation Programs refer to the following programs: Distribution Routine, Distribution Second Patrol, Focus Tree inspections, Vegetation Management for Operational Mitigations, Tree Removal Inventory, Focused Tree Inspection (FTI), Transmission, Pole Clearing and Field Quality Control (FQC). a. Provide the criteria for “critical attributes” evaluated by QA/QC inspectors for each Vegetation Program. b. Provide three examples of “critical attributes” evaluated by QA/QC inspectors for each Vegetation Program. c. Provide the criteria for “conformance attributes” evaluated by QA/QC inspectors for each Vegetation Program. d. Provide three examples of “conformance attributes” evaluated by QA/QC inspectors for each Vegetation Program. e. Define the criteria assessed for the “critical pass rate” for each Vegetation Program. Comment on how it relates to “critical attributes” and “conformance attributes.” f. Provide PG&E’s standards for QA and QC for each Vegetation Program. g. Provide the survey used by QA and QC inspectors to record information for each Vegetation Program. h. Describe how an attribute is assessed as a pass/fail and then aggregated up to the pass rate for Vegetation Program. i. Define “Locations”, as used in Table 8-18-1 (Revised) and Table 8-18-2 (Revised). j. Explain when QC or QA would have different criteria for evaluation and discuss how this manifests in the pass rate for each type. For instance, when would work pass QA but not QC and vice versa. k. “WMP-Discovery2023_DR_CalAdvocates_015-Q018Atch01.docx” states the pass rate is: Total Passing responses for Critical and Conformance Attributes divided by (Total Responses for Critical and Conformance Attributes minus N/A responses) whereas footnote 224 on page 708 of “TN13804_20240402T112956_PGE's_20232025_Wildfire_Mitigation_Plan_Revision_5” indicates that the pass rate is based on: the number of assets reviewed by QC that do not have a Critical Attribute (as defined by Asset Strategy) failure or miss divided by the number of assets reviewed by QC. The definition of pass rate appears to be different in a few ways such as (1) the units are different (number of attributes versus number of assets) and (2) one includes conformance attribute, whereas the other does not. Explain the discrepancies between these two criteria and describe how they are used. l. Provide the last 5 completed QC reviews for Distribution Routine that include a finding. m. Provide the last 5 completed QA reviews for Distribution Routine that include a finding. n. Explain why “WMP-Discovery2023-2025_DR_CalAdvocates_039-Q001Atch04.docx” has multiple rows of data where there were 0 trees inspected and 0 trees failed? i. Define trees inspected. (Is this number of strike trees between two poles? Is this just five random trees near a pole?) o. Explain the process of an inspection for Routine Distribution Inspections and FTI for both QA and QC. Specifically discuss the required/other tasks an inspector performs when sent to a location. |  | Henry Sweat | 2024-05-30 | 2024-06-04 | 2024-06-04 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_016.zip | 16 | N/A | 8.2.3.6 | Vegetation Management and Inspections | High-Risk Species | N/A |  | CPUC - SPD (Safety Policy Division) | 016 | 6 | 15 | Mona Hedin | Hitesh Bhatt; Cherimae (VM( | VM; Theresa Tusch | Sarah Carlson; Josh Keene | Lauren Ruby; Aaron Shapiro | Angela Sanford | Yes |  |  |  | Yes | Yes | Yes |  | 2024-06-04 | [16 empty] | 6 | VM; Theresa Tusch | Sarah Carlson; Josh Keene | Mona Hedin | Hitesh Bhatt; Cherimae (VM( | Lauren Ruby; Aaron Shapiro | 15 |  |  |  |  | completed | 0 | 0 | 0 | 0
640 | CPUC - SPD (Safety Policy Division) | 014 | CPUC - SPD (Safety Policy Division)_014 | 9 | CPUC - SPD (Safety Policy Division)_014_Q9 | When does the field engineer get involved with addressing a high (A, X, B) priority tag? Provide examples. a. Can the field engineer change the priority of a tag? Provide examples. b. Describe the role of field engineers in the process for working on high priority tags. | a. No, field engineers do not change the priority level of a tag. b. If the work is assigned to a General Construction crew or contractor, then a Field Engineer coordinates the work required for the tag. PG&E inspectors create and identify the tag’s priority. | Henry Sweat | 2024-05-14 | 2024-05-28 | 2024-05-28 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_014.zip | 0 | N/A | 8 | 8.0 Wildfire Mitigations | 8.1.3 Asset Inspections | N/A |  | CPUC - SPD (Safety Policy Division) | 014 | 9 | 2 | Mona Hedin | Nelson Lau | System Inspections Jo Fogolin | Stacie Doyle Bob Brock | Aaron Shapiro | Jason Regan | Yes | Yes | Yes |  | Yes | Yes |  |  | 2024-05-28 | [16 empty] | 9 | System Inspections Jo Fogolin | Stacie Doyle Bob Brock | Mona Hedin | Nelson Lau | Aaron Shapiro | 2 |  |  |  |  | completed | 0 | 0 | 0 | 0
639 | CPUC - SPD (Safety Policy Division) | 014 | CPUC - SPD (Safety Policy Division)_014 | 8 | CPUC - SPD (Safety Policy Division)_014_Q8 | What would motivate an inspector to override the prioritization for a tag in the job aid and increase the priority or deadline? a. In this scenario, what prevents a de‐prioritization of the tag during the review by a supervisor or other PG&E employee? | An Inspector may override a tag priority if, in the Inspector’s opinion, the situation is more urgent than the minimum priority outlined in the job aid. This could be because of exposure or severity of condition. PG&E’s Centralized Inspection Review Team (CIRT) also reviews tags following an inspection and could increase the priority of a tag if they determine the equipment’s impact of failure or impact of exposure to the public is at risk. a. There is a system control within SAP’s Gatekeeper screen that prevents Electric Corrective (EC) tags from being created with a priority lower than the minimum allowed for the FDA selected. Currently, CIRT Gatekeeper (Qualified Electrical Worker who performs desktop review of tags after they are submitted) may de-prioritize a tag prior to creation, but not beyond its minimum priority assigned in per PG&E guidance (existing procedures such as the OH/UG job aid, etc). Once an EC tag has been created in the system, the required end date field is locked in the system and access is not granted to update this field. | Henry Sweat | 2024-05-14 | 2024-05-28 | 2024-05-28 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_014.zip | 0 | N/A | 8 | 8.0 Wildfire Mitigations | 8.1.3 Asset Inspections | N/A |  | CPUC - SPD (Safety Policy Division) | 014 | 8 | 1 | Mona Hedin | Nelson Lau | System Inspections Sheryll Cruz CIRT Mina Amir Sravani Ayyaluru Jo Fogolin | Stacie Doyle Eric Thomas Heather Duncan | Aaron Shapiro | Jason Regan | Yes | Yes | Yes |  | Yes | Yes | Yes |  | 2024-05-28 | [16 empty] | 8 | System Inspections Sheryll Cruz CIRT Mina Amir Sravani Ayyaluru Jo Fogolin | Stacie Doyle Eric Thomas Heather Duncan | Mona Hedin | Nelson Lau | Aaron Shapiro | 1 |  |  |  |  | completed | 0 | 0 | 0 | 0
638 | CPUC - SPD (Safety Policy Division) | 014 | CPUC - SPD (Safety Policy Division)_014 | 7 | CPUC - SPD (Safety Policy Division)_014_Q7 | Provide the count of tags for each tag type in 2024 where an existing tag was re‐prioritized to a more urgent priority and the priority to which it was re‐assigned due to an inspection. | PG&E interprets this as a request for tags that were re-prioritized to a more urgent priority during an inspection and not during the oversight process. This would occur when an asset with an existing tag was scheduled for an inspection due to General Order 165 requirements. Please see the table below for the requested information. Original Priority Tag Count Escalated Priority B 0 N/A E 216 B F 62 B Please note, A tags are the highest priority. Tags identified as X priority can get upgraded to an A priority, however, this occurs procedurally, and not during an inspection. | Henry Sweat | 2024-05-14 | 2024-05-28 | 2024-05-28 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_014.zip | 0 | N/A | 8 | 8.0 Wildfire Mitigations | 8.1.3 Asset Inspections | N/A |  | CPUC - SPD (Safety Policy Division) | 014 | 7 | 0 | Mona Hedin | Nelson Lau | System Inspections Sheryll Cruz Mina Amir Sravani Ayyaluru Lakshmi Kumar Tripti Uprety | Cynthia King-Felix | Aaron Shapiro | Jason Regan | Yes |  | Yes |  | Yes |  | Yes |  | 2024-05-28 | [16 empty] | 7 | System Inspections Sheryll Cruz Mina Amir Sravani Ayyaluru Lakshmi Kumar Tripti Uprety | Cynthia King-Felix | Mona Hedin | Nelson Lau | Aaron Shapiro | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
637 | CPUC - SPD (Safety Policy Division) | 014 | CPUC - SPD (Safety Policy Division)_014 | 6 | CPUC - SPD (Safety Policy Division)_014_Q6 | Explain tag re‐prioritization oversight process where an inspector’s initial prioritization is changed. a. Provide the number of tags in 2024 found during inspections where the inspector identified A, X, and B tags where the tag was re‐prioritized to a less urgent priority, and which priority it was re‐assigned. b. Provide inspection reports and work orders, including all photos, for the last 10 created tags found during inspections for each of A, X and B where the tag was re‐prioritized to a less urgent priority. c. Provide a list of all tags found in April during inspections where the inspector identified A, X, and B tags where the tag was re‐prioritized to a less urgent priority. The list should include (1) the notification number, (2) the date each tag was found, (3) the original priority, (4) the changed priority and (5) a description of the finding. | PG&E understands this to be requesting tags related to overhead (OH) inspections. Please see below for tags responsive to this request. If an A or X tag are determined not to be emergency tags during the oversight process, the tag is cancelled and a new tag is created with a lesser priority. If a Gatekeeper determines a B tag’s initial prioritization should be de-prioritized, logic in the gatekeeper screen will force the gatekeeper to provide reasons for de-prioritization. These reasons/responses are sent to the submitter via an SAP auto-email generation to finalize the changes made. a. Please see the table below for the requested information, which is current as of May 20, 2024: Tag Count Original Priority Less Urgent Priority 1 A X 1 A B 661 B E 18 B F 2 X B 1 X C 2 X Re-assessed and cancelled b. Please see attachment “WMP-Discovery2023-2025_DR_SPD_014-Q006Atch01CONF.zip” for the requested Priority B tags and associated inspection reports. Please see attachment “WMP-Discovery2023-2025_DR_SPD_014-Q006Atch02CONF.zip” for Priority A and X tags and associated inspection reports. Please note, PG&E only identified eight Priority A and X tags during inspections where the tag was re-prioritized to a less urgent priority. c. Please see attachment “WMP-Discovery2023-2025_DR_SPD_014-Q006Atch03.xlsx” for the requested information. | Henry Sweat | 2024-05-14 | 2024-05-31 | 2024-05-28 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_014.zip | 3 | N/A | 8 | 8.0 Wildfire Mitigations | 8.1.3 Asset Inspections | N/A |  | CPUC - SPD (Safety Policy Division) | 014 | 6 | 3 | Mona Hedin | Nelson Lau | System Inspections Sheryll Cruz CIRT Mina Amir Sravani Ayyaluru Lakshmi Kumar Tripti Uprety Ajuba Riyaz | Cynthia King-Felix/Craig Kurtz | Aaron Shapiro | Jason Regan | Yes |  | Yes |  | Yes |  |  |  | 2024-05-31 |  | 5/23/2024 - j1oz - extension requested on 5/22 due to volume of data and approved by engineer | 5/23/2024 - j1oz - extension requested on 5/22 due to volume of data and approved by engineer | [13 empty] | 6 | System Inspections Sheryll Cruz CIRT Mina Amir Sravani Ayyaluru Lakshmi Kumar Tripti Uprety Ajuba Riyaz | Cynthia King-Felix/Craig Kurtz | Mona Hedin | Nelson Lau | Aaron Shapiro | 3 |  |  |  |  | completed | 0 | 0 | 0 | 0
636 | CPUC - SPD (Safety Policy Division) | 014 | CPUC - SPD (Safety Policy Division)_014 | 5 | CPUC - SPD (Safety Policy Division)_014_Q5 | Provide number of A, B, X, E, F for Aerial, Ground and Pole Test and Treat finds during inspecions in 2023, and 2024 broken down by HFTD and non‐HFTD. Include number of inspecions and find rate for each tag type. Submit the same informaion in the same format as Table RN‐PG&E‐23‐04‐7 (attached in email) for 2023 and 2024 from PG&E’s 2023‐2025 Wildfire Mitgation Plan Supplemental Response to Revision Notice, except provide the actual tag finds, rather than “Forecast Tag Finds.” Indicate if helicopters or planes were used for any of the aerial inspec􀆟ons. | 2023-2024 Actual Finds by Inspection Type Annual Inspections 2023 Annual Inspections 2024 (YTD) Inspection Type Tier Priority Find Rate Actual Inspections by Tier Actual Tag Find Find Rate Actual Inspections by Tier Actual Tag Find Aerial Non-HFTD /HFRA A #N/A* 700 #N/A* 0.32% 1,581 5 X #N/A* #N/A* 0.89% 14 B #N/A* #N/A* 1.14% 18 E #N/A* #N/A* 15.31% 242 F #N/A* #N/A* 0.38% 6 Tier 2 A #N/A* 30,000 #N/A* 0.25% 42,538 107 X #N/A* #N/A* 0.50% 214 B 2.58% 774 3.20% 1,361 E 1.57% 471 13.74% 5,844 F 0.49% 147 0.40% 170 Tier 3 A #N/A* 7,300 #N/A* 0.23% 25,762 58 X #N/A* #N/A* 0.47% 120 B 2.42% 177 3.53% 910 E 0.82% 60 12.67% 3,263 F 0.22% 16 0.42% 109 Ground Non-HFTD /HFRA A 0.73% 4,908 36 4.76% 84 4 X 0.00% 0 0.00% 0 B 2.38% 117 0.00% 0 E 27.87% 1,368 2.38% 2 Annual Inspections 2023 Annual Inspections 2024 (YTD) Inspection Type Tier Priority Find Rate Actual Inspections by Tier Actual Tag Find Find Rate Actual Inspections by Tier Actual Tag Find F 7.58% 372 1.19% 1 Tier 2 A 0.46% 221,021 1,006 1.30% 1,926 25 X 0.00% 0 0.52% 10 B 3.32% 7,327 3.01% 58 E 27.00% 59,670 9.29% 179 F 5.27% 11,654 2.80% 54 Tier 3 A 1.06% 9,803 104 1.54% 455 7 X 0.00% 0 0.22% 1 B 2.54% 249 3.08% 14 E 15.21% 1,491 13.19% 60 F 4.09% 401 4.62% 21 Zone 1 A 0.67% 1,486 10 0.00% 47 0 X 0.00% 0 0.00% 0 B 1.88% 28 2.13% 1 E 21.40% 318 6.38% 3 F 3.97% 59 6.38% 3 PTT Non-HFTD /HFRA A 0.00% 504 0 0.00% 83 0 X 0.00% 0 1.20% 1 B 0.99% 5 0.00% 0 E 2.98% 15 3.61% 3 F 0.00% 0 0.00% 0 Tier 2 A 0.00% 11,684 0 0.10% 2,041 2 X 0.00% 0 0.00% 0 B 0.39% 45 0.83% 17 E 4.73% 553 5.19% 106 F 0.00% 0 0.10% 2 Tier 3 A 0.00% 7,321 0 0.00% 956 0 X 0.00% 0 0.00% 0 B 0.18% 13 0.31% 3 E 4.66% 341 5.54% 53 F 0.00% 0 0.10% 1 Zone 1 E 5.26% 76 4 0.00% 8 0 * PG&E is using the same aerial data for 2023 that was previously provided in Table RN-PG&E-23-04-7 since it was based off 2023 actuals, per footnote (a). Note: No helicopters or planes were used for any of the aerial inspections. Only drones were used. | Henry Sweat | 2024-05-14 | 2024-05-28 | 2024-05-28 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_014.zip | 0 | N/A | 8 | 8.0 Wildfire Mitigations | 8.1.3 Asset Inspections | N/A |  | CPUC - SPD (Safety Policy Division) | 014 | 5 | 0 | Mona Hedin | Nelson Lau | System Inspections Jared Leong Josh Houston Aasha Sachdev Jeet Yogendra Raithatha | Stacie Doyle Jim Gill | Aaron Shapiro | Jason Regan | Yes | Yes | Yes |  | Yes |  | Yes |  | 2024-05-28 | [16 empty] | 5 | System Inspections Jared Leong Josh Houston Aasha Sachdev Jeet Yogendra Raithatha | Stacie Doyle Jim Gill | Mona Hedin | Nelson Lau | Aaron Shapiro | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
635 | CPUC - SPD (Safety Policy Division) | 014 | CPUC - SPD (Safety Policy Division)_014 | 4 | CPUC - SPD (Safety Policy Division)_014_Q4 | Provide all job bulletins related to ‘X’ tags. | PG&E does not have a job bulletin related to “X” tags, however, please see “WMP-Discovery2023-2025_DR_SPD_014-Q004Atch01CONF.pdf” for PG&E’s X tag Standard “Level 2 Priority X Electric Corrective (EC) Standard.” | Henry Sweat | 2024-05-14 | 2024-05-28 | 2024-05-28 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_014.zip | 1 | N/A | 8 | 8.0 Wildfire Mitigations | 8.1.3 Asset Inspections | N/A |  | CPUC - SPD (Safety Policy Division) | 014 | 4 | 0 | Mona Hedin | Nelson Lau | Arvind Simhadri | Jim Gill/Jared Leong | Aaron Shapiro | Martin Wyspianski | Yes | Yes | Yes |  | Yes | Yes | Yes |  | 2024-05-28 | [16 empty] | 4 | Arvind Simhadri | Jim Gill/Jared Leong | Mona Hedin | Nelson Lau | Aaron Shapiro | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
634 | CPUC - SPD (Safety Policy Division) | 014 | CPUC - SPD (Safety Policy Division)_014 | 3 | CPUC - SPD (Safety Policy Division)_014_Q3 | Provide the last 100 created Priority B work orders and associated inspection report. Include all photos from work orders or inspection report. a. A minimum of 50 tags must be identified during inspections. b. A minimum of 50 tags must be from the HFTD. c. If the 100 latest created tags do not meet the criteria from a) and b), supplement the request with the latest created tags for a) and b) until all requirements are met. SPD expects the maximum number of tags to be submitted to be 200. | PG&E understands this to be requesting tags related to overhead (OH) inspections. Please note, as tags can be created outside of inspections, not all tags have associated inspection reports. a. Please see “WMP-Discovery2023-2025_DR_SPD_014-Q003Atch01CONF.zip” for 50 Priority B tags that were identified during inspections and their associated inspection reports. b. Please see “WMP-Discovery2023-2025_DR_SPD_014-Q003Atch02CONF.zip” for 24 Priority B tags that were located in HFTD. As these tags were created during inspections, this attachment also contains their associated inspection reports. c. Please see “WMP-Discovery2023-2025_DR_SPD_014-Q003Atch03CONF.zip” for 26 additional Priority B tags to satisfy subpart (c) of this request. As these tags were created during inspections, this attachment also contains their associated inspection reports. | Henry Sweat | 2024-05-14 | 2024-05-31 | 2024-05-31 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_014.zip | 3 | N/A | 8 | 8.0 Wildfire Mitigations | 8.1.3 Asset Inspections | N/A |  | CPUC - SPD (Safety Policy Division) | 014 | 3 | 3 | Mona Hedin | Nelson Lau | System Inspections Ronny Montgomery | Stacie Doyle | Aaron Shapiro | Jason Regan | Yes | Yes | Yes |  | Yes |  | Yes |  | 2024-05-31 | [16 empty] | 3 | System Inspections Ronny Montgomery | Stacie Doyle | Mona Hedin | Nelson Lau | Aaron Shapiro | 3 |  |  |  |  | completed | 0 | 0 | 0 | 0
633 | CPUC - SPD (Safety Policy Division) | 014 | CPUC - SPD (Safety Policy Division)_014 | 2 | CPUC - SPD (Safety Policy Division)_014_Q2 | Provide the last 100 created Priority X work orders and associated inspection report. Include all photos from work orders or inspection report. a. A minimum of 50 tags must be identified during inspections. b. A minimum of 50 tags must be from the HFTD. c. If the 100 latest created tags do not meet the criteria from a) and b), supplement the request with the latest created tags for a) and b) until all requirements are met. SPD expects the maximum number of tags to be submitted to be 200. | PG&E understands this to be requesting tags related to overhead (OH) inspections. Please note, as tags can be created outside of inspections, not all tags have associated inspection reports. a. Please see “WMP-Discovery2023-2025_DR_SPD_014-Q002Atch01CONF.zip” for 45 Priority X tags and 44 associated inspection reports. Please note, tags 128778454 and 128778509 were created during the same inspection and are associated with inspection report “OHI_100311564_CONF.pdf” located within the referenced zip folder. b. Please see “WMP-Discovery2023-2025_DR_SPD_014-Q002Atch02CONF.zip” for 48 Priority X tags that were located in HFTD. c. Please see “WMP-Discovery2023-2025_DR_SPD_014-Q002Atch03CONF.zip” for seven additional Priority X tags to satisfy this subpart (c) of this request. | Henry Sweat | 2024-05-14 | 2024-05-31 | 2024-05-31 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_014.zip | 3 | N/A | 8 | 8.0 Wildfire Mitigations | 8.1.3 Asset Inspections | N/A |  | CPUC - SPD (Safety Policy Division) | 014 | 2 | 3 | Mona Hedin | Nelson Lau | Emily Ketcherside Lakshmi Kumar Ronny Montgomery | Stacie Doyle | Aaron Shapiro | Craig Kurtz | Yes | Yes | Yes |  | Yes |  |  |  | 2024-05-31 | [16 empty] | 2 | Emily Ketcherside Lakshmi Kumar Ronny Montgomery | Stacie Doyle | Mona Hedin | Nelson Lau | Aaron Shapiro | 3 |  |  |  |  | completed | 0 | 0 | 0 | 0
632 | CPUC - SPD (Safety Policy Division) | 014 | CPUC - SPD (Safety Policy Division)_014 | 1 | CPUC - SPD (Safety Policy Division)_014_Q1 | Provide the last 100 created Priority A tags and associated inspection report. Include all photos from tags or inspection report. a. A minimum of 50 tags must be identified during inspections. b. A minimum of 50 tags must be from the HFTD. c. If the 100 latest created tags do not meet the criteria from a) and b), supplement the request with the latest created tags for a) and b) until all requirements are met. SPD expects the maximum number of tags to be submitted to be 200. | PG&E understands this to be requesting tags related to overhead (OH) inspections. Please note, as tags can be created outside of inspections, not all tags have associated inspection reports. a. Please see “WMP-Discovery2023-2025_DR_SPD_014-Q001Atch01CONF.zip” for 41 Priority A tags and 41 associated inspection reports. b. Please see “WMP-Discovery2023-2025_DR_SPD_014-Q001Atch02CONF.zip” for 50 Priority B tags that were located in HFTD. c. Please see “WMP-Discovery2023-2025_DR_SPD_014-Q001Atch03CONF.zip” for nine additional tags to satisfy subpart (c) of this request. | Henry Sweat | 2024-05-14 | 2024-05-31 | 2024-05-31 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_014.zip | 3 | N/A | 8 | 8.0 Wildfire Mitigations | 8.1.3 Asset Inspections | N/A |  | CPUC - SPD (Safety Policy Division) | 014 | 1 | 3 | Mona Hedin | Nelson Lau | Emily Ketcherside Lakshmi Kumar Ronny Montgomery | Stacie Doyle | Aaron Shapiro | Craig Kurtz | Yes | Yes | Yes |  | Yes |  | Yes |  | 2024-05-31 | [16 empty] | 1 | Emily Ketcherside Lakshmi Kumar Ronny Montgomery | Stacie Doyle | Mona Hedin | Nelson Lau | Aaron Shapiro | 3 |  |  |  |  | completed | 0 | 0 | 0 | 0
721 | CalPA | Set WMP-54 | CalPA_Set WMP-54 | 4 | CalPA_Set WMP-54_Q4 | a) Has PG&E done any research into other devices (aside from the types referenced in questions 1-3) that can de-energize powerlines in less than 10 milliseconds for wildfire mitigation? b) If yes, please provide a brief description of the research PG&E has done, including at least the minimum following information: Research Study Name Description of Research Objectives Results Start Date End Date c) Has PG&E evaluated the potential use of these other fast-trip devices in PG&E’s system for wildfire mitigation purposes? d) If the answer to part (c) is yes, please provide a brief description of all potential use case(s) PG&E has evaluated for these other fast-trip devices. e) If the answer to part (c) is yes, state the time frame during which this evaluation took place. f) If the answer to part (c) is yes, list all benefits that PG&E has identified regarding the use of these other fast-trip devices in PG&E’s system. g) If the answer to part (c) is yes, list all downsides that PG&E has identified regarding the use of these other fast-trip devices in PG&E’s system. h) If the answer to part (c) is yes, state the estimated cost (may be a range) regarding the use of these other fast-trip devices in PG&E’s system. i) Please provide all research documents and reports that PG&E has written, commissioned, or funded on this topic. j) Does PG&E plan to perform evaluation in the future regarding the use of these other fasttrip devices in PG&E’s system for wildfire mitigation purposes? State approximately when, if yes. | a) No, we have not done research into other devices (aside from the types referenced in questions 1-3) that can de-energize powerlines in less than 10 milliseconds for wildfire mitigation. b) N/A c) No, we have not evaluated the potential use of other devices (aside from the types referenced in questions 1-3) that can de-energize powerlines in less than 10 milliseconds in our system for wildfire mitigation purposes. d) N/A e) N/A f) N/A g) N/A h) N/A i) N/A j) No, we do not plan to perform evaluation in the future regarding the use of other devices (aside from the types referenced in questions 1-3) that can de-energize powerlines in less than 10 milliseconds in our system for wildfire mitigation purposes. | Tyler Holzschuh | 2024-10-29 | 2024-11-13 | 2024-11-13 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_054.zip | 0 | N/A | N/A | N/A | N/A | N/A |  | CalPA | Set WMP-54 | 4 | 10 | Kevin Laxalt-Nomura | Nelson Lau | Franz Stadtmueller/James Tuccillo/Jason Cook/Scott Hayes/John Mead | Satvir Nagra/Wen Tu/Eric Lamoureux | Aaron Shapiro | Bryon Winget/Shay Bahramirad/Mark Quinlan | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | 2024-11-13 | [16 empty] | 4 | Franz Stadtmueller/James Tuccillo/Jason Cook/Scott Hayes/John Mead | Satvir Nagra/Wen Tu/Eric Lamoureux | Kevin Laxalt-Nomura | Nelson Lau | Aaron Shapiro | 10
720 | CalPA | Set WMP-54 | CalPA_Set WMP-54 | 3 | CalPA_Set WMP-54_Q3 | a) Has PG&E done any research into thyristor crowbars8 for wildfire mitigation?9 b) If yes, please provide a brief description of the research PG&E has done, including at least the minimum following information: Research Study Name Description of Research Objectives Results Start Date End Date c) Has PG&E evaluated the potential use of thyristor crowbars in PG&E’s system for wildfire mitigation purposes? d) If the answer to part (c) is yes, please provide a brief description of all potential use case(s) PG&E has evaluated for thyristor crowbars. e) If the answer to part (c) is yes, state the time frame during which this evaluation took place. f) If the answer to part (c) is yes, list all benefits that PG&E has identified regarding the use of thyristor crowbars in PG&E’s system. g) If the answer to part (c) is yes, list all downsides that PG&E has identified regarding the use of thyristor crowbars in PG&E’s system. h) If the answer to part (c) is yes, state the estimated cost (may be a range) regarding the use of thyristor crowbars in PG&E’s system. i) Please provide all research documents and reports that PG&E has written, commissioned, or funded on this topic. j) Does PG&E plan to perform evaluation in the future regarding the use of thyristor crowbars in PG&E’s system for wildfire mitigation purposes? State approximately when, if yes. | a) No, we have not done research into thyristor crowbars for wildfire mitigation. b) Not applicable, please see the response to subpart (a) above. c) No, we have not evaluated the potential use of thyristor crowbars in our system for wildfire mitigation purposes. d) Not applicable, please see the response to subpart (c) above. e) Not applicable, please see the response to subpart (c) above. f) Not applicable, please see the response to subpart (c) above. g) Not applicable, please see the response to subpart (c) above. h) Not applicable, please see the response to subpart (c) above. i) Not applicable, please see the response to subpart (c) above. j) No, we do not plan to perform evaluation in the future regarding the use of thyristor crowbars in our system for wildfire mitigation purposes. | Tyler Holzschuh | 2024-10-29 | 2024-11-13 | 2024-11-13 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_054.zip | 0 | N/A | N/A | N/A | N/A | N/A |  | CalPA | Set WMP-54 | 3 | 10 | Kevin Laxalt-Nomura | Nelson Lau | Franz Stadtmueller/James Tuccillo/Jason Cook/Scott Hayes/John Mead | Satvir Nagra/Wen Tu/Eric Lamoureux | Aaron Shapiro | Bryon Winget/Shay Bahramirad/Mark Quinlan | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | 2024-11-13 | [16 empty] | 3 | Franz Stadtmueller/James Tuccillo/Jason Cook/Scott Hayes/John Mead | Satvir Nagra/Wen Tu/Eric Lamoureux | Kevin Laxalt-Nomura | Nelson Lau | Aaron Shapiro | 10
719 | CalPA | Set WMP-54 | CalPA_Set WMP-54 | 2 | CalPA_Set WMP-54_Q2 | a) Has PG&E done any research into semiconductor assisted circuit breakers6 for wildfire mitigation?7 b) If yes, please provide a brief description of the research PG&E has done, including at least the minimum following information: Research Study Name Description of Research Objectives Results Start Date End Date c) Has PG&E evaluated the potential use of semiconductor assisted circuit breakers in PG&E’s system for wildfire mitigation purposes? d) If the answer to part (c) is yes, please provide a brief description of all potential use case(s) PG&E has evaluated for semiconductor assisted circuit breakers. e) If the answer to part (c) is yes, state the time frame during which this evaluation took place. f) If the answer to part (c) is yes, list all benefits that PG&E has identified regarding the use of semiconductor assisted circuit breakers in PG&E’s system. g) If the answer to part (c) is yes, list all downsides that PG&E has identified regarding the use of semiconductor assisted circuit breakers in PG&E’s system. h) If the answer to part (c) is yes, state the estimated cost (may be a range) regarding the use of semiconductor assisted circuit breakers in PG&E’s system. i) Please provide all research documents and reports that PG&E has written, commissioned, or funded on this topic. j) Does PG&E plan to perform evaluation in the future regarding the use of semiconductor assisted circuit breakers in PG&E’s system for wildfire mitigation purposes? State approximately when, if yes. | a) No, we have not done research into semiconductor assisted circuit breakers for wildfire mitigation. b) Not applicable, please see the response to subpart (a) above. c) Yes, we have evaluated the potential use of semiconductor assisted circuit breakers limiters in our system for wildfire mitigation purposes. d) In approximately 2019-2020, we evaluated a proposal from SciBreak to develop a distribution class circuit breaker that could interrupt fault current in about three milliseconds using power electronics. e) This evaluation took place in approximately 2019-2020. f) The primary benefit identified was the potential to reduce fault energy by reducing fault clearing times. g) We determined that the proposed technology was novel and largely unproven. SciBreak did not offer a finished product and was not proposing circuit breakers that would meet many of the ANSI/IEEE standards for medium voltage circuit breakers that are industry standard. h) We do not have an estimated cost regarding the use of semiconductor assisted circuit breakers in our system. i) We are not aware of any research documents or reports that we have written, commissioned, or funded on this topic. j) No, we do not plan to perform evaluation in the future regarding the use of semiconductor assisted circuit breakers limiters in our system for wildfire mitigation purposes. | Tyler Holzschuh | 2024-10-29 | 2024-11-13 | 2024-11-13 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_054.zip | 0 | N/A | N/A | N/A | N/A | N/A |  | CalPA | Set WMP-54 | 2 | 10 | Kevin Laxalt-Nomura | Nelson Lau | Franz Stadtmueller/James Tuccillo/Jason Cook/Scott Hayes/John Mead | Satvir Nagra/Wen Tu/Eric Lamoureux | Aaron Shapiro | Bryon Winget/Shay Bahramirad/Mark Quinlan | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | 2024-11-13 | [16 empty] | 2 | #REF! | #REF! | Kevin Laxalt-Nomura | #REF! | #REF! | 10
718 | CalPA | Set WMP-54 | CalPA_Set WMP-54 | 1 | CalPA_Set WMP-54_Q1 | a) Has PG&E done any research into Is limiters4 for wildfire mitigation?5 b) If yes, please provide a brief description of the research PG&E has done, including at least the minimum following information: Research Study Name Description of Research Objectives Results Start Date End Date c) Has PG&E evaluated the potential use of Is limiters in PG&E’s system for wildfire mitigation purposes? d) If the answer to part (c) is yes, please provide a brief description of all potential use case(s) PG&E has evaluated for Is limiters. e) If the answer to part (c) is yes, state the time frame during which this evaluation took place. f) If the answer to part (c) is yes, list all benefits that PG&E has identified regarding the use of Is limiters in PG&E’s system. g) If the answer to part (c) is yes, list all downsides that PG&E has identified regarding the use of Is limiters in PG&E’s system. h) If the answer to part (c) is yes, state the estimated cost (may be a range) regarding the use of Is limiters in PG&E’s system. i) Please provide all research documents and reports that PG&E has written, commissioned, or funded on this topic. j) Does PG&E plan to perform evaluation in the future regarding the use of Is limiters in PG&E’s system for wildfire mitigation purposes? State approximately when, if yes. | a) No, we have not done research into Is limiters for wildfire mitigation. b) Not applicable, please see the response to subpart (a) above. c) No, we have not evaluated the potential use of Is limiters in our system for wildfire mitigation purposes. d) Not applicable, please see the response to subpart (c) above. e) Not applicable, please see the response to subpart (c) above. f) Not applicable, please see the response to subpart (c) above. g) Not applicable, please see the response to subpart (c) above. h) Not applicable, please see the response to subpart (c) above. i) Not applicable, please see the response to subpart (c) above. j) No, we do not plan to perform evaluation in the future regarding the use of Is limiters in our system for wildfire mitigation purposes. | Tyler Holzschuh | 2024-10-29 | 2024-11-13 | 2024-11-13 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_054.zip | 0 | N/A | N/A | N/A | N/A | N/A |  | CalPA | Set WMP-54 | 1 | 10 | Kevin Laxalt-Nomura | Nelson Lau | Franz Stadtmueller/James Tuccillo/Jason Cook/Scott Hayes/John Mead | Satvir Nagra/Wen Tu/Eric Lamoureux | Aaron Shapiro | Bryon Winget/Shay Bahramirad/Mark Quinlan | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | 2024-11-13 | [16 empty] | 1 | Franz Stadtmueller/James Tuccillo/Jason Cook/Scott Hayes/John Mead | Satvir Nagra/Wen Tu/Eric Lamoureux | Kevin Laxalt-Nomura | Nelson Lau | Aaron Shapiro | 10
692 | CalPA | Set WMP-52 | CalPA_Set WMP-52 | 10 | CalPA_Set WMP-52_Q10 | The following questions relate to your WMP Quarterly Data Report for Q2 of 2024, Table 13, received on August 2, 2024, which reports asset-related corrective notifications on electric circuits that were open at the end of the quarter. This follow-up data request seeks information for ALL open work orders in your territory, not only open work orders in High Fire Threat Districts. In Table 13 of your 2024 Q2 QDR, there are 139 X tags (which require completion within 7 days) with an average of 29 days past due. i. Please explain what delay factors PG&E has encountered in remediation of X tags. ii. How does PG&E intend to address delays in completing X tags? iii. What has been PG&E’s average completion time for X tags in the first half of 2024? In other words, for all X tags closed in the first half of 2024, what was the average number of days open? | PG&E disagrees with the statement that there are 139 X tags with an average of 29 days past due in Table 13 of the 2024 Quarter 2 Quarterly Data Report (QDR). Please see Columns E-F of attachment “WMP-Discovery2023-2025_DR_CalAdvocates_052- Q010Atch01.xlsx” which shows that of the 139 X Tags referenced, PG&E completed work on an average of three days. i. Factors that can contribute to potential delays in completing tag work can include work that starts on day seven and is not able to be completed until day eight, a lack of resources when critical emergencies need to be prioritized, and a syncing issue that was identified in June 2024 between iPads (used to create tags) and SAP (PG&E’s system of record). This issue occurred when users were in low network mode, no network, or airplane mode, and created a delay in seeing tags needing to be completed. ii. PG&E underwent a syncing enhancement update in August 2024 which now requires users to resolve syncing issue before proceeding with other work. iii. In the first half of 2024, PG&E has been able to average completing work on X tags in approximately 2.4 days. | Benjamin Katzenberg | 2024-08-19 | 2024-09-06 | 2024-09-06 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_052.zip | 1 | N/A | QDR | N/A | N/A | N/A |  | CalPA | Set WMP-52 | 10 | 3 | Mona Hedin | Nelson Lau | Matthew Horowitz Andrea Morales Mina Amir John Jones | Brittany Beston | Aaron Shapiro | Martin Wyspianski | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | 2024-09-06 | [16 empty] | 10 | Matthew Horowitz Andrea Morales Mina Amir John Jones | Brittany Beston | Mona Hedin | Nelson Lau | Aaron Shapiro | 3 |  |  |  |  | completed | 0 | 0 | 0 | 0
691 | CalPA | Set WMP-52 | CalPA_Set WMP-52 | 9 | CalPA_Set WMP-52_Q9 | The following questions relate to your WMP Quarterly Data Report for Q2 of 2024, Table 13, received on August 2, 2024, which reports asset-related corrective notifications on electric circuits that were open at the end of the quarter. This follow-up data request seeks information for ALL open work orders in your territory, not only open work orders in High Fire Threat Districts. Do you use performance metrics to determine the effectiveness of your bundling approach to remediating open work orders (as described in Advice Letter 7167-E-A)? i. If yes, please provide a list of the performance metrics including a brief description and how each metric is calculated/determined. ii. If no, please explain how you validate the effectiveness of your bundling approach to remediation of open work orders. | i. Yes, PG&E uses performance metrics to determine the effectiveness of the bundling approach to remediate open work orders as described in the referenced Advice Letter. Please see below for the requested description for each metric. Bundling Percentage - The percent of completed tags that were bundled through Operational Bundling. Metric Calculation/Description: The percent of completed tag jobs that were bundled with other work. A notification is considered bundled if it was completed on the same day as another job in the same isolation zone OR was completed on the same isolation zone during the duration of another longer term job. Bundled Unit Cost Reduction – The percent reduction in unit cost of the bundled work compared to the 2023 Unit Cost. Metric Calculation/Description: The percent difference between an operationally bundled tag's or Mega Bundle tag’s unit cost and the 2023 unit cost. For operational bundling, this is measured for internally resourced jobs. For Mega Bundle's frozen scope of work, this is measured through a mix of internally resourced work and work contracted through a competitive lowest cost bidding process. Mega Bundle Completion - The percent completion of 2024 Mega Bundle Scope. Metric Calculation/Definition: The number of completed tags in the Mega Bundle scope divided by the number of total tags within the Mega Bundle scope. Please note, The Mega Bundle Scope includes Circuit Projects which combine approximately 10,000 individual scopes of work to be executed collectively as projects by circuit and isolation zone. Through these bundled scopes, it allows for effective planning to increase productivity, reduce truck rolls, minimize planned customer outages, and achieve cost-effective negotiated contract pricing. ii. Not applicable. Please see response to subpart (i). | Benjamin Katzenberg | 2024-08-19 | 2024-09-06 | 2024-09-06 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_052.zip | 0 | N/A | QDR | N/A | N/A | N/A |  | CalPA | Set WMP-52 | 9 | 2 | Mona Hedin | Nelson Lau | Matthew Horowitz Andrea Morales Mina Amir John Jones | Brittany Beston | Aaron Shapiro | Martin Wyspianski | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | 2024-09-06 | [16 empty] | 9 | Matthew Horowitz Andrea Morales Mina Amir John Jones | Brittany Beston | Mona Hedin | Nelson Lau | Aaron Shapiro | 2 |  |  |  |  | completed | 0 | 0 | 0 | 0
690 | CalPA | Set WMP-52 | CalPA_Set WMP-52 | 8 | CalPA_Set WMP-52_Q8 | The following questions relate to your WMP Quarterly Data Report for Q2 of 2024, Table 13, received on August 2, 2024, which reports asset-related corrective notifications on electric circuits that were open at the end of the quarter. This follow-up data request seeks information for ALL open work orders in your territory, not only open work orders in High Fire Threat Districts. Do you use performance metrics to determine the effectiveness of the changes applied to your distribution infrastructure inspection procedure? i. If yes, please provide a list of the performance metrics including a brief description and how each metric is calculated/determined. ii. If no, please explain how you validate the effectiveness of changes to your inspection process. | PG&E is developing performance metrics to measure the effectiveness of the changes applied to the distribution infrastructure inspection procedure. PG&E is evaluating multiple strategies, which include reviewing the volume of locations that have been escalated, in addition to reviewing the volume of locations that failed in the field, prior to notification execution. As the inspection procedure was recently updated in 2024, PG&E does not plan to finalize performance metrics until at least 2025, to allow for a minimum of one full year of data to be collected and analyzed. | Benjamin Katzenberg | 2024-08-19 | 2024-09-06 | 2024-09-06 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_052.zip | 0 | N/A | QDR | N/A | N/A | N/A |  | CalPA | Set WMP-52 | 8 | 2 | Mona Hedin | Nelson Lau | Matthew Horowitz Andrea Morales Mina Amir John Jones | Brittany Beston | Aaron Shapiro | Martin Wyspianski | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | 2024-09-06 | [16 empty] | 8 | Matthew Horowitz Andrea Morales Mina Amir John Jones | Brittany Beston | Mona Hedin | Nelson Lau | Aaron Shapiro | 2 |  |  |  |  | completed | 0 | 0 | 0 | 0
689 | CalPA | Set WMP-52 | CalPA_Set WMP-52 | 7 | CalPA_Set WMP-52_Q7 | The following questions relate to your WMP Quarterly Data Report for Q2 of 2024, Table 13, received on August 2, 2024, which reports asset-related corrective notifications on electric circuits that were open at the end of the quarter. This follow-up data request seeks information for ALL open work orders in your territory, not only open work orders in High Fire Threat Districts. Please provide the most recent version of your distribution infrastructure inspection checklist. | PG&E does not have a PDF or Excel version of the distribution checklist to provide as the checklist is embedded in an electronic application. As such, a physical copy of the checklist is unavailable, however, please see “WMP-Discovery2023- 2025_DR_CalAdvocates_052-Q007Atch01CONF.pdf” for a copy of the presentation provided to inspectors which outlines the questions and conditions of the current checklist as well as guidance in completing accurately. The specific steps included in the checklist start on page seven of the attachment. | Benjamin Katzenberg | 2024-08-19 | 2024-09-06 | 2024-09-06 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_052.zip | 1 | N/A | QDR | N/A | N/A | N/A |  | CalPA | Set WMP-52 | 7 | 0 | Mona Hedin | Nelson Lau | Matthew Horowitz Andrea Morales Mina Amir John Jones | Brittany Beston | Aaron Shapiro | Martin Wyspianski | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | 2024-09-06 | [16 empty] | 7 | Matthew Horowitz Andrea Morales Mina Amir John Jones | Brittany Beston | Mona Hedin | Nelson Lau | Aaron Shapiro | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
688 | CalPA | Set WMP-52 | CalPA_Set WMP-52 | 6 | CalPA_Set WMP-52_Q6 | The following questions relate to your WMP Quarterly Data Report for Q2 of 2024, Table 13, received on August 2, 2024, which reports asset-related corrective notifications on electric circuits that were open at the end of the quarter. This follow-up data request seeks information for ALL open work orders in your territory, not only open work orders in High Fire Threat Districts. Please provide a list of work orders closed in Q1 and Q2 of 2024 using the format and including details consistent with Table 13 of your 2024 Q2 QDR. | Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_052- Q006Atch01.xlsx” for the requested information. The following notes provide additional context on data for Transmission assets: • Some notifications, including the three closed notifications that were created before 2019, were reopened temporarily for administrative reasons, such as delinking from order numbers or making other minor corrections to notification information, and then closed again in 2024. These notifications received an SAP completion date based on the date in 2024 when they were closed following the administrative changes, and not the original closure date. | Benjamin Katzenberg | 2024-08-19 | 2024-09-06 | 2024-09-06 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_052.zip | 1 | N/A | QDR | N/A | N/A | N/A |  | CalPA | Set WMP-52 | 6 | 0 | Mona Hedin | Nelson Lau | Matthew Horowitz Andrea Morales Mina Amir John Jones | Brittany Beston | Aaron Shapiro | Martin Wyspianski | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | 2024-09-06 | [16 empty] | 6 | Matthew Horowitz Andrea Morales Mina Amir John Jones | Brittany Beston | Mona Hedin | Nelson Lau | Aaron Shapiro | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
687 | CalPA | Set WMP-52 | CalPA_Set WMP-52 | 5 | CalPA_Set WMP-52_Q5 | The following questions relate to your WMP Quarterly Data Report for Q2 of 2024, Table 13, received on August 2, 2024, which reports asset-related corrective notifications on electric circuits that were open at the end of the quarter. This follow-up data request seeks information for ALL open work orders in your territory, not only open work orders in High Fire Threat Districts. Please provide an excel spreadsheet listing work orders that were open as of May 31, 2018. If possible, provide this list in a format and including details consistent with Table 13 of your 2024 Q2 QDR. If some of the information included in Table 13 is not available, please include: i. Work Order Identifier ii. Priority of the original notification, using internal priority level codes in use at the time iii. Date on which the work order was created iv. Date on which the work order was closed. | Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_052- Q005Atch01.xlsx” for the requested information. | Benjamin Katzenberg | 2024-08-19 | 2024-09-06 | 2024-09-06 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_052.zip | 1 | N/A | QDR | N/A | N/A | N/A |  | CalPA | Set WMP-52 | 5 | 4 | Mona Hedin | Nelson Lau | Matthew Horowitz Andrea Morales Mina Amir John Jones | Brittany Beston | Aaron Shapiro | Martin Wyspianski | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | 2024-09-06 | [16 empty] | 5 | Matthew Horowitz Andrea Morales Mina Amir John Jones | Brittany Beston | Mona Hedin | Nelson Lau | Aaron Shapiro | 4 |  |  |  |  | completed | 0 | 0 | 0 | 0
686 | CalPA | Set WMP-52 | CalPA_Set WMP-52 | 4 | CalPA_Set WMP-52_Q4 | The following questions relate to your WMP Quarterly Data Report for Q2 of 2024, Table 13, received on August 2, 2024, which reports asset-related corrective notifications on electric circuits that were open at the end of the quarter. This follow-up data request seeks information for ALL open work orders in your territory, not only open work orders in High Fire Threat Districts. Please provide an excel spreadsheet listing open work orders as of July 31, 2024, that were first created: i. Between May 9, 2016 and May 31, 2018. ii. Prior to May 9, 2016. | Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_052- Q004Atch01.xlsx” for the requested information. The following notes provide additional context for data related to Transmission assets: • Notifications 126761436 and 128202924 were created in 2023 and 2024, respectively, from distribution Electric Corrective (EC) notifications and were assigned a notification date (date when the condition was found in the field) from the original distribution EC. • Notification 114337373 was created for broken glass insulators and originally was closed in 2018 after repairs to the insulators. It was reopened in 2023 due to chipped/cracked insulators with a note stating that “insulators are considered as the switch components and cannot be change[d] out without the switch replacement." | Benjamin Katzenberg | 2024-08-19 | 2024-09-06 | 2024-09-06 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_052.zip | 1 | N/A | QDR | N/A | N/A | N/A |  | CalPA | Set WMP-52 | 4 | 2 | Mona Hedin | Nelson Lau | Matthew Horowitz Andrea Morales Mina Amir John Jones | Brittany Beston | Aaron Shapiro | Martin Wyspianski | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | 2024-09-06 | [16 empty] | 4 | Matthew Horowitz Andrea Morales Mina Amir John Jones | Brittany Beston | Mona Hedin | Nelson Lau | Aaron Shapiro | 2 |  |  |  |  | completed | 0 | 0 | 0 | 0
685 | CalPA | Set WMP-52 | CalPA_Set WMP-52 | 3 | CalPA_Set WMP-52_Q3 | The following questions relate to your WMP Quarterly Data Report for Q2 of 2024, Table 13, received on August 2, 2024, which reports asset-related corrective notifications on electric circuits that were open at the end of the quarter. This follow-up data request seeks information for ALL open work orders in your territory, not only open work orders in High Fire Threat Districts. Please provide any internal categories or codes you use to prioritize asset-related corrective notifications and work orders. For each internal category, please provide: i. your working definition; and ii. the General Order 95, Rule 18 priority level to which it corresponds. | The table below shows PG&E’s internal priority levels and timelines, the corresponding General Order (GO) 95, Rule 18 levels and required timelines, and a description of the priority levels. | Benjamin Katzenberg | 2024-08-19 | 2024-09-06 | 2024-09-06 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_052.zip | 0 | N/A | QDR | N/A | N/A | N/A |  | CalPA | Set WMP-52 | 3 | 2 | Mona Hedin | Nelson Lau | Matthew Horowitz Andrea Morales Mina Amir John Jones | Brittany Beston | Aaron Shapiro | Martin Wyspianski | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | 2024-09-06 | [16 empty] | 3 | Matthew Horowitz Andrea Morales Mina Amir John Jones | Brittany Beston | Mona Hedin | Nelson Lau | Aaron Shapiro | 2 |  |  |  |  | completed | 0 | 0 | 0 | 0
684 | CalPA | Set WMP-52 | CalPA_Set WMP-52 | 2 | CalPA_Set WMP-52_Q2 | The following questions relate to your WMP Quarterly Data Report for Q2 of 2024, Table 13, received on August 2, 2024, which reports asset-related corrective notifications on electric circuits that were open at the end of the quarter. This follow-up data request seeks information for ALL open work orders in your territory, not only open work orders in High Fire Threat Districts. Please provide a list of structures, assets, and facilities that may qualify as “other” in column b (“Equipment type”) of Table 13. | Transmission equipment included under “other” in Table 13, Column B includes the “object” types (see the response to Question No. 001, subpart vi) associated with the assets/components below: • Markers/signs • Tower foundations (including bay water towers) • Hardware • Shield wire/optical ground wire • Animal/raptor guards • Dampers • Spacers • Jumpers • FAA lighting and batteries • Anti-climbing guards • Tie wire • Cathodic protection • Clearance infractions • Emergency. Distribution equipment included under “other” in Table 13, Column B includes the “object” types (see the response to Question No. 001, subpart vi) associated with the assets/components below: • High Sign • Tree/Vine • Marking • Hardware/Framing • Molding • Ground • OH Facility • Pole Step • Bird Protection • Guy Marker. | Benjamin Katzenberg | 2024-08-19 | 2024-09-06 | 2024-09-06 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_052.zip | 0 | N/A | QDR | N/A | N/A | N/A |  | CalPA | Set WMP-52 | 2 | 0 | Mona Hedin | Nelson Lau | Matthew Horowitz Andrea Morales Mina Amir John Jones | Brittany Beston | Aaron Shapiro | Martin Wyspianski | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | 2024-09-06 | [16 empty] | 2 | Matthew Horowitz Andrea Morales Mina Amir John Jones | Brittany Beston | Mona Hedin | Nelson Lau | Aaron Shapiro | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
683 | CalPA | Set WMP-52 | CalPA_Set WMP-52 | 1 | CalPA_Set WMP-52_Q1 | The following questions relate to your WMP Quarterly Data Report for Q2 of 2024, Table 13, received on August 2, 2024, which reports asset-related corrective notifications on electric circuits that were open at the end of the quarter. This follow-up data request seeks information for ALL open work orders in your territory, not only open work orders in High Fire Threat Districts. Please add the following information to each row of Table 13 in separate columns: i. Name of the associated circuit ii. ID number of the associated circuit iii. Geographic latitude in decimal degrees, truncated to seven decimal places iv. Geographic longitude in decimal degrees, truncated to seven decimal places v. Priority of the original notification, using PG&E’s internal priority level codes vi. Object/damage code or other internal description of defect vii. Poses ignition risk (Y/N) viii. General Order 95 Exception Granted (Y/N) ix. Circuit Segment Identification Number x. Past Due as of July 31, 2024 (Y/N) | Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_052- Q001Atch01.xlsx” for the requested information. The following explanatory notes provide context for the data: • Column K in Table 13 (Column h. in the attachment) in the QDR provides the original priority using PG&E’s internal priority level. Column Q (responsive to subpart v) in the attached dataset provides the current priority using PG&E’s internal priority level. Conditions that pose an ignition risk (responsive to subpart vii) within HFTD or PG&E High Fire Risk Areas (HFRA) are evaluated using a combination of object/damage codes and individual review during gatekeeping by the Centralized Inspection Review Team (CIRT). Since the same object/damage codes can contain both ignition and non-ignition risk conditions and non-HFTD non-HFRA notifications are not individually reviewed for ignition risk, ignition risk is only labeled for notifications within HFTD or HFRA. • PG&E has not requested from the Commission, or been granted, formal exceptions for maintenance tags under General Order (GO) 95, Rule 18. However, PG&E has internally identified maintenance tags that have been extended under reasonable circumstances including those identified under GO 95, Rule 18, which have been noted in Column U (responsive to subpart viii). • Notifications are not associated with circuit segments. The Functional Location has been provided for the Circuit Segment Identification Number, located in Column V of the attachment. | Benjamin Katzenberg | 2024-08-19 | 2024-09-06 | 2024-09-06 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_052.zip | 1 | N/A | QDR | N/A | N/A | N/A |  | CalPA | Set WMP-52 | 1 | 10 | Mona Hedin | Nelson Lau | Matthew Horowitz Andrea Morales Mina Amir John Jones | Brittany Beston | Aaron Shapiro | Martin Wyspianski | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | 2024-09-06 | [16 empty] | 1 | Matthew Horowitz Andrea Morales Mina Amir John Jones | Brittany Beston | Mona Hedin | Nelson Lau | Aaron Shapiro | 10 |  |  |  |  | completed | 0 | 0 | 0 | 0
681 | CalPA | Set WMP-51 | CalPA_Set WMP-51 | 1 | CalPA_Set WMP-51_Q1 | On page 410 of PG&E’s 2023-2025 WMP R6, Table PG&E-8.1.2-3 is presented as the following (referred to herein as the July 5 table): IMAGE On April 5, 2024, in response to data request CalAdvocates-PGE-2025WMP-03, question 11 (CalAdvocates_039-Q011), PG&E provided the following version of Table PG&E-8.1.2-3 (referred to herein as the April 5 table): IMAGE State the basis for why PG&E made each of the following changes to Table PG&E-8.1.2-3 in the three months from April 5, 2024 to July 5, 2024: a) In 2023, the total number of miles in the “Fire Rebuild” category is 109 miles in the April 5 table, but 111 miles in the July 5 table. b) In 2024, the total number of miles in the “Top 20% Risk-Ranked Circuit Segments” category is 204 miles in the April 5 table, but 180 miles in the July 5 table. c) In 2024, the total number of miles in the “Fire Rebuild” category is 49 miles in the April 5 table, but 55 miles in the July 5 table. d) In 2024, the total number of miles in the “PSPS” category is 33 miles in the April 5 table, but 29 miles in the July 5 table. e) In 2024, the total number of miles in the “Other UG Programs” category is 2 miles in the April 5 table, but 0 miles in the July 5 table. f) In the two-year period from 2025 to 2026, the total number of miles in the “Top 20% Risk-Ranked Circuit Segments” category is 795 miles in the April 5 table, but 711 miles in the July 5 table. g) In the two-year period from 2025 to 2026, the total number of miles in the “Fire Rebuild” category is 44 miles in the April 5 table, but 41 miles in the July 5 table. h) In the two-year period from 2025 to 2026, the total number of miles in the “PSPS” category is 2 miles in the April 5 table, but 7 miles in the July 5 table. i) In the two-year period from 2025 to 2026, the total number of miles in the “UG System Hardening” category is 4 miles in the April 5 table, but 12 miles in the July 5 table. j) In the two-year period from 2025 to 2026, the total number of miles in the “Other UG Programs” category is 2 miles in the April 5 table, but 5 miles in the July 5 table. | As described in our WMP Section 8.1.2.2, PG&E’s undergrounding workplan evolves overtime. Project schedules can change because of project dependencies, such as permitting and easement delays. Further, the workplan evolved to account for the 2023 GRC Decision. Below describes the changes specifically made between when the two workplans were submitted between April 5 and July 5. a) The July 5 table incorporates miles from Greenville Community Rebuild projects. These projects were inadvertently missing from all versions of the summary table prior to the July 5 version. b) This change was driven by seven projects shifting schedules from 2024 to 2025 and one from 2024 to 2026. c) As with subpart (a), the July 5 table incorporates miles from Greenville Community Rebuild projects. These projects were inadvertently missing from all versions of the summary table prior to the July 5 version. d) This change was driven by two projects shifting schedules from 2024 to 2025. e) This change was driven by one project shifting schedule from 2024 to 2025. f) The primary driver in the reduction of miles for 2025-2026 is the need to align the workplan to the 2023-2026 GRC mileage targets. These changes include removing existing projects and adding/scoping to drive to the GRC risk reduction targets. g) This change was driven by Butte Rebuild project schedule changes between 2024 and 2025 (one project moved from 2024 to 2025, another from 2025 to 2024), resulting in a net impact of increased miles in 2024 and reduced miles in 2025-2026. h) This change was driven by the same two projects described in subpart (d), plus one project being removed from the workplan. i) One four-mile project from the April 5 table has been removed from the July 5 table, and 12 miles from eight projects were added. Of the 12 miles added, 11 miles are in the Top 20% Risk category and will be moved accordingly once risk reduction calculations have been updated in our system of record for the associated projects. j) This change was driven by the same project described in subpart (e), as well as a single new project that was missing risk rank data at the time of the July 5 report creation. This will be updated in our system of record and will be included in future iterations of this table. | Holly Wehrman | 2024-07-09 | 2024-07-12 | 2024-07-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_051.zip | 0 | N/A | 8 | Section 8.1.2 - Grid Design and System Hardening | 8.1.2.11.2 Other grid topology improvements to mitigate or reduce PSPS events - Distribution | N/A |  | CalPA | Set WMP-51 | 1 | 10 | Mona Hedin | Saritha Basani | Brad Koelling/Merih Tekeste/PSPS/Risk/UG (?) | Jim Gill/Satvir Nagra/Shawn Holder/Megan Ardell (?) | Kenny Lee | Martin Wyspianski/Mark Quinlan (?) | Yes | Yes | Yes |  | Yes | Yes | Yes |  | 2024-07-12 | [16 empty] | 1 | Brad Koelling/Merih Tekeste/PSPS/Risk/UG (?) | Jim Gill/Satvir Nagra/Shawn Holder/Megan Ardell (?) | Mona Hedin | Saritha Basani | Kenny Lee | 10 |  |  |  |  | completed | 0 | 0 | 0 | 0
671 | CalPA | Set WMP-50 | CalPA_Set WMP-50 | 1 | CalPA_Set WMP-50_Q1 | The Filsinger Energy Partners’ PG&E Independent Safety Monitor Status Update Report, October 6, 2023 (ISM Report 3) stated that there were 1,400 action items in the Multiple Outage Review and Evaluation (MORE) for 2022. However, in 2023 WMP data request CalAdvocates-PGE- 2023WMP-34, Question 1, there are apparently 900 action items listed. Please explain the discrepancy. | The ISM Report 3 included items that were not actual action items to be performed on the circuit, but rather captured the action item of the review by the MORE team. The referenced CalAdvocate data set did not include the review as an action item. The discrepancy is due in large part to the removal of the review action item called “MORE Assessment.” A MORE Assessment was completed for each circuit that reached trigger level criteria at the time, which resulted in action items such as a settings review, planned work opportunities, etc. As such, these action items were removed in order to provide a cleaner data set as a part of the CalAdvocates data request response. Additionally in 2024, the MORE process has fully migrated from a manual spreadsheet tracking system to a digital platform to better keep records and provide transparency across the organization for action item tracking. | Amanda Asadi | 2024-06-24 | 2024-07-09 | 2024-07-09 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_050.zip | 0 | N/A | 8.1.8.1.1 | Grid Operations and Procedures | Protective Equipment and Device Settings | N/A |  | CalPA | Set WMP-50 | 1 | 0 | Mona Hedin | Saritha Basani | Katherine Hee/Tim Bedford | Eric Lamoureux | Kenny Lee | Mark Quinlan | Yes |  | Yes | Yes | Yes | Yes |  |  | 2024-07-09 | [16 empty] | 1 | Katherine Hee/Tim Bedford | Eric Lamoureux | Mona Hedin | Saritha Basani | Kenny Lee | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
597 | CalPA | Set WMP-46 | CalPA_Set WMP-46 | 10 | CalPA_Set WMP-46_Q10 | In response to data request CalAdvocates-PGE-2025WMP-03, question 1, PG&E provided attachment “WMP-Discovery2023-2025_DR_CalAdvocates_039-Q006Atch01.xlsx,” which relates to asset inspections in 2023. Line 16 indicates that, out of 2820 distribution intrusive pole inspections reviewed by desktop QC, 1672 failed QC review. Line 17 indicates that, out of 1491 distribution intrusive pole inspections reviewed by field QC, 1021 failed QC review. a) Has PG&E made any changes to its intrusive inspection practices for distribution pole inspections as a result of the high QC failure rates? b) If the answer to part (a) is yes, describe the changes PG&E has made. c) Provide any relevant procedures, specifications, job aids, bulletins, or other documentation to support your answer to part (b). d) If the answer to part (a) is no, state why not. e) Has PG&E made any changes to its QC review process for intrusive inspections of distribution poles as a result of the high QC failure rates? f) If the answer to part (e) is yes, describe the changes PG&E has made. g) Provide any relevant procedures, specifications, job aids, bulletins, or other documentation to support your answer to part (f). h) If the answer to part (e) is no, state why not. i) Please describe any other actions PG&E took as a result of the high QC failure rates in 2023 noted above. j) What were the primary reasons for distribution intrusive pole inspections to fail desktop QC review in 2023? k) What were the primary reasons for distribution intrusive pole inspections to fail field QC review in 2023? | Please see the responses to Question No. 009, subparts (a) to (k), which also apply to this request and provide the information sought. | Holly Wehrman | 2024-04-17 | 2024-04-25 | 2024-04-25 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_046.zip | 0 | N/A | 8.1.6 | Section 8.1.6 - Quality Assurance and Quality Control | 8.1.6.1 Quality Assurance (QA) | N/A |  | CalPA | Set WMP-46 | 10 | 11 | Mona Hedin | Nelson Lau | Teresa Tusch | Eric Thomas | Aaron Shapiro | Stephen Simon | Yes |  | Yes |  | Yes | Yes |  |  | 2024-04-25 | [16 empty] | 10 | Teresa Tusch | Eric Thomas | Mona Hedin | Nelson Lau | Aaron Shapiro | 11 |  |  |  |  | completed | 0 | 0 | 0 | 0
596 | CalPA | Set WMP-46 | CalPA_Set WMP-46 | 9 | CalPA_Set WMP-46_Q9 | In response to data request CalAdvocates-PGE-2025WMP-03, question 1, PG&E provided attachment “WMP-Discovery2023-2025_DR_CalAdvocates_039-Q006Atch01.xlsx,” which relates to asset inspections in 2023. Line 8 indicates that, out of 133 transmission intrusive pole inspections reviewed by desktop QC, 108 failed QC review. Line 9 indicates that, out of 149 transmission intrusive pole inspections reviewed by field QC, 134 failed QC review. a) Has PG&E made any changes to its intrusive inspection practices for transmission pole inspections as a result of the high QC failure rates? b) If the answer to part (a) is yes, describe the changes PG&E has made. c) Provide any relevant procedures, specifications, job aids, bulletins, or other documentation to support your answer to part (b). d) If the answer to part (a) is no, state why not. e) Has PG&E made any changes to its QC review process for intrusive inspections of transmission poles as a result of the high QC failure rates? f) If the answer to part (e) is yes, describe the changes PG&E has made. g) Provide any relevant procedures, specifications, job aids, bulletins, or other documentation to support your answer to part (f). h) If the answer to part (e) is no, state why not. i) Please describe any other actions PG&E took as a result of the high QC failure rates in 2023 noted above. j) What were the primary reasons for transmission intrusive pole inspections to fail desktop QC review in 2023? k) What were the primary reasons for transmission intrusive pole inspections to fail field QC review in 2023? | a) Yes, PG&E is in the process of updating Utility Procedure TD-2325P-01, which provides instruction for intrusively inspective, testing, restoring, reinforcing, treating, and reusing wood poles. As part of this procedure revision, PG&E is addressing potential inspection quality concerns. Please see the response to subpart (j) for additional information regarding the referenced “failure” rates. b) Please see the response to subpart (a) for the requested information. c) We are still in the process of finalizing Revision 4 of TD-2325P-01 and will provide a copy when it is finalized. As of this response, we do not have a specific date for when we expect it to be finalized. d) Not applicable, please see the response to subpart (a). e) Yes, please see the response to subpart (a). f) Please see the response to subpart (a). g) The revised procedures are still being drafted, please see response to subpart (c). h) Not applicable, please see the response to subpart (e). i) Another action that PG&E took was to grow its Pole Test and Treat Program to include a field team and dedicated staff to mitigate quality findings. j) The “failure” rate indicated in the referenced spreadsheet does not represent a failed inspection. PG&E marks “failed” during the QC review process if an inspector did not accurately identify a checklist attribute. k) Please see the response to subpart (j) above. | Holly Wehrman | 2024-04-17 | 2024-04-25 | 2024-04-25 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_046.zip | 0 | N/A | 8.1.6 | Section 8.1.6 - Quality Assurance and Quality Control | 8.1.6.1 Quality Assurance (QA) | N/A |  | CalPA | Set WMP-46 | 9 | 11 | Mona Hedin | Nelson Lau | Teresa Tusch | Eric Thomas Tiffany Pazdan | Aaron Shapiro | Stephen Simon | Yes | Yes | Yes |  | Yes | Yes |  |  | 2024-04-25 | [16 empty] | 9 | Teresa Tusch | Eric Thomas Tiffany Pazdan | Mona Hedin | Nelson Lau | Aaron Shapiro | 11 |  |  |  |  | completed | 0 | 0 | 0 | 0
595 | CalPA | Set WMP-46 | CalPA_Set WMP-46 | 8 | CalPA_Set WMP-46_Q8 | In response to data request CalAdvocates-PGE-2025WMP-03, question 1, PG&E provided attachment “WMP-Discovery2023-2025_DR_CalAdvocates_039-Q001Atch08.xlsx”. The following questions refer to the tab “2023 SI Transmission Desktop QC”: a) Please explain what an entry of “Photos are not adequate per compliance training” in Discrepancy Code Description (column I) means. b) If photos are not adequate per compliance training, is it possible to complete QC for that inspection? Explain why or why not. c) Please provide any relevant procedures, specifications, job aids, bulletins, or other documentation to support your answer to part (b). d) If photos are not adequate per compliance training, what actions do QC personnel take to complete QC? e) Please provide any relevant procedures, specifications, job aids, bulletins, or other documentation to support your answer to part (d). | An attachment to this response contains CONFIDENTIAL information provided pursuant to the accompanying confidentiality declaration. a) The referenced entry represented when the photos provided do not meet the guidance specified in the Transmission Ground New Inspector Training. b) If photos are not adequate, it is possible to complete QC for that inspection through a desktop review which verifies inspection results of attributes that can be validated from the available compliant photographs on the inspection record. A Field review is also completed at the asset location to assesses the conditions in real time as well as utilizing the photographs from the original inspection record. c) Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_046- Q008Atch01CONF.pdf” for PG&E’s Transmission Ground New Inspector Training. d) Desktop QC will document all inspection photograph discrepancies on the QC record for tracking and trending. QC will complete review of all available sections/attributes of the inspection record where compliant photographs were available. QC will discontinue review and recommend a reinspection of the asset as a follow up if: (1) the structure number is not visible in inspection record in any section of the inspection and QC cannot confirm inspector was at the correct location; or (2) there are no photos of insulators, or all photos of insulators appear to be from a different structure. e) PG&E does not have a formal standard for the process outlined in subpart (d). | Holly Wehrman | 2024-04-17 | 2024-04-25 | 2024-04-25 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_046.zip | 1 | N/A | 8.1.6 | Section 8.1.6 - Quality Assurance and Quality Control | 8.1.6.1 Quality Assurance (QA) | N/A |  | CalPA | Set WMP-46 | 8 | 5 | Mona Hedin | Andrew Trombley | Teresa Tusch | Eric Thomas Yachi Kumari | Aaron Shapiro | Stephen Simon | Yes |  | Yes |  | Yes | Yes |  |  | 2024-04-25 | [16 empty] | 8 | Teresa Tusch | Eric Thomas Yachi Kumari | Mona Hedin | Andrew Trombley | Aaron Shapiro | 5 |  |  |  |  | completed | 0 | 0 | 0 | 0
594 | CalPA | Set WMP-46 | CalPA_Set WMP-46 | 7 | CalPA_Set WMP-46_Q7 | In response to data request CalAdvocates-PGE-2025WMP-03, question 1, PG&E provided attachment “WMP-Discovery2023-2025_DR_CalAdvocates_039-Q001Atch03.xlsx”. The following questions refer to the tab “Pole Clearing”: a) Please define “QC Date” (column P). b) Please define “QV Date” (column N). c) Does PG&E have a standard for the maximum amount of time that is allowable between an inspection and the QC date? d) If the answer to part (c) is yes, what is the maximum amount of time that is allowable between an inspection and the QC date? e) If the answer to part (c) is yes, please provide any relevant procedures, specifications, job aids, bulletins, or other documentation to support your answer. f) If the answer to part (c) is no, why not? g) Does PG&E have a standard for the maximum amount of time that is allowable between an inspection and the QV date? h) If the answer to part (g) is yes, what is the maximum amount of time that is allowable between an inspection and the QV date? i) If the answer to part (g) is yes, please provide any relevant procedures, specifications, job aids, bulletins, or other documentation to support your answer. j) If the answer to part (g) is no, why not? | Please see the responses to Question No. 005, subparts (a) to (j), which also apply to this request and provide the information sought. | Holly Wehrman | 2024-04-17 | 2024-04-25 | 2024-04-25 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_046.zip | 0 | N/A | 8.1.6 | Section 8.1.6 - Quality Assurance and Quality Control | 8.1.6.1 Quality Assurance (QA) | N/A |  | CalPA | Set WMP-46 | 7 | 10 | Mona Hedin | Andrew Trombley | Teresa Tusch | Josh Keene/Kevin Lieberman | Aaron Shapiro | Stephen Simon | Yes |  | Yes |  | Yes | Yes |  |  | 2024-04-25 | [16 empty] | 7 | Teresa Tusch | Josh Keene/Kevin Lieberman | Mona Hedin | Andrew Trombley | Aaron Shapiro | 10 |  |  |  |  | completed | 0 | 0 | 0 | 0
593 | CalPA | Set WMP-46 | CalPA_Set WMP-46 | 6 | CalPA_Set WMP-46_Q6 | In response to data request CalAdvocates-PGE-2025WMP-03, question 1, PG&E provided attachment “WMP-Discovery2023-2025_DR_CalAdvocates_039-Q001Atch03.xlsx”. The following questions refer to the tab “Transmission”: a) Please define “QC Date” (column S). b) Please define “QV Date” (column Q). c) Does PG&E have a standard for the maximum amount of time that is allowable between an inspection and the QC date? d) If the answer to part (c) is yes, what is the maximum amount of time that is allowable between an inspection and the QC date? e) If the answer to part (c) is yes, please provide any relevant procedures, specifications, job aids, bulletins, or other documentation to support your answer. f) If the answer to part (c) is no, why not? g) Does PG&E have a standard for the maximum amount of time that is allowable between an inspection and the QV date? h) If the answer to part (g) is yes, what is the maximum amount of time that is allowable between an inspection and the QV date? i) If the answer to part (g) is yes, please provide any relevant procedures, specifications, job aids, bulletins, or other documentation to support your answer. j) If the answer to part (g) is no, why not? | Please see the responses to Question No. 005, subparts (a) to (j), which also apply to this request and provide the information sought. | Holly Wehrman | 2024-04-17 | 2024-04-25 | 2024-04-25 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_046.zip | 0 | N/A | 8.1.6 | Section 8.1.6 - Quality Assurance and Quality Control | 8.1.6.1 Quality Assurance (QA) | N/A |  | CalPA | Set WMP-46 | 6 | 10 | Mona Hedin | Andrew Trombley | Teresa Tusch | Josh Keene/Kevin Lieberman | Aaron Shapiro | Stephen Simon | Yes |  | Yes |  | Yes | Yes |  |  | 2024-04-25 | [16 empty] | 6 | Teresa Tusch | Josh Keene/Kevin Lieberman | Mona Hedin | Andrew Trombley | Aaron Shapiro | 10 |  |  |  |  | completed | 0 | 0 | 0 | 0
592 | CalPA | Set WMP-46 | CalPA_Set WMP-46 | 5 | CalPA_Set WMP-46_Q5 | In response to data request CalAdvocates-PGE-2025WMP-03, question 1, PG&E provided attachment “WMP-Discovery2023-2025_DR_CalAdvocates_039-Q001Atch03.xlsx”. The following questions refer to the tab “Routine”: a) Please define “QC Date” (column R). b) Please define “QV Date” (column P). c) Does PG&E have a standard for the maximum amount of time that is allowable between an inspection and the QC date? d) If the answer to part (c) is yes, what is the maximum amount of time that is allowable between an inspection and the QC date? e) If the answer to part (c) is yes, please provide any relevant procedures, specifications, job aids, bulletins, or other documentation to support your answer. f) If the answer to part (c) is no, why not? g) Does PG&E have a standard for the maximum amount of time that is allowable between an inspection and the QV date? h) If the answer to part (g) is yes, what is the maximum amount of time that is allowable between an inspection and the QV date? i) If the answer to part (g) is yes, please provide any relevant procedures, specifications, job aids, bulletins, or other documentation to support your answer. j) If the answer to part (g) is no, why not? | An attachment to this response contains CONFIDENTIAL information provided pursuant to the accompanying confidentiality declaration. a) “QC Date” is the date when the QC Specialist completed the review. b) “QV Date” is the date the Quality Assurance-Performance (QA-P) auditor completed the review. c) Yes, PG&E has a standard for the maximum amount of time that is allowable between an inspection and the QC date. d) A QC review should occur before the next routine Vegetation Management (VM) Execution routine inspection. e) Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_046- Q005Atch01CONF.pdf” for PG&E’s Quality Control Vegetation Management Business Process Document. f) Not applicable, please see the response to subpart (c) above. g) No, PG&E does not have a standard for the maximum amount of time that is allowable between an inspection and the QV date. h) Not applicable, please see the response to subpart (g) above. i) Not applicable, please see the response to subpart (g) above. j) The QV (QA) date is dependent on QC date, which is consequently dependent on work Execution date. Inspections past the next routine cycle would be excluded prior to QA sampling as a result of the QC exclusion process. QA-P is currently performing its reviews within 30 days of QC completion. | Holly Wehrman | 2024-04-17 | 2024-04-25 | 2024-04-25 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_046.zip | 1 | N/A | 8.1.6 | Section 8.1.6 - Quality Assurance and Quality Control | 8.1.6.1 Quality Assurance (QA) | N/A |  | CalPA | Set WMP-46 | 5 | 10 | Mona Hedin | Andrew Trombley | Teresa Tusch | Josh Keene/Kevin Lieberman | Aaron Shapiro | Stephen Simon | Yes |  | Yes |  | Yes | Yes |  |  | 2024-04-25 | [16 empty] | 5 | Teresa Tusch | Josh Keene/Kevin Lieberman | Mona Hedin | Andrew Trombley | Aaron Shapiro | 10 |  |  |  |  | completed | 0 | 0 | 0 | 0
591 | CalPA | Set WMP-46 | CalPA_Set WMP-46 | 4 | CalPA_Set WMP-46_Q4 | In response to data request CalAdvocates-PGE-2025WMP-03, question 1, PG&E provided attachment “WMP-Discovery2023-2025_DR_CalAdvocates_039-Q001Atch02.xlsx”. The following questions refer to the tab “2023 QASI Transmission YTD Raw”: a) Seven entries have a QC Date (column D) that is earlier than the Inspection Date (column F). For each such entry, explain why this is the case. b) Please define “QC Date” (column D). c) Please define “QA Completion Date” (column C). d) Does PG&E have a standard for the maximum amount of time that is allowable between an inspection and the QC date? e) If the answer to part (d) is yes, what is the maximum amount of time that is allowable between an inspection and the QC date? f) If the answer to part (d) is yes, please provide any relevant procedures, specifications, job aids, bulletins, or other documentation to support your answer. g) If the answer to part (d) is no, why not? h) Does PG&E have a standard for the maximum amount of time that is allowable between an inspection and the QA completion date? i) If the answer to part (h) is yes, what is the maximum amount of time that is allowable between an inspection and the QA completion date? j) If the answer to part (h) is yes, please provide any relevant procedures, specifications, job aids, bulletins, or other documentation to support your answer. k) If the answer to part (h) is no, why not? | a) The inspection date should be earlier than the QC date. The referenced entries were errors which occurred for specific instances when a reinspection was performed. In these instances, the system of record automatically updated the original inspection date to the reinspection date. PG&E has since corrected this automated error in its system. b) “QC Date” (column D) refers to the date that the QC inspection was completed. c) "QA Completion Date” is the date that the Subject Matter Expert completes the review process and submits the record to the database as approved/accurate/complete. d) No, PG&E does not have a standard for the maximum amount of time that is allowable between the completion of the QC inspection and the start of the QA inspection. Generally, QA will inspect the asset three to six weeks after the completion of the QC inspection and the majority of the QA inspections are completed in this time frame. Times will vary due to the review and verification process conducted by QC for each individual asset assessment. e) Not applicable, please see the response to subpart (d) above. f) Not applicable, please see the response to subpart (d) above. g) Please see the response to subpart (d) for the requested explanation. h) PG&E does not have a standard for the maximum amount of time allowable between the QA inspection start and the QA completion date. Generally, the time from sample availability to audit completion is seven days and the majority of the QA inspections are completed in this timeframe. Occasionally, additional time is required for review and alignment which is done as rapidly as possible and is usually completed within an additional seven days. i) Not applicable, please see the response to subpart (h) above. j) Not applicable, please see the response to subpart (h) above. k) Please see response to subpart (h) for the requested explanation. | Holly Wehrman | 2024-04-17 | 2024-04-25 | 2024-04-25 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_046.zip | 0 | N/A | 8.1.6 | Section 8.1.6 - Quality Assurance and Quality Control | 8.1.6.1 Quality Assurance (QA) | N/A |  | CalPA | Set WMP-46 | 4 | 11 | Mona Hedin | Andrew Trombley | Teresa Tusch | Josh Keene | Aaron Shapiro | Stephen Simon | Yes |  |  |  | Yes | Yes |  |  | 2024-04-25 | [16 empty] | 4 | Teresa Tusch | Josh Keene | Mona Hedin | Andrew Trombley | Aaron Shapiro | 11 |  |  |  |  | completed | 0 | 0 | 0 | 0
590 | CalPA | Set WMP-46 | CalPA_Set WMP-46 | 3 | CalPA_Set WMP-46_Q3 | In response to data request CalAdvocates-PGE-2025WMP-03, question 1, PG&E provided attachment “WMP-Discovery2023-2025_DR_CalAdvocates_039-Q001Atch01.xlsx” The following questions refer to the tab “2023 QASI Distribution YTD Raw”. a) 47 entries have “Yes” for ObservationOrNonconf (column J) and “None” for FindingPriority (column P). Please explain the circumstances under which there would be findings with no priority assigned. b) Please explain what an entry of “OTR” in SpeccFinding (column Q) means. | a) Circumstances that would have a “Yes” for ObservationOrNonconf (column J) would include findings that may or may not require a tag to be written. The majority of the 47 entries listed are photo discrepancies that are not assigned any priority (FindingPriority column P). Additional examples would include documentation errors, for example, previous tags created in error or existing tags requiring additional information and Third Party notifications. The remainder of the 47 entries are data entry errors that should have been labeled “CritAtt” or “Re-Insp”” as E or F tags were created. These will be used for training and improvement examples. b) Column Q “OTR” is the entry for any “other” type of finding that is not identified as “Bprty”, “CritAtt”, “Emerg”, or “Re-Insp”. It also identifies any inspection that has multiple findings associated with the asset. | Holly Wehrman | 2024-04-17 | 2024-04-25 | 2024-04-25 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_046.zip | 0 | N/A | 8.1.6 | Section 8.1.6 - Quality Assurance and Quality Control | 8.1.6.1 Quality Assurance (QA) | N/A |  | CalPA | Set WMP-46 | 3 | 2 | Mona Hedin | Andrew Trombley | Teresa Tusch | Josh Keene | Aaron Shapiro | Stephen Simon | Yes |  | Yes |  | Yes | Yes |  |  | 2024-04-25 | [16 empty] | 3 | Teresa Tusch | Josh Keene | Mona Hedin | Andrew Trombley | Aaron Shapiro | 2 |  |  |  |  | completed | 0 | 0 | 0 | 0
580 | CalPA | Set WMP-44 | CalPA_Set WMP-44 | 10 | CalPA_Set WMP-44_Q10 | The following table is from PG&E’s 2022 Annual Electric Reliability Report, page 12: a) Please provide an updated version of this table with an additional row for 2023. b) If PG&E is unable to provide any of the requested data from part (a), please provide a reason for each data point. c) If PG&E is unable to provide any of the requested data from part (a), please provide an estimate of when this data will be available. | a) An updated version of the requested table is not currently available, as described in subpart (b) below. b) PG&E publishes the Annual Electric Reliability Report each July for the prior year. The referenced table will be included in the 2023 Annual Electric Reliability Report, which is tentatively scheduled to be published in July 2024 at the following link: https://www.pge.com/en/about/pge-systems/electric-systems/electric-reliabilityreports.html. c) Please see the response to subpart (b) above. | Holly Wehrman | 2024-04-15 | 2024-04-18 | 2024-04-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_044.zip | 0 | N/A | N/A | N/A | N/A | N/A |  | CalPA | Set WMP-44 | 10 | 3 | Mona Hedin | Saritha Basani | Tom Huynh | Satvir Nagra | Aaron Shapiro | Mark Quinlan | Yes | Yes | Yes |  | Yes | Yes | Yes |  | 2024-04-18 | [16 empty] | 10 | Tom Huynh | Satvir Nagra | Mona Hedin | Saritha Basani | Aaron Shapiro | 3 |  |  |  |  | completed | 0 | 0 | 0 | 0
651 | CPUC - SPD (Safety Policy Division) | 016 | CPUC - SPD (Safety Policy Division)_016 | 8 | CPUC - SPD (Safety Policy Division)_016_Q8 | Provide additional information on the criteria for “Red Flag” Conditions – it appears that PG&E also refers to them as “dry wind” conditions [see page 10 of 2025 WMP Update and PG&E’s response to MGRA_Data Request No. 9_Q2]. a. Reconcile the terminology –are these synonyms? Explain why if not. b. Explain how this partition has impacted modeling in WDRM v4. c. Provide the percentage of WDRM v4 risk associated with these days. d. Provide the percentage of WDRM v3 risk associated with these days. e. Discuss how the risk Bow Tie differs in its use of these days compared to WDRM v4 and v3. f. Explain how this criteria compares to classification of weather in both FPI v4.0 and v5.0. Is it similar to R4 or R5 (or another level)? Why/why not? g. Explain how this criteria connects to weather that would result in PG&E’s use of a PSPS event. h. Explain how this criteria relates to PG&E’s enablement criteria for EPSS. i. Provide a list of all CPUC-reportable ignitions for each year from 2014 through April 30, 2024 that occurred during “Red Flag” conditions, Provide the data in the same format as the CPUC-Reportable Ignitions Template submitted yearly to the CPUC, with an additional column indicating if the ignition was in the (1) Tier 2, (2) Tier 3, (3) HFRA (exclusive of HFTD) and (4) non-HFTD/HFRA. j. Provide the number of circuit mile days on an annual basis that met the “Red Flag” conditions criteria starting in 1980 (or the first year PG&E’s 30-year meteorology data set) through April 30, 2024. k. Provide the predicted number of circuit mile days per year expected to meet the “Red Flag” conditions criteria based on PG&E’s modeling. l. In PG&E’s response to MGRA_Data Request No. 9_Q2, PG&E states that the additional explanatory power of dry wind is modest over the predictive destructive condition. Explain. i. Discuss if this is related to the predictive destructive condition already being predicated on an FPI threshold. | a. “Red Flag” conditions are not the same as “dry wind” conditions. Dry Wind Conditions (DWC) status was developed for the consequence modeling in response to both internal and external reviews of Wildfire Consequence (WFC) model v3.4 recommending the inclusion of Red Flag Warnings (RFW) issued by the National Weather Service (NWS). RFW warnings are issued by the NWS when there are weather conditions that would intensify fires. These RFW warnings are issued across a mixture of watershed areas, ridgelines, and jurisdictional boundaries such as county lines. The criteria for issuing a RFW warning is also not consistent across all these areas. The inconsistencies in RFW criteria causes problems when trying to fit it as a model covariate as the result may be a prediction based on RFW definition rather than the actual local conditions. To avoid the RFW inconsistency issue, the DWC was developed as an internal status covariate for use in the WFC model that could be used across the entire PG&E service territory. The DWC conditions criteria is listed in this table. Measurement Limit (daily average) Wind Speed >= 19 mph 10-hr Dry Fuel Moisture <= 6% Relative Humidity <= 30% b. Wildfires seem to occur in ‘regimes’ defined by the location, topography, near environment (natural and human), weather (short-term and cumulative), climate, et al. • The objective is to identify regimes, that are both discriminative of wildfire characteristics, and well enough populated to provide robust statistics. • With the addition of PGE-DryWind in v4, we have three factors whose combinations (of Boolean values) define 8 regimes: HFRA, Predicted-Destructive, and PGE-DryWind. The PGE-DryWind definition relies on wind-speed and relative humidity crossing thresholds which approximate Federal Red-flag conditions in PG&E service territory. While a very large component of this is already captured by the criteria defining 'Predicted Destructive' conditions via the FPI models, those models rely heavily on burnable fuel presence and characteristics in addition to weather. We find that there is merit in considering extreme conditions of wind and relative humidity in isolation, to identify areas and conditions conducive to wildfires even in sparse fuel conditions. c. In the WDRM v4 consequence, roughly 6.5% of the total wildfire consequence is associated with historical Dry Wind conditions. This approximation to consequence is obtained with the weighted sum over the 8 strata defined by the labels given in the table below. The weights are the fraction of days each pixel is in each of the 8 strata, and the summand is the mean MAVF of historical fires in each strata. WMP-Discovery2023-2025_DR_SPD_016-Q008 Page 3 The product of the MAVF and the Percent of Grid Pixel-Days approximates the relative importance of contributions of each stratum to the total consequence and hence risk. The percentage of strata with Dry Wind True is roughly 6.5%. Specifically, from the table below, (502x0.07 + 1.78x0.16 + 1.8x0.04 + 0.46x1.16) / (502x0.07 + 1.78x0.16 + 1.8x0.04 + 0.46x1.16 + 180x2.36 + 1.96x31.56 + 8.64x0.17 + 0.37x64.49) = 6.5%. HFRA Dry Wind Conditions Predicted Destructive MAVf Percent of Grid Pixel-Days True True True 502 0.07 True True False 1.78 0.16 True False True 180 2.36 True False False 1.96 31.56 False True True 1.80 0.04 False True False 0.46 1.16 False False True 8.64 0.17 False False False 0.37 64.49 d. For WDRM v3, we did not have the PGE Dry-Wind strata for historical fires. Therefore, the MAVF value takes only 4 values corresponding to the combination of HFRA X Predicted Destructive labels. e. The risk bow-tie uses red-flag warning days as they were historically called by weather forecasters using region specific criteria. As described in the response to subpart (a) above, the dry-wind condition is different but designed to retain the predictive power of RFW. f. The R1 to R5 conditions are an output of the FPI model which uses factors such as wind speed and fuel moisture as inputs. The “dry wind” conditions are a classification of wind speeds, fuel moisture, and humidity. While there is likely to be a significant overlap in areas with high R scores from the FPI model and areas that meet the “dry wind” conditions criteria, they are not directly correlated. g. PSPS decisions are driven by the R1-R5 conditions which are an output of the FPI model which uses factors such as wind speed and fuel moisture as inputs. The “dry wind” conditions are a classification of wind speeds, fuel moisture, and humidity. While there is likely to be a significant overlap in areas with high R scores from the FPI model and areas that meet the “dry wind” conditions criteria, “dry wind” conditions are not directly used as an input to PSPS decision making. h. Similar to PSPS, EPSS enablement criteria uses R scores from the FPI model which is similar to the DWC “dry winds” criteria as explained in subparts (f) and (g). i. Please see attachment “WMP-Discovery2023-2025_DR_SPD_016-Q008Atch01.csv” for the training fires used in fitting the Wildfire consequence model. They are VIIRS detected fires within the training season (June-November inclusive) with lightning fires removed from low-fire danger days (as non-representative). The predicted_destructive_flag, the pdw_flag (PG&E Dry wind) flags, and the rfw_flag (red flag warning) flags are present. j. Since the WFC model does not use RFW days as a direct input as described in response to subpart (a) for this question, an export showing “Red Flag” conditions over the requested period is not available. k. The WFC model is designed to quantify Wildfire Consequence. It is not designed to make predictions of future weather conditions which determine “Red Flag” conditions. l. Yes. The explanatory power of dry wind is modest. PGE-Dry Wind definition relies on wind-speed and relative humidity crossing thresholds which approximate Federal Red-flag conditions in PG&E service territory. While a very large component of this is already captured by the criteria defining 'Predicted Destructive' conditions via the FPI models, these models rely heavily on burnable fuel presence and characteristics in addition to weather. There is merit in considering extreme conditions of wind and relative humidity in isolation, to identify areas and conditions conducive to wildfires even in sparse fuel conditions even if the additional impact is small. | Henry Sweat | 2024-05-30 | 2024-06-12 | 2024-06-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_016.zip | 1 | N/A | 6 | 6.0 Risk Methodology and Assessment | 6.2.1 Risk and Risk Component Identification | 1. Signfiicant Updates to Risk Models (WDRM v4 & WTRM v2) |  | CPUC - SPD (Safety Policy Division) | 016 | 8 | 13 | Mona Hedin | Mandy Knockaert | Manuj Sharma | Jon Eric Thalman | Aaron Shapiro | Andy Abranches | Yes |  | Yes | Yes | Yes | Yes | Yes |  | 2024-06-12 |  | extension - data not readily available and will take time to pull | [14 empty] | 8 | Manuj Sharma | Jon Eric Thalman | Mona Hedin | Mandy Knockaert | Aaron Shapiro | 13 |  |  |  |  | completed | 0 | 0 | 0 | 0
645 | CPUC - SPD (Safety Policy Division) | 016 | CPUC - SPD (Safety Policy Division)_016 | 2 | CPUC - SPD (Safety Policy Division)_016_Q2 | Generally, what is PG&E’s corporate process and strategic procedure for switching to a new model to support decision-making regarding mitigation alternatives (e.g., migrating from WDRM v3 to WDRM v4)? What steps are involved? | PG&E utilizes Utility Standard: TD-7201S, Wildfire Risk Management Distribution Standard to help guide its decision-making in this area. Specifically, section 4 describes our management of change process. Section 4 of this procedure is copied below. 4. WDRM Management of Change 4.1 In support of PG&E’s stand that “Catastrophic Wildfires Shall Stop,” the nascent science of wildfire risk modeling necessitates updates and improvements on a frequent basis. 1. The risk models based on machine learning (ML) and artificial intelligence (AI) provide advanced technics to support this stand. While advanced and powerful, they are statistical forecasts. As such, the statistical or predictive performance of one model and then a subsequent improved model can be evaluated. 4.2 The prioritization of locations or assets provided by models is not necessarily similar. Models with similar statistical predictive performance can be achieved with different model results. 1. For example, if two models with similar predictive performances address 75% of future outage locations, the actual ranked prioritization in which 75% is identified can differ. a. IF one of the statistically close models incorporates data that improves identified required corrective work to mitigate the risk, THEN the work plan may need to rely more heavily on that model. 4.3 In accordance with the above facts, base the transition from one model to the next for work plan development on both the improvement in predictive performance and the nature of the work plan related to the model features. 4.4 Programs with a long lead time where work plans are developed a year or more in advance (such as system hardening/undergrounding) may decide to keep or “grandfather” all or a portion of the existing work plan commitment before switching to the new model version. Other programs with shorter work plan cycle times may switch to the new model sooner. 4.5 For each of the programs identified in the following Section 5, guidelines for transitioning to new models are provided. 1. The WRGSG must approve both the WDRM and the Wildfire Consequence Model before they are released for prioritizing and planning work. | Henry Sweat | 2024-05-30 | 2024-06-04 | 2024-06-04 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_016.zip | 0 | N/A | 6 | 6.0 Risk Methodology and Assessment | 6.2.1 Risk and Risk Component Identification | 1. Signfiicant Updates to Risk Models (WDRM v4 & WTRM v2) |  | CPUC - SPD (Safety Policy Division) | 016 | 2 | 0 | Mona Hedin | Mandy Knockaert | Meagan Nolan | Jon Eric Thalman | Aaron Shapiro | Andy Abranches | Yes | Yes | Yes |  | Yes | Yes | Yes |  | 2024-06-04 | [16 empty] | 2 | Meagan Nolan | Jon Eric Thalman | Mona Hedin | Mandy Knockaert | Aaron Shapiro | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
587 | MGRA | Data Request No. 11 | MGRA_Data Request No. 11 | 3 | MGRA_Data Request No. 11_Q3 | If E3 or another consulting group has analyzed WDRM v4, please provide a nonconfidential version of its report. | E3 is currently conducting an independent review of the WDRM v4, which is scheduled to be available by the end of Q2 2024. | Joseph Mitchell | 2024-04-16 | 2024-04-19 | 2024-04-19 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_011.zip | 0 | N/A | 6.2.1 | 6.0 Risk Methodology and Assessment | 6.2.1 Risk and Risk Component Identification | 1. Signficant Updates to Risk Models (WDRM v4 & WTRM v2) |  | MGRA | Data Request No. 11 | 3 | 0 | Mona Hedin | Mandy Knockaert | Richard Anderson | Jon Eric Thalman | Aaron Shapiro | Andy Abranches | Yes | Yes | Yes |  | Yes | Yes |  |  | 2024-04-19 | [16 empty] | 3 | Richard Anderson | Jon Eric Thalman | Mona Hedin | Mandy Knockaert | Aaron Shapiro | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
586 | MGRA | Data Request No. 11 | MGRA_Data Request No. 11 | 2 | MGRA_Data Request No. 11_Q2 | Please provide a non-confidential version of documentation containing a description of WDRM v4, including testing and validation. | PG&E objects to this request on the grounds that it is overbroad and unduly burdensome to provide what can be interpreted as all “documentation containing a description of WDRM v4.” Gathering and providing all “documentation containing a description of WDRM v4” could take many weeks of work and require reviewing many thousands of documents. PG&E also objects to this request on the grounds that it is vague and ambiguous as to what is included in all “documentation containing a description of WDRM v4.” PG&E further objects to this request insofar as it seeks information protected by the attorney-client privilege and attorney work product privilege. PG&E also objects to the request on the grounds that it exceeds the scope of this regulatory proceeding, as PG&E’s 2025 WMP notes that WDRM v4 has not yet been used for any wildfire mitigation work. Notwithstanding and without waiving these objections, PG&E responds as follows: we anticipate that WDRM v4 model documentation, including a validation report, will be available by the end of Q2 2024. | Joseph Mitchell | 2024-04-16 | 2024-04-19 | 2024-04-19 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_011.zip | 0 | N/A | 6.2.1 | 6.0 Risk Methodology and Assessment | 6.2.1 Risk and Risk Component Identification | 1. Signficant Updates to Risk Models (WDRM v4 & WTRM v2) |  | MGRA | Data Request No. 11 | 2 | 0 | Mona Hedin | Mandy Knockaert | Richard Anderson | Jon Eric Thalman | Aaron Shapiro | Andy Abranches | Yes | Yes |  |  | Yes | Yes |  |  | 2024-04-19 |  |  | 4/17-j1oz- objection per law | [13 empty] | 2 | Richard Anderson | Jon Eric Thalman | Mona Hedin | Mandy Knockaert | Aaron Shapiro | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
585 | MGRA | Data Request No. 11 | MGRA_Data Request No. 11 | 1 | MGRA_Data Request No. 11_Q1 | Please provide non-confidential versions of any responses to Cal Advocates data requests if the responses to Cal Advocates are confidential. | PG&E objects to this request on the grounds that it seeks to impose a continuing discovery obligation on PG&E. Continuing discovery obligations are not permitted under California law. Biles v. Exxon Mobile Corp., 124 Cal.App.4th 1315, 1328 (2004); Code Civ. Proc. § 2030.060(g). Additionally, PG&E objects to this request on the grounds that it is overbroad and unduly burdensome. PG&E receives an enormous volume of data requests in the window of time between submitting its WMP and the deadline to submit public comments. This burden is exacerbated by the default three business day turnaround period for all responses. Imposing this continuous discovery obligation on PG&E during this period is not tenable. Furthermore, any effort to provide the requested information would be further exacerbated because MGRA has refused to sign a confidentiality or non-disclosure agreement, and providing this information would require manually redacting all confidential information from each response. PG&E notes that the Public Advocates Office is a government agency that has broad statutory authority that exceeds this single regulatory proceeding and allows the Public Advocates Office to obtain information that exceeds what MGRA, as a private organization, would be able to obtain through this proceeding. Lastly, MGRA may obtain non-confidential versions of PG&E responses to Cal Advocates data requests at the following website: https://www.pge.com/en/outagesand-safety/safety/community-wildfire-safety-program.html#accordion-6b52828ca7-itema47a0617be. If you would like to discuss this request and our response, please do not hesitate to reach out as we are happy to meet and confer on this issue. | Joseph Mitchell | 2024-04-16 | 2024-04-19 | 2024-04-19 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_011.zip | 0 | N/A | 6.2.1 | 6.0 Risk Methodology and Assessment | 6.2.1 Risk and Risk Component Identification | 1. Signficant Updates to Risk Models (WDRM v4 & WTRM v2) |  | MGRA | Data Request No. 11 | 1 | 0 | Mona Hedin | Mandy Knockaert | Richard Anderson | Jon Eric Thalman | Aaron Shapiro | Andy Abranches | Yes | Yes |  |  | Yes | Yes |  |  | 2024-04-19 |  |  | 4/17-j1oz- objection per law | [13 empty] | 1 | Richard Anderson | Jon Eric Thalman | Mona Hedin | Mandy Knockaert | Aaron Shapiro | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
598 | OEIS | 016 | OEIS_016 | 1 | OEIS_016_Q1 | Q01. Regarding PG&E’s Response to PG&E-23-15 a. In PG&E’s response to PG&E-23-15, it says that “the following information will be digitally recorded for trees prescribed for removal.”1 i. Did PG&E “enhance the One VM application for Routine, and Second Patrol to include capability to capture factors for prescribing trees for removal” by its target completion date of 1/31/2024?2 (1) If not, explain the reason for the delay and provide an updated target completion date for inclusion of this capability in One VM. ii. Provide the One VM form that “capture[s] factors for prescribing trees for removal.” iii. Is PG&E on track to “Enhance the application for the Vegetation Management for Operational Mitigations (VMOM) - VMPI2 - and Tree Removal Inventory (TRI) - Field Maps - program to include capability to capture factors for prescribing trees for removal” by its target completion date of 11/15/2024?3 (1) If not, explain the reason for the delay and provide an updated target completion date for this planned enhancement. b. In PG&E’s response to PG&E-23-15, it says that “PG&E will be making digital record enhancements to FTI potential strike trees.”4 i. Did PG&E “Enhance record keeping practices for the Focused Tree Inspection program (FTI) by creating records of all potential strike trees inspected using a digitized Tree Risk Assessment form” by it target completion date of 3/31/2024?5 (1) If not, explain the reason for the delay and provide an updated timeline for inclusion of this capability in One VM. ii. Provide PG&E’s digitized Tree Risk Assessment form. | a. i. Yes, PG&E completed our enhancement of the One VM application for Routine and Second Patrol to include capabilities to capture factors for prescribing trees for removal by January 31, 2024. • Please see the 5 Minute Meeting “WMP-Discovery2023- 2025_DR_OEIS_016-Q001Atch01CONF.pdf” delivered to VM personnel via VM Program Communications on January 31, 2024, that calls out the requirement to document reasons for removals within system of record. • Please see Utility Bulletin TD-7102P-01-B036 “WMP-Discovery2023- 2025_DR_OEIS_016-Q001Atch02CONF.pdf” referenced in the 5MM published on January 30, 2024 with an effective date of January 30, 2024 that provides instructions on how to document ‘reasons for removal’ within One VM. ii. Please note, PG&E believes the use of ‘form’ here is incorrect. One VM is an application and the enhancement referenced above was completed within the One VM mobile application utilized by our VM personnel. Please see screenshots below showing that this field is now available within the One VM application. Please see “WMP-Discovery2023-2025_DR_OEIS_016-Q001Atch03.pdf” for additional examples of the ’Removal Reason’ field in the One VM application. iii. Yes, PG&E is still on track to enhance VMOM and TRI program to include the capability to capture factors for prescribing trees for removal by November 15, 2024. Please note, since this objective was written, the timeline of programs to be onboarded onto the One VM platform has changed, and by the time this objective is due, both the VMOM and TRI programs will be integrated into the One VM platform, and no longer utilizing VMPI2 or Field Maps. The One VM application already captures factors for prescribing trees for removal, so the objective intent will still be met. b. i. Yes, PG&E completed the digitization of the TRAQ form on March 25, 2024, however, based upon feedback from both the Operational Observer and Energy Safety, PG&E’s operational approach to FTI was changed to only fill out a TRAQ form on trees prescribed for work. Filling out TRAQ forms on inventory only trees required excessive use of limited TRAQ certified resources, which did not meet the intent of the program. A level 2 inspection will still be performed on all strike potential trees. All strike potential trees between January 1, 2024 to April 8, 2024 will have a record with a Paper TRAQ form attached. On April 8, 2024, PG&E readjusted our approach for FTI and requires a level 2 inspection and a paper TRAQ form to be attached to records with assigned prescriptions. Records marked ‘no work’ will receive a level 2 inspection and TRAQ forms are not required to be attached. With this change, new enhancements are required for us to utilize the digital TRAQ form in One VM. We expect to implement the use of the digitized TRAQ forms in Q3 2024. ii. Please see “WMP-Discovery2023-2025_DR_OEIS_016- Q001Atch04CONF.pdf” for an example of the PG&E digitized Tree Risk Assessment form housed within the One VM application. | Brad Hill | 2024-04-22 | 2024-04-25 | 2024-04-25 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/OEIS_016.zip | 4 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--15 Implementation of Focused Tree Inspections and Addressing the Risk from Hazard Trees | ACI 23-15 Implementation of Focused Tree Inspections and Addressing the Risk from Hazard Trees |  | OEIS | 016 | 1 | 2 | Mona Hedin | Cherimae Vail | VM Data Requests | Sarah Carlson | Lauren Ruby | Andy Abranches Angela Sanford | Yes | Yes |  |  | Yes | Yes |  |  | 2024-04-25 | [16 empty] | 1 | VM Data Requests | Sarah Carlson | Mona Hedin | Cherimae Vail | Lauren Ruby | 2 |  |  | DRU-14606 |  | completed | 0 | 0 | 0 | 0
608 | OEIS | 017 | OEIS_017 | 4 | OEIS_017_Q4 | Regarding the Joint Utility Monthly Meetings on the WMP PG&Es 2025 Update mentions that “The Joint Utilities conduct a monthly meeting that discusses many areas of the WMP in depth. PG&E, Southern California Edison Company (SCE), and SDG&E each take turns leading the meetings. Topics for these meetings generally cover mitigation strategy and implementation, regulatory developments, and knowledge sharing.” (p. 47, response to PG&E-23-04 “Cross-Utility Collaboration on Best Practices for Inclusion of Climate Change Forecasts in Consequence Modeling, Inclusion of Community Vulnerability in Consequence Modeling, and Utility Vegetation Management for Wildfire Safety”). 1. Are these meetings in response to a specific Area of Continued Improvement? a. If so, please state which Area of Continued Improvement. b. If not, please state what directive these meetings were in response to. 2. Are these monthly meetings the same as the Joint Utility meetings mentioned on page 48 of PG&Es 2025 Update (“Furthermore, as described above, PG&E, SCE, and SDG&E developed standing monthly Joint Utility meetings, creating a forum to keep one another updated and discuss wildfire topics.”)? a. If yes, please confirm in your response. b. If not, please describe how they are different. | 1. No, these meetings are not in response to a specific Area of Continued Improvement. a. Not applicable, please see the response to subpart (1). b. These meetings were not in response to any directive. Following the joint utility collaboration and benchmarking on the 2023-2025 Maturity Survey in 2022 and 2023, the Joint IOUs decided to continue meeting regularly to discuss wildfire topics as the process of sharing best practices and talking through issues was beneficial. Please see attachment “WMP-Discovery2023-2025_DR_OEIS_017- Q004Atch01CONF.pdf” for the Meeting Charter that describes the purpose, scope, membership, and logistics for the meetings. 2. Yes, these meetings are the same as the Joint Utility meetings mentioned on page 48 of PG&E’s 2025 WMP Update. a. Please see the response to subpart (2) above. b. Not applicable, please see the response to subpart (2) above. | Brad Hill | 2024-04-29 | 2024-05-02 | 2024-05-02 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/OEIS_017.zip | 1 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--04 | ACI 23-04 Cross-Utility Collaboration on Best Practicies |  | OEIS | 017 | 4 | 6 | Mona Hedin | Desiree Marton | Mandy Knockaert Jay Leyno Desiree Marton | Jay Leyno | Aaron Shapiro | Andy Abranches | Yes | Yes |  |  |  | Yes | Yes |  | 2024-05-02 | [16 empty] | 4 | Mandy Knockaert Jay Leyno Desiree Marton | Jay Leyno | Mona Hedin | Desiree Marton | Aaron Shapiro | 6 |  |  |  |  | completed | 0 | 0 | 0 | 0
607 | OEIS | 017 | OEIS_017 | 3 | OEIS_017_Q3 | Regarding the Standing Joint Utility Monthly Meetings PG&Es 2025 Update mentions that “Furthermore, as described above, PG&E, SCE, and SDG&E developed standing monthly Joint Utility meetings, creating a forum to keep one another updated and discuss wildfire topics.” (p. 48, response to PG&E-23-04 “Cross-Utility Collaboration on Best Practices for Inclusion of Climate Change Forecasts in Consequence Modeling, Inclusion of Community Vulnerability in Consequence Modeling, and Utility Vegetation Management for Wildfire Safety”). Please provide the following: 1. Provide the following information about these standing monthly joint utility sessions. a. Each working session’s date, time, and host organization. b. The agenda for each working session. 2. Does PG&E plan to continue these sessions in the future? 3. Are there any plans to include Bear Valley, Liberty, or PacifiCorp in these meetings? a. If yes, please state any past or future attempts to include these utilities. | 1. PG&E, SCE and SDG&E held six Joint Utility meetings to discuss wildfire topics between January and April in 2024. Each utility rotates to host two monthly meetings, one in-person and one virtually. In-person meetings are typically held over two days. Virtual meetings are typically held on one day. Each meeting is approximately four hours in duration. a. The working session dates, time and host organization are as follows: January in-person meetings hosted by SCE: January 10, 2024, 12:00 p.m. – 4:30 p.m. January 11, 2024, 8:00 a.m. – 12:00 p.m. February virtual meeting hosted by SCE: February 9, 2024, 8:00 a.m. – 12:00 p.m. March in-person meetings hosted by PG&E: March 13, 2024, 12:00 p.m. – 4:00 p.m. March 14, 2024, 8:00 a.m. – 12:00 p.m. April virtual meeting hosted by PG&E: April 12, 2024, 8:00 a.m. – 12:00 p.m. b. Please see the table below for the agendas for the monthly working sessions: Meeting Attachment Name January in-person meetings hosted by SCE WMP-Discovery2023-2025_DR_OEIS_017- Q003Atch01CONF.pdf February virtual meeting hosted by SCE WMP-Discovery2023-2025_DR_OEIS_017- Q003Atch02CONF.pdf March in-person meetings hosted by PG&E WMP-Discovery2023-2025_DR_OEIS_017- Q003Atch03CONF.pdf April virtual meeting hosted by PG&E WMP-Discovery2023-2025_DR_OEIS_017- Q003Atch04CONF.pdf 2. Yes, PG&E plans to continue these sessions in the future. 3. PG&E, SCE and SDG&E collectively extended the invitation to Bear Valley, Liberty and PacifiCorp to join these meetings. On January 11th , Bear Valley and PacifiCorp participated in the Joint Utility meeting. Bear Valley also participated in the March 13th and 14th meetings. | Brad Hill | 2024-04-29 | 2024-05-02 | 2024-05-02 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/OEIS_017.zip | 4 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--04 | ACI 23-04 Cross-Utility Collaboration on Best Practicies |  | OEIS | 017 | 3 | 6 | Mona Hedin | Desiree Marton | Mandy Knockaert Jay Leyno Desiree Marton | Jay Leyno | Aaron Shapiro | Andy Abranches | Yes | Yes |  |  | Yes | Yes | Yes |  | 2024-05-02 | [16 empty] | 3 | Mandy Knockaert Jay Leyno Desiree Marton | Jay Leyno | Mona Hedin | Desiree Marton | Aaron Shapiro | 6 |  |  |  |  | completed | 0 | 0 | 0 | 0
606 | OEIS | 017 | OEIS_017 | 2 | OEIS_017_Q2 | Regarding the Utility Undergrounding Working Group Meetings PG&Es 2025 Update mentions that “Lastly, the utilities also developed an undergrounding working group to discuss lessons learned and the challenges associated with undergrounding.” (p. 48, response to PG&E-23-04 “Cross-Utility Collaboration on Best Practices for Inclusion of Climate Change Forecasts in Consequence Modeling, Inclusion of Community Vulnerability in Consequence Modeling, and Utility Vegetation Management for Wildfire Safety”). Please explain the following: 1. Which utilities were present at these working group meetings. 2. The general duration of these meetings: a. Are these monthly, weekly, or quarterly meetings? Please specify. 3. If these meetings were in response to a specific Area of Continued Improvement a. If so, please state which Area of Continued Improvement. b. If not, please state what directive these meetings were in response to. | 1. The Joint Investor-Owned Utility (IOU) meetings are held with SDG&E and Southern California Edison (SCE). 2. a. Starting in October 2023, the meeting cadence was monthly. However, in 2024, our cadence has changed to quarterly as agreed upon by members from participating utilities. 3. a. No, these meetings were not in response to a specific Area of Continued Improvement (ACI). b. During the Joint IOU meetings, we discuss (and continue to discuss) a series of topics such as Customer Engagement Strategies, Vegetation Management, Undergrounding Project Cycle Times, Cost, and Innovative Technologies, among other items. Additionally, PG&E has participated in and will continue to participate in utility workshops hosted by entities such as Electric Power Research Institute (EPRI), where we have an opportunity to share best practices and learn from other utilities. Topics discussed during the most recent EPRI workshop included: • Excavation / Burial / Installation • Easements / Joint Use • New Equipment / Components / Tools • Customers / Community Engagement • Underground Commissioning, Maintenance and Operations | Brad Hill | 2024-04-29 | 2024-05-02 | 2024-05-02 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/OEIS_017.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--04 | ACI 23-04 Cross-Utility Collaboration on Best Practicies |  | OEIS | 017 | 2 | 6 | Mona Hedin | Mandy Knockaert | Jasmine Gideon/Mandy Knockaert | Justin Sadler | Aaron Shapiro | Matt Pender | Yes | Yes |  |  | Yes | Yes | Yes |  | 2024-05-02 | [16 empty] | 2 | Jasmine Gideon/Mandy Knockaert | Justin Sadler | Mona Hedin | Mandy Knockaert | Aaron Shapiro | 6 |  |  |  |  | completed | 0 | 0 | 0 | 0
605 | OEIS | 017 | OEIS_017 | 1 | OEIS_017_Q1 | Regarding the Joint Utility Covered Conductor Effectiveness Weekly Meetings PG&Es 2025 Update mentions that it participated in weekly meetings with utilities in 2023 “to benchmark and share information regarding covered conductor effectiveness.” (p. 48, response to PG&E-23-04 “Cross-Utility Collaboration on Best Practices for Inclusion of Climate Change Forecasts in Consequence Modeling, Inclusion of Community Vulnerability in Consequence Modeling, and Utility Vegetation Management for Wildfire Safety”). Please explain the following: 1. Which utilities were present at these weekly meetings. 2. The first month these meetings began. 3. If these meetings were in response to a specific Area of Continued Improvement. a. If so, please state which Area of Continued Improvement. b. If not, please state what directive these meetings were in response to. | Southern California Edison (SCE) hosted the Joint Utility Covered Conductor Effectiveness Weekly meetings. Thus, PG&E reached out to SCE to confirm the information provided in response to Question No. 001. 1. SCE confirmed that participants to the referenced meetings included San Diego Gas & Electric (SDG&E), SCE, PacifiCorp, PG&E, Liberty Utilities, and Bear Valley Electric Service, Inc. 2. The meetings began in April 2023. 3. Yes, these meetings were conducted in response to Area of Continued Improvement (ACI) ACI PG&E-22--11 Covered Conductor Effectiveness Lessons Learned as well as PG&E-23-06 Continuation of Grid Hardening Joint Studies (see pages 62-67 of PG&E’s 2025 WMP Update). | Brad Hill | 2024-04-29 | 2024-05-02 | 2024-05-02 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/OEIS_017.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--04 | ACI 23-04 Cross-Utility Collaboration on Best Practicies |  | OEIS | 017 | 1 | 5 | Mona Hedin | Desiree Marton | Carmen Fewless Noel Wickham | Jay Leyno | Aaron Shapiro | Andy Abranches | Yes |  |  |  | Yes | Yes | Yes |  | 2024-05-02 | [16 empty] | 1 | Carmen Fewless Noel Wickham | Jay Leyno | Mona Hedin | Desiree Marton | Aaron Shapiro | 5 |  |  |  |  | completed | 0 | 0 | 0 | 0
617 | OEIS | 018 | OEIS_018 | 2 | OEIS_018_Q2 | Regarding Back-Up Batteries Completed in 2023: In its WMP Update, PG&E states that it completed 4,700 units of new or replacement portable and permanent batteries (PS-06). a. Provide, in tabular format, a list of accounts that received a battery in 2023, including: i. Whether the battery was new or a replacement. ii. Whether that battery was portable or permanent. iii. Whether | Please see attachment “WMP-Discovery2023-2025_DR_OEIS_018- Q002Atch01CONF.xlsx” for the requested information. Note that all batteries received by customers through the Portable Battery Program or the Disability Disaster Access & Resources program in 2023 were fully subsidized. | Brad Hill | 2024-05-03 | 2024-05-08 | 2024-05-08 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/OEIS_018.zip | 1 | N/A | 8.5.3 | 8.0 Wildfire Mitigations | 8.5.3 Engagement with Access and Functional Needs Populations | 2.1.2 PS-06: Provide 12,000 cumulative new or replacement portable batteries |  | OEIS | 018 | 2 | 1 | Mona Hedin | Kaet Bulkowski | Megan Geraci/Jacklin Campos/Perez | Vitaly Tyurin | Aaron Shapiro | Vitaly Tyurin | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | 2024-05-08 | [16 empty] | 2 | Megan Geraci/Jacklin Campos/Perez | Shawn Holder | Mona Hedin | TBD | Aaron Shapiro | 1 |  |  |  |  | completed | 0 | 0 | 0 | 0
650 | CPUC - SPD (Safety Policy Division) | 016 | CPUC - SPD (Safety Policy Division)_016 | 7 | CPUC - SPD (Safety Policy Division)_016_Q7 | Mitigation Effectiveness a. Regarding use of the WBCA tool to incorporate cost effectiveness components, reliability considerations, and location-specific mitigation effectiveness calculations, as described in the 2025 WMP Update on page 51, list all mitigations which will employ location-specific mitigation effectiveness calculations when WBCA is adopted, with their WMP Initiative Activity name and Utility Initiative Tracking ID code. b. Provide the data used to create Table ACI-PG&E-23-05-3. i. SPD expects to see a CPZ-level breakdown of the risk and the expected mitigation effectiveness for each driver. ii. The data should include how the CPZ data is aggregated up to the level in the Table ACI-PG&E-23-05-3, and an explanation for how this occurs. iii. The data should also include how the risk for each driver is aggregated and an explanation for how this occurs. iv. Provide the data used to determine each mitigation effectiveness. c. PG&E stated the following: Another compounding factor is PG&E’s heavily forested service territory in the highest wildfire risk portions of High-Fire Threat District (HFTD). It is common for vegetation induced faults to bring down distribution wires in a way that they touch each other and create line-to-line or two-line-to-ground faults. These types of faults are not as likely in service territories that have more chapparal or low-lying brush vegetation because it is far less common for overhead strike potential to introduce multi-phase system fault conditions. Implementation of REFCL in areas with significant large tree habitats with high tree strike potential would not produce the same effectiveness as areas like California’s high desert. An accurate assessment of the effectiveness of REFCL systems requires consideration of the specific geographic risk factors for the circuits upon which this technology is installed. Provide data which substantiates this claim. Provide data which shows the prevalence of SLG, LL, LLG, LLL and LLLG faults on circuits in the HFTD. Provide data which shows the prevalence of SLG, LL, LLG, LLL LLLG faults for vegetation induced faults. Discuss how effective PG&E expects REFCL to be for each fault type and risk driver. | a. The WBCA will evaluate different mitigations and combinations of mitigations that will likely change as we introduce new mitigation technology onto our system and/or replace existing mitigation approaches with new ones. Additionally, mitigations may change as we receive additional guidance from Energy Safety. The current list of alternatives that PG&E can analyze with the WBCA are shown in Table 1 below. The WBCA analyzes location-specific information at the circuit segment level for alternatives 1 through 8. The WBCA does not analyze Alternative 9, REFCL, because it can only be analyzed at the substation level. The WBCA cannot conduct circuit segment level analysis of REFCL. The WMP Initiative Activity name and Tracking ID for the alternative mitigations are shown in Table 1 below. Table 1 – WBCA Mitigation Alternatives WMP Activity Name and Tracking IDs Alternative WMP Activity Name WMP Tracking ID Notes Alternative 1 - Baseline Represents the current state of the grid and is not a named WMP initiative. Alternative 2 - Underground Primary 10K Undergrounding GH-04 Alternative 3 - Underground All PG&E is evaluating its approach regarding the undergrounding of secondary and service lines. Underground All is not a named WMP initiative. Alternative 4 - Covered Conductor with EPSS and Downed Conductor Detection (DCD) System Hardening – Distribution Protective Equipment and Device Settings GH-01 GM-07 Alternative 5 - Bare Conductor Rebuild with EPSS and DCD Downed Conductor Detection Protective Equipment and Device Settings GM-06 GM-07 Alternative 6 – Line Removal with Remote Grid 10K Undergrounding GH-04 Line removal with remote grid is included in PG&E’s overall system hardening program. Alternative 7 - EPSS including DCD/Partial Voltage with Bare Conductor Protective Equipment and Device Settings GM-07 Bare conductor is not a named WMP initiative. Alternative 8 – EPSS, DCD and PSPS with Bare Conductor While we originally analyzed this alternative that was included in WMP ACI 23-05, it is not included in the Attachment 1 because inclusion of PSPS as part of long term mitigation planning it is not an alternative we are considering. Alternative 9 – REFCL REFCL is not a named WMP initiative. It was considered but not selected for this WMP period. (See PG&E 2023-2025 WMP R5, pp. 283-284). Additionally, because REFCL cannot be analyzed at the circuit segment level it is not included in Attachment 1. Alternative 10 – Covered Conductor System Hardening – Distribution GH-01 b. Please see “WMP-Discovery2023-2025_DR_SPD_016-Q007Atch01.xlsx.” i. The data used to create Table ACI-PG&E-23-05-3 does not use CPZ-level breakdown of the risk. Instead, Table ACI-PG&E-23-05-3 utilizes subject matter expertise review of the outage combinations, and subsequently, applies this against historical risk events in order to derive the effectiveness for the mitigation. See the following worksheets in the attachment with the associated data provided: • The worksheet titled ‘Outage_HFTD’ shows the risk event data. • The worksheet titled ‘Grid Hardening SME Input_v3’ shows the SME review of each outage combination and the mitigation solution’s potential effectiveness. • The worksheet titled ‘Mapping’ shows the conversion of SME defined effectiveness to percentage effectiveness (e.g. low = 20%). • The worksheet titled ‘Result’ shows the computed effectiveness across the historical outage dataset to arrive at the summarized values of Table ACI-PG&E-23-05-3. ii. Not applicable. As discussed in subpart b(i) above, the CPZ data is not aggregated up to the level in the Table ACI-PG&E-23-05-3. iii. Not applicable. The risk for each driver at the CPZ level was not aggregated to calculate the mitigation effectiveness for Table ACI-PG&E-23-05-3. iv. The data used to create Table ACI-PG&E-23-05-3 is shown in attachment “WMP-Discovery2023-2025_DR_SPD_016-Q007Atch01.xlsx.” c. The original response was not provided from a predefined dataset but rather based upon subject matter expertise. Please see “WMP-Discovery2023-2025_DR_SPD_016-Q007Atch02.xlsx,” which is a summary of EPSS outages from 2022 to present and which demonstrates that a high percentage of primary system faults for known vegetation causes involve multiple phases based upon captured relay target information. Table 2 below summarizes the information in this attachment. Events involving multiple phases would show a decreased effectiveness of REFCL on ignitions as REFCL is only effective for single line to ground faults. Various correlations can be observed showing an increased probability of multi-phase faults due to increasing HFTD tier as well as tree strike potential risk. Table 2. Vegetation Caused Faults on EPSS Circuits (2022 – Present) Fault Condition % of Events % Circuit primary overhead miles in Tier 2 % Circuit Primary Overhead Miles in Tier 3 % of Priority Tree Mitigation Multiphase Target 54.50% 52.39% 55.50% 57.26% Single Phase Target 43.67% 44.69% 42.47% 39.85% Fault Condition % of Events % Circuit primary overhead miles in Tier 2 % Circuit Primary Overhead Miles in Tier 3 % of Priority Tree Mitigation No Fault Target 1.83% 2.92% 2.03% 2.89% | Henry Sweat | 2024-05-30 | 2024-06-20 | 2024-06-20 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_016.zip | 2 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--05 – Updating Grid Hardening Decision Making | ACI 23-05 Updating Grid Hardening Decision Making |  | CPUC - SPD (Safety Policy Division) | 016 | 7 | 7 | Mona Hedin | Nelson Lau | Benson Wong/James Tuccillo | Paul McGregor/Eric Lamoureux (JB Birch on behalf)/Justin Stadler | Aaron Shapiro | Mark Quinlan/Martin Wyspianski | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | 2024-06-20 |  | 6/4/2024 - Extension to 6/19 approved by Wade Greenacre. Kxfk | 6/4/2024 - Extension to 6/19 approved by Wade Greenacre. Kxfk | [13 empty] | 7 | Benson Wong/James Tuccillo | Paul McGregor/Eric Lamoureux (JB Birch on behalf)/Justin Stadler | Mona Hedin | Nelson Lau | Aaron Shapiro | 7 |  |  |  |  | completed | 0 | 0 | 0 | 0
575 | CalPA | Set WMP-44 | CalPA_Set WMP-44 | 5 | CalPA_Set WMP-44_Q5 | Page 57 of PG&E’s 2025 WMP Update states, “Regarding cost effectiveness scores, the undergrounding projects in PG&E’s current workplan were previously selected using a methodology (WDRM V2 and V3) that did not incorporate cost effectiveness scores for individual projects. Therefore, cost effectiveness scores are not available.” a) Define the term “undergrounding project” in the above statement. b) Has PG&E used the outputs from WDRM v4 to calculate the cost effectiveness scores for the undergrounding projects in PG&E’s current workplan? c) If the answer to part (b) is yes, please provide the cost effectiveness scores for all projects in PG&E’s current undergrounding workplan. d) If the answer to part (b) is no, explain why not. e) Does PG&E plan to use the outputs from WDRM v4 to calculate the cost effectiveness scores for the undergrounding projects in PG&E’s current workplan? f) If the answer to part (e) is yes, when does PG&E anticipate completing this analysis? g) If the answer to part (e) is no, explain why not. | a) As stated in PG&E’s Comments on CPUC Safety Policy Division staff’s original proposed guidelines for the SB 884 program (September 27, 2023), PG&E defines a “project” at the circuit segment level (also referred to as circuit protection zone (CPZ)) because our current risk model measures risk at the circuit segment level and does not have more granular risk detail. When projects are scoped and planned for near-term completion (generally within 3 to 4 years), we create sub-projects, or jobs, which will reflect portions of a CPZ. PG&E identifies jobs based on mileage, diversity of risk ranking, dependencies (e.g., easements, environmental permitting issues) and constructability. As the risk models are periodically updated and released, projects may be added to the workplan, reprioritized, or removed. b) No, WDRM v4 has not been used for the current workplan. c) Not applicable, please see the response to subpart (b) above. d) WDRM v2 and v3 were applicable for the current workplan. WDRM v4 analysis is intended to be applied to the workplan for projects that will be completed starting from 2027. PG&E does not currently anticipate completing any projects selected with WDRM v4 in the 2023 GRC period. It is possible, but unlikely, that some of these projects may be completed prior to 2027 based on the timing to complete and construct the project in relation to all other projects in the current workplan. e) No, the current workplan uses WDRM v2 and v3 only. WDRM v4 analysis is intended to be applied to the workplan from 2027. f) Not applicable, please see the response to subpart (e) above. g) Per the requirements of SB-884, PG&E is developing the Wildfire Benefit Cost Analysis (WBCA) tool to evaluate the costs and benefits of undergrounding and other alternative mitigations. PG&E intends to use the outputs of WDRM v4 in the WBCA, which is intended to be applied to the workplan for projects completed starting in 2027. | Holly Wehrman | 2024-04-15 | 2024-04-18 | 2024-04-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_044.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--05 – Updating Grid Hardening Decision Making | ACI 23-05 Updating Grid Hardening Decision Making |  | CalPA | Set WMP-44 | 5 | 7 | Mona Hedin | Mandy Knockaert | Christopher Wong Kamran Bhatti UG Team Jerry Santos Julie Cerio Lucy Morris Benson Wong James Ash | Matthew Whorton Megan Ardell Paul McGregor Jim Gill | Aaron Shapiro | Matt Pender Andy Abranches | Yes | Yes | Yes |  |  | Yes |  |  | 2024-04-18 | [16 empty] | 5 | Christopher Wong Kamran Bhatti UG Team Jerry Santos Julie Cerio Lucy Morris Benson Wong James Ash | Matthew Whorton Megan Ardell Paul McGregor Jim Gill | Mona Hedin | Mandy Knockaert | Aaron Shapiro | 7 |  |  |  |  | completed | 0 | 0 | 0 | 0
574 | CalPA | Set WMP-44 | CalPA_Set WMP-44 | 4 | CalPA_Set WMP-44_Q4 | Page 56 of PG&E’s 2025 WMP Update discusses Undergrounding versus Overhead Hardening. Undergrounding is stated to have greater total permanent risk reduction, but it takes longer and costs more to install. a) Has PG&E conducted an analysis of its transmission and distribution system to determine the estimated remaining useful life of its assets? b) If the answer to part (a) is yes, does PG&E consider the remaining life of assets when evaluating benefits of overhead hardening, which is faster to deploy? c) If the answer to part (a) is yes, please provide any applicable analysis relevant to the condition of PG&E’s transmission and distribution system assets. | a) No, the Wildfire Transmission Risk Model (WTRM) and Wildfire Distribution Risk Model (WDRM) incorporate age, in addition to other parameters, to assess risk based on the probability of an asset failure leading to an ignition occurring and the consequence of a wildfire if it were to occur. The model helps determine whether assets may require mitigation response. For example, an asset with high wildfire risk may drive the response of a detailed inspection, which could then result in the need to replace or repair the asset. The age of the asset when it requires replacement pinpoints the end of its useful life. Therefore, while the WTRM and WDRM help determine what assets are most likely to fail, they do not specifically predict the date an asset will fail, i.e. its “useful life.” b) Not applicable, please see the response to subpart (a) above. c) Not applicable, please see the response to subpart (a) above. | Holly Wehrman | 2024-04-15 | 2024-04-18 | 2024-04-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_044.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--05 – Updating Grid Hardening Decision Making | ACI 23-05 Updating Grid Hardening Decision Making |  | CalPA | Set WMP-44 | 4 | 3 | Mona Hedin | Mandy Knockaert | Issam El Ayadi Tiffany Pazdan Matthew Horowitz Michelle Sakamoto Natalie Dawley Benson Wong James Ash | Jim Gill | Aaron Shapiro | Andy Abranches/Martin Wyspianski | Yes |  | Yes |  |  | Yes |  |  | 2024-04-18 | [16 empty] | 4 | Issam El Ayadi Tiffany Pazdan Matthew Horowitz Michelle Sakamoto Natalie Dawley Benson Wong James Ash | Jim Gill | Mona Hedin | Mandy Knockaert | Aaron Shapiro | 3 |  |  |  |  | completed | 0 | 0 | 0 | 0
573 | CalPA | Set WMP-44 | CalPA_Set WMP-44 | 3 | CalPA_Set WMP-44_Q3 | Page 54 of PG&E’s 2025 WMP Update states, “To determine circuit segment-level mitigation effectiveness, the WBCA will adjust for the outage combinations likely to occur on a given circuit segment, their estimated frequency, and their contribution to overall risk on the circuit segment.” a) Will the WBCA adjust for outage combinations on a scale smaller than a circuit segment? For example, a very long circuit segment may not have uniform outage characteristics along its entire length. b) If the answer to part (a) is yes, please explain the methods and criteria PG&E plans to use to adjust the WBCA for outage combinations on a scale smaller than a circuit segment. c) If the answer to part (a) is no, please explain why not. | a) The WBCA will not adjust for outage combinations on a scale smaller than a circuit segment. b) Not applicable, please see the response to subpart (a) above. c) Outputs from the Wildfire Distribution Risk Model (WDRM) are aggregated to the circuit segment level as the best model view for system hardening work. While individual pixel level data is available, the circuit segment view has less noise than the pixel level output. As such, the mean probability of ignition for each sub-driver, as output from WDRM, is assumed to be uniform across an entire circuit segment. Accordingly, the risks from individual sub-driver “outage combinations” are assumed to be uniform across that circuit segment as well. | Holly Wehrman | 2024-04-15 | 2024-04-18 | 2024-04-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_044.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--05 – Updating Grid Hardening Decision Making | ACI 23-05 Updating Grid Hardening Decision Making |  | CalPA | Set WMP-44 | 3 | 3 | Mona Hedin | Mandy Knockaert | Benson Wong James Ash | Paul McGregor | Aaron Shapiro | Andy Abranches | Yes | Yes | Yes |  |  | Yes | Yes |  | 2024-04-18 | [16 empty] | 3 | Benson Wong James Ash | Paul McGregor | Mona Hedin | Mandy Knockaert | Aaron Shapiro | 3 |  |  |  |  | completed | 0 | 0 | 0 | 0
572 | CalPA | Set WMP-44 | CalPA_Set WMP-44 | 2 | CalPA_Set WMP-44_Q2 | Page 54 of PG&E’s 2025 WMP Update states, “To determine circuit segment-level mitigation effectiveness, the WBCA will adjust for the outage combinations likely to occur on a given circuit segment, their estimated frequency, and their contribution to overall risk on the circuit segment.” a) Please describe the methods used in the WBCA to adjust for the outage combinations likely to occur on a given circuit segment. b) Please describe the methods used in the WBCA to adjust for the estimated frequency of outage combinations on a given circuit segment. c) Please describe the methods used in the WBCA to adjust for the contribution of outage combinations to overall risk on a given circuit segment. | a) As stated on pp. 51-52 of PG&E’s 2025 WMP Update, “outage combinations”, refers to “potential ignition(s) resulting from particular combinations of unplanned outage events and equipment attributes”. The likely “outage combinations” on a given circuit segment are based on the fifteen unique probability of ignition risk subdrivers output from Version 3 of the Wildfire Distribution Risk Model (WDRM v3). These include: • Vegetation (Branch); • Vegetation (Trunk); • Vegetation (other); • Animal (Bird); • Animal (Squirrel); • Animal (other); • Third Party (Balloon); • Third Party (Vehicle); • Third Party (other); • Primary Conductor; • Secondary Conductor; • Equipment (Support Structure); • Equipment (Transformer); • Equipment (Voltage Control); and • Equipment (other). b) As described above, each circuit segment has a unique likelihood of an outage and ignition based on the 15 subdrivers from WDRM v3. In the WBCA, based on the mitigation effectiveness of associated with each individual subdriver, the residual frequency on a given circuit segment can be computed. As a hypothetical example, the mitigation effectiveness for a program is 50% for vegetation (branch) and 60% for equipment (support structure). Circuit segment #1 has a vegetation (branch) subdriver frequency of 0.2 and equipment (support structure) subdriver of 0.8. Circuit segment #2 has a vegetation (branch) subdriver frequency of 0.5 and equipment (support structure) subdriver of 0.5. The resulting mitigation frequency for CS #1 is (0.2)*(1-50%) + (0.8)*(1-60%) = 0.42 frequency or 58% effective while CS #2 mitigation frequency is (0.5)*(1-50%) + (0.5)*(1-60%) = 0.45 or 55% effective. As a result, even though the circuit segments start with the same baseline frequency, due to the difference in the frequency of the individual 15 subdrivers and its associated mitigation effectiveness, the resulting change in frequency is different for each circuit segment. c) Similar to the response to part b, each circuit segment has a unique risk based on the 15 subdrivers from WDRM v3. In the WBCA, based on the mitigation effectiveness of associated with each individual subdriver, the residual risk on a given circuit segment can be computed. As a hypothetical example, the mitigation effectiveness for a program is 50% for vegetation (branch) and 60% for equipment (support structure). Circuit segment #1 has a vegetation (branch) subdriver risk 2 and equipment (support structure) subdriver of 8. Circuit segment #2 has a vegetation (branch) subdriver risk of 5 and equipment (support structure) subdriver of 5. The resulting mitigation risk for CS #1 is (2)*(1-50%) + (8)*(1-60%) = 4.2 risk or 58% effective while CS #2 mitigation frequency is (5)*(1-50%) + (5)*(1-60%) = 4.5 or 55% effective. As a result, even though the circuit segments start with the same baseline risk, due to the difference in the risk of the individual 15 subdrivers and its associated mitigation effectiveness, the resulting change in risk is different for each circuit segment. | Holly Wehrman | 2024-04-15 | 2024-04-18 | 2024-04-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_044.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--05 – Updating Grid Hardening Decision Making | ACI 23-05 Updating Grid Hardening Decision Making |  | CalPA | Set WMP-44 | 2 | 3 | Mona Hedin | Mandy Knockaert | Benson Wong James Ash | Paul McGregor | Aaron Shapiro | Andy Abranches | Yes | Yes | Yes |  |  | Yes | Yes |  | 2024-04-18 | [16 empty] | 2 | Benson Wong James Ash | Paul McGregor | Mona Hedin | Mandy Knockaert | Aaron Shapiro | 3 |  |  |  |  | completed | 0 | 0 | 0 | 0
571 | CalPA | Set WMP-44 | CalPA_Set WMP-44 | 1 | CalPA_Set WMP-44_Q1 | Page 52 of PG&E’s 2025 WMP Update states: We assessed the effectiveness of each of the mitigation alternatives against more than 2,200 outage combinations that have occurred in PG&E’s HFTD during wildfire season. PG&E SMEs reviewed each of the outage combinations…and assigned an effectiveness rating for each mitigation at preventing each outage combination. a) How many SMEs were involved in reviewing outage combinations and assigning effectiveness ratings? b) Please describe the methods used by PG&E SMEs to review outage combinations and assign effectiveness ratings. c) Do the 2,200 outage combinations represent a specific time period? Please explain your answer. d) Do the 2,200 outage combinations include outage combinations that occurred in PG&E’s HFRA but not in the HFTD? Please explain your answer. | a) For the initial qualitative assessment, experts in the Electric Distribution Engineering, EPSS, Remote Grid, Electric Distribution Reliability and REFCL teams were engaged with the Grid Design team. Three experts on the Design team reviewed the data from Grid Design. In addition, several data analysts were included in the calculations of the effectiveness. b) The following steps were taken to review outage combinations and determine effectiveness ratings: • Outages were initially reviewed by similar outage (or outage cause) types, for example splice failure, vegetation, bird, etc.; • Reviewed line by line to confirm accuracy; and • Methodology checked and confirmed by additional Grid Design SME’s. c) The outage cause, equipment outage combinations were based on the 2015-2022 study period’s outage history in the HFTD. d) No, the study that was produced for the WMP was a snapshot of the HFTD information only. There is currently no tool that can pull HFRA information for each outage; the existing tool was only designed to perform spatial analysis on HFTD layer and information. | Holly Wehrman | 2024-04-15 | 2024-04-18 | 2024-04-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_044.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--05 – Updating Grid Hardening Decision Making | ACI 23-05 Updating Grid Hardening Decision Making |  | CalPA | Set WMP-44 | 1 | 4 | Mona Hedin | Mandy Knockaert | UG Team Jerry Santos Julie Cerio Lucy Morris SH Team | Jim Gill Megan Ardell | Aaron Shapiro | Matt Pender/Martin Wyspianski | Yes | Yes | Yes |  |  | Yes |  |  | 2024-04-18 | [16 empty] | 1 | UG Team Jerry Santos Julie Cerio Lucy Morris SH Team | Jim Gill Megan Ardell | Mona Hedin | Mandy Knockaert | Aaron Shapiro | 4 |  |  |  |  | completed | 0 | 0 | 0 | 0
556 | CalPA | Set WMP-43 | CalPA_Set WMP-43 | 9 | CalPA_Set WMP-43_Q9 | The table lists the assumption, “EPSS and DCD are only active when conditions are greater than R1.” a) State the basis for this assumption. b) Are weather events an applicable attribute in the outage combinations used in PG&E’s mitigation effectiveness assessments? c) Please provide a list of all applicable attributes to be used in outage combinations. | a) EPSS and DCD settings are not engaged in the system when the FPI rating is R1, which forms the basis for this assumption. However, the calculations behind engaging EPSS are complex and, for more information, please see our Base 2023- 2025 WMP, R5 (April 2, 2024) on page numbers 570-571 and our 2022 Revised WMP (July 26, 2022) on page numbers 848-852.1 b) No, a specific weather attribute is not directly included in the outage combination analysis. c) For alternative 1-9, each considered the basic cause, supplemental cause, failed/involved equipment, and equipment condition. Additionally, Alt 9 considered the type of outage i.e., phase-to-phase, single line-to-ground, and double line-toground to distinguish REFCL’s impact as it has a specific effectiveness for each fault type. The FPI rating was considered in the analysis to distinguish when specific setting configurations would be enabled for REFCL. | Holly Wehrman | 2024-04-12 | 2024-04-17 | 2024-04-17 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_043.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--05 – Updating Grid Hardening Decision Making | ACI 23-05 Updating Grid Hardening Decision Making |  | CalPA | Set WMP-43 | 9 | 3 | Mona Hedin | Saritha Basani | Patrick McCabe | Jim Gill | Aaron Shapiro | Martin Wyspianski | Yes | Yes | Yes |  |  | Yes | Yes |  | 2024-04-17 | [16 empty] | 9 | Patrick McCabe | Jim Gill | Mona Hedin | Saritha Basani | Aaron Shapiro | 3 |  |  |  |  | completed | 0 | 0 | 0 | 0
555 | CalPA | Set WMP-43 | CalPA_Set WMP-43 | 8 | CalPA_Set WMP-43_Q8 | The table lists the assumption, “Analysis assumes no Overhead degradation for life of the asset.” a) State the basis for this assumption. b) Does PG&E have plans to include overhead degradation of assets in its mitigation effective analysis in the future? c) How does the WBCA consider benefits and costs over the lifetime of the asset if the analysis assumes no overhead degradation? | a) PG&E chose to consistently assume no degradation of assets in each effectiveness calculation. Given that the book life of overhead versus underground assets is comparable, a degradation factor was not considered necessary within the analysis. b) PG&E does not currently have plans to integrate degradation of assets into effectiveness analyses. c) The net present value of installation costs plus expected lifetime operations and maintenance costs are considered in the WBCA. Similarly, the net present value of risk reduction benefits is considered over the expected life of the asset. | Holly Wehrman | 2024-04-12 | 2024-04-17 | 2024-04-17 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_043.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--05 – Updating Grid Hardening Decision Making | ACI 23-05 Updating Grid Hardening Decision Making |  | CalPA | Set WMP-43 | 8 | 3 | Mona Hedin | Andrew Trombley | James Ash | Paul McGregor | Aaron Shapiro | Andy Abranches | Yes |  | Yes |  |  | Yes | Yes |  | 2024-04-17 | [16 empty] | 8 | James Ash | Paul McGregor | Mona Hedin | Andrew Trombley | Aaron Shapiro | 3 |  |  |  |  | completed | 0 | 0 | 0 | 0
554 | CalPA | Set WMP-43 | CalPA_Set WMP-43 | 7 | CalPA_Set WMP-43_Q7 | The table lists the assumption, “Mitigation effectiveness for other Environmental caused outages: None for Overhead and All for Underground.” State the basis for this assumption. | The referenced table should not have reflected “None for Overhead and All for Underground” for mitigation effectiveness for other environmental caused outages. Some outage combinations did have a savings assigned in the final study, these were mostly related to overhead transformer equipment failures where enhanced safety settings or overhead hardening would mitigate risk. The environmental/external basic cause is assigned to an outage during a significant weather or environmental event. Overhead construction would still be susceptible to earthquakes, erosion, lightning and ice events. The enhanced safety settings and overhead hardening would still apply for transformer and equipment failure related outages and reduce the chance of an ignition for some environmental/external outages. | Holly Wehrman | 2024-04-12 | 2024-04-26 | 2024-04-17 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_043.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--05 – Updating Grid Hardening Decision Making | ACI 23-05 Updating Grid Hardening Decision Making |  | CalPA | Set WMP-43 | 7 | 0 | Mona Hedin | Andrew Trombley | Patrick McCabe | Jim Gill | Aaron Shapiro | Martin Wyspianski | Yes | Yes | Yes |  |  | Yes | Yes |  | 2024-04-26 |  | yes | 4/15 - j1oz - new due date per call with CALPA | [13 empty] | 7 | Patrick McCabe | Jim Gill | Mona Hedin | Andrew Trombley | Aaron Shapiro | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
553 | CalPA | Set WMP-43 | CalPA_Set WMP-43 | 6 | CalPA_Set WMP-43_Q6 | The table notes, “Not all substations are capable of having REFCL applied, and it cannot be isolated to a circuit segment only.” a) How many substations does PG&E have that serve circuit segments within its HFTD/HFRA? b) How many of the substations in your response to part (a) are not capable of having REFCL applied? c) Provide a list of the substations in part (b). For each substation, state the reasons why REFCL cannot be applied. d) If PG&E has not conducted the analysis necessary to respond to parts (b) and (c) in full, please explain why not. | a) Approximately 435 distribution substations serve circuit segments within HFTD/HFRA. b) After preliminary screening, 302 of these distribution substations are not feasible for REFCL deployment. c) Please see attachment WMP-Discovery2023-2025_DR_CalAdvocates_043- Q006Atch01.xlsx, which includes a list of all substations within an HFTD/HFRA (column A). Column B (Pass/Fail) denotes if the substation meets (Pass) or does not meet (Fail) the requirements where REFCL can or cannot be applied. Substations that are categorized as not feasible (Fail) in the analysis are due to one or a combination of the following reasons below: • Column C (kV): Connected circuits are not 12 kV; • Column D (3 Wire or 4 Wire): Substations have 4-wire multi-grounded distribution circuits connected to the substation or a mix of connections. • Column E (HFTD Miles): Total HFTD/HFRA circuit miles is less than twenty miles; • Column F (Auto in the Sub): Autotransformer located inside the substation. • Column G (Field Auto Analysis): Circuit mileage downstream of autotransformers is greater than twenty percent; and • Column I (Coil Charge Amps): The total charging current exceeds 167 Amps, for each Distribution Substation bank (number of banks per substation outlined in Column H). The Coil Charge Amps are calculated as an alternative way to measure the proportion of a circuit underground (less than 50% of circuit is underground). d) Not applicable, please see the responses provided in subparts (b) and (c) above. | Holly Wehrman | 2024-04-12 | 2024-04-26 | 2024-04-17 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_043.zip | 1 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--05 – Updating Grid Hardening Decision Making | ACI 23-05 Updating Grid Hardening Decision Making |  | CalPA | Set WMP-43 | 6 | 4 | Mona Hedin | Saritha Basani | Patrick McCabe | Jim Gill | Aaron Shapiro | Martin Wyspianski | Yes | Yes | Yes |  |  | Yes | Yes |  | 2024-04-26 |  | yes | 4/15 - j1oz - new due date per call with CALPA | [13 empty] | 6 | Patrick McCabe | Jim Gill | Mona Hedin | Saritha Basani | Aaron Shapiro | 4 |  |  |  |  | completed | 0 | 0 | 0 | 0
552 | CalPA | Set WMP-43 | CalPA_Set WMP-43 | 5 | CalPA_Set WMP-43_Q5 | Alternative 8 is the only alternative that appears to include PSPS. a) Is PSPS considered in any of the other alternatives? b) Why is the effectiveness for alternative 8 higher than similar alternatives that appear to include more mitigation techniques? c) If the answer to part (a) is no, why not? | a) No, PSPS is not considered in any of the other alternatives. b) This effectiveness value was calculated in a different manner from others in the study. For alternative 8, the observed effectiveness of PSPS (78%) was applied to the residual risk post-alternative 7. This resulted in an effectiveness of: 60.4% + 78% x (100%-60.4%) = 91.3%. With the exception of alternatives 8 & 9, each effectiveness value was calculated based on each mitigation’s expected effectiveness in preventing an ignition resulting from over 2,000 unplanned failure modes (outage types) captured in PG&E’s historical HFTD outage dataset between 2015 and 2022. The study for PSPS cannot be completed in this same manner because an unplanned outage cannot occur simultaneously to pro-active PSPS de-energization. | Holly Wehrman | 2024-04-12 | 2024-04-17 | 2024-04-17 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_043.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--05 – Updating Grid Hardening Decision Making | ACI 23-05 Updating Grid Hardening Decision Making |  | CalPA | Set WMP-43 | 5 | 3 | Mona Hedin | Andrew Trombley | James Ash | Paul McGregor | Aaron Shapiro | Andy Abranches | Yes |  | Yes |  |  | Yes | Yes |  | 2024-04-17 | [16 empty] | 5 | James Ash | Paul McGregor | Mona Hedin | Andrew Trombley | Aaron Shapiro | 3 |  |  |  |  | completed | 0 | 0 | 0 | 0
551 | CalPA | Set WMP-43 | CalPA_Set WMP-43 | 4 | CalPA_Set WMP-43_Q4 | The table notes, “All of these effectiveness values represent a blended average effectiveness at the circuit segment level with the exception of ‘Alt. 9 – REFCL, CC Overhead, EPSS and DCD’ which is a substation effectiveness score. Not all substations are capable of having REFCL applied, and it cannot be isolated to a circuit segment only.” a) Explain the difference in “substation effectiveness score” and “blended average effectiveness at the circuit segment level.” b) Does alternative nine assume that, for circuits where REFCL cannot be applied to the substation, there are no mitigations applied? c) If the answer to part (b) is yes, state the basis for this assumption. d) Describe how PG&E would implement alternative 9 on circuits served by substations where REFCL could be applied. e) Describe how PG&E would implement alternative 9 on circuits served by substations where REFCL could not be applied. | a) “Substation effectiveness score” starts with a pass/fail preliminary review. All requirements for REFCL must be met to pass. The preliminary screening requirements are: o Single voltage 3 wire 12 kV substation; o Minimum of 20 OH miles in HFTD; o No Autotransformer located inside the substation; o The total charging current not exceeding 167 Amps for each Distribution Transformer Bank in a substation; and o Less than 20% of circuit mileage past autotransformers outside of the substation Blended average effectiveness refers to the average effectiveness of REFCL based on weather days with instantaneous off/on. b) For substations where REFCL cannot be applied due to technical feasibility, we excluded these from the study all together. Therefore, Alternative 9 only shows effectiveness on substations that met the high-level requirements for REFCL implementation. c) The substations that were excluded were not included in the base dataset for the REFCL effectiveness calculation. d) To implement REFCL on these circuits, additional engineering review of the substation layout would be performed to ensure adequate room for installation of the REFCL equipment and review of substation and distribution equipment ratings to identify necessary upgrades to allow for REFCL operation. REFCL would be applied independently of other mitigations. Additional CPZ level review would be needed to determine which segments should receive covered conductor and which should include underground in a blend such that we don’t compromise REFCL. e) PG&E would not implement alternative 9 on substations that do not meet the preliminary review for REFCL requirements. These substations would be evaluated for Alternatives 1-8. | Holly Wehrman | 2024-04-12 | 2024-04-26 | 2024-04-17 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_043.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--05 – Updating Grid Hardening Decision Making | ACI 23-05 Updating Grid Hardening Decision Making |  | CalPA | Set WMP-43 | 4 | 5 | Mona Hedin | Saritha Basani | Patrick McCabe | Jim Gill | Aaron Shapiro | Martin Wyspianski | Yes | Yes | Yes |  |  | Yes | Yes |  | 2024-04-26 |  | yes | 4/15 - j1oz - new due date per call with CALPA | [13 empty] | 4 | Patrick McCabe | Jim Gill | Mona Hedin | Saritha Basani | Aaron Shapiro | 5 |  |  |  |  | completed | 0 | 0 | 0 | 0
550 | CalPA | Set WMP-43 | CalPA_Set WMP-43 | 3 | CalPA_Set WMP-43_Q3 | List the assumptions unique to each of the ten alternatives. | The assumptions for each of the 10 alternatives are as follows. Alt. 1 – Baseline There are no assumed savings or ignition reduction in the Baseline scenario. Alt. 2 – Underground Primary All primary overhead outages for lines that are undergrounded are mitigated, 100% of ignition risk is reduced. Secondary/service conductor phase-to-phase outage ignition reduction is significant, however, there is still a chance for contact failure. Secondary/service conductor phase-to-ground ignition reduction is less than average. No additional ignition risk reduction is achieved via enhanced settings. Alt. 3 – Underground All All primary and secondary overhead outages for lines that are undergrounded are mitigated, 100% of ignition risk is reduced. No additional ignition risk reduction is achieved via enhanced settings. Alt. 4 – Covered Conductor (CC) Overhead with EPSS and DCD Phase-to-phase outage ignition risk is mostly reduced, but overhead construction still leaves potential for ignition. Phase-on-ground and line-to-ground outage ignition reduction was less than average (40%). Splice/jumper failure ignition risk is mostly reduced, but overhead construction still leaves potential for ignition. Pole/crossarm failure ignition risk reduction is significant, but there is still a chance for contact failure. Secondary/service conductor phase-to-phase outage ignition risk reduction is significant but there is still a chance for contact failure. Secondary/service conductor phase-to-ground outage ignition risk reduction was less than average. Additional ignition risk mitigation is achieved via enhanced settings. Alt. 5 – Bare Conductor Rebuild with EPSS and DCD Replacing overhead conductor, including removing splices & replacing jumpers, reduced most of the risk of those conductor ignition types, however, there is still potential for ignition. There is no phase-to-phase and phase-to-ground outage ignition reduction. Additional ignition risk mitigation is achieved via enhanced settings. Alt. 6 – Line Removal with Remote Grid All primary overhead outages are mitigated, there are no overhead ignition events. Secondary/service conductor phase-to-phase outage ignition risk reduction is significant, however, there is still a chance for contact failure. Secondary/service conductor phase-to-ground ignition risk reduction is less than average. There are no additional ignition reductions achieved via enhanced settings. Alt. 7 – EPSS including downed conductor detection (DCD)/Partial Voltage (with bare conductor) Phase-to-phase outage ignition risk is mostly reduced, but overhead construction still leaves potential for ignition. Phase-on-ground and line-to-ground outage ignition reduction was less than average (40%). No effectiveness savings for secondary/service. Alt. 8 – EPSS and PSPS (with bare conductor) The analysis for alternative 8 varies from the prior 7 alternatives due to the inclusion of PSPS. This is because unplanned outages cannot occur simultaneously to pro-active PSPS de-energization. Instead, alternative 7 was used as the basis for step 1 of the analysis to establish the effectiveness of bare conductor with EPSS as 60.4%. Subsequently, the observed effectiveness of PSPS, 78%, was added as an incremental reduction to the residual risk post-alternative 7. The resulting calculation is shown below: Effectiveness = 60.4% + 78% x (100%-60.4%) = 91.3% Alt. 9 – Rapid Earth Fault Current Limiter (REFCL), CC Overhead, EPSS and DCD REFCL only mitigates risk for phase to ground faults. REFCL Transient Outage (90%) – Transient type faults that the three second delay would prevent from impacting the system. Savings also applied to unknown cause outages with line-to-ground fault targets. Additionally, with instantaneous setting enabled REFCL Single Line to Ground 80% effective, REFCL Double Line to Ground faults 65% effective. Additionally, please see the response to Request No. 6 for additional details of high-level bank screening assumptions. Covered Conductor Rebuild – New The analysis for Covered Conductor Rebuild – New mirrors the baseline assumptions of Alternative 4 without considering EPSS/DCD | Holly Wehrman | 2024-04-12 | 2024-04-17 | 2024-04-17 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_043.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--05 – Updating Grid Hardening Decision Making | ACI 23-05 Updating Grid Hardening Decision Making |  | CalPA | Set WMP-43 | 3 | 0 | Mona Hedin | Saritha Basani | Patrick McCabe | Jim Gill | Aaron Shapiro | Martin Wyspianski | Yes | Yes |  |  |  | Yes | Yes |  | 2024-04-17 |  | Yes | 4/15 - j1oz - new due date per call with CALPA | [13 empty] | 3 | Patrick McCabe | Jim Gill | Mona Hedin | Saritha Basani | Aaron Shapiro | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
549 | CalPA | Set WMP-43 | CalPA_Set WMP-43 | 2 | CalPA_Set WMP-43_Q2 | The blended average effectiveness for alternative 9 (REFCL with covered conductor, EPSS, and DCD) is lower than alternative 4 (covered conductor with EPSS). a) Why does the effectiveness for alternative 9 appear lower than alternative 4, although alternative 9 appears to include more mitigation techniques? | The reported blended average effectiveness for Alt 9 was based on a study focused on a specific subset of circuits and associated substations where REFCL could be utilized. Please see the response to Request No. 6 for details on this study. The effectiveness of Alternative 9 is less in comparison to that of the full population in the Alternative 4 study primarily due to the following reasons: (1) Different study periods were used to determine the outages addressed by each alternative based on data availability (2017 – 2020 for Alt. 9 REFCL and 2015- 2022 for Alt. 4), and (2) The Alt 9 effectiveness results were based on 133 substations vs. 435 substations (that were split into CPZ’s) studied in Alt 4. The blend of outages and mitigations assessed for each alternative resulted in different overall effectiveness values. | Holly Wehrman | 2024-04-12 | 2024-04-17 | 2024-04-17 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_043.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--05 – Updating Grid Hardening Decision Making | ACI 23-05 Updating Grid Hardening Decision Making |  | CalPA | Set WMP-43 | 2 | 1 | Mona Hedin | Saritha Basani | System Hardening- Brad Koelling/Merih Tekeste /UG | Megan Ardell/Jim Gill | Aaron Shapiro | Matt Pender/Martin Wyspianski | Yes | Yes | Yes |  |  | Yes |  |  | 2024-04-17 | [16 empty] | 2 | System Hardening- Brad Koelling/Merih Tekeste /UG | Megan Ardell/Jim Gill | Mona Hedin | Saritha Basani | Aaron Shapiro | 1 |  |  |  |  | completed | 0 | 0 | 0 | 0
548 | CalPA | Set WMP-43 | CalPA_Set WMP-43 | 1 | CalPA_Set WMP-43_Q1 | There does not appear to be an option of covered conductor with both EPSS and DCD. a) Did PG&E consider an alternative that consists of covered conductor with EPSS and DCD? b) If the answer to part (a) is yes, why is this option not included as one of the possible alternatives in the WBCA? c) If the answer to part (a) is no, why not? | a) Yes, PG&E did consider an alternative option consisting of covered conductor with both EPSS and DCD, which is provided in Table ACI-PG&E-23-05-3 as, “Alt. 4 – Covered conductor (CC) Overhead with EPSS.” Please note, this option is not labeled in the table as DCD enabled; however, all EPSS options include DCD. b) Please see the response to subpart (a). The Alt. 4 option referenced above is included in one of the possible alternatives in the WBCA. c) Please see the response to subpart (a). | Holly Wehrman | 2024-04-12 | 2024-04-17 | 2024-04-17 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_043.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--05 – Updating Grid Hardening Decision Making | ACI 23-05 Updating Grid Hardening Decision Making |  | CalPA | Set WMP-43 | 1 | 3 | Mona Hedin | Saritha Basani | Brad Koelling | Jim Gill | Aaron Shapiro | Martin Wyspianski | Yes | Yes | Yes |  |  | Yes | Yes |  | 2024-04-17 | [16 empty] | 1 | Brad Koelling | Jim Gill | Mona Hedin | Saritha Basani | Aaron Shapiro | 3 |  |  |  |  | completed | 0 | 0 | 0 | 0
513 | CalPA | Set WMP-40 | CalPA_Set WMP-40 | 7 | CalPA_Set WMP-40_Q7 | PG&E states on page 51 of its 2025 WMP Update that, in response to ACI PG&E-23-05 – Updating Grid Hardening Decision Making, “PG&E is developing a WBCA [Wildfire Benefit Cost Analysis] tool to incorporate cost effectiveness components, reliability considerations, and location-specific mitigation effectiveness calculations.” PG&E further states that undergrounding projects “scoped with the WBCA in 2024 and 2025 will likely have a completion date in 2027 or later.” a) Will the WBCA tool be used to scope any projects that will be tracked in the System Hardening Accountability Report required by D.23-11-069? 7 b) If the answer to part (a) is yes, please explain how this will be identified in the SHAR. c) If the answer to part (a) is yes, please identify any changes to the SHAR template (e.g. adding fields) that would need to be made to include the necessary information to track such projects. d) Does PG&E expect to request any changes to the SHAR to facilitate tracking projects scoped using the WBCA? Please explain your response. | a. No, the System Hardening Accountability Report (SHAR) required by D.23-11-069 will only include projects completed in the GRC period (2023 – 2026). Project details will not be included for projects that will be completed in 2027 and beyond. At this time, we are intending for projects selected using the WBCA tool in accordance with SB 884 to be completed in 2027 and beyond. In the event projects selected using the WBCA are planned for completion during the GRC time period (2023-2026), these projects will be tracked in the SHAR as required by D.23-11-069. b. Not applicable, please see the response to subpart (a) above. c. Not applicable, please see the response to subpart (a) above. d. No, please see the response to sub-part (a) above for the requested explanation. | Miles Gordon | 2024-04-05 | 2024-04-10 | 2024-04-10 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_040.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--05 – Updating Grid Hardening Decision Making | ACI 23-05 Updating Grid Hardening Decision Making |  | CalPA | Set WMP-40 | 7 | 4 | Mona Hedin | Andrew Trombley Alex Quintana | System Hardening Merih Tekeste Brad Koelling Heidi Ramos UG Data Requests Jerry Santos Julie Cerio Lucy Morris | Megan Ardell | Aaron Shapiro | Matt Pender | Yes | Yes | Yes |  | Yes |  | Yes |  | 2024-04-10 | [16 empty] | 7 | System Hardening Merih Tekeste Brad Koelling Heidi Ramos UG Data Requests Jerry Santos Julie Cerio Lucy Morris | Megan Ardell | Mona Hedin | Andrew Trombley Alex Quintana | Aaron Shapiro | 4 |  |  | DRU13430 |  | completed | 0 | 0 | 0 | 0
534 | MGRA | Data Request No. 9 | MGRA_Data Request No. 9 | 12 | MGRA_Data Request No. 9_Q12 | Table ACE PG&E-23-06-01 Please provide the slides presented at these workshops, redacted for any confidential material. | Please reference the table below for presentation materials for the workshops identified. Workshop Title Attachment Name Kickoff and Corrosion Testing Date: May 3, 2023 WMP-Discovery2023-2025_DR_MGRA_009-Q012Atch01.pdf Aging Susceptibility Date: June 12, 2023 WMP-Discovery2023-2025_DR_MGRA_009-Q012Atch02.pdf New Technologies Date: July 17, 2023 WMP-Discovery2023-2025_DR_MGRA_009-Q012Atch03.pdf Maintenance and Inspections Date: July 24, 2023 WMP-Discovery2023-2025_DR_MGRA_009-Q012Atch04.pdf Effectiveness Testing Date: August 7, 2023 WMP-Discovery2023-2025_DR_MGRA_009-Q012Atch05.pdf Workshop Title Attachment Name New Technologies – EFD Date: September 20, 2023 WMP-Discovery2023-2025_DR_MGRA_009-Q012Atch06.pdf New Technologies Date: November 8, 2023 WMP-Discovery2023-2025_DR_MGRA_009-Q012Atch07.pdf | Joseph Mitchell | 2024-04-08 | 2024-04-11 | 2024-04-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_009.zip | 7 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23-06 – Continuation of Grid Hardening Joint Studies | ACI 23-06 Continuation of Grid Hardening Joint Studies |  | MGRA | Data Request No. 9 | 12 | 0 | Mona Hedin | Mandy Knockaert | Ricky Harris | Andy Abranches | Aaron Shapiro | Andy Abranches |  |  | Yes |  | Yes | Yes |  |  | 2024-04-11 | [16 empty] | 12 | Ricky Harris | Andy Abranches | Mona Hedin | Mandy Knockaert | Aaron Shapiro | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
588 | CalPA | Set WMP-46 | CalPA_Set WMP-46 | 1 | CalPA_Set WMP-46_Q1 | Regarding Attachment “2024-04-02_PGE_2025_WMP-Update _R0_ACI-23-26_Atch01_CONF.xlsx” of PG&E’s 2025 WMP Update: a) Please provide a description or definition of each column in both worksheets. b) Please state the basis for using $1.615/minute as the conversion factor for column T (impact_community_values) in the “Outage Data” worksheet. c) The range of data for column U (2023_percentage_epss_enabled) in the “CPZ Data” worksheet is 0-99%. Please clarify the time scale this is applicable for. For example, is this 0-99% of the calendar year? d) Please clarify what the data reported in column V (2023_epss_protected_circuit_mile_days) of the “CPZ Data” worksheet represents. | a) Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_046- Q001Atch01.xlsx” for the requested information. b) As originally requested as part of ACI PG&E-22-32, the “impact on community values, including intangibles (e.g. livelihood)” of EPSS was measured using PG&E’s preliminary monetized value of attributes for Electric Reliability of $3.23 as presented in PG&E’s February 7, 2024, Pre-RAMP CPUC Workshop filing. For the purposes of this calculation, the estimated incremental impact from EPSS settings being enabled was assumed to be double the number of customer outage minutes per outage. As such, the total number of interruption minutes was multiplied by the monetized value of attributes for Electric Reliability divided by two to represent the incremental impact of EPSS. c) Column U, “2023_percentage_epss_enabled”, in the “CPZ Data” tab referenced reflects the number of days in 2023 in which a circuit was enabled with EPSS reflected as a percentage of the 2023 calendar year. d) Column V, “2023_epss_protected_circuit_mile_days”, in the “CPZ Data” tab referenced reflects the number of days in 2023 in which a circuit was enabled with EPSS multiplied by the circuit miles. | Holly Wehrman | 2024-04-17 | 2024-04-22 | 2024-04-22 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_046.zip | 1 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23-06 – Continuation of Grid Hardening Joint Studies | ACI 23-06 Continuation of Grid Hardening Joint Studies |  | CalPA | Set WMP-46 | 1 | 4 | Mona Hedin | Hema Sukumar | Benson Wong James Ash Jr | Paul McGregor Eric Lamoureux | Aaron Shapiro | Andy Abranches | Yes | Yes | Yes |  | Yes | Yes |  |  | 2024-04-22 | [16 empty] | 1 | Benson Wong James Ash Jr | Paul McGregor Eric Lamoureux | Mona Hedin | Hema Sukumar | Aaron Shapiro | 4 |  |  |  |  | completed | 0 | 0 | 0 | 0
559 | CalPA | Set WMP-43 | CalPA_Set WMP-43 | 12 | CalPA_Set WMP-43_Q12 | Page 67 of PG&E’s 2025 WMP Update states, “In 2023, the utilities discussed the unit costs of CC and undergrounding and compared, at a high level, the different cost drivers.” a) Provide the unit costs of covered conductor that were discussed in 2023 for each of the Joint Utilities. b) Provide the unit costs of undergrounding that were discussed in 2023 for each of the Joint Utilities. c) Describe the cost drivers that were discussed in 2023 for each of the Joint Utilities. d) List any other findings from the monthly meetings in 2023 noted above. | a) Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_043- Q010Atch01.pdf” for the Joint IOU Covered Conductor Working Group discussion, which includes the requested cost information. The section discussing covered conductor costs begins on page 39. b) Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_043- Q010Atch01.pdf” for the Joint IOU Covered Conductor Working Group discussion, which includes the requested cost information. The section discussing undergrounding costs begins on page 40. c) Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_043- Q010Atch01.pdf” for the Joint IOU Covered Conductor Working Group discussion, which includes the requested cost information. The section discussing cost drivers begins on page 39. d) Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_043- Q010Atch01.pdf” for the Joint IOU Covered Conductor Working Group discussion, which includes the findings from the monthly meetings. | Holly Wehrman | 2024-04-12 | 2024-04-17 | 2024-04-17 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_043.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23-06 – Continuation of Grid Hardening Joint Studies | ACI 23-06 Continuation of Grid Hardening Joint Studies |  | CalPA | Set WMP-43 | 12 | 4 | Mona Hedin | Andrew Trombley | System Hardening- Brad Koelling/Merih Tekeste /UG | Megan Ardell/Jim Gill | Aaron Shapiro | Matt Pender/Martin Wyspianski | Yes |  | Yes |  | Yes | Yes | Yes |  | 2024-04-17 | [16 empty] | 12 | Andrew Trombley | Megan Ardell/Jim Gill | Mona Hedin | Andrew Trombley | Aaron Shapiro | 4 |  |  |  |  | completed | 0 | 0 | 0 | 0
558 | CalPA | Set WMP-43 | CalPA_Set WMP-43 | 11 | CalPA_Set WMP-43_Q11 | Pages 66-67 of PG&E’s 2025 WMP Update list three workshops the Joint Utilities held with Energy Safety: June 2023 Distribution Fault Anticipation, July 2023 Early Fault Detection, August 2023 REFCL. a) Provide a copy of any materials prepared by PG&E for each of the three workshops. b) Provide a copy of any reports, minutes, recordings, or other output of the three workshops. c) List any findings from each of the three workshops. d) List any action items PG&E took on from each of the three workshops. | a) Please see the table below for presentation materials for the workshops identified. Workshop Date & Title Attachment Name June 2023 Distribution Fault Anticipation (DFA) WMP-Discovery2023-2025_DR_CalAdvocates_043- Q011Atch01.pdf WMP-Discovery2023-2025_DR_CalAdvocates_043- Q011Atch02.pdf July 2023 Early Fault Detection (EFD) WMP-Discovery2023-2025_DR_CalAdvocates_043- Q011Atch03.pdf August 2023 Rapid Earth Fault Current Limiter (REFCL) WMP-Discovery2023-2025_DR_CalAdvocates_043- Q011Atch04.pdf b) No reports, minutes, recordings were taken or prepared at the referenced workshops. Please see the response to subpart (a) for the presentation materials from the workshops. c) The findings from the workshops are as follows: 1) For the June 2023 DFA workshop, SCE and SDG&E are finding similar successes using this technology as PG&E. SDG&E is using a different system, however, are able to find precursors to underground elbow failures. 2) For the July 2023 EFD workshop, SCE is finding similar successes using this technology as PG&E and is also using this technology on transmission lines. 3) For the August 2023 REFCL workshop, we did not have any specific takeaways or findings. d) PG&E’s action item from these workshops is to continue the discussions and collaboration about uses of EFD and DFA, and implement our WMP commitments on these technologies. We are also still evaluating the usage of REFCL to determine the potential value it could add to our system, if any. | Holly Wehrman | 2024-04-12 | 2024-04-17 | 2024-04-17 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_043.zip | 4 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23-06 – Continuation of Grid Hardening Joint Studies | ACI 23-06 Continuation of Grid Hardening Joint Studies |  | CalPA | Set WMP-43 | 11 | 4 | Mona Hedin | Kaet Bulkowski | Ravi Nair Eric Schoenman | Craig Kurtz | Aaron Shapiro | Mark Quinlan | Yes | Yes | Yes |  |  | Yes |  |  | 2024-04-17 | [16 empty] | 11 | Ravi Nair Eric Schoenman | Craig Kurtz | Mona Hedin | Kaet Bulkowski | Aaron Shapiro | 4 |  |  |  |  | completed | 0 | 0 | 0 | 0
557 | CalPA | Set WMP-43 | CalPA_Set WMP-43 | 10 | CalPA_Set WMP-43_Q10 | Page 66 of PG&E’s 2025 WMP Update states, “The Joint Utilities have met monthly in 2023 to discuss the results of recorded and estimated effectiveness for covered conductor.” a) Provide the results of recorded effectiveness for covered conductor that were discussed in 2023 for each of the Joint Utilities. b) Provide the results of estimated effectiveness for covered conductor that were discussed in 2023 for each of the Joint Utilities. c) List any other findings from the monthly meetings in 2023 noted above. | a) Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_043- Q010Atch01.pdf” for the Joint IOU Covered Conductor Working Group Report, which includes the results of recorded and estimated effectiveness for covered conductors discussed during 2023 monthly Joint Utility meetings. b) Please see the response to subpart (a) for the requested information. c) PG&E is not aware of additional findings outside of those in the Joint IOU Covered Conductor Working Group Report, identified in subpart (a). | Holly Wehrman | 2024-04-12 | 2024-04-17 | 2024-04-17 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_043.zip | 1 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23-06 – Continuation of Grid Hardening Joint Studies | ACI 23-06 Continuation of Grid Hardening Joint Studies |  | CalPA | Set WMP-43 | 10 | 3 | Mona Hedin | Andrew Trombley | Issam El Ayadi/Tiffany Pazdan/Matthew Horowitz/Michelle Sakamoto/Natalie Dawley | Jim Gill | Aaron Shapiro | Martin Wyspianski | Yes |  | Yes |  | Yes | Yes | Yes |  | 2024-04-17 | [16 empty] | 10 | Issam El Ayadi/Tiffany Pazdan/Matthew Horowitz/Michelle Sakamoto/Natalie Dawley | Jim Gill | Mona Hedin | Andrew Trombley | Aaron Shapiro | 3 |  |  |  |  | completed | 0 | 0 | 0 | 0
536 | MGRA | Data Request No. 9 | MGRA_Data Request No. 9 | 14 | MGRA_Data Request No. 9_Q14 | What would be the final year that a circuit will be undergrounded that might potentially be implemented with an EFD? | Not applicable, please see the response to Question No. 13 for an explanation. | Joseph Mitchell | 2024-04-08 | 2024-04-11 | 2024-04-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_009.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23-07 – Deployment of New Technologies | ACI 23-07 – Deployment of New Technologies |  | MGRA | Data Request No. 9 | 14 | 0 | Mona Hedin | Alex Quintana | PSPS PMO Ravi Nair UG Team Jerry Santos Julie Cerio Lucy Morris | Craig Kurtz Megan Ardell | Aaron Shapiro | Matt Pender | Yes | Yes | Yes |  | Yes | Yes | Yes |  | 2024-04-11 | [16 empty] | 14 | PSPS PMO Ravi Nair UG Team Jerry Santos Julie Cerio Lucy Morris | Craig Kurtz Megan Ardell | Mona Hedin | Alex Quintana | Aaron Shapiro | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
535 | MGRA | Data Request No. 9 | MGRA_Data Request No. 9 | 13 | MGRA_Data Request No. 9_Q13 | Early Fault Detection/Distribution Fault Anticipation Are EFD circuits being deployed on circuits that are being scoped for undergrounding? | PG&E has avoided selecting circuits/circuit segments with known undergrounding schedules for Early Fault Detection (EFD) deployment. | Joseph Mitchell | 2024-04-08 | 2024-04-11 | 2024-04-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_009.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23-07 – Deployment of New Technologies | ACI 23-07 – Deployment of New Technologies |  | MGRA | Data Request No. 9 | 13 | 0 | Mona Hedin | Kaet Bulkowski | Chris Brady Ravi Nair Nick Babb | Craig Kurtz Andy Abranches | Aaron Shapiro | Andy Abranches | Yes | Yes | Yes |  | Yes | Yes | Yes |  | 2024-04-11 | [16 empty] | 13 | Chris Brady Ravi Nair Nick Babb | Craig Kurtz Andy Abranches | Mona Hedin | Kaet Bulkowski | Aaron Shapiro | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
561 | CalPA | Set WMP-43 | CalPA_Set WMP-43 | 14 | CalPA_Set WMP-43_Q14 | Page 69 of PG&E’s 2025 WMP Update states, “As of December 2023, PG&E moved beyond pilot and into production of these technologies, having deployed EFD technology on 103 locations over 6 distribution circuits and DFA technology at 79 substations.” a) State the approximate number of circuit miles on which EFD is currently active. b) State the approximate number of circuit miles on which DFA is currently active. c) Describe PG&E’s standards and criteria for determining where to install EFD technology. d) Describe PG&E’s standards and criteria for determining where to install DFA technology. e) Please describe the results of the pilot program mentioned in the quote above, which prompted PG&E to move into production and deployment of these technologies in December 2023. f) Provide any reports, analyses, or other documentation of the results of the pilot program. | a) PG&E currently has 321 circuit miles currently active for EFD. b) PG&E currently has 7,536 circuit miles currently active for DFA. c) EFD circuit/location selection criteria are based on highest HFRA/HFTD risk score, reliable cellular coverage availability, and areas that are not significantly included in our near-term undergrounding effort. d) DFA circuit/location selection criteria are based on highest HFRA/HFTD risk score, reliability impacted customers (CEMI 2), areas highly-impacted by EPSS, and reliable cellular coverage availability. e) Please see the EPIC 2.34 report for the results of the EFD/DFA pilot program, which is available at the following link: https://www.pge.com/assets/pge/docs/about/corporate-responsibility-andsustainability/PGE-EPIC-Project-2.34.pdf. PG&E spent 2022 and 2023 operationalizing these technologies. This operationalizing work included: (1) developing install standards (2022); (2) working to get materials standardized and established between suppliers and PG&E sourcing (2022); (3) developing streamlined alert analysis (2023); and (4) developing investigation workflows (2023). f) Please see the EPIC 2.34 report, a link to which is provided in response to subpart (e) above, for a report and analyses of the EFD/DFA pilot program. | Holly Wehrman | 2024-04-12 | 2024-04-17 | 2024-04-17 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_043.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23-07 – Deployment of New Technologies | ACI 23-07 – Deployment of New Technologies |  | CalPA | Set WMP-43 | 14 | 6 | Mona Hedin | Kaet Bulkowski | Ravi Nair/Eric Schoenman | Craig Kurtz | Aaron Shapiro | Mark Quinlan | Yes |  | Yes |  |  | Yes |  |  | 2024-04-17 | [16 empty] | 14 | Ravi Nair/Eric Schoenman | Craig Kurtz | Mona Hedin | Kaet Bulkowski | Aaron Shapiro | 6 |  |  |  |  | completed | 0 | 0 | 0 | 0
560 | CalPA | Set WMP-43 | CalPA_Set WMP-43 | 13 | CalPA_Set WMP-43_Q13 | Page 68 of PG&E’s 2025 WMP Update states, with regard to the REFCL pilot at the Calistoga substation, “Although we are committed to continuing this demonstration project, several factors have caused delays in commissioning this program, including equipment failure, extended lead time of equipment, and the need to procure additional equipment to further stabilize the system.” a) List and describe each equipment failure that occurred during 2021, 2022, or 2023 and delayed the commissioning of the program. b) List and describe each instance of extended lead time that occurred during 2021, 2022, or 2023 and delayed the commissioning of the program. c) List and describe PG&E’s current needs to procure additional equipment to further stabilize the system. d) When does PG&E currently anticipate receiving actionable results from the REFCL pilot at the Calistoga substation? e) List each of the efforts PG&E made in 2023 to accelerate the REFCL pilot at the Calistoga substation. f) List each of the efforts PG&E plans to make in 2024 to accelerate the REFCL pilot at the Calistoga substation. g) List each of the efforts PG&E plans to make in 2025 to accelerate the REFCL pilot at the Calistoga substation. | a) Three equipment failures that occurred during 2021 and 2022 delayed the commissioning of the program: 1) In 2021, a substation voltage regulator failure occurred during a test program; 2) In 2022, a substation grounding transformer failure occurred; and 3) In 2022, a GFN RCC failure occurred. b) Three instances of extended lead time occurred during 2021 and 2022 that delayed the commissioning of the program: 1) In 2021 — mobile test resistor for fault testing; 2) In 2021 — replacement substation voltage regulators; and 3) In 2022 — replacement of grounding transformer and RCC. c) PG&E has procured a damping resistor to reduce high standing neutral voltage to stabilize the operation of the REFCL system. At this time, we have no plans to procure additional equipment. d) PG&E currently anticipates receiving actionable results from the REFCL pilot at the Calistoga substation at the end of 2024. e) In order to accelerate the REFCL pilot at the Calistoga substation in 2023, PG&E worked with the supplier to design and supply a damping resistor to reduce neutral voltage. This was necessary due to PG&E observing high standing neutral voltage which could not be reduced even with balancing the ground currents. This forced PG&E to temporarily disable REFCL and work with the supplier for the resistor installation in order to move the project forward. f) In order to accelerate the REFCL pilot in 2024, PG&E is installing and testing the damping resistor to allow the REFCL system to be put back into service. g) PG&E cannot, at this time, identify discrete efforts that it will make in 2025 to accelerate the REFCL pilot because the 2025 workplan is dependent on the results of the work in 2024, which are still unknown. | Holly Wehrman | 2024-04-12 | 2024-04-17 | 2024-04-17 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_043.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23-07 – Deployment of New Technologies | ACI 23-07 – Deployment of New Technologies |  | CalPA | Set WMP-43 | 13 | 7 | Mona Hedin | Andrew Trombley | Franz Stadtmueller/Fred Skillman | Wen Tu | Aaron Shapiro | Joe Bentley | Yes | Yes | Yes |  |  | Yes | Yes |  | 2024-04-17 | [16 empty] | 13 | Franz Stadtmueller/Fred Skillman | Wen Tu | Mona Hedin | Andrew Trombley | Aaron Shapiro | 7 |  |  |  |  | completed | 0 | 0 | 0 | 0
599 | OEIS | 016 | OEIS_016 | 2 | OEIS_016_Q2 | Q02. Regarding PG&E’s Quarterly Targets for Routine Patrol In PG&E’s 2025 WMP Update, PG&E sets quarterly targets for Routine Patrol – Distribution (VM-16); 2023 and 2024 targets are included for reference: PG&E’s Routine Patrol Targets by Year in Circuit Miles6 Year End of Q2 End of Q3 End of Year 2023 41,761 61,806 79,000 2024 39,325 58,988 78,650 2025 31,280 50,830 78,200 %△ 2023-2025 -28.7% -19.5% -1% While PG&E’s end of year target has remained relatively constant from 2023 to 2025, the end of Q2 and end of Q3 targets have decreased year-over-year. a. Why have PG&E’s end of Q2 and end of Q3 targets for routine patrol decreased year-over-year since 2023? b. What percentage of PG&E’s end of Q2 and end of Q3 2025 targets will be completed within the HFTD? c. How will PG&E ensure that the HFTD and other high fire risk areas are inspected in a timely manner to mitigate wildfire risk before and during wildfire season? | a. The targets were reduced in Q2 and Q3 in subsequent years to provide the operations team with greater flexibility during the course of the year. PG&E anticipated slowdowns due to the change in software platform, incorporating other planned vegetation program inspections into the routine patrol where possible, and changes to other VM programs that would impact our routine work. The weather and other external factors can also cause delays in the inspection schedule. b. Approximately 50% of the Q2 end mileage is located in HFTD, and approximately 45% of the Q3 end mileage is located in HFTD. c. PG&E has designed its program through the routine and second patrols to patrol the entire HFTD/HFRA portions of the system twice a year. Once in the first half and once in the second half. Or, in other words, once in the routine patrol and once in the second patrol. | Brad Hill | 2024-04-22 | 2024-04-25 | 2024-04-25 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/OEIS_016.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23-09 – Decrease in Detailed Distribution Inspections | ACI 23-09 – Decrease in Detailed Distribution Inspections |  | OEIS | 016 | 2 | 3 | Mona Hedin | Nelson Lau | Joanna Sturges VM Data Requests Helen Vesser Luke Roy Kevin La | Jim Gill Sarah Carlson | Aaron Shapiro | Martin Wyspianski Angela Sanford | Yes | Yes |  |  | Yes | Yes |  |  | 2024-04-25 | [16 empty] | 2 | Joanna Sturges VM Data Requests Helen Vesser Luke Roy Kevin La | Jim Gill Sarah Carlson | Mona Hedin | Nelson Lau | Aaron Shapiro | 3 |  |  |  |  | completed | 0 | 0 | 0 | 0
660 | CPUC - SPD (Safety Policy Division) | 016 | CPUC - SPD (Safety Policy Division)_016 | 17 | CPUC - SPD (Safety Policy Division)_016_Q17 | CONFIDENTIAL – This question refers to the table labeled “AG Population, B Find Rates” on slide 29 of the presentation to the Wildfire Risk Governance Committee presented on October 12th, 2023 (sent to SPD as “WMP-Discovery2023-2025_DR_SPD_014-Q010Atch01CONF"). Provide an explanation of the table. Specifically discuss the difference between a CIRT aligned B tag versus those found by an Aerial Inspection/Ground Inspection. a. Provide an explanation of the table. b. Define a “CIRT-aligned B tag” and discuss the difference between a CIRT-aligned B tag versus those found by an Aerial Inspection/Ground Inspection. c. Provide the actual numbers of tags identified by Ground and Aerial inspections in the table. d. Provide the unique number of tags identified by Aerial (i.e. those tags not identified by Aerial and not identified by Ground inspections) in the table. e. For “Crossarm Decayed/Rotten”, does the table imply that of the 53 B-tags found in the sample, that Aerial Inspections identified 50-75% of the B-tags and that Ground Inspections identified 25-50% of the B-tags? i. Does this mean a minimum of 13, and a maximum of 26 of the B-Tags were identified by Ground and not identified by Aerial? a. What was the sample size for this table? | a. The table is a view of the number of B tags for the FDAs listed (Crossarm and Pole). It is an analysis of the finds by each method, where they overlap, and where they did not. “AG” refers to Aerial Inspection/Ground Inspection. b. A CIRT review was the process step after Ground or Aerial performed their inspection. CIRT then reviewed the prioritization assignment. This phrase reflects those instances in which CIRT agreed with the priority assigned. c. For the Ground and Aerial inspections reflected in the Harvey balls, 325 were Aerial inspections and 196 were Ground inspections. The total number of unique tags is 463. d. PG&E interprets this to mean tags identified by Aerial inspection and not identified by Ground inspection. 267 tags were identified by Aerial inspection and not by Ground inspection. e. Yes. For “Crossarm Decayed/Rotten”, the table does imply that of the 53 B-tags found in the sample, that Aerial Inspections identified 50-75% of the B-tags and that Ground Inspections identified 25-50% of the B-tags. i. Yes. A minimum of 13, and a maximum of 26 of the B-Tags were identified by Ground inspection and not identified by Aerial inspection. f. The sample size for this table for the entire Aerial and Ground population study was 12,126 inspections. | Henry Sweat | 2024-05-30 | 2024-06-10 | 2024-06-10 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_016.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23-09 – Decrease in Detailed Distribution Inspections | ACI 23-09 – Decrease in Detailed Distribution Inspections |  | CPUC - SPD (Safety Policy Division) | 016 | 17 | 7 | Mona Hedin | Nelson Lau | Aasha Sachdev Joanna Sturges; CIRT; SI Keli Thurston | Jim Gill | Aaron Shapiro | Martin Wyspianski | Yes | Yes | Yes |  | Yes |  |  |  | 2024-06-10 |  | 6/4/2024 - Extension to 6/10 approved by Wade Greenacre. Kxfk | 6/4/2024 - Extension to 6/10 approved by Wade Greenacre. Kxfk | [13 empty] | 17 | Aasha Sachdev Joanna Sturges; CIRT; SI Keli Thurston | Jim Gill | Mona Hedin | Nelson Lau | Aaron Shapiro | 7 |  |  |  |  | completed | 0 | 0 | 0 | 0
659 | CPUC - SPD (Safety Policy Division) | 016 | CPUC - SPD (Safety Policy Division)_016 | 16 | CPUC - SPD (Safety Policy Division)_016_Q16 | CONFIDENTIAL - Provide the data in excel format used to create the chart on slide 2, 5, 6, 8 of the presentation to the Wildfire Risk Governance Committee presented on October 12th, 2023 (sent to SPD as “WMP-Discovery2023-2025_DR_SPD_014-Q010Atch01CONF"). | Please see attachment “WMP-Discovery2023-2025_DR_SPD_016-Q016Atch01.xlsx” for the requested information. | Henry Sweat | 2024-05-30 | 2024-06-10 | 2024-06-10 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_016.zip | 1 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23-09 – Decrease in Detailed Distribution Inspections | ACI 23-09 – Decrease in Detailed Distribution Inspections |  | CPUC - SPD (Safety Policy Division) | 016 | 16 | 0 | Mona Hedin | Nelson Lau | Arvind Simhardi | Jim Gill | Aaron Shapiro | Martin Wyspianski | Yes |  | Yes |  | Yes |  | Yes |  | 2024-06-10 |  | 6/4/2024 - Extension to 6/10 approved by Wade Greenacre. Kxfk | 6/4/2024 - Extension to 6/10 approved by Wade Greenacre. Kxfk | [13 empty] | 16 | Arvind Simhardi | Jim Gill | Mona Hedin | Nelson Lau | Aaron Shapiro | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
641 | CPUC - SPD (Safety Policy Division) | 014 | CPUC - SPD (Safety Policy Division)_014 | 10 | CPUC - SPD (Safety Policy Division)_014_Q10 | Discuss the process for updating the Distribution Inspection Job Aid. a. What is the process? b. Who has final say? c. Which licensed civil (structural practitioner) or structural engineers reviewed the job aid? Provide their feedback and comments in full, including any email correspondence. Summarize any comments made in meetings discussing the Job Aid. d. Provide meeting notes from meetings discussing changes to Job Aid from the Wildfire Steering Governance Committee, or a similar type of committee governing distribution assets or inspections, provide them. | a. PG&E follows a management of change process which includes identifying stakeholders, documenting approvals through System Inspections and Asset Strategy Leadership, and communicating the updates with the target audience for the job aid. b. During the process outlined above, a defined standards council is identified who is responsible for reviewing and approving the final job aid. PG&E’s Director of System Inspections and Director of Asset Management finalized the referenced Distribution Inspection job aid. c. The stakeholders that participate in the update process include engineers from Engineering Standards, Work Methods, Asset Strategy, and Applied Technology Services (ATS). In addition, stakeholders included personnels from System Inspections and Field Operations. Feedback was received from the stakeholders over multiple meetings. Meeting notes are not available, however, several studies were conducted by PG&E’s ATS engineering team in collaboration with Asset Strategy and Standards engineers which provided an engineering basis for several of the changes made to the job aid. Please see the following attachments for copies of the studies and meeting presentations contributing to the referenced job aid. WMP-Discovery2023-2025_DR_SPD_014-Q010 Page 2 Attachment Description WMP-Discovery2023-2025_DR_SPD_014- Q010Atch01CONF.pdf Wildfire Risk Committee Presentation WMP-Discovery2023-2025_DR_SPD_014- Q010Atch02CONF.pdf Effects of Splice Location on Distribution Lines WMP-Discovery2023-2025_DR_SPD_014- Q010Atch03CONF.pdf FDA Tag Evaluation WMP-Discovery2023-2025_DR_SPD_014- Q010Atch04CONF.pdf Electric Distributions Engineering Criteria for Allowable Broken Strands for a Conductor WMP-Discovery2023-2025_DR_SPD_014- Q010Atch05CONF.pdf Electric Distributions Engineering Criteria for Remaining Circumference and Horizontal Cut Depth WMP-Discovery2023-2025_DR_SPD_014- Q010Atch06CONF.pdf Electric Distributions Engineering Criteria for Woodpecker Feeding Holes WMP-Discovery2023-2025_DR_SPD_014- Q010Atch07CONF.pdf Electric Distributions Engineering Criteria for Woodpecker Starter and Nesting Holes WMP-Discovery2023-2025_DR_SPD_014- Q010Atch08CONF.pdf Electric Distributions Engineering Criteria for Hole Proximity on Wood Poles d. Please see the response to subpart (c) above for the requested information. | Henry Sweat | 2024-05-14 | 2024-05-28 | 2024-05-28 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_014.zip | 8 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23-09 – Decrease in Detailed Distribution Inspections | ACI 23-09 – Decrease in Detailed Distribution Inspections |  | CPUC - SPD (Safety Policy Division) | 014 | 10 | 4 | Mona Hedin | Nelson Lau | Arvind Simhadri Mina Amir Jo Fogolin Tiffany Pazdan Cindy Wong | Wen Tu | Aaron Shapiro | Marting Wyspianski Jason Regan | Yes | Yes | Yes |  | Yes |  |  |  | 2024-05-28 | [16 empty] | 10 | Arvind Simhadri Mina Amir Jo Fogolin Tiffany Pazdan Cindy Wong | Wen Tu | Mona Hedin | Nelson Lau | Aaron Shapiro | 4 |  |  |  |  | completed | 0 | 0 | 0 | 0
589 | CalPA | Set WMP-46 | CalPA_Set WMP-46 | 2 | CalPA_Set WMP-46_Q2 | PG&E’s Community Wildfire Safety Program website4 includes two procedures related to infrared (IR) inspections: TD-1001P-14 and TD-2022P-01. a) Please describe the circumstances in which PG&E utilizes the TD-1001P-14 procedure. b) Please describe the circumstances in which PG&E utilizes the TD-2022P-01 procedure. c) Please provide copies of all current bulletins or job aids associated with TD-1001P-14 that direct inspectors on how to perform IR inspections. d) Please provide copies of all current bulletins or job aids associated with TD-2022P-01 that direct inspectors on how to perform IR inspections. e) Please provide copies of all prior revisions of TD-1001P-14, including bulletins or job aids associated with those prior revisions. f) Please provide copies of all prior revisions of TD-2022P-01, including bulletins or job aids associated with those prior revisions. g) Please identify all procedures (including associated bulletins or job aids) related to infrared inspections of distribution infrastructure that were in effect during 2023. h) Please provide copies of each document responsive to part (g) that has not been provided in response to previous parts of this question. i) Please identify all procedures (including associated bulletins or job aids) related to infrared inspections of distribution infrastructure that were in effect during 2020. j) Please provide copies of each document responsive to part (i) that has not been provided in response to previous parts of this question. k) Please identify all procedures (including associated bulletins or job aids) related to infrared inspections of distribution infrastructure that were in effect during 2017. l) Please provide copies of each document responsive to part (k) that has not been provided in response to previous parts of this question. m) Please identify all procedures (including associated bulletins or job aids) related to infrared inspections of distribution infrastructure that were in effect during 2014. n) Please provide copies of each document responsive to part (m) that has not been provided in response to previous parts of this question. | a) PG&E performs infrared inspections on overhead transmission lines in accordance with the frequency defined in TD-8123P-100 “Transmission Patrols and Enhanced Inspection Frequency Guidelines” and inspection method requirements defined in TD-1001P-14 “Infrared (IR) Inspection Procedures”. Please see attachment “WMPDiscovery2023-2025_DR_CalAdvocates_046-Q002Atch01CONF.pdf” for a copy of TD-8123P-100, Revision (Rev.) 1, and attachment “WMP-Discovery2023- 2025_DR_CalAdvocates_046-Q002Atch02CONF.pdf” for a copy of TD-1001P-14, Rev 4. b) PG&E performs infrared inspections on overhead and underground electric distribution facilities in accordance with inspection method requirements defined in with TD-2022P-01 Rev 2 “Infrared (IR) Inspections of Electric Distribution Facilities” and TD-2305M Electric Distribution Preventative Maintenance Manual, available on PG&E’s website at the following link: https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparednessand-support/TD-2305M.pdf. Please see attachment “WMP-Discovery2023- 2025_DR_CalAdvocates_046-Q002Atch03CONF.pdf” for the current version of procedure TD-2022P-01 (Rev 2). c) Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_046- Q002Atch04.pdf” for the current Rev 2 of TD-1001M-JA19 “Evaluating Conditions from Infrared (IR) Inspections in Transmission Lines.” d) Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_046- Q002Atch05CONF.pdf" for TD-2305M-JA03, Rev 4, for the Underground Inspection Job Aid associated with TD-2022P-01. e) Please see the following for table for prior revisions of TD-1001P-14 and its associated Job Aid (JA)19. Procedure Name Attachment Name TD-1001P-14, Rev 0 Published August 2020 WMP-Discovery2023-2025_DR_CalAdvocates_046-Q002Atch06CONF.pdf TD-1001P-14, Rev 1 Published April 2021 WMP-Discovery2023-2025_DR_CalAdvocates_046-Q002Atch07CONF.pdf TD-1001P-14, Rev 2 Published December 2021 WMP-Discovery2023-2025_DR_CalAdvocates_046-Q002Atch08CONF.pdf TD-1001P-14, Rev 3 Published December 2022 WMP-Discovery2023-2025_DR_CalAdvocates_046-Q002Atch09CONF.pdf TD-1001P-14, Rev 4 Published April 2024 WMP-Discovery2023-2025_DR_CalAdvocates_046-Q002Atch10CONF.pdf TD-1001M-JA19 Rev 0 Effective March 2020 WMP-Discovery2023-2025_DR_CalAdvocates_046-Q002Atch11.pdf TD-1001M-JA19 Rev 1 Effective April 2021 WMP-Discovery2023-2025_DR_CalAdvocates_046-Q002Atch12.pdf Procedure Name Attachment Name TD-1001M-JA19 Rev 2 Effective February 2023 WMP-Discovery2023-2025_DR_CalAdvocates_046-Q002Atch04.pdf f) Please see the following for table for prior revisions of TD-2022P-01 and its associated Job Aid (JA) 03. Procedure Name Attachment Name TD-2022P-01 Rev 0 Published December 2013 WMP-Discovery2023-2025_DR_CalAdvocates_046-Q002Atch13CONF.pdf TD-2022P-01 Rev 1 Published May 2018 WMP-Discovery2023-2025_DR_CalAdvocates_046-Q002Atch14CONF.pdf TD-2022P-01 Rev 2 Published December 2023 WMP-Discovery2023-2025_DR_CalAdvocates_046-Q002Atch03.pdf TD 2305M-JA03, Rev 2* Published October 2012 WMP-Discovery2023-2025_DR_CalAdvocates_046-Q002Atch15.pdf TD 2305M-JA03, Rev 3 Published March 2013 WMP-Discovery2023-2025_DR_CalAdvocates_046-Q002Atch16CONF.pdf TD 2305M-JA03, Rev 2.3 Published July 2015 WMP-Discovery2023-2025_DR_CalAdvocates_046-Q002Atch17.pdf TD 2305M-JA03, Rev 3 Published January 2020 WMP-Discovery2023-2025_DR_CalAdvocates_046-Q002Atch18CONF.pdf TD 2305M-JA03, Rev 4 Effective August 2022 WMP-Discovery2023-2025_DR_CalAdvocates_046-Q002Atch05CONF.pdf *Despite a reasonable search of available records, PG&E was unable to locate revisions to 2305M-JA03 prior to 2012. g) Please see “WMP-Discovery2023-2025_DR_CalAdvocates_046- Q002Atch06CONF.pdf “ for the procedure and “WMP-Discovery2023- 2025_DR_CalAdvocates_046-Q002Atch14CONF.pdf” for the JA in effect during 2023. h) Please see the attachments identified in response to subpart (g) and included with this response. i) Please see “WMP-Discovery2023-2025_DR_CalAdvocates_046-Q002Atch04.pdf” for the procedure and “WMP-Discovery2023-2025_DR_CalAdvocates_046- Q002Atch18CONF.pdf” for the JA in effect during 2020. j) Please see the attachment identified in response to subpart (i) and included with this response. k) Please see “WMP-Discovery2023-2025_DR_CalAdvocates_046- Q002Atch13CONF.pdf” for PG&E’s procedure specific to infrared inspections or distribution infrastructure that was in effect in 2017 and “WMP-Discovery2023- 2025_DR_CalAdvocates_046-Q002Atch17.pdf” for the JA in effect during 2017. l) Please see the attachment identified in response to subpart (k) and included with this response. m) Please see and “WMP-Discovery2023-2025_DR_CalAdvocates_046- Q002Atch13CONF.pdf” for the procedure and “WMP-Discovery2023- 2025_DR_CalAdvocates_046-Q002Atch17.pdf" for the JA in effect during 2014. n) Please see the attachments identified in response to subpart (m) and included with this response. | Holly Wehrman | 2024-04-17 | 2024-04-22 | 2024-04-22 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_046.zip | 18 | N/A | 8.1.3.1.4 | 8.0 Wildfire Mitigations | 8.1.3.1.4 Infrared Inspection | ACI 23-09 – Decrease in Detailed Distribution Inspections |  | CalPA | Set WMP-46 | 2 | 14 | Mona Hedin | Nelson Lau | Joanna Sturges Aasha Sachdev (D) | Jim Gill | Aaron Shapiro | Martin Wyspianski | Yes | Yes | Yes |  | Yes | Yes |  |  | 2024-04-22 | [16 empty] | 2 | Joanna Sturges Aasha Sachdev (D) | Jim Gill | Mona Hedin | Nelson Lau | Aaron Shapiro | 14 |  |  |  |  | completed | 0 | 0 | 0 | 0
564 | CalPA | Set WMP-43 | CalPA_Set WMP-43 | 17 | CalPA_Set WMP-43_Q17 | Page 76 of PG&E’s 2025 WMP Update states, Inspecting high consequence assets annually by ground would increase both the eyes-on-risk and the cost of the inspection plan relative to inspecting these assets every other year. PG&E calculates that approximately 37,000 additional inspections would need to be performed annually at a cost of roughly $4.3 million. Similarly, inspecting medium consequence structures every other year would result in 15,000 more inspections at an additional annual cost of $1.7 million. a) What would be the annual cost of performing approximately 37,000 additional detailed aerial inspections of high consequence assets? b) What would be the annual cost of performing approximately 15,000 additional detailed aerial inspections of medium consequence assets? c) What would be the estimated benefit, in dollars, of inspecting high consequence assets annually? d) What would be the estimated benefit, in dollars, of inspecting medium consequence assets annually? | a) The annual cost of performing approximately 37,000 additional detailed aerial inspections of high consequence assets is roughly $5.5 million. b) The annual cost of performing approximately 15,000 additional detailed aerial inspections of medium consequence assets is roughly $2.25 million. c) PG&E does not quantify the estimated benefit, in dollars, of inspecting high or medium consequence assets annually. The main benefit of additional inspections is identifying additional maintenance needs, but PG&E does not have a standardized approach to calculating a dollar benefit associated with identifying additional notifications, as PG&E treats inspections as a foundational program that supports PG&E’s maintenance program. As noted in our 2025 WMP Update, additional inspection finds do not mitigate risk unless maintenance work is actually performed. d) Please see the response to subpart (c) above for the requested explanation. | Holly Wehrman | 2024-04-12 | 2024-04-17 | 2024-04-17 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_043.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23-09 – Decrease in Detailed Distribution Inspections | ACI 23-09 – Decrease in Detailed Distribution Inspections |  | CalPA | Set WMP-43 | 17 | 4 | Mona Hedin | Nelson Lau | Aasha Sachdev Joanna Sturges | Jim Gill | Aaron Shapiro | Martin Wyspianski | Yes | Yes | Yes |  |  | Yes | Yes |  | 2024-04-17 | [16 empty] | 17 | Aasha Sachdev Joanna Sturges | Jim Gill | Mona Hedin | Nelson Lau | Aaron Shapiro | 4 |  |  |  |  | completed | 0 | 0 | 0 | 0
563 | CalPA | Set WMP-43 | CalPA_Set WMP-43 | 16 | CalPA_Set WMP-43_Q16 | Table ACI-PG&E-23-09-1 on page 75 of PG&E’s 2025 WMP Update lists the number of HFTD structures in each consequence level from E&S to Medium. a) Has PG&E used the WDRM v4 to re-rank its structures and plat maps? If no, explain why not. b) If the answer to part (a) is no, does PG&E plan to use the WDRM v4 to re-rank its structures and plat maps? If no, explain why not. c) If the answer to either parts (a) or (b) is yes, does PG&E plan to adjust its detailed inspection program to use the updated plat map ranking? If no, explain why not. d) If the answer to part (c) is yes, will PG&E use the same inspection frequencies for the updated plat map ranking? If no, explain why not. e) If the answer to part (c) is yes, when does PG&E plan to adjust its detailed inspection program to use the updated plat map ranking? | a) Yes, PG&E has used WDRM v4 to see how its structures and plat maps would rank under the new modeling. b) Not applicable, please see the response to subpart (a) above. c) Yes, PG&E plans to adjust its detailed inspection program to use the updated plat map ranking that incorporates WDRV v4. d) Yes, PG&E currently plans to use the same inspection frequencies for the updated plat map ranking. e) PG&E currently plans to adjust its detailed inspection program to use the updated plat map ranking in 2025. | Holly Wehrman | 2024-04-12 | 2024-04-17 | 2024-04-17 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_043.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23-09 – Decrease in Detailed Distribution Inspections | ACI 23-09 – Decrease in Detailed Distribution Inspections |  | CalPA | Set WMP-43 | 16 | 5 | Mona Hedin | Nelson Lau | Jared Leong/Joanna Sturges/Jon Eric Thalman | Jim Gill | Aaron Shapiro | Martin Wyspianski/Andy Abranches | Yes | Yes | Yes |  |  |  | Yes |  | 2024-04-17 | [16 empty] | 16 | Jared Leong/Joanna Sturges/Jon Eric Thalman | Jim Gill | Mona Hedin | Nelson Lau | Aaron Shapiro | 5 |  |  |  |  | completed | 0 | 0 | 0 | 0
562 | CalPA | Set WMP-43 | CalPA_Set WMP-43 | 15 | CalPA_Set WMP-43_Q15 | Table ACI-PG&E-23-09-1 on page 75 of PG&E’s 2025 WMP Update lists the number of HFTD structures in each consequence level from E&S to Medium. a) Provide an updated version of this table with additional rows to show the structures with a consequence rank lower than Medium. b) Please provide an updated version of this table (including the additional rows from part (a)) that lists structures in the HFTD/HFRA (not only the HFTD). c) Explain the methodology PG&E used to segregate its plat maps by consequence rank. d) Provide any procedures, reports, analyses, or other documentation to support your response to part (c). | a) Please see below for an updated Table ACI-PG&E-23-09-1. Consequence Rank All HFTD/HFRA Structures Eyes-on-Risk (EOR) Risk/Structure E&S 11,464 10.60% 9.2 x 10-6 E&S – Tier 3 2,874 2.80% 9.7 x 10-6 E&S – Tier 2/HFRA 8,590 7.70% 9.0 x 10-6 High 68,481 37.80% 5.5 x 10-6 High – Tier 3 27,697 15.60% 5.6 x 10-6 High – Tier 2/HFRA 40,784 22.20% 5.4 x 10-6 Medium 93,218 27.40% 2.9 x 10-6 Medium – Tier 3 33,408 10.00% 3.0 x 10-6 Medium – Tier 2/HFRA 59,810 17.40% 2.9 x 10-6 Low 485,488 24.30% 0.5 x 10-6 Low – Tier 3 138,965 8.50% 0.6 x 10-6 Low – Tier 2/HFRA 346,523 15.80% 0.5 x 10-6 b) Table ACI-PG&E-23-09-1 includes HFTD/HFRA structures in its Tier 2 counts and should have been labeled as such to begin with. PG&E has corrected the labels in the table above. c) PG&E uses WDRM v3 to create the maps, which provides wildfire consequence scores at the structure level. For HFTD and HFRA areas, these consequence scores are the basis for plat map consequence scores and inspection frequencies. The WDRM v3 risk model calculates wildfire probabilities of ignition, consequence, and risk scores for structures in the overhead distribution system in areas of PG&E’s service territory. d) Please see “Section 4 – Source Data” in attachment WMP-Discovery2023- 2025_DR_CalAdvocates_043-Q015Atch01.pdf” for the requested procedure. | Holly Wehrman | 2024-04-12 | 2024-04-17 | 2024-04-17 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_043.zip | 1 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23-09 – Decrease in Detailed Distribution Inspections | ACI 23-09 – Decrease in Detailed Distribution Inspections |  | CalPA | Set WMP-43 | 15 | 4 | Mona Hedin | Nelson Lau | Jared Leong | Jim Gill | Aaron Shapiro | Martin Wyspianski | Yes | Yes | Yes |  |  | Yes |  |  | 2024-04-17 | [16 empty] | 15 | Jared Leong | Jim Gill | Mona Hedin | Nelson Lau | Aaron Shapiro | 4 |  |  |  |  | completed | 0 | 0 | 0 | 0
570 | MGRA | Data Request No. 10 | MGRA_Data Request No. 10 | 6 | MGRA_Data Request No. 10_Q6 | As per discussions in the April 8th meet and confer, please provide distribution unplanned outage data for the 2023 calendar year in any format required to remove transmission data or any other confidential information. This can be unrelated to the format required by the Spatial Quarterly Data Report. | Please see attachment “WMP-Discovery2023-2025_DR_MGRA_010-Q006Atch01.xlsx” for the requested information. | Joseph Mitchell | 2024-04-12 | 2024-04-17 | 2024-04-17 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_010.zip | 1 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--14 Effectiveness Analysis for EPSS Including Implementation of DCD | ACI 23-14 Effectiveness Analysis for EPSS |  | MGRA | Data Request No. 10 | 6 | 0 | Mona Hedin | Saritha Basani | Tom Huynh | Satvir Nagra | Kenny Lee | Martin Wyspianski | Yes | Yes | Yes |  | Yes | Yes | Yes |  | 2024-04-17 | [16 empty] | 6 | Tom Huynh | Satvir Nagra | Mona Hedin | Saritha Basani | Kenny Lee | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
569 | MGRA | Data Request No. 10 | MGRA_Data Request No. 10 | 5 | MGRA_Data Request No. 10_Q5 | Please provide the 2022 and 2023 EPSS reliability studies referred to on p. 8 and p. 12 of TN13808_20240402T112956_20240402_PGE_2025_WMPUpdate_R0_ACI2315_ Atch01.pdf. | For the narrative associated with PG&E’s 2022 EPSS Reliability Study, please reference pdf page 1120 at the following link: https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/pge-wmp-r4-010824.pdf Please also reference “WMP-Discovery2023-2025_DR_MGRA_010-Q005Atch01.xlsx” for the 2022 EPSS Reliability Study. For PG&E’s 2023 EPSS Reliability Study, please reference the following attachments: • WMP-Discovery2023-2025_DR_MGRA_010-Q005Atch02.pdf • WMP-Discovery2023-2025_DR_MGRA_010-Q005Atch03.xlsx | Joseph Mitchell | 2024-04-12 | 2024-04-17 | 2024-04-17 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_010.zip | 3 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--14 Effectiveness Analysis for EPSS Including Implementation of DCD | ACI 23-14 Effectiveness Analysis for EPSS |  | MGRA | Data Request No. 10 | 5 | 0 | Mona Hedin | Saritha Basani | Katherine Hee Saritha Basani | Eric Lamoureux | Kenny Lee | Mark Quinlan | Yes | Yes | Yes |  | Yes | Yes |  |  | 2024-04-17 | [16 empty] | 5 | Katherine Hee Saritha Basani | Eric Lamoureux | Mona Hedin | Saritha Basani | Kenny Lee | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
568 | MGRA | Data Request No. 10 | MGRA_Data Request No. 10 | 4 | MGRA_Data Request No. 10_Q4 | During todays (April 8th) meet and confer, the ADMS technology was mentioned that could allow much faster switching of fast trip configurations. Please describe ADMS and for what mitigations it could be used, and how much it might help to improve the false trip rate. | Advanced Distribution Management System (ADMS) is an operating platform where supervisory control and data acquisition (SCADA), the real-time system network model, and other operational applications are used to monitor and control the grid. The EPSS application within ADMS currently being developed will be used to streamline the routine enablement and disablement of EPSS devices as an operational mitigation to current manual practices. The ADMS EPSS application will not directly impact the way EPSS performs as a protective function and therefore will not have an effect on the false trip rate. | Joseph Mitchell | 2024-04-12 | 2024-04-17 | 2024-04-17 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_010.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--14 Effectiveness Analysis for EPSS Including Implementation of DCD | ACI 23-14 Effectiveness Analysis for EPSS |  | MGRA | Data Request No. 10 | 4 | 0 | Mona Hedin | Saritha Basani | James Tuccillo ADMS Team | Eric Lamoureux | Kenny Lee | Mark Quinlan | Yes | Yes | Yes | Yes |  | Yes |  |  | 2024-04-17 | [16 empty] | 4 | James Tuccillo ADMS Team | Eric Lamoureux | Mona Hedin | Saritha Basani | Kenny Lee | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
567 | MGRA | Data Request No. 10 | MGRA_Data Request No. 10 | 3 | MGRA_Data Request No. 10_Q3 | Are DCD algorithms based on prevailing weather conditions? If so, please describe how sensitivity of DCD is adjusted according to weather. | The Downed Conductor Detection (DCD) algorithm and corresponding protective function element is directly tied to EPSS enablement criteria. No additional weather or enablement criteria is applied when enabling DCD. | Joseph Mitchell | 2024-04-12 | 2024-04-17 | 2024-04-17 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_010.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--14 Effectiveness Analysis for EPSS Including Implementation of DCD | ACI 23-14 Effectiveness Analysis for EPSS |  | MGRA | Data Request No. 10 | 3 | 0 | Mona Hedin | Saritha Basani | James Tuccillo | Eric Lamoureux | Kenny Lee | Mark Quinlan | Yes | Yes | Yes | Yes |  | Yes |  |  | 2024-04-17 | [16 empty] | 3 | James Tuccillo | Eric Lamoureux | Mona Hedin | Saritha Basani | Kenny Lee | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
579 | CalPA | Set WMP-44 | CalPA_Set WMP-44 | 9 | CalPA_Set WMP-44_Q9 | Page 88 of PG&E’s 2025 WMP Update states, “CPUC reportable fire ignitions on EPSS enabled circuits were reduced by approximately 72% relative to the three-year historical average.” a) Please provide copies of any reports, analysis, or other documentation to support PG&E’s statement quoted above. b) Are EPSS outages with DCD-enablement distinguishable in the EPSS monthly reports served by PG&E? c) If the answer to part (b) is yes, please state how such outages are distinguishable. d) If the answer to part (b) is no, does PG&E plan to make such outages distinguishable in future EPSS monthly reports? | a) Please see the below presentation that supports the ignition reduction effectiveness calculation referenced on page 88 of PG&E’s 2025 Wildfire Mitigation Plan Update. b) No, outages on DCD-enabled devices are not currently identified separately in the EPSS monthly reports provided to SED. c) Not applicable, please see the response to subpart (b) above. d) No, PG&E does not currently plan to differentiate outages on DCD-enabled devices in future EPSS monthly reports. | Holly Wehrman | 2024-04-15 | 2024-04-18 | 2024-04-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_044.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--14 Effectiveness Analysis for EPSS Including Implementation of DCD | ACI 23-14 Effectiveness Analysis for EPSS |  | CalPA | Set WMP-44 | 9 | 4 | Mona Hedin | Mandy Knockaert | Katherine Hee | Eric Lamoureux | Aaron Shapiro | Mark Quinlan | Yes | Yes | Yes |  |  | Yes |  |  | 2024-04-18 | [16 empty] | 9 | Katherine Hee | Eric Lamoureux | Mona Hedin | Mandy Knockaert | Aaron Shapiro | 4 |  |  |  |  | completed | 0 | 0 | 0 | 0
545 | CalPA | Set WMP-42 | CalPA_Set WMP-42 | 7 | CalPA_Set WMP-42_Q7 | Page 24 of PG&E’s 2025 WMP Update states that PG&E is adjusting target PS-07 (Reduce PSPS Impacts to Customers) in 2025 downward by 40% to account for a 40% decrease in underground miles. Does PG&E expect a similar reduction in the number of EPSS customer events mitigated in 2025? Explain your answer. | While PG&E anticipates EPSS outage volume would reduce commensurately with reduced overhead line exposure, specific EPSS-related outage targets specifically considering reduced UG work have not been calculated. As risk is the primary driver of PG&E’s approach to selecting sites to underground, it is possible portions of a circuit versus the entire circuit may be scoped for undergrounding. As such, portions of the circuit remaining in High Fire Risk Areas (HFRAs) and EPSS buffer areas may continue to be protected by EPSS-capable devices and would be enabled when criteria are met. It is possible a fault may occur downstream of one of these devices when enabled, resulting in an outage impacting downstream customers, regardless of undergrounding status. If undergrounding were to replace all HFRA and EPSS buffer overhead line exposure of a circuit, the circuit would be removed from EPSS scope which would significantly reduce EPSS enablement. Opportunities for full undergrounding continue to be evaluated during project scoping, focusing on undergrounding in areas where it can be most beneficial in reducing wildfire risk as well as PSPS and EPSS impact reduction for customers and critical facilities. | Holly Wehrman | 2024-04-09 | 2024-04-12 | 2024-04-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_042.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--14 Effectiveness Analysis for EPSS Including Implementation of DCD | ACI 23-14 Effectiveness Analysis for EPSS |  | CalPA | Set WMP-42 | 7 | 0 | Mona Hedin | Wilson Wong Saritha Basani | Tommy Van Katherine Hee | Shawn Holder Eric Lamoureux | Kenny Lee | Mark Quinlan | Yes | Yes |  |  |  | Yes | Yes |  | 2024-04-12 | [16 empty] | 7 | Tommy Van Katherine Hee | Shawn Holder Eric Lamoureux | Mona Hedin | Wilson Wong Saritha Basani | Kenny Lee | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
667 | OEIS | 022 | OEIS_022 | 1 | OEIS_022_Q1 | Regarding Monitoring Potential Hazard Trees a. For Focused Tree Inspections, does One VM have the capability to document potential defects or issues found with “inventory only trees”1 so that PG&E may monitor the condition of those trees? b. For all other VM inspection types, are inspectors able to document potential defects or issues found with trees not prescribed for work so that PG&E may monitor the condition of those trees? | a. For the FTI program, the One VM application is not set up to document potential defects or issues with 'inventory only trees." Inspectors prescribe work based off potential defects or issues that would cause the tree to fail within 15 months. Vegetation is inspected twice a year in HFTD areas which allows PG&E to continually monitor the health of the vegetation along its lines. b. For other VM programs housed within One VM, the application is not set up to document potential defects or issues when a tree is not prescribed for work. | Brad Hill | 2024-06-11 | 2024-06-14 | 2024-06-14 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/OEIS_022.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23-19 – Continued Progression of Vegetation Management Maturity | ACI 23-19 Continued Progresion of Vegatation Management Maturity |  | OEIS | 022 | 1 | 2 | Mona Hedin | Cherimae Vail | VMDR | Sarah Carlson | Lauren Ruby | Angela Sanford | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | 2024-06-14 | [16 empty] | 1 | VMDR | Sarah Carlson | Mona Hedin | Cherimae Vail | Lauren Ruby | 2 |  |  |  |  | completed | 0 | 0 | 0 | 0
616 | OEIS | 018 | OEIS_018 | 1 | OEIS_018_Q1 | Regarding FTI Inventory Only Trees In response to Data Request OEIS-P-WMP_2024-PG&E-001, Question 1(b)(i), PG&E stated that “PG&E’s operational approach to FTI was changed to only fill out a TRAQ form on trees prescribed for work.” PG&E describes these trees that are inspected but not prescribed work “inventory only trees.” a. What information does PG&E record in One VM for inventory only trees? b. Provide screenshots of One VM showing the fields inspectors must populate for inventory only trees. | a. Please see “WMP-Discovery2023-2025_DR_OEIS_018-Q001Atch01.xlsx” for a data dictionary for the information we record in One VM for inventory-only trees. Each tab describes the fields populated in One VM and their potential domain values, as follows: • The “VegPoint” tab contains the list of attributes inspectors populate for vegetation points within the One VM application. • The “VM-Prescriptions-c” tab contains the workflow for capturing vegetation details and assigned prescriptions within the One VM application. • The “DV-WorkCode” tab contains the list of all prescription codes available within the One VM application. Please note, these fields are populated by inspectors for both ‘inventory-only’ trees and for trees that require work. b. Please see pages 4-8 of “WMP-Discovery2023-2025_DR_OEIS_018- Q001Atch02.pdf” for screenshots of the fields completed by inspectors when populating ‘inventory only’ tree entries. Please note, the ‘inventory only’ vegetation point is completed once ‘no work needed’ is selected in the drop-down menu for the ”Prescription Action” field in step 13. All subsequent steps would only be for trees prescribed for work. | Brad Hill | 2024-05-03 | 2024-05-08 | 2024-05-08 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/OEIS_018.zip | 2 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23-19 – Continued Progression of Vegetation Management Maturity | ACI 23-19 Continued Progresion of Vegatation Management Maturity |  | OEIS | 018 | 1 | 2 | Mona Hedin | Cherimae Vail | VMDR | Sarah Carlson | Lauren Ruby | Angela Sanford | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | 2024-05-08 | [16 empty] | 1 | VMDR | Sarah Carlson | Mona Hedin | Cherimae Vail | Lauren Ruby | 2 |  |  |  |  | completed | 0 | 0 | 0 | 0
581 | CalPA | Set WMP-44 | CalPA_Set WMP-44 | 11 | CalPA_Set WMP-44_Q11 | Page 97 of PG&E’s 2025 WMP Update states: The 2023 FTI [focused tree inspection] program explored enhanced inspection practices and evaluated improvements to situational awareness to further inform and guide clearance recommendations. Based on results of the program, PG&E is moving forward with executing 1,500 miles of work in 2024.” a) Please describe the results of the program on which PG&E is basing the decision to move forward with executing 1,500 miles of work in 2024. b) Provide any available reports, analyses, or other documentation of the results of the program. | a) The 2023 pilot performed inspections in Areas of Concern (AOC) in Butte, Calaveras, Napa, and El Dorado counties. Inspections utilized Tree Risk Assessment Qualified (TRAQ) arborists exclusively to identify trees to be worked and followed the Distribution Inspection Procedure guidance of Level 1 & Level 2 visual inspections. PG&E also performed 100% Quality Control field review on all miles post-inspection. The pilot yielded 7,170 trees identified for work across approximately 260 miles. In 2024, the program is being expanded to 1,500 miles; the AOCs represent where our distribution system is most likely to see higher rates of tree failures during wildfire season or winter storms. The objective of the program is to reduce vegetation-caused outages and ignitions from occurring in these areas where there is highest potential for such outages and ignitions. To that end, in 2024, a Level 2 visual assessment will be performed on all strike potential trees within the 1,500 miles. TRAQ arborists will continue to be the only inspectors performing inspections. PG&E based its decision to move forward with executing 1,500 miles of FTI work based on internal and external factors that supported program development or maturity. The FTI program was initiated in response to RN-22-09 which committed PG&E to benchmark with other utilities to define best practices and mitigations for hazard tree mitigation, evaluate appropriate inspection intervals and inspection levels. This resulted in PG&E developing its first version of Vegetation Management specific Areas of Concern (AOCs) and a series of commitments to mature the program to more holistic application by 2025. While PG&E was piloting the Focused Tree Inspection program in 2023, RN-23-07 was issued and assigned “Remedy b” which mandated that PG&E create “a plan to fully implement (beyond the pilot) and mature Focused Tree Inspections during the WMP cycle”. This directive required PG&E to continue forward with FTI in advance of completion of the FTI program pilot. In addition to the two revision notices, the FTI program also created responses to address 2023-2025 WMP Decision ACI(s)1 as well as, WMP Maturity Survey questions2. These responses prompted further advancement of the FTI program while it was still in its initial phases of development. Initial mileage targets for the FTI program were higher than the 1,500 miles committed in the 2024 WMP targets. Internal target setting decisions were made based on the operational realities resulting from the initial pilot, as well as the increased rigor and expectations to further enhance a program that focused on hazard tree identification, developing more specific guidance on thresholds for Level 2 inspections as well as continue working to bolster Annual and Second patrol Vegetation Management programs in the HFTD for thorough wildfire mitigation of hazard trees. Footnotes 1. ACI references from 202302025 WMP Decision: PG&E-23-15. Implementation of Focused Tree Inspections and Addressing the Risk from Hazard Trees. PG&E-23- 19. Continued Progression of Vegetation Management Maturity. PG&E-23-21. Identification of High-Risk Species for Focused Tree Inspections 2. 04.01.02.Q01 - Does the vegetation database include all vegetation within the right of the way and within strike of the potential assets? 04.02.02.Q01- Do the measured parameters and procedures applied during vegetation inspections enable identifying higher risk areas and vegetation? 04.02.04.Q04 - Is the relative risk reduction and cost of vegetation inspections considered in strategy development? 04.03.02.Q01- Does the electrical corporation proactively trim trees based on predictive modeling results (such as species-specific vegetative growth and limb, trunk, or root failure rates)? 07.05.01.Q06 - Does the electrical corporation cooperate or participate in best practice sharing through comparing vegetation inspection, management, treatment procedures, training, and lessons learned with other electrical corporations? b) Please see the table below for the results of the 2023 FTI pilot program: | Holly Wehrman | 2024-04-15 | 2024-04-18 | 2024-04-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_044.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23-19 – Continued Progression of Vegetation Management Maturity | ACI 23-19 Continued Progresion of Vegatation Management Maturity |  | CalPA | Set WMP-44 | 11 | 2 | Mona Hedin | Cherimae Vail | VMDR | Bahar Hajian Kamran Rasheed | Lauren Ruby | Peter Kenny | Yes | Yes |  |  |  | Yes | Yes |  | 2024-04-18 | [16 empty] | 11 | VMDR | Bahar Hajian Kamran Rasheed | Mona Hedin | Cherimae Vail | Lauren Ruby | 2 |  |  |  |  | completed | 0 | 0 | 0 | 0
615 | MGRA | Data Request No. 14 | MGRA_Data Request No. 14 | 5 | MGRA_Data Request No. 14_Q5 | How many “false” DCD signals were received that resulted in outages in 2023? What were the number of customers and customer minutes affected? | In 2023, a total of 252 DCD outage events occurred where either: (1) no identifiable visual fault condition could be found following a patrol; or (2) the event was related to planned switching activities. The 252 outages affected 269,307 customers for a total of 55,305,653 total customer interruption minutes. For events where no obvious visual fault condition could be found following a patrol, it is likely—after reviewing event data—that in a portion of these cases, a transient high impedance ground fault occurred but the problem was not identifiable during the visual patrol due to a self-correcting temporary condition (e.g., a branch touching the line and then subsequently falling to ground). In other cases, there may be an explainable nonfault system disturbance that may have led to the DCD event. Therefore, to clarify, PG&E does not consider this category of event generically to be “false” signals. | Joseph Mitchell | 2024-05-02 | 2024-05-13 | 2024-05-13 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_014.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--25 Fire Potential Index (FPI) and Ignition Probability Weather (IPW) Enhancements | ACI 23-25 Fire Potential Index and Ignition Probability Weather Enhancements |  | MGRA | Data Request No. 14 | 5 | 0 | Mona Hedin | Mandy Knockaert | Katherine Hee James Tuccillo | Eric Lamoureux | Aaron Shapiro | Mark Quinlan | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | 2024-05-13 |  | 5/7 - j1oz - extension requested due to SME unavailability | [14 empty] | 5 | Katherine Hee James Tuccillo | Eric Lamoureux | Mona Hedin | Mandy Knockaert | Aaron Shapiro | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
614 | MGRA | Data Request No. 14 | MGRA_Data Request No. 14 | 4 | MGRA_Data Request No. 14_Q4 | Please provide detailed cause information for the 17 “near miss” events that PG&E claims may have been averted by DCD activation, as well as outage dates and times. | Please see the below table for a list of the 17 potentially avoided ignitions PG&E observed in 2023 for which the outage fault was detected by DCD technology. Outages FNL End_Date Cause 23-0087355 6/29/2023 19:34 6/30/2023 10:59 Equipment Failure/Involved 23-0087372 6/29/2023 21:43 6/30/2023 11:28 Vegetation 23-0090190 7/9/2023 2:02 7/9/2023 13:43 Vegetation 23-0090168 7/8/2023 20:52 7/9/2023 19:30 Equipment Failure/Involved 23-0099878 8/3/2023 3:34 8/3/2023 7:59 Equipment Failure/Involved 23-0104635 8/15/2023 13:49 8/15/2023 17:07 Vegetation 23-0108800 8/24/2023 18:00 8/25/2023 13:37 Vegetation 23-0119701 9/22/2023 10:27 9/22/2023 17:12 Vegetation 23-0121348 9/27/2023 8:36 9/27/2023 16:25 Equipment Failure/Involved 23-0126506 10/10/2023 11:38 10/10/2023 22:26 Equipment Failure/Involved 23-0128272 10/14/2023 9:14 10/14/2023 10:07 Animal 23-0128164 10/13/2023 15:55 10/14/2023 17:42 Vegetation 23-0131224 10/23/2023 9:20 10/23/2023 11:53 Vegetation 23-0131619 10/24/2023 3:58 10/24/2023 17:11 Equipment Failure/Involved 23-0133597 10/28/2023 17:43 10/29/2023 9:06 Vegetation 23-0133715 10/29/2023 14:22 10/29/2023 20:44 Equipment Failure/Involved 23-0147117 12/12/2023 16:43 12/12/2023 17:53 Animal | Joseph Mitchell | 2024-05-02 | 2024-05-07 | 2024-05-07 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_014.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--25 Fire Potential Index (FPI) and Ignition Probability Weather (IPW) Enhancements | ACI 23-25 Fire Potential Index and Ignition Probability Weather Enhancements |  | MGRA | Data Request No. 14 | 4 | 0 | Mona Hedin | Mandy Knockaert | Katherine Hee | Eric Lamoureux | Aaron Shapiro | Mark Quinlan | Yes | Yes | Yes | Yes | Yes | Yes |  |  | 2024-05-07 | [16 empty] | 4 | Katherine Hee | Eric Lamoureux | Mona Hedin | Mandy Knockaert | Aaron Shapiro | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
613 | MGRA | Data Request No. 14 | MGRA_Data Request No. 14 | 3 | MGRA_Data Request No. 14_Q3 | Please provide the full cause (as reported to the CPUC) for the ignitions that occurred on the DCD-enabled circuits. | Please see the table below for the full cause, as reported to the CPUC, for ignitions that occurred on the DCD-enabled circuits. Index Date Time HFTD Suspected Cause Failure driver Failure sub-driver Asset Type 20230627 7/2/2023 22:12 Non-HFTD Equipment - PG&E All types of equipment / facility failure Splice/ Clamp/ Connector Primary 20230636 7/4/2023 4:40 Non-HFTD Vegetation Contact from Object Contact - Vegetation Primary 20230676 7/10/2023 21:27 Tier 2 Equipment - PG&E All types of equipment / facility failure Transformer failure Primary 20230692 7/14/2023 4:40 Tier 2 Vegetation Contact from Object Contact - Vegetation Primary 20230716 7/16/2023 20:21 Non-HFTD Vandalism Vandalism Vandalism Primary 20230784 7/27/2023 10:43 Non-HFTD Equipment - PG&E All types of equipment / facility failure Capacitor bank failure Primary 20230842 8/6/2023 10:58 Non-HFTD Contact - 3rd Party Contact from Object Contact - Balloon Primary WMP-Discovery2023-2025_DR_MGRA_014-Q003 Page 2 Index Date Time HFTD Suspected Cause Failure driver Failure sub-driver Asset Type 20230899 8/17/2023 19:37 Non-HFTD Vegetation Contact from Object Contact - Vegetation Primary 20230973 8/29/2023 16:55 Tier 2 Contact - 2nd Party Contact from Object Contact - Vegetation Primary 20231096 9/27/2023 20:09 Non-HFTD Vegetation Contact from Object Contact - Vegetation Primary 20231247N 11/4/2023 13:50 Tier 2 Contact - 3rd Party Contact from Object Contact - Vehicle Primary | Joseph Mitchell | 2024-05-02 | 2024-05-07 | 2024-05-07 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_014.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--25 Fire Potential Index (FPI) and Ignition Probability Weather (IPW) Enhancements | ACI 23-25 Fire Potential Index and Ignition Probability Weather Enhancements |  | MGRA | Data Request No. 14 | 3 | 0 | Mona Hedin | Mandy Knockaert | Nick Babb Krista Benson | Andy Abranches | Aaron Shapiro | Andy Abranches | Yes |  | Yes |  | Yes | Yes |  |  | 2024-05-07 | [16 empty] | 3 | Nick Babb Krista Benson | Andy Abranches | Mona Hedin | Mandy Knockaert | Aaron Shapiro | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
612 | MGRA | Data Request No. 14 | MGRA_Data Request No. 14 | 2 | MGRA_Data Request No. 14_Q2 | Were any of the verified ignitions on DCD-enabled circuits associated with wiredowns? If so provide the wire-down identifier from PG&E’s GIS data, since PG&E included no time data in its wire down data set. | Yes, out of the 11 ignitions that occurred where Downed Conductor Detection (DCD) was enabled on the upstream protective device at the time of the ignition, six ignitions involved one or more primary conductors down. Please see Column A in attachment “WMP-Discovery2023-2025_DR_MGRA_013-Q001Atch01.xlsx” with the following corresponding index numbers for these instances: 20230627; 20230636; 20230716; 20230899; 20230973; and 20231247N. | Joseph Mitchell | 2024-05-02 | 2024-05-07 | 2024-05-07 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_014.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--25 Fire Potential Index (FPI) and Ignition Probability Weather (IPW) Enhancements | ACI 23-25 Fire Potential Index and Ignition Probability Weather Enhancements |  | MGRA | Data Request No. 14 | 2 | 0 | Mona Hedin | Mandy Knockaert | Nick Babb Krista Benson | Andy Abranches | Aaron Shapiro | Andy Abranches | Yes | Yes | Yes |  | Yes | Yes |  |  | 2024-05-07 | [16 empty] | 2 | Nick Babb Krista Benson | Andy Abranches | Mona Hedin | Mandy Knockaert | Aaron Shapiro | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
611 | MGRA | Data Request No. 14 | MGRA_Data Request No. 14 | 1 | MGRA_Data Request No. 14_Q1 | The excel spreadsheet WMP-Discovery2023-2025_DR_MGRA_013- Q001Atch01.xlsx contains 11 ignitions in which the circuit was activated with DCD, while only four occurred in the HFTD. PG&E’s WMP Update says that only two ignitions occurred. Please explain this apparent discrepancy. | PG&E’s previous response includes 11 ignition events where Downed Conductor Detection (DCD) technology was enabled at the time of ignition. In two cases out of the 11 ignitions, including corresponding index numbers 20230692 and 20231247N, the fault associated with the ignition was detected by DCD and resulted in an outage. Note that the other nine incidents are not faults that DCD is designed to catch. | Joseph Mitchell | 2024-05-02 | 2024-05-07 | 2024-05-07 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_014.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--25 Fire Potential Index (FPI) and Ignition Probability Weather (IPW) Enhancements | ACI 23-25 Fire Potential Index and Ignition Probability Weather Enhancements |  | MGRA | Data Request No. 14 | 1 | 0 | Mona Hedin | Mandy Knockaert | Katherine Hee | Eric Lamoureux | Aaron Shapiro | Mark Quinlan | Yes |  |  |  | Yes | Yes |  |  | 2024-05-07 | [16 empty] | 1 | Katherine Hee | Eric Lamoureux | Mona Hedin | Mandy Knockaert | Aaron Shapiro | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
609 | MGRA | Data Request No. 13 | MGRA_Data Request No. 13 | 1 | MGRA_Data Request No. 13_Q1 | The PG&E response supplied to MGRA in WMP-Discovery2023- 2025_DR_MGRA_009-Q015Atch01-IngitionsAT was incomplete and nonresponsive because: a. It contained on ID that could be crossed-referenced to PG&E’s reported ignition data base. b. It contained only ignition date, not ignition time, which makes it impossible to distinguish them, since many ignitions often occur on the same day. The existing response therefore has not been made usable for any potential investigation regarding cause or whether and is of limited utility. Please provide an updated version containing standard ignition IDs and times. | PG&E objects to, and disagrees with, the categorization of its responses to the referenced data requests as being “incomplete and non-responsive.” PG&E notes that the requesting party could have participated in the meet and confer process—as the parties have done multiple times in the past—if it was unhappy with the responses provided and PG&E would have done its best to accommodate the requesting party. a. PG&E objects to subpart (a) on the grounds that it is vague, ambiguous, and confusing. PG&E interprets this subpart as requesting clarification regarding the index number that was included in Column A of “WMP-Discovery2023- 2025_DR_MGRA_009-Q015Atch01.xlsx.” Please note, the index number is the unique identifier for the event in PG&E’s ignitions database. The index number represents the year the ignition occurred and its unique identification number (ID). For example, Index “20220142” represents a year 2022 ignition with the unique id of 0142. b. Please see attachment “WMP-Discovery2023-2025_DR_MGRA_013- Q001Atch01.xlsx” for an updated spreadsheet which includes the time the ignition was reported in Column “C.” Please note, PG&E is unable to confirm the exact start time of an ignition, however, is providing the timestamp for when the first responder reported the incident. | Joseph Mitchell | 2024-04-30 | 2024-05-03 | 2024-05-01 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_013.zip | 1 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--25 Fire Potential Index (FPI) and Ignition Probability Weather (IPW) Enhancements | ACI 23-25 Fire Potential Index and Ignition Probability Weather Enhancements |  | MGRA | Data Request No. 13 | 1 | 2 | Mona Hedin | Mandy Knockaert | Nick Babb | Andy Abranches | Aaron Shapiro | Andy Abranches | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | 2024-05-03 | [16 empty] | 1 | Nick Babb | Andy Abranches | Mona Hedin | Mandy Knockaert | Aaron Shapiro | 2 |  |  |  |  | completed | 0 | 0 | 0 | 0
538 | MGRA | Data Request No. 9 | MGRA_Data Request No. 9 | 16 | MGRA_Data Request No. 9_Q16 | Please provide a list of outages for the last two years including the following additional attributes: a. rating system at the time of the outage (R0, R1, R2, etc) b. whether circuit was implemented with active DCD c. whether circuit was implemented with active EPSS | Please see attachment “WMP-Discovery2023-2025_DR_MGRA_009-Q016Atch01.xlsx” for the requested information. | Joseph Mitchell | 2024-04-08 | 2024-04-17 | 2024-04-17 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_009.zip | 1 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--25 Fire Potential Index (FPI) and Ignition Probability Weather (IPW) Enhancements | ACI 23-25 Fire Potential Index and Ignition Probability Weather Enhancements |  | MGRA | Data Request No. 9 | 16 | 3 | Mona Hedin | Mandy Knockaert | Katherine Hee Shaun Tanner Tom Huynh John Birch | Eric Lamoureux | Aaron Shapiro | Mark Quinlan Martin Wyspianski | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | 2024-04-17 |  | j1oz - 4/12/24 - extension granted per meeting with MGRA | [14 empty] | 16 | Katherine Hee Shaun Tanner Tom Huynh John Birch | Eric Lamoureux | Mona Hedin | Mandy Knockaert | Aaron Shapiro | 3 |  |  |  |  | completed | 0 | 0 | 0 | 0
537 | MGRA | Data Request No. 9 | MGRA_Data Request No. 9 | 15 | MGRA_Data Request No. 9_Q15 | Please provide a list of reportable ignitions for the last two years including the following additional attributes: a. rating system at the time of the ignition (R0, R1, R2, etc) b. whether circuit was implemented with active DCD c. whether circuit was implemented with active EPSS d. whether PSPS was activated anywhere on the system. | Please see attachment “WMP-Discovery2023-2025_DR_MGRA_009-Q015Atch01.xlsx” for the requested information. Please note that for subpart (a), PG&E produces Fire Potential Index (FPI) ratings only for circuits with a Fire Index Area (FIA). | Joseph Mitchell | 2024-04-08 | 2024-04-11 | 2024-04-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_009.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--25 Fire Potential Index (FPI) and Ignition Probability Weather (IPW) Enhancements | ACI 23-25 Fire Potential Index and Ignition Probability Weather Enhancements |  | MGRA | Data Request No. 9 | 15 | 4 | Mona Hedin | Mandy Knockaert | Nick Babb | Andy Abranches | Aaron Shapiro | Andy Abranches |  |  | Yes |  | Yes | Yes |  |  | 2024-04-11 | [16 empty] | 15 | Nick Babb | Andy Abranches | Mona Hedin | Mandy Knockaert | Aaron Shapiro | 4 |  |  |  |  | completed | 0 | 0 | 0 | 0
533 | MGRA | Data Request No. 9 | MGRA_Data Request No. 9 | 11 | MGRA_Data Request No. 9_Q11 | p. 57 - Non-Underground Mitigations “This consideration of location-specific benefits and risks is consistent with the prior decision-tree approach we used to select projects and mitigations for completion in 2023 to 2025.” In what ways does the new calculation differ from the previous decision-tree based analysis and in what ways does it differ? | PG&E objects to this question on the grounds that it is vague and ambiguous, including that the repetition of the statement “in what ways does [it] differ” may imply that the intent of the question may have not been fully articulated. Nonetheless, PG&E interprets the question as asking for clarity on the difference between the Wildfire Benefit Cost Analysis (WBCA), which we interpret to be the “new calculation” referenced in the question, and the tools used to select system hardening projects prior to the WBCA tool. We have, therefore, answered based on that understanding of the question. PG&E’s system hardening program starts by using a model to determine where (which circuit segments) we should complete wildfire system hardening work. Once a circuit segment is selected, PG&E’s Grid Design engineers use a decision tree to evaluate the sections of that circuit segment to determine the right mitigation approach along the circuit segment. The primary element that has changed over the last few years is the “model” used to select the majority of circuit segments to then be scoped for hardening, for example: • Projects selected using PG&E’s Wildfire Distribution Risk Model (WDRM) v2 identified work located in the top 20% circuit segments, selected solely based on wildfire risk scores, and • Projects selected using WDRM v3 incorporated feasibility factors in combination with wildfire risk scores to create a Wildfire Feasibility Effectiveness (WFE) score. Going forward, the WBCA is an analytical framework that will compute the total lifetime costs and total lifetime benefits of different mitigations, and combinations of mitigations, at the circuit segment level. As discussed in our 2025 WMP update, the WBCA tool incorporates wildfire risk, as well as reliability, public safety, and cost efficiency in accordance with the requirements of SB 884. Reliability and public safety are new inputs to the selection process that is used by the WBCA which informs the selection of hardening projects from these additional inputs. The cost efficiency data incorporated into WBCA is more comprehensive than the feasibility score used in WFE. Cost efficiency accounts for benefits associated with wildfire, public safety, and reliability risk reduction, as well as costs associated with vegetation management, lifecycle maintenance costs/operating expenses of various mitigations. Cost efficiency also includes the upfront capital installation costs which were previously incorporated into the WFE score. Once a project is selected for hardening using the appropriate model as described above, the decision tree was/is used to assess circuit segment factors along the length of the segment to: (a) incorporate the reality that all conditions are not uniform along the length of a circuit segment and different approaches may be necessary within a single circuit segment; and (b) account for additional factors not fully captured by the model used to select projects. These factors include: (1) tree fall-in risk; (2) ingress/egress risk; and (3) PSPS mitigation (see PG&E’s 2023-2025 Base WMP R5 at page 430). In summary, the decision tree approach used by our Grid Engineers to scope hardening projects is very similar from 2023-2025 and into the future. What is changing is our analytical “model” being used to select which circuit segments to harden as the WBCA tool represents a meaningful step forward, incorporating additional inputs (as described above) from the WDRM v2 or WDRM v3/WFE models that were used in the past to select nearly all of the 2023-2025 projects. | Joseph Mitchell | 2024-04-08 | 2024-04-11 | 2024-04-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_009.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--25 Fire Potential Index (FPI) and Ignition Probability Weather (IPW) Enhancements | ACI 23-25 Fire Potential Index and Ignition Probability Weather Enhancements |  | MGRA | Data Request No. 9 | 11 | 0 | Mona Hedin | Mandy Knockaert | UG Team Benson Wong James Ash Jr | Paul McGregor Megan Ardell | Aaron Shapiro | Andy Abranches | Yes | Yes | Yes |  | Yes | Yes |  |  | 2024-04-11 | [16 empty] | 11 | UG Team Benson Wong James Ash Jr | Paul McGregor Megan Ardell | Mona Hedin | Mandy Knockaert | Aaron Shapiro | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
532 | MGRA | Data Request No. 9 | MGRA_Data Request No. 9 | 10 | MGRA_Data Request No. 9_Q10 | Please provide the above table ACI-PG&E-23-05-3 under the assumption that Covered Conductor wildfire ignition reduction effectiveness is 85.0%, not 66.4%. | This is not feasible to provide based on the methodology of PG&E’s study. Mitigation effectiveness cannot be predetermined (i.e. 85% overall wildfire ignition reduction effectiveness is not an input). Rather, the average effectiveness value of 66.4% is the result of assessing the aggregated mitigation effectiveness against more the 2,000 modes of failure, each with an effectiveness ranging from 0% to 100%. Much of the benefits of covered conductor overlap the benefits of the operational mitigations, such as EPSS. Because of that, we chose a more granular analysis of outage causes to assign effectiveness to differentiate the multiple combined mitigations so as not to “double count” benefits. | Joseph Mitchell | 2024-04-08 | 2024-04-11 | 2024-04-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_009.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--25 Fire Potential Index (FPI) and Ignition Probability Weather (IPW) Enhancements | ACI 23-25 Fire Potential Index and Ignition Probability Weather Enhancements |  | MGRA | Data Request No. 9 | 10 | 0 | Mona Hedin | Mandy Knockaert | UG Team Benson Wong James Ash Jr Brad Koelling | Paul McGregor Eric Lamoureux Jim Gill | Aaron Shapiro | Andy Abranches | Yes | Yes | Yes |  | Yes | Yes |  |  | 2024-04-11 | [16 empty] | 10 | UG Team Benson Wong James Ash Jr Brad Koelling | Paul McGregor Eric Lamoureux Jim Gill | Mona Hedin | Mandy Knockaert | Aaron Shapiro | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
531 | MGRA | Data Request No. 9 | MGRA_Data Request No. 9 | 9 | MGRA_Data Request No. 9_Q9 | Table ACI-PG&E-23-05-3: Ignition mitigation effectiveness For Alt 4 – Covered conductor + EPSS, effectiveness is rated at 78.2%. Alt 9 includes CC + EPSS, but also REFCL and DCD and shows an effectiveness of 65%. How is it possible that adding additional mitigations reduces the effectiveness? If this calculation is in error please provide a corrected value. Perform this as a circuit analysis, not a substation analysis, assuming all circuits are REFCL enabled. | The reported blended average effectiveness for Alt 9 was based on a study focused on a specific subset of circuits where REFCL could be utilized. This same Alt 9 analysis cannot be performed assuming all circuits are REFCL enabled. The REFCL analysis was applied to substations that met the following requirements: • Single voltage 3 wire 12 kV substation; • Minimum of 20 OH miles in HFTD; • Less than 50% of circuit UG; and • Less than 20% of circuit past autobanks. The effectiveness of the other mitigation types (CC Overhead, EPSS, DCD) on the Alt 9 population is less in comparison to that of the full population in the Alt 4 study. Therefore, the overall blended average effectiveness of Alt 9 is lower than Alt 4. | Joseph Mitchell | 2024-04-08 | 2024-04-11 | 2024-04-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_009.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--25 Fire Potential Index (FPI) and Ignition Probability Weather (IPW) Enhancements | ACI 23-25 Fire Potential Index and Ignition Probability Weather Enhancements |  | MGRA | Data Request No. 9 | 9 | 0 | Mona Hedin | Mandy Knockaert | UG Team Julie Cerio Jerry Santos Lucy Morris Benson Wong James Ash Jr Brad Koelling | Paul McGregor Eric Lamoureux Jim Gill | Aaron Shapiro | Andy Abranches | Yes | Yes | Yes |  | Yes | Yes | Yes |  | 2024-04-11 | [16 empty] | 9 | UG Team Julie Cerio Jerry Santos Lucy Morris Benson Wong James Ash Jr Brad Koelling | Paul McGregor Eric Lamoureux Jim Gill | Mona Hedin | Mandy Knockaert | Aaron Shapiro | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
526 | MGRA | Data Request No. 9 | MGRA_Data Request No. 9 | 4 | MGRA_Data Request No. 9_Q4 | Will the “dry wind” weather days be associated with a probability driver also correlated with “dry wind” weather days and if howso. | PG&E interprets this question to ask whether the dry wind days data, used in the development of Wildfire Consequence, is directly used in the development of the probability of ignition sub models. If so, the response is: no, but the same source meteorological wind and humidity observations used in the development of the dry wind days in the wildfire consequence model are used in the development of the probability of ignition sub-models. | Joseph Mitchell | 2024-04-08 | 2024-04-11 | 2024-04-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_009.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--25 Fire Potential Index (FPI) and Ignition Probability Weather (IPW) Enhancements | ACI 23-25 Fire Potential Index and Ignition Probability Weather Enhancements |  | MGRA | Data Request No. 9 | 4 | 0 | Mona Hedin | Mandy Knockaert | Jon Eric Thalman | Andy Abranches | Aaron Shapiro | Andy Abranches | Yes | Yes | Yes |  | Yes | Yes | Yes |  | 2024-04-11 | [16 empty] | 4 | Jon Eric Thalman | Andy Abranches | Mona Hedin | Mandy Knockaert | Aaron Shapiro | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
525 | MGRA | Data Request No. 9 | MGRA_Data Request No. 9 | 3 | MGRA_Data Request No. 9_Q3 | Will this “dry wind” consequence assessment also be couple to driver weather days also characterized by high winds? | PG&E interprets this question to be requesting whether the dry wind definition corresponds to days with drier weather and higher winds. In this case, yes, the dry wind definition is based on relative humidity being lower than a threshold and the wind speed being higher than a threshold. In this way, it does serve to identify dry and windy days. | Joseph Mitchell | 2024-04-08 | 2024-04-11 | 2024-04-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_009.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--25 Fire Potential Index (FPI) and Ignition Probability Weather (IPW) Enhancements | ACI 23-25 Fire Potential Index and Ignition Probability Weather Enhancements |  | MGRA | Data Request No. 9 | 3 | 0 | Mona Hedin | Mandy Knockaert | Jon Eric Thalman | Andy Abranches | Aaron Shapiro | Andy Abranches | Yes | Yes | Yes |  | Yes | Yes | Yes |  | 2024-04-11 | [16 empty] | 3 | Jon Eric Thalman | Andy Abranches | Mona Hedin | Mandy Knockaert | Aaron Shapiro | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
524 | MGRA | Data Request No. 9 | MGRA_Data Request No. 9 | 2 | MGRA_Data Request No. 9_Q2 | Please provide information available on the introduction of “an assessment of dry wind conditions for predicting areas of high consequence”. | As indicated on page 10 of the 2025 PG&E WMP Update, one of the key updates to the v4 Wildfire Consequence (WFC) model is the addition of an analog for Red Flag conditions. Red Flag conditions are correlated with fire outcomes. However, due to inconsistencies with the way Red Flag conditions are forecast and reported, a proxy for Red Flag conditions has been developed that is consistent across the territory. The WFC model uses one of the definitions for Red Flag conditions found in Northern California and estimates the so-called “dry wind” conditions from PG&E historic meteorology data. Dry wind conditions enter as a partition in the baseline consequence model, similar to the way the risk bowtie uses Red Flag warnings. Like Red Flag warnings, dry wind remains correlated with severe fire outcomes. However, the additional explanatory power of dry wind over the predicted destructive condition has proven to be more modest. | Joseph Mitchell | 2024-04-08 | 2024-04-11 | 2024-04-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_009.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--25 Fire Potential Index (FPI) and Ignition Probability Weather (IPW) Enhancements | ACI 23-25 Fire Potential Index and Ignition Probability Weather Enhancements |  | MGRA | Data Request No. 9 | 2 | 0 | Mona Hedin | Mandy Knockaert | Jon Eric Thalman | Andy Abranches | Aaron Shapiro | Andy Abranches | Yes | Yes | Yes |  | Yes | Yes | Yes |  | 2024-04-11 | [16 empty] | 2 | Jon Eric Thalman | Andy Abranches | Mona Hedin | Mandy Knockaert | Aaron Shapiro | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
523 | MGRA | Data Request No. 9 | MGRA_Data Request No. 9 | 1 | MGRA_Data Request No. 9_Q1 | Table PG&E-B.1.1-2 Event Probability Model Predictive Performance In the table, predictive ability for drivers of ignitions from Primary Conductor (Other, Wire Down) fare relatively poorly compared to regular attributes. Explain why this is so. | This is a topic of current study. The wire-down model addresses primary wire-down ignitions due to equipment failures and not vegetation related failures. Current investigations are focused on the fact that most failure events occur in coastal areas and ignitions do not follow the same pattern. Work is ongoing to improve the model’s ability to represent this spatial pattern | Joseph Mitchell | 2024-04-08 | 2024-04-11 | 2024-04-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_009.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--25 Fire Potential Index (FPI) and Ignition Probability Weather (IPW) Enhancements | ACI 23-25 Fire Potential Index and Ignition Probability Weather Enhancements |  | MGRA | Data Request No. 9 | 1 | 0 | Mona Hedin | Mandy Knockaert | Jon Eric Thalman | Andy Abranches | Aaron Shapiro | Andy Abranches | Yes | Yes | Yes |  | Yes | Yes |  |  | 2024-04-11 | [16 empty] | 1 | Jon Eric Thalman | Andy Abranches | Mona Hedin | Mandy Knockaert | Aaron Shapiro | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
618 | CPUC - SPD (Safety Policy Division) | 013 | CPUC - SPD (Safety Policy Division)_013 | 1 | CPUC - SPD (Safety Policy Division)_013_Q1 | I’m looking for the following documents: Data Request: CalAdvocates_039-Q014 (CalAdvocates-PGE2025WMP-03) Data Request Date: March 22, 2024 PG&E Date of Response to Data Request: April 5, 2024 PG&E Document No. or Title: WMP-Discovery2023-2025_DR_CalAdvocates_039-Q014Atch01CONF.xlsx WMP-Discovery2023-2025_DR_CalAdvocates_039-Q014Atch02CONF.xlsx WMP-Discovery2023-2025_DR_CalAdvocates_039-Q014Atch03CONF.xlsx WMP-Discovery2023-2025_DR_CalAdvocates_039-Q014Atch04CONF.xlsx | Please see the following files for the requested information. Please note, these attachments were provided as pdf files and not excel files. • WMP-Discovery2023-2025_DR_CalAdvocates_039-Q014Rev01Atch01CONF.pdf • WMP-Discovery2023-2025_DR_CalAdvocates_039-Q014Rev01Atch02CONF.pdf • WMP-Discovery2023-2025_DR_CalAdvocates_039-Q014Rev01Atch03CONF.pdf • WMP-Discovery2023-2025_DR_CalAdvocates_039-Q014Atch04CONF.pdf While reviewing your request, PG&E identified confidential information that was erroneously left unmarked in Attachments 01-03, submitted to The Public Advocates Office (CalAdvocates) on April 5, 2024. PG&E has amended its response to CalAdvocates and is providing the updated, amended, Attachments 01-03. | Henry Sweat | 2024-05-14 | 2024-05-22 | 2024-05-16 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_013.zip | 4 | N/A | 8 | Section 8.3 - Situational Awareness and Forecasting | 8.3.4.1 Existing Ignition Detection Sensors and Systems | ACI 23-25 Fire Potential Index and Ignition Probability Weather Enhancements |  | CPUC - SPD (Safety Policy Division) | 013 | 1 | 0 | Mona Hedin | Hema Sukumar | Nick Babb | Andy Abranches | Aaron Shapiro | Mark Quinlan | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | 2024-05-22 | [16 empty] | 1 | Nick Babb | Andy Abranches | Mona Hedin | Hema Sukumar | Aaron Shapiro | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
578 | CalPA | Set WMP-44 | CalPA_Set WMP-44 | 8 | CalPA_Set WMP-44_Q8 | Figure ACI-PG&E-23-02-1 on page 40 of PG&E’s 2025 WMP Update indicates that wildfire risk is approximately $20,668 million, and PSPS and EPSS combined reduce the wildfire risk by approximately $16.359 million. a) Has PG&E estimated the incremental wildfire risk reduction (in dollars) attributed to widescale deployment of REFCL? Please provide this estimate if yes. b) If the answer to part (a) is no, why has PG&E not conducted that analysis? c) Has PG&E estimated the incremental risk increase attributed to widescale deployment of REFCL? Please provide this estimate if yes. d) If the answer to part (c) is no, why has PG&E not conducted that analysis? e) Has PG&E estimated the incremental lifetime expenditure attributed to widescale deployment of REFCL? Please provide this estimate if yes. f) If the answer to part (e) is no, why has PG&E not conducted that analysis? | a) No, PG&E has not estimated the incremental wildfire risk reduction (in dollars) attributed to widescale deployment of REFCL. b) This study has not been conducted because REFCL cannot be deployed widescale on PG&E’s electric assets. REFCL can only be applied to substations that meet the following minimum requirements: • Single voltage 3-wire 12 kV substation; • At least 20 overhead miles in HFTD; • Less than 50% of circuit underground; • Less than 20% of circuit past autobanks; and • Sufficient physical space to deploy equipment. c) PG&E has not estimated the incremental risk increase attributed to widescale deployment of REFCL. d) Please see the response to subpart (b) above, as the reasoning is the same. e) PG&E has not estimated the incremental lifetime expenditure attributed to widescale deployment of REFCL. f) Please see the response to subpart (b) above, as the reasoning is the same. | Holly Wehrman | 2024-04-15 | 2024-04-18 | 2024-04-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_044.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23-02 – PSPS and Wildfire Risk Trade-Off Transparency | ACI PG&E-23-02 – PSPS and Wildfire Risk Trade-Off Transparency |  | CalPA | Set WMP-44 | 8 | 6 | Mona Hedin | Mandy Knockaert | Benson Wong James Ash | Paul McGregor Jim Gill | Aaron Shapiro | Martin Wyspianski | Yes | Yes | Yes |  | Yes | Yes | Yes |  | 2024-04-18 | [16 empty] | 8 | Benson Wong James Ash | Paul McGregor Jim Gill | Mona Hedin | Mandy Knockaert | Aaron Shapiro | 6 |  |  |  |  | completed | 0 | 0 | 0 | 0
577 | CalPA | Set WMP-44 | CalPA_Set WMP-44 | 7 | CalPA_Set WMP-44_Q7 | Figure ACI-PG&E-23-02-1 on page 40 of PG&E’s 2025 WMP Update indicates that wildfire risk is approximately $20,668 million, and PSPS and EPSS combined reduce the wildfire risk by approximately $16.359 million. a) Are the $20,668 million wildfire risk and the $16.359 million risk reduction estimates annual values? Please explain if no. b) Do the $20,668 million wildfire risk and the $16.359 million risk reduction estimates apply to PG&E’s entire service territory? Please explain if no. | a) The $20,668 million wildfire risk and respective $16,359 million risk reduction are both annual values. b) The $20,668 million wildfire risk and respective $16,359 million risk reduction apply to PG&E’s entire service territory, but this risk is densely focused within the HFTD and HFRA. | Holly Wehrman | 2024-04-15 | 2024-04-18 | 2024-04-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_044.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23-02 – PSPS and Wildfire Risk Trade-Off Transparency | ACI PG&E-23-02 – PSPS and Wildfire Risk Trade-Off Transparency |  | CalPA | Set WMP-44 | 7 | 2 | Mona Hedin | Mandy Knockaert | Benson Wong James Ash | Paul McGregor | Aaron Shapiro | Andy Abranches | Yes | Yes | Yes |  |  | Yes | Yes |  | 2024-04-18 | [16 empty] | 7 | Benson Wong James Ash | Paul McGregor | Mona Hedin | Mandy Knockaert | Aaron Shapiro | 2 |  |  |  |  | completed | 0 | 0 | 0 | 0
576 | CalPA | Set WMP-44 | CalPA_Set WMP-44 | 6 | CalPA_Set WMP-44_Q6 | Figure ACI-PG&E-23-02-1 on page 40 of PG&E’s 2025 WMP Update states, “When considering the overall Wildfire Risk with EPSS and PSPS, this is still ~3x of Distribution Overhead.” a) Define the phrase “Distribution Overhead” in this context. b) Please state the significance of the “~3x” ratio of “overall Wildfire Risk with EPSS and PSPS” compared to “Distribution Overhead.” | a) “Distribution Overhead” in this context refers to the reliability risks associated with PG&E’s “Failure of Electric Distribution Overhead Assets” risk, excluding EPSS and PSPS outages, from its forthcoming 2024 RAMP Report. This risk was previewed in the February 7, 2024 CPUC-hosted PG&E 2024 RAMP (pre-filing) workshop #1. b) The significance of this statement is to emphasize that Wildfire Risk is still the primary focus of system hardening mitigations, rather than reliability risks. | Holly Wehrman | 2024-04-15 | 2024-04-18 | 2024-04-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_044.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23-02 – PSPS and Wildfire Risk Trade-Off Transparency | ACI PG&E-23-02 – PSPS and Wildfire Risk Trade-Off Transparency |  | CalPA | Set WMP-44 | 6 | 2 | Mona Hedin | Mandy Knockaert | Benson Wong James Ash | Paul McGregor | Aaron Shapiro | Andy Abranches | Yes | Yes | Yes |  |  | Yes | Yes |  | 2024-04-18 | [16 empty] | 6 | Benson Wong James Ash | Paul McGregor | Mona Hedin | Mandy Knockaert | Aaron Shapiro | 2 |  |  |  |  | completed | 0 | 0 | 0 | 0
601 | MGRA | Data Request No. 12 | MGRA_Data Request No. 12 | 1 | MGRA_Data Request No. 12_Q1 | Please provide an Excel spreadsheet giving the mapping between PG&E weather station IDs and IDs used by Synoptic for the PG&E mesonet if these IDs are different. | PG&E weather station identification numbers (ID) directly correspond to Synoptic weather station IDs. However, Synoptic allows less characters for their IDs. PG&E slightly alters their 8-digit weather IDs to accommodate this character limit by removing the first digit of PG&E’s ID. For example, PG&E weather station with Synoptic ID "PG868" reflects PG&E weather station “PGE-1868” and Synoptic ID “608PG” reflects “PGE-2608”. | Joseph Mitchell | 2024-04-25 | 2024-04-30 | 2024-04-29 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_012.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23-23 – Weather Station Maintenance and Calibration | ACI PG&E-23-23 – Weather Station Maintenance and Calibration |  | MGRA | Data Request No. 12 | 1 | 0 | Mona Hedin | Mandy Knockaert | Josh VandeVelde Bria Goggins | David Klein | Aaron Shapiro | Mark Quinlan | Yes | Yes | Yes |  | Yes | Yes |  |  | 2024-04-30 | [16 empty] | 1 | Josh VandeVelde Bria Goggins | David Klein | Mona Hedin | Mandy Knockaert | Aaron Shapiro | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
583 | CalPA | Set WMP-44 | CalPA_Set WMP-44 | 13 | CalPA_Set WMP-44_Q13 | Table ACI-PG&E-23-23-1 on page 113 of PG&E’s 2025 WMP Update includes the following entry: a) Explain why the last calibration date of this weather station was recorded as 11/1/2022, over one month after the station was removed on September 17, 2022. b) Provide any records of the calibration on 11/1/2022. c) When did PG&E become aware that the station had been removed? d) When does PG&E plan to relocate the station? | a) This calibration date was recorded erroneously due to a data pull error. This station has never been calibrated as it was removed on July 19, 2021, due to a pole replacement and then asked to be relocated due to shading. This station was originally installed in August 2020. b) There is no proof of calibration since the station was installed for under 12 months. c) The station was scheduled by PG&E to be removed due to a pole replacement on July 19, 2021. d) PG&E is currently working on reinstalling this station. | Holly Wehrman | 2024-04-15 | 2024-04-18 | 2024-04-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_044.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23-23 – Weather Station Maintenance and Calibration | ACI PG&E-23-23 – Weather Station Maintenance and Calibration |  | CalPA | Set WMP-44 | 13 | 4 | Mona Hedin | Mandy Knockaert | Josh VandeVelde Bria Goggins | David Klein | Aaron Shapiro | Mark Quinlan | Yes |  | Yes |  | Yes | Yes | Yes |  | 2024-04-18 | [16 empty] | 13 | Josh VandeVelde Bria Goggins | David Klein | Mona Hedin | Mandy Knockaert | Aaron Shapiro | 4 |  |  |  |  | completed | 0 | 0 | 0 | 0
582 | CalPA | Set WMP-44 | CalPA_Set WMP-44 | 12 | CalPA_Set WMP-44_Q12 | Table ACI-PG&E-23-23-1 on page 112 of PG&E’s 2025 WMP Update includes the following entry: a) Explain why the last calibration date of this weather station was recorded as 9/1/2022, over three months after the site was destroyed on May 21, 2022. b) Provide any records of the calibration on 9/1/2022. c) When did PG&E become aware that the site had been destroyed? d) When does PG&E plan to replace the destroyed site? | a) The September 1, 2022, date, was the scheduled due date for the calibration and recorded by erroneously due to a data pull error. The actual date for the last calibration was August 4, 2021. b) Please see response to subpart A. The September 1, 2022, date was recorded in error. c) PG&E first became aware of an issue with this weather station around June 6, 2022. PG&E was able to confirm the site had been destroyed during the 2022 scheduled calibration on July 29, 2022. d) PG&E is currently working on reinstalling this station. | Holly Wehrman | 2024-04-15 | 2024-04-18 | 2024-04-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_044.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23-23 – Weather Station Maintenance and Calibration | ACI PG&E-23-23 – Weather Station Maintenance and Calibration |  | CalPA | Set WMP-44 | 12 | 4 | Mona Hedin | Mandy Knockaert | Josh VandeVelde Bria Goggins | David Klein | Aaron Shapiro | Mark Quinlan | Yes | Yes | Yes |  | Yes | Yes | Yes |  | 2024-04-18 | [16 empty] | 12 | Josh VandeVelde Bria Goggins | David Klein | Mona Hedin | Mandy Knockaert | Aaron Shapiro | 4 |  |  |  |  | completed | 0 | 0 | 0 | 0
630 | OEIS | 019 | OEIS_019 | 2 | OEIS_019_Q2 | WMP-Discovery2023- 2025_DR_OEIS_016-Q003Supp01Atch01.xlsx, attached to Data Request OEIS_016-Q003, only shows 14 circuit segments, whereas the original Tables 6-5 and 7-2 in the 2023-2025 WMP have 41 circuit segments listed. a. Provide the number of circuit segments used to determine the top 5% for both the original tables (V3) and the updated tables (V4). b. Provide the overall utility risk score used to determine the top 5% for both the original tables (V3) and the updated tables (V4). | a. PG&E used the following number of circuit segments to determine the top 5% for the referenced version(v)3 and v4 WDRM model: • WDRM v3 – 11,171 circuit segments, risk ranked by total utility risk summary. • WDRM v4 – 11,482 circuit segments, risk ranked by total utility risk summary. b. PG&E used the following utility risk scores to determine the top 5% for the referenced (v)3 and v4 WDRM model: • WDRM v3 + Public Safety Power Shutoff (PSPS): 25,146.54. • WDRM v4 + PSPS: 25,103.75. | Brad Hill | 2024-05-16 | 2024-05-21 | 2024-05-21 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/OEIS_019.zip | 0 | N/A | 6.1.2 | Section 6 - Risk Methodology and Assessment | 6.1.2 Summary of Risk Models | B.1.1. WDRM v4 |  | OEIS | 019 | 2 | 2 | Mona Hedin | Mandy Knockaert | Richard Anderson | Jon Eric Thalman | Aaron Shapiro | Andy Abranches | Yes | Yes | Yes |  | Yes | Yes | Yes |  | 2024-05-21 | [16 empty] | 2 | Richard Anderson | Jon Eric Thalman | Mona Hedin | Mandy Knockaert | Aaron Shapiro | 2 |  |  |  |  | completed | 0 | 0 | 0 | 0
600 | OEIS | 016 | OEIS_016 | 3 | OEIS_016_Q3 | Q03. Regarding PG&E’s Adjustments to its WDRM In its 2025 WMP Update, PG&E discusses the changes made between its Wildfire Distribution Risk Model (WDRM) Version 3 (V3) to Version 4 (V4). Based off those changes, provide: a. An updated version of Table 6-5 from its 2023-2025 WMP based on any changes made to the top risk circuit segments between V3 and V4. b. An updated version of Table 7-2 from its 2023-2025 WMP based on any changes made to the top risk circuit segments between V3 and V4. c. An updated version of Table 6-5 from its 2023-2025 WMP based on any changes made to the top risk circuit segments between V3 and V4. d. An updated version of Figure 7-1 from its 2023-2025 WMP based on any changes made to the top risk circuit segments between V3 and V4. e. An updated version of Table 7-4 from its 2023-2025 WMP based on any changes made to the top risk circuit segments between V3 and V4. f. A graph demonstrating the overlayed risk scores between V3 and V4, similar to the graph provided in Data Request OEIS-PG&E-22-016 Question 17 showing the difference in output between V2 and V3. | PG&E released WDRM v4 for use in January of 2024 and is currently evaluating associated work plans in future years anticipated to be described in PG&E’s 2026 WMP. Much of the analysis for the tables and figures requested in parts (a) through (f) below are included in this work and are underway. As this analysis only recently started and is still ongoing, parts (a) through (d) and (f) will require more time and part (e) will not be available until later in 2024. Please let us know if you would like to meet and confer to discuss this request, the work that needs to be done to create the requested information, and why the information is not currently available. a. The information being requested is under development and anticipated to be available around May 8, 2024. b. The information being requested is under development and anticipated to be available around May 8, 2024. c. The information being requested is under development and anticipated to be available around May 8, 2024. d. The information being requested is under development and anticipated to be available around May 8, 2024. PG&E will provide this information once it is available. However, we anticipate this analysis taking several months to complete as the WDRM v4 model was only recently released. We will provide this information once it is available. | Brad Hill | 2024-04-22 | 2024-04-25 | 2024-04-25 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/OEIS_016.zip | 0 | N/A | 6 | Section 6 - Risk Methodology and Assessment | 6.1.2 Summary of Risk Models | B.1.1. WDRM v4 |  | OEIS | 016 | 3 | 6 | Mona Hedin | Mandy Knockaert | Richard Anderson | Jon Eric Thalman | Aaron Shapiro | Andy Abranches | Yes | Yes | Yes |  | Yes | Yes | Yes |  | 2024-04-25 | [16 empty] | 3 | Richard Anderson | Jon Eric Thalman | Mona Hedin | Mandy Knockaert | Aaron Shapiro | 6 |  |  |  |  | completed | 0 | 0 | 0 | 0
643 | CPUC - SPD (Safety Policy Division) | 015 | CPUC - SPD (Safety Policy Division)_015 | 1 | CPUC - SPD (Safety Policy Division)_015_Q1 | I’m requesting these files: Data Request: CalAdvocates_041-Q003 (CalAdvocates-PGE2025WMP-05) Data Request Date: April 8, 2024 PG&E Date of Response to Data Request: April 29, 2024 PG&E Document No. or Title: WMP-Discovery2023-2025_DR_CalAdvocates_041-Q003Atch01CONF.zip | Please see the following for PG&E’s complete response to WMP-Discovery2023-2025_DR_CalAdvocates_041-Q003: • WMP-Discovery2023-2025_DR_CalAdvocates_041-Q003.pdf • WMP-Discovery2023-2025_DR_CalAdvocates_041-Q003Atch01CONF.zip • WMP-Discovery2023-2025_DR_CalAdvocates_041-Q003Atch02.xlsx | Henry Sweat | 2024-05-24 | 2024-05-28 | 2024-05-28 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_015.zip | 3 | N/A | 6 | Section 6 - Risk Methodology and Assessment | 6.1.2 Summary of Risk Models | B.1.1. WDRM v4 |  | CPUC - SPD (Safety Policy Division) | 015 | 1 | 0 | Mona Hedin | Mandy Knockaert | Richard Anderson Eszter Tompos | Jon Eric Thalman | Aaron Shapiro | Andy Abranches | [8 empty] | 2024-05-28 | [16 empty] | 1 | Richard Anderson Eszter Tompos | Jon Eric Thalman | Mona Hedin | Mandy Knockaert | Aaron Shapiro | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
714 | CalPA | Set WMP-53 | CalPA_Set WMP-53 | 6 | CalPA_Set WMP-53_Q6 | In response to CalAdvocates-PGE-2025WMP-05 Question 9 on whether PG&E has created a detailed overview document that details WDRM v4, PG&E answered that “PG&E is currently creating the detailed overview documentation for the WDRM v4. It is scheduled to be available by the end of Q2 2024.” a) If the detailed overview document has been completed, please provide a copy, including any supporting workpapers. b) If instead the detailed overview document has not been completed, when does PG&E expect the document to be completed? | a) Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_053-Q006Atch01CONF.zip” for the requested WDRM v4 documentation suite. b) Not applicable, please see the response to subpart (a) above. | Matthew Taul | 2024-09-18 | 2024-10-02 | 2024-09-27 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_053.zip | 1 | N/A | 6.1.2 | Section 6 - Risk Methodology and Assessment | 6.1.2 Summary of Risk Models | B.1.1. WDRM v4 |  | CalPA | Set WMP-53 | 6 | 2 | Kevin Laxalt-Nomura | Nelson Lau | Richard Anderson | Jon Eric Thalman | Aaron Shapiro | Andy Abranches | Yes | Yes | Yes | [5 empty] | 2024-10-02 | [17 empty] | Richard Anderson | Jon Eric Thalman | Kevin Laxalt-Nomura | Nelson Lau | Aaron Shapiro | [5 empty] | completed | 0 | 0 | 0 | 0
713 | CalPA | Set WMP-53 | CalPA_Set WMP-53 | 5 | CalPA_Set WMP-53_Q5 | In response to CalAdvocates-PGE-2025WMP-05 Question 8 on whether an entity was performing an independent review of WDRM V4, PG&E answered that “The E3 review is scheduled to be available by the end of Q2 2024.” a) If the E3 independent review of the WDRM v4 has completed, please provide a copy of any reports and outputs. b) If instead the E3 independent review has not concluded, when does PG&E expect the review to be completed? | a) Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_053-Q005Atch01CONF.pdf” for the requested E3 Review of PG&E WDRM v4 and Transmission Composite Model (TCM). b) Not applicable, please see the response to subpart (a) above. | Matthew Taul | 2024-09-18 | 2024-10-02 | 2024-09-27 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_053.zip | 1 | N/A | 6.1.2 | Section 6 - Risk Methodology and Assessment | 6.1.2 Summary of Risk Models | B.1.1. WDRM v4 |  | CalPA | Set WMP-53 | 5 | 2 | Kevin Laxalt-Nomura | Nelson Lau | Richard Anderson | Jon Eric Thalman | Aaron Shapiro | Andy Abranches | Yes | Yes | Yes | [5 empty] | 2024-10-02 | [17 empty] | Richard Anderson | Jon Eric Thalman | Kevin Laxalt-Nomura | Nelson Lau | Aaron Shapiro | [5 empty] | completed | 0 | 0 | 0 | 0
712 | CalPA | Set WMP-53 | CalPA_Set WMP-53 | 4 | CalPA_Set WMP-53_Q4 | For those probability models for ignition risk left out of WDRM v4 that were present in WDRM v3, please explain the reasons this model was excluded in the most recent version. In the event this risk model was incorporated into a different model in WDRM v4, please clarify. | There were no probability models left out of WDRM v4 that were present in WDRM v3. Please reference PG&E’s response to Question No. 001, which provides the correct mapping between models. | Matthew Taul | 2024-09-18 | 2024-10-02 | 2024-09-27 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_053.zip | 0 | N/A | 6.1.2 | Section 6 - Risk Methodology and Assessment | 6.1.2 Summary of Risk Models | B.1.1. WDRM v4 |  | CalPA | Set WMP-53 | 4 | 0 | Kevin Laxalt-Nomura | Nelson Lau | Andrea Morales | Jon Eric Thalman | Aaron Shapiro | Andy Abranches | Yes | Yes | Yes | [5 empty] | 2024-10-02 | [17 empty] | Andrea Morales | Jon Eric Thalman | Kevin Laxalt-Nomura | Nelson Lau | Aaron Shapiro | [5 empty] | completed | 0 | 0 | 0 | 0
711 | CalPA | Set WMP-53 | CalPA_Set WMP-53 | 3 | CalPA_Set WMP-53_Q3 | For the newly introduced probability models for ignition risk introduced in WDRM v4 that were not present in WDRM v3, please provide a data dictionary to describe these new risk models and what additional risk they represent. | There were no new probability models introduced in WDRM v4 that captured additional risk which were not present in WDRM v3. Please reference PG&E’s response to Question No. 001, which provides the correct mapping between models and accounts for the referenced highlighted sub-models. Each WDRM v4 model is described in detail in the Event Probability Model documentation. | Matthew Taul | 2024-09-18 | 2024-10-02 | 2024-09-27 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_053.zip | 0 | N/A | 6.1.2 | Section 6 - Risk Methodology and Assessment | 6.1.2 Summary of Risk Models | B.1.1. WDRM v4 |  | CalPA | Set WMP-53 | 3 | 0 | Kevin Laxalt-Nomura | Nelson Lau | Andrea Morales | Jon Eric Thalman | Aaron Shapiro | Andy Abranches | Yes | Yes | Yes | [5 empty] | 2024-10-02 | [17 empty] | Andrea Morales | Jon Eric Thalman | Kevin Laxalt-Nomura | Nelson Lau | Aaron Shapiro | [5 empty] | completed | 0 | 0 | 0 | 0
710 | CalPA | Set WMP-53 | CalPA_Set WMP-53 | 2 | CalPA_Set WMP-53_Q2 | For each probability sub-model that was present in WDRM v3 and has a corresponding nearly-identically-named sub-model in WDRM v4, please list and describe the ways in which the sub-model in WDRM v4 differs from the sub-model in WDRM v3. | The evolution of the Distribution Event Probability Models (sub-models) is described in the WDRM v4 Documentation suite that has been provided as attachment “WMP-Discovery2023-2025_DR_CalAdvocates_053-Q006Atch01CONF.zip.” Relevant sections included in the “Distribution Event Probability Models v4 Documentation.pdf” include: • Section 2.1, Version Evolution, provides an overview of event probability model evolution from v3 to v4. In particular, it showcases the transition from spatial pixel-based models to asset-based models for most equipment asset models for v4. • Section 2.2, Probability of Failure/Outage Improvements, details general improvements that were made for v4 event probability models. • Section 3.5, Probability of Failure/Outage Improvements, individually documents the development of each of the v4 event probability models. Each model section includes a Key Developments sub-section that describes important changes for v4. | Matthew Taul | 2024-09-18 | 2024-10-02 | 2024-09-27 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_053.zip | 0 | N/A | 6.1.2 | Section 6 - Risk Methodology and Assessment | 6.1.2 Summary of Risk Models | B.1.1. WDRM v4 |  | CalPA | Set WMP-53 | 2 | 0 | Kevin Laxalt-Nomura | Nelson Lau | Andrea Morales | Jon Eric Thalman | Aaron Shapiro | Andy Abranches | Yes | Yes | Yes | [5 empty] | 2024-10-02 | [17 empty] | Andrea Morales | Jon Eric Thalman | Kevin Laxalt-Nomura | Nelson Lau | Aaron Shapiro | [5 empty] | completed | 0 | 0 | 0 | 0
709 | CalPA | Set WMP-53 | CalPA_Set WMP-53 | 1 | CalPA_Set WMP-53_Q1 | Does PG&E agree with the mapping of similar risk sub-models between WDRM versions v3 and v4 as shown Table 1? If not, please arrange the table so that sub-models found in WDRM v3 are aligned with the similar sub-model found in WDRM v4. In the event that multiple sub-models in one version have been incorporated into a single sub-model in another version, please clarify. | PG&E does not agree with the mapping shown in Table 1 and has re-arranged the table to show the mapping between sub-models. There is no Support Structure Leaking model. To clarify some of the mappings: • The v3 voltage control equipment model was split into the v4 voltage regulator and v4 capacitor bank models. • The v4 DPD, v4 Fuse, and v4 Switch models were previously included in one of the v3 conductor models based on their voltage level (i.e. primary vs. secondary). The other models maintained a one-to-one mapping. WDRM v3 WDRM v4 1 Animal Bird 1 Animal – Bird 2 Animal Squirrel 2 Animal – Squirrel 3 Animal Other 3 Animal – Other 4 Primary Conductor 5 DPD (primary) 6 Fuse (primary) 13 Switch (primary) 7 Primary Conductor – Line Slap 8 Primary Conductor – Wire Down 9 Primary Conductor – Other 5 Secondary Conductor 10 Secondary Conductor 5 DPD (secondary) 6 Fuse (secondary) 13 Switch (secondary) 6 Support Structure Equipment cause 12 Support Structure – Equipment 7 Support Structure Electrical 11 Support Structure – Electrical 8 Third-party Balloon 14 Third Party – Balloon 9 Third-party Vehicle 15 Third Party – Vehicle 10 Third-party Other 16 Third Party – Other 11 Transformer Equipment Cause 17 Transformer – Equipment 12 Transformer Equipment Leaking 18 Transformer – Leaking 13 Vegetation Branch 19 Vegetation – Branch 14 Vegetation Trunk 20 Vegetation – Trunk 15 Vegetation Other 21 Vegetation – Other 16 Voltage Control Equipment 22 Voltage Regulator 4 Capacitor Bank 17 Other Equipment 23 Other Equipment | Matthew Taul | 2024-09-18 | 2024-10-02 | 2024-09-27 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_053.zip | 0 | N/A | 6.1.2 | Section 6 - Risk Methodology and Assessment | 6.1.2 Summary of Risk Models | B.1.1. WDRM v4 |  | CalPA | Set WMP-53 | 1 | 0 | Kevin Laxalt-Nomura | Nelson Lau | Andrea Morales | Jon Eric Thalman | Aaron Shapiro | Andy Abranches | Yes | Yes | Yes | [5 empty] | 2024-10-02 | [17 empty] | Andrea Morales | Jon Eric Thalman | Kevin Laxalt-Nomura | Nelson Lau | Aaron Shapiro | [5 empty] | completed | 0 | 0 | 0 | 0
584 | CalPA | Set WMP-45 | CalPA_Set WMP-45 | 1 | CalPA_Set WMP-45_Q1 | Regarding its usage of Wildfire Distribution Risk Model (WDRM) v4 in scoping covered conductor and undergrounding projects, and the reflection of such in its System Hardening Accountability Report required by D.23-11-069,4 PG&E states the following in response to Question 6 of data request CalAdvocates-PGE-2025WMP-04: The scope of the SHAR [System Hardening Accountability Report] includes System Hardening work completed in the GRC period (2023-2026). Projects in this time period are not currently anticipated to be informed by WDRM v4. In the event projects selected by WDRM v4 do end up being planned for completion during this time period, WDRM v4 information would be included in the SHAR in the existing risk-related fields (i.e., Applicable Risk Model, Risk Reduction %, etc.). a) In the event projects selected with WDRM v4 do end up being planned for completion in the GRC period, how will PG&E show that it is meeting the risk reduction targets outlined in D.23-11-069?5 b) In the event projects selected with WDRM v4 do end up being planned for completion in the GRC period, will PG&E file a Petition for Modification (PFM) of D.23-11-069 to reflect usage of WDRM V4? Please explain your answer. c) In the event projects selected with WDRM v4 do end up being planned for completion in the GRC period, will PG&E submit an advice letter to modify the SHAR template to reflect usage of WDRM v4? Please explain your answer. d) In the event projects selected with WDRM v4 do end up being planned for completion in the GRC period, will PG&E use different means (other than a PFM of D.23-11-069 or an advice letter) to modify the SHAR reporting requirements or SHAR template contents? Please explain your answer. | a) PG&E does not anticipate completing any projects selected with WDRM V4 in the 2023 GRC period. As noted in response to question CalAdvocates 040-Q006, WDRM v4 may begin to inform scoping of undergrounding projects as early as the second half of 2024 for undergrounding projects planned for completion in 2027 and beyond. It is possible, but unlikely, that some of these projects may be completed prior to 2027. Were this to take place, we would follow the logic and methodology described in Advice Letter 7150-E-A. Specifically, where the excel templates for the baseline sheet for forecasted risk reduction (Table 1) and the completed sheet for completed project risk reduction (Table 2) currently include rows for WDRM 2 and WDRM 3 and their summed totals, we would add a new row for WDRM 4 and include those values in the summed totals. b) If PG&E were to complete in the 2023 GRC period any projects selected with WDRM V4, we would not file a PFM of D.23-11-069 because no modification of the decision would be necessary. As written, the decision recognizes the evolving nature of risk models and explicitly allows for the use of “any other future version” of WDRM beyond V2 and V3.3 c) In the unlikely event PG&E selects projects with WDRM V4 for completion in the 2023 GRC period, WDRM v4 information would be included in the SHAR in the existing risk-related fields (i.e., Applicable Risk Model, Risk Reduction %, etc.). If there are other additional substantial changes needed to the template, PG&E would work with SPD staff who, per D.23-11-069, have ministerial authority to adjust the requirements for the SHAR report.4 d) Yes. Please see response to sub-part c above. | Holly Wehrman | 2024-04-15 | 2024-04-18 | 2024-04-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_045.zip | 0 | N/A | 6.2.2.2 | 6.0 Risk Methodology and Assessment | 6.2.2.2 Consequence | B.1.1. WDRM v4 |  | CalPA | Set WMP-45 | 1 | 4 | Mona Hedin | Andrew Trombley | Lucy Morris/Julie Cerio/Kathy Wade | Jon Eric Thalman | Joel Crane/Charles Middlekauff/Walker Matthews | Matt Pender/Andy Abranches | Yes | Yes | Yes |  | Yes |  | Yes |  | 2024-04-18 | [16 empty] | 1 | Lucy Morris/Julie Cerio/Kathy Wade | Jon Eric Thalman | Mona Hedin | Andrew Trombley | Joel Crane/Charles Middlekauff/Walker Matthews | 4 |  |  |  |  | completed | 0 | 0 | 0 | 0
547 | CalPA | Set WMP-42 | CalPA_Set WMP-42 | 9 | CalPA_Set WMP-42_Q9 | In comparison to PG&E’s WDRM v3, does WDRM v4: a) Move 10 percent or more of ignition risk into or out of the top ignition risk circuits, segments, or spans? If yes, please provide the data in the format of Table 1-1 in section 1.1.1 of the 2025 Wildfire Mitigation Plan Update Guidelines for both WDRM v3 and v4. b) Move 10 percent or more of PSPS risk into or out of the top PSPS risk circuits, segments, or spans? If yes, please provide the data in the format of Table 1-2 in section 1.1.1 of the 2025 Wildfire Mitigation Plan Update Guidelines for both WDRM v3 and v4. | PG&E clarifies that the referenced Table1-1 in Section 1.1.1 was not provided in the 2025 update, as directed by the Office of Energy and Infrastructure Safety (OEIS) since it is not intended to be operationalized in 2025. Furthermore, the requested data pertains to the WDRM v4 which was recently approved for use in developing workplans that will be described in PG&E’s 2026-2028 WMP. As such the requested data were not used in the development of workplans described in PG&E’s 2025 WMP update. a. Yes, 10 percent or more of WDRM v3 circuit segments move out of the top 10 percent of circuit segments in WDRM v4 when prioritizing by average circuit segment wildfire risk. Please reference “WMP-Discovery2023- 2025_DR_CalAdvocates_042-Q009Atch01.xlsx” for the requested data. b. The PSPS model is separate from the WDRM and has not been updated since PG&E’s 2024 WMP. As such the population of top 10 percent of PSPS risk has not changed. ATTACHMENT: WMP-Discovery2023-2025_DR_CalAdvocates_042-Q009Atch01.xlsx | Holly Wehrman | 2024-04-09 | 2024-04-12 | 2024-04-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_042.zip | 1 | N/A | 6.2.1 | 6.0 Risk Methodology and Assessment | 6.2.1 Risk and Risk Component Identification | B.1.1. WDRM v4 |  | CalPA | Set WMP-42 | 9 | 2 | Mona Hedin | Mandy Knockaert | Jon Eric Thalman Nick Babb | Jon Eric Thalman | Aaron Shapiro | Andy Abranches | Yes | Yes |  |  | Yes | Yes | Yes |  | 2024-04-12 | [16 empty] | 9 | Jon Eric Thalman Nick Babb | Jon Eric Thalman | Mona Hedin | Mandy Knockaert | Aaron Shapiro | 2 |  |  |  |  | completed | 0 | 0 | 0 | 0
542 | CalPA | Set WMP-42 | CalPA_Set WMP-42 | 4 | CalPA_Set WMP-42_Q4 | Table PG&E-B.1.1-1 on page 8 of PG&E’s 2025 WMP Update indicates that WDRM v4 includes wind direction in its vegetation models. a) Describe how wind direction is incorporated in the vegetation models in WDRM v4. b) List the data sources that PG&E uses to incorporate wind direction into its risk model. c) Describe the benefits of incorporating wind direction into the risk model. | The basis for incorporating wind direction comes from the paper “Towards Simulation and Risk Assessment of Weather-Related Outages” by Rui Yao found here: https://web.eecs.utk.edu/~kaisun/papers/2018-TSG_Yao_Weather.pdf Within this paper, a probability density function is defined (equation 14) which quantifies the probability per angle that anything from a spatial location, in this case a tree’s location, will project itself into a conductor given the conductor’s normal vector and direction of the wind. This probability density is integrated along the conductor, via the angle, to calculate the total probability of strike given a wind’s direction, the tree’s location, and the location of the conductor segment. Due to the unavailability of LiDAR for the distribution system, Planet’s canopy height raster (Fall 2020) is used, the snapshot of the distribution grid (v4) and an average distribution line height of 8 meters to determine which of the pixels within the canopy height raster which can fall into a conductor and, approximately, which pixels kinematically have a chance of branches/debris from the tree falling into a conductor. For wind vectors, Meteorology’s POMMS system is used. The data is in 2 km by 2 km cells and communicates the wind vector components at 10m and the roughness length to easily calculate speeds at heights other than 10m. This data occurs in one-hour intervals and covers the years 2015 to 2021. Only the fire season and wind speeds above 6.7 meters per second is considered. Please note that the value 6.7 m/s was the value that the odds of a tree falling in a storm are equal to a tree falling not in a storm studied in the paper. The covariate calculation is as follows: The grid is divided into segments of 5 meters in length. For each 5-meter segment, and for each strike tree for that segment, the total probability along that 5-meter segment is calculated for all one-hour intervals of wind speeds greater than 6.7 m/s. All calculated probabilities are summed over that time for each tree-segment pair. A second quantity is calculated by weighting each hourly probability by the increased odds of wind damage during the storm by turning the log-odds (equation 13) into a probability, then multiply by the directional probability and finally multiplying by the inverse distance from the vegetation pixel to the 5-meter segment before summing over time. The total wind direction index is then found for each 5-meter segment by summing over all trees that influence it. Finally, each 5-meter segment is assigned to a pixel of the 100-meter-by100-meter resolution raster used in the WDRM and all segment’s indices found within a single pixel are summed. Two more indices are formed by taking the above two quantities and dividing by the total number of trees within the 100-meter pixel for a total of four new wind directional covariates. Wind is a vector quantity and has magnitude and direction. Magnitude has been present in the WDRM before but has been a low-value covariate. The reason for this is that higher speeds don’t necessarily mean higher risk when the wind direction is pointing away from an asset and the tree is oriented in location which is not impactful to the line. | Holly Wehrman | 2024-04-09 | 2024-04-12 | 2024-04-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_042.zip | 0 | N/A | 6.2.1 | 6.0 Risk Methodology and Assessment | 6.2.1 Risk and Risk Component Identification | B.1.1. WDRM v4 |  | CalPA | Set WMP-42 | 4 | 3 | Mona Hedin | Mandy Knockaert | Jon Eric Thalman Meteorology Team VMDR | Jon Eric Thalman Scott Strenfel | Aaron Shapiro | Andy Abranches Mark Quinlan | Yes | Yes |  |  |  | Yes | Yes |  | 2024-04-12 | [16 empty] | 4 | Jon Eric Thalman Meteorology Team VMDR | Jon Eric Thalman Scott Strenfel | Mona Hedin | Mandy Knockaert | Aaron Shapiro | 3 |  |  |  |  | completed | 0 | 0 | 0 | 0
541 | CalPA | Set WMP-42 | CalPA_Set WMP-42 | 3 | CalPA_Set WMP-42_Q3 | Page 7 of PG&E’s 2025 WMP Update states, with regard to PG&E’s distribution event probability models, “Significant efforts were made to improve asset, ignitions, and outage data quality.” List and explain the significant efforts discussed above. | As mentioned on page 7 of PG&E’s 2025 WMP, the following is a more detailed list of specific data quality improvements that are a result of the continuous effort to improve the quality and utilization of model data for assets, ignitions, and outages. Asset data quality improvements included: • Tracing asset failures and asset history back in time to identify the asset that failed and its characteristics. • Gathering asset information related to causal pathways as recommended by Subject Matter Experts (SMEs). o For support structures, this included: • Incorporating pole remaining strength as a feature in the model. o For primary conductors, this included: • Gathering distribution load flow software outputs. • Shifting conductor material and size types from categorical model inputs to continuous model inputs (i.e. conductor diameter, conductor strength, and conductor weight). • Using LiDAR data and splice observations where available in HFTD areas. • Incorporating Finite Element Analysis (FEA) model developed by the Applied Technology Services (ATS) team that assessed fault current and wind-driven line slap scenarios. • Including open tags. o For dynamic protective devices, fuses, switches, capacitor banks, and voltage regulators: • Gathering asset attributes as captured in EDGIS over time (2016-2022). • Including open tags. o Creating methodologies to estimate asset age when missing. • Reporting asset data quality issues to the Asset Knowledge Management team to resolve. Ignition data quality improvements were primarily focused on: • Enhancing wildfire ignition data for use in the wildfire consequence model. • Reporting data quality issues back to the Ignitions Investigation team to resolve. Outage data quality improvements included: • Improving the incorporating vegetation outage report latitude & longitude locations to improve outage fault locations. • Utilizing latitude & longitude locations from notification repair records where available to improve outage fault locations. • Assigning historical equipment failure-caused outages to the equipment ID of the asset that failed. • Working with Distribution Asset Strategy to help improve field personnel reporting of outages. • Shifting to a data pipeline that updates daily to categorize emergent outages to the appropriate model. • Developing 100% unit test coverage of data pipeline supporting functions to enhance reliability of the data. | Holly Wehrman | 2024-04-09 | 2024-04-12 | 2024-04-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_042.zip | 0 | N/A | 6.2.2.2 | 6.0 Risk Methodology and Assessment | 6.2.2.2 Consequence | B.1.1. WDRM v4 |  | CalPA | Set WMP-42 | 3 | 0 | Mona Hedin | Mandy Knockaert | Nick Babb Jon Eric Thalman | Andy Abranches | Aaron Shapiro | Andy Abranches | Yes | Yes |  |  |  | Yes | Yes |  | 2024-04-12 | [16 empty] | 3 | Jon Eric Thalman Benson Wong James Ash | Jon Eric Thalman | Mona Hedin | Mandy Knockaert | Aaron Shapiro | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
540 | CalPA | Set WMP-42 | CalPA_Set WMP-42 | 2 | CalPA_Set WMP-42_Q2 | Page 1021 of PG&E’s 2023-2025 WMP R4 states, in response to ACI PG&E-22-05, In general, 24-hour simulations result in higher impacts as simulated fires are more likely to reach highly populated areas despite decreasing reliability on the weather forecasts as time progresses, and unknown suppression effectiveness over time. Sensitivity analysis is continuing, and PG&E will be able to provide results in 2023 that quantify the effectiveness of shorter versus longer simulation durations. a) Describe the result of the sensitivity analysis discussed above. b) Provide any written results, reports, or other output of the sensitivity analysis discussed above. | a) PG&E ran comparisons of both 24-hour and 8-hour simulations for historical fires in the VIIRS dataset (fires detected from space in California above latitude 35.5, not restricted to fire season). The plot below is a comparison between actual acreage burned measured via satellite (y axis) against simulated acreage burned by Technosylva (x axis) for 24-hour and 8-hour simulations. Every dot represents a historic fire and a paired Technosylva simulation. The correlation between acres burned and Technosylva simulated acres burned is slight. Please see below for the output of this analysis. By binning the simulation acreage (x) values and averaging the historical acres (y) burned per bin, we can discern a more nuanced relationship. See below. The trend in the orange dots (24-hr simulation) is smoother than the trend in the blue dots (8-hr) especially where the y-axis predictions rise above the blue line. WFC takes this to mean that 24-hr TS simulations >1000 acres are more reliably predictive of larger historical fires. This is the primary support for utilizing 24-hour simulations in the WFC. b) Please see response to subpart a) above. | Holly Wehrman | 2024-04-09 | 2024-04-12 | 2024-04-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_042.zip | 0 | N/A | 6.2.2.2 | 6.0 Risk Methodology and Assessment | 6.2.2.2 Consequence | B.1.1. WDRM v4 |  | CalPA | Set WMP-42 | 2 | 2 | Mona Hedin | Mandy Knockaert | Jon Eric Thalman Benson Wong James Ash | Jon Eric Thalman | Aaron Shapiro | Andy Abranches | Yes | Yes |  |  |  | Yes | Yes |  | 2024-04-12 | [16 empty] | 2 | Jon Eric Thalman Benson Wong James Ash | Jon Eric Thalman | Mona Hedin | Mandy Knockaert | Aaron Shapiro | 2 |  |  |  |  | completed | 0 | 0 | 0 | 0
539 | CalPA | Set WMP-42 | CalPA_Set WMP-42 | 1 | CalPA_Set WMP-42_Q1 | Page 10 of PG&E’s 2025 WMP Update states that, for version 4 of PG&E’s Wildfire Consequence Model, PG&E increased the fire simulation time from eight to 24 hours. a) List the reasons why PG&E chose to increase the fire simulation time to 24 hours. b) Is PG&E aware of any potential detrimental effects associated with increasing the fire simulation time from eight to 24 hours? c) If the answer to part (b) is yes, list any such potential detrimental effects. d) What has PG&E done so far to validate the accuracy of 24-hour fire simulations? | a) There were two main drivers for evaluating and eventually utilizing longer fire simulations: 1. Expert consensus. Interveners and the E3 model validation for the WDRM v3 model recommended moving to longer simulation times to capture fire impacts. 2. As outlined in more detail in the response to Request No. 002, there is a slightly more robust relationship between simulation acreage and actual acreage burned in historic fires. b) No. c) Not applicable, please see the response to subpart (b) above. d) As outlined in the response to Request No. 002, there is a slightly more robust relationship between simulation acreage and acreage burned in historic fires. | Holly Wehrman | 2024-04-09 | 2024-04-12 | 2024-04-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_042.zip | 0 | N/A | 6.2.2.2 | 6.0 Risk Methodology and Assessment | 6.2.2.2 Consequence | B.1.1. WDRM v4 |  | CalPA | Set WMP-42 | 1 | 4 | Mona Hedin | Mandy Knockaert | Jon Eric Thalman Benson Wong James Ash | Jon Eric Thalman | Aaron Shapiro | Andy Abranches | Yes | Yes |  |  |  | Yes | Yes |  | 2024-04-12 | [16 empty] | 1 | Jon Eric Thalman Benson Wong James Ash | Jon Eric Thalman | Mona Hedin | Mandy Knockaert | Aaron Shapiro | 4 |  |  |  |  | completed | 0 | 0 | 0 | 0
522 | CalPA | Set WMP-41 | CalPA_Set WMP-41 | 9 | CalPA_Set WMP-41_Q9 | a) Has PG&E created a detailed overview document that details the WDRM v4, similar to the “2021 Wildfire Distribution Risk Model Overview” that PG&E submitted following the public workshop held on October 5 and 6, 2021? b) If the answer to part (a) is yes, please provide a copy of the document. c) If the answer to part (a) is no, does PG&E plan to create such a document? d) If the answer to part (c) is no, please explain why not. e) If the answer to part (c) is yes, when does PG&E expect the document to be completed? | a) PG&E is currently creating the detailed overview documentation for the WDRM v4. It is scheduled to be available by the end of Q2 2024. b) Not applicable, please see the response to subpart (a) above. c) Not applicable, please see the response to subpart (a) above. d) Not applicable, please see the response to subpart (a) above. e) Please see the response to subpart (a) above. | Holly Wehrman | 2024-04-05 | 2024-04-11 | 2024-04-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_041.zip | 0 | N/A | 6 | Section 6 - Risk Methodology and Assessment | 6.1.2 Summary of Risk Models | B.1.1. WDRM v4 |  | CalPA | Set WMP-41 | 9 | 5 | Mona Hedin | Mandy Knockaert | Richard Anderson | Jon Eric Thalman | Aaron Shapiro | Andy Abranches | Yes | Yes |  |  | Yes | Yes | Yes |  | 2024-04-11 | [16 empty] | 9 | Richard Anderson | Jon Eric Thalman | Mona Hedin | Mandy Knockaert | Aaron Shapiro | 5 |  |  |  |  | completed | 0 | 0 | 0 | 0
521 | CalPA | Set WMP-41 | CalPA_Set WMP-41 | 8 | CalPA_Set WMP-41_Q8 | a) Has E3 or another entity completed an independent review of the WDRM v4? b) If the answer to part (a) is yes, please provide a copy of any reports and outputs from the independent review. c) If the answer to part (a) is no, when does PG&E expect the review to be completed? | a) E3 is currently conducting an independent review of the WDRM v4. b) The E3 review is scheduled to be available by the end of Q2 2024. c) Please see the response to subpart (b) above. | Holly Wehrman | 2024-04-05 | 2024-04-11 | 2024-04-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_041.zip | 0 | N/A | 6 | Section 6 - Risk Methodology and Assessment | 6.1.2 Summary of Risk Models | B.1.1. WDRM v4 |  | CalPA | Set WMP-41 | 8 | 3 | Mona Hedin | Mandy Knockaert | Richard Anderson | Jon Eric Thalman | Aaron Shapiro | Andy Abranches | Yes | Yes |  |  | Yes | Yes | Yes |  | 2024-04-11 | [16 empty] | 8 | Richard Anderson | Jon Eric Thalman | Mona Hedin | Mandy Knockaert | Aaron Shapiro | 3 |  |  |  |  | completed | 0 | 0 | 0 | 0
520 | CalPA | Set WMP-41 | CalPA_Set WMP-41 | 7 | CalPA_Set WMP-41_Q7 | Please provide a GIS file that details the most granular level available for the Wildfire Consequence Model version used in the WDRM v3. This file should contain the following: a) Geometric features detailing the most granular level available for consequence (it is Cal Advocates’ understanding that the consequence model uses “pixels”). b) For each geometric feature, please include all relevant consequence values (if there are multiple) as attributes. | Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_041- Q003Atch01CONF.zip” for a GIS file containing the requested Wildfire Consequence (WFC) v3.4 model pixel results. | Holly Wehrman | 2024-04-05 | 2024-04-29 | 2024-04-29 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_041.zip | 0 | N/A | 6 | Section 6 - Risk Methodology and Assessment | 6.1.2 Summary of Risk Models | B.1.1. WDRM v4 |  | CalPA | Set WMP-41 | 7 | 2 | Mona Hedin | Mandy Knockaert | Richard Anderson Eszter Tompos | Jon Eric Thalman | Aaron Shapiro | Andy Abranches | Yes |  | Yes |  | Yes | Yes | Yes |  | 2024-04-29 |  | 4/25/2024 - extension needed for Q3, Q4, Q6, and Q7 to 4/29 due to file size and time needed to QC. kxfk 4/18/2024 - per Mona Hedin, Q3, Q4, Q6, Q7 have been extended to 4/26 due to SME delay. kxfk | 4/25/2024 - extension needed for Q3, Q4, Q6, and Q7 to 4/29 due to file size and time needed to QC. kxfk 4/18/2024 - per Mona Hedin, Q3, Q4, Q6, Q7 have been extended to 4/26 due to SME delay. kxfk | [13 empty] | 7 | Richard Anderson Eszter Tompos | Jon Eric Thalman | Mona Hedin | Mandy Knockaert | Aaron Shapiro | 2 |  |  |  |  | completed | 0 | 0 | 0 | 0
519 | CalPA | Set WMP-41 | CalPA_Set WMP-41 | 6 | CalPA_Set WMP-41_Q6 | Pages 9-11 of PG&E’s 2025 WMP Update discuss version 4 of PG&E’s Wildfire Consequence Model. Please provide a GIS file that details the most granular level available for the Wildfire Consequence Model, version 4. This file should contain the following: a) Geometric features detailing the most granular level available for consequence (it is Cal Advocates’ understanding that the consequence model uses “pixels”). b) For each geometric feature, please include all relevant consequence values (if there are multiple) as attributes. | Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_041- Q003Atch01CONF.zip” for a GIS file containing for the requested Wildfire Consequence (WFC) v4 model pixel results. | Holly Wehrman | 2024-04-05 | 2024-04-29 | 2024-04-29 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_041.zip | 0 | N/A | 6 | Section 6 - Risk Methodology and Assessment | 6.1.2 Summary of Risk Models | B.1.1. WDRM v4 |  | CalPA | Set WMP-41 | 6 | 2 | Mona Hedin | Mandy Knockaert | Richard Anderson Eszter Tompos | Jon Eric Thalman | Aaron Shapiro | Andy Abranches | Yes |  | Yes |  | Yes | Yes | Yes |  | 2024-04-29 |  | 4/25/2024 - extension needed for Q3, Q4, Q6, and Q7 to 4/29 due to file size and time needed to QC. kxfk 4/18/2024 - per Mona Hedin, Q3, Q4, Q6, Q7 have been extended to 4/26 due to SME delay. kxfk | 4/25/2024 - extension needed for Q3, Q4, Q6, and Q7 to 4/29 due to file size and time needed to QC. kxfk 4/18/2024 - per Mona Hedin, Q3, Q4, Q6, Q7 have been extended to 4/26 due to SME delay. kxfk | [13 empty] | 6 | Richard Anderson Eszter Tompos | Jon Eric Thalman | Mona Hedin | Mandy Knockaert | Aaron Shapiro | 2 |  |  |  |  | completed | 0 | 0 | 0 | 0
518 | CalPA | Set WMP-41 | CalPA_Set WMP-41 | 5 | CalPA_Set WMP-41_Q5 | Question 5 refers to the risk scores generated from WDRM v4. This should be understood to refer to PG&E’s responses to questions 1 and 2 above. Please provide a spreadsheet that lists (as rows) each circuit-segment that is included in the Wildfire Distribution Risk Model v4. This spreadsheet should include, at minimum, the following columns. a) Name or ID number of each circuit segment. b) Circuit name for the circuit that each segment is part of. c) Circuit ID for the circuit that each segment is part of. d) Nominal voltage. e) The pixel count of the circuit segment (as applicable, e.g., for pixel-based sub-models). f) The average risk value(s) associated with each pixel along the circuit segment (as applicable, e.g., for pixel-based sub-models). g) The asset count of the circuit segment (as applicable, e.g., for asset-based sub-models).5 h) The risk value(s) associated with each asset along the circuit segment (as applicable, e.g., for asset-based sub-models).5 i) The risk per line mile of the circuit-segment (as applicable). j) Total circuit-miles on the circuit-segment. k) Total overhead circuit-miles on the circuit-segment. l) Total non-HFTD overhead circuit-miles on the circuit-segment. m) Total Tier 2 overhead circuit-miles on the circuit-segment. n) Total Tier 3 overhead circuit-miles on the circuit-segment. o) Total underground circuit-miles on the circuit-segment. p) Total non-HFTD underground circuit-miles on the circuit-segment. q) Total Tier 2 underground circuit-miles on the circuit-segment. r) Total Tier 3 underground circuit-miles on the circuit-segment. s) A separate, labeled column for each risk score identified in question 1(a) that is used at the circuit-segment level to inform wildfire mitigation initiatives. (May require multiple columns.) t) A separate, labeled column for each composite risk score identified in question 2(a) that is used at the circuit-segment level to inform wildfire mitigation initiatives. (May require multiple columns.) | a) - t) Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_041- Q005Atch01.xlsx” for the requested information. ATTACHMENT: WMP-Discovery2023-2025_DR_CalAdvocates_041-Q005Atch01.xlsx | Holly Wehrman | 2024-04-05 | 2024-04-11 | 2024-04-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_041.zip | 1 | N/A | 6 | Section 6 - Risk Methodology and Assessment | 6.1.2 Summary of Risk Models | B.1.1. WDRM v4 |  | CalPA | Set WMP-41 | 5 | 20 | Mona Hedin | Mandy Knockaert | Richard Anderson | Jon Eric Thalman | Aaron Shapiro | Andy Abranches | Yes | Yes |  |  | Yes | Yes | Yes |  | 2024-04-11 | [16 empty] | 5 | Richard Anderson | Jon Eric Thalman | Mona Hedin | Mandy Knockaert | Aaron Shapiro | 20 |  |  |  |  | completed | 0 | 0 | 0 | 0
517 | CalPA | Set WMP-41 | CalPA_Set WMP-41 | 4 | CalPA_Set WMP-41_Q4 | Please provide a GIS file that details the risk scores at the same granularity that is currently used to inform wildfire mitigation measures (as discussed in questions 1(f) and 2(f)). This file should contain the following: a) Geometric features detailing the relevant geometry for each risk score. This may be polygons that depict “pixels,” lines that depict circuit segments, points that depict assets, or other geometry that best suits the relevant risk scores. If multiple risk scores share geometry (e.g., multiple risk scores that are used to inform mitigation measures at the circuit segment level), there is no need to include multiple layers that depict the same physical geometry. b) For each geometric feature, please include all relevant risk scores from questions 1(a) and 2(a) as attributes. c) For each geometric feature, include the circuit identification number as an attribute. d) For each geometric feature, include the circuit name as an attribute. e) For each geometric feature, include the circuit segment name as an attribute. f) As needed, include unique identification for each geometric feature (e.g., asset ID, substation name, etc.) | Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_041- Q003Atch01CONF.zip” for the requested System Hardening and Vegetation Management composite models. | Holly Wehrman | 2024-04-05 | 2024-04-29 | 2024-04-29 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_041.zip | 0 | N/A | 6 | Section 6 - Risk Methodology and Assessment | 6.1.2 Summary of Risk Models | B.1.1. WDRM v4 |  | CalPA | Set WMP-41 | 4 | 6 | Mona Hedin | Mandy Knockaert | Richard Anderson Eszter Tompos | Jon Eric Thalman | Aaron Shapiro | Andy Abranches | Yes |  | Yes |  | Yes | Yes | Yes |  | 2024-04-29 |  | 4/25/2024 - extension needed for Q3, Q4, Q6, and Q7 to 4/29 due to file size and time needed to QC. kxfk 4/18/2024 - per Mona Hedin, Q3, Q4, Q6, Q7 have been extended to 4/26 due to SME delay. kxfk | 4/25/2024 - extension needed for Q3, Q4, Q6, and Q7 to 4/29 due to file size and time needed to QC. kxfk 4/18/2024 - per Mona Hedin, Q3, Q4, Q6, Q7 have been extended to 4/26 due to SME delay. kxfk | [13 empty] | 4 | Richard Anderson Eszter Tompos | Jon Eric Thalman | Mona Hedin | Mandy Knockaert | Aaron Shapiro | 6 |  |  |  |  | completed | 0 | 0 | 0 | 0
516 | CalPA | Set WMP-41 | CalPA_Set WMP-41 | 3 | CalPA_Set WMP-41_Q3 | Questions 3 and 4 refer to the risk scores generated from WDRM v4. This should be understood to refer to PG&E’s responses to questions 1 and 2 above. If PG&E possesses geospatial data that is not in the specific format requested in questions 3 and 4, but that PG&E believes substantially contains the information requested in questions 3 and 4, please contact the originators to discuss the format of your responses. Question 3 Please provide a GIS file that details the most granular level (as discussed in questions 1(e) and 2(e)) available for each risk score identified in questions 1(a) and 2(a). This file should contain the following: a) Geometric features detailing the most granular level available for each risk score. This may be polygons that depict “pixels,” lines that depict circuit segments, points that depict assets, or other geometry that best suits the relevant risk scores. If multiple risk scores share geometry (e.g., multiple risk scores that are calculated at the “pixel” level), there is no need to include multiple layers that depict the same physical geometry. b) For each geometric feature, please include all relevant risk scores from questions 1(a) and 2(a) as attributes. | a) Please see “WMP-Discovery2023-2025_DR_CalAdvocates_041- Q003Atch01CONF.zip” for GIS files which include the combined pixel-based models (Vegetation, Animal, Third Party, Secondary Conductor, and Other Equipment), and individual Asset Equipment models. Please note, Asset Equipment model results are referenced to point geometry locations, while the pixel-model results are referenced to 100m-by-100m square grid pixel locations that overlay the PG&E service territory. When converting PG&E native data sets into GIS format, the original model column names were unfortunately truncated to 10-character lengths for GIS Field names. This truncation made identifying contributing model results in composite files difficult. Therefore, more descriptive Field names were substituted for the truncated versions. A companion Excel workbook, “WMP-Discovery2023- 2025_DR_CalAdvocates_041-Q003Atch02.xlsx,” has been provided with GIS File specific tabs to cross-reference the substituted Field names to the original model result. b) Please see the answer to subpart a) above. | Holly Wehrman | 2024-04-05 | 2024-04-29 | 2024-04-29 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_041.zip | 2 | N/A | 6 | Section 6 - Risk Methodology and Assessment | 6.1.2 Summary of Risk Models | B.1.1. WDRM v4 |  | CalPA | Set WMP-41 | 3 | 2 | Mona Hedin | Mandy Knockaert | Richard Anderson Eszter Tompos | Jon Eric Thalman | Aaron Shapiro | Andy Abranches | Yes |  | Yes |  | Yes | Yes | Yes |  | 2024-04-29 |  | 4/25/2024 - extension needed for Q3, Q4, Q6, and Q7 to 4/29 due to file size and time needed to QC. kxfk 4/18/2024 - per Mona Hedin, Q3, Q4, Q6, Q7 have been extended to 4/26 due to SME delay. kxfk | 4/25/2024 - extension needed for Q3, Q4, Q6, and Q7 to 4/29 due to file size and time needed to QC. kxfk 4/18/2024 - per Mona Hedin, Q3, Q4, Q6, Q7 have been extended to 4/26 due to SME delay. kxfk | [13 empty] | 3 | Richard Anderson Eszter Tompos | Jon Eric Thalman | Mona Hedin | Mandy Knockaert | Aaron Shapiro | 2 |  |  |  |  | completed | 0 | 0 | 0 | 0
515 | CalPA | Set WMP-41 | CalPA_Set WMP-41 | 2 | CalPA_Set WMP-41_Q2 | a) Please list all composite (or aggregate) risk scores generated by PG&E’s WDRM v4. For example, WDRM v3 generated five composite risk scores. b) For each risk score in part (a), please provide a category or brief description of the type of risk the score represents. c) For each risk score in part (a), please provide a brief explanation of how PG&E intends to use that risk score. d) For each risk score in part (a), please list all PG&E wildfire mitigation initiatives that are informed by that risk score (if PG&E expects to utilize a risk score to inform a mitigation initiative in the future, please so note). e) For each risk score in part (a), please state the most granular level available for that risk score. f) For each risk score in part (a), please state the granularity at which the risk score is used to inform wildfire mitigation initiatives (e.g. circuit segment, circuit, individual asset, individual miles, etc.). | There are three composite risk scores available from WDRM v4 at a circuit segment level that produce ignition risk values: • All (Total Risk); • System Hardening; and • Vegetation. Responses to parts (b) through (f) of this request are described in the table below. a) Composite Risk Score b) Category / Description c) Intended Use d) Mitigation Initiatives e) Granularity f) Risk Granularity All Composite All 23 event risk drivers Inform on total system risk TBD* Asset and Pixel (100m2 ) Circuit Segment System Hardening Composite 21 event risk drivers that System Hardening mitigation addresses, excludes: •Support Structure – Electrical •Transformer – Leaking Inform System Hardening prioritization System Hardening Asset and Pixel (100m2 ) Circuit Segment Vegetation 3 event risk drivers that vegetation mitigation addresses, includes: •Vegetation – Branch •Vegetation – Trunk •Vegetation – Other Inform mitigation aimed at reducing vegetation related ignitions TBD* Pixel (100m2 ) Circuit Segment *To be determined in 2026-2028 Base WMP. | Holly Wehrman | 2024-04-05 | 2024-04-11 | 2024-04-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_041.zip | 0 | N/A | 6 | Section 6 - Risk Methodology and Assessment | 6.1.2 Summary of Risk Models | B.1.1. WDRM v4 |  | CalPA | Set WMP-41 | 2 | 6 | Mona Hedin | Mandy Knockaert | Richard Anderson | Jon Eric Thalman | Aaron Shapiro | Andy Abranches | Yes | Yes |  |  | Yes | Yes | Yes |  | 2024-04-11 | [16 empty] | 2 | Richard Anderson | Jon Eric Thalman | Mona Hedin | Mandy Knockaert | Aaron Shapiro | 6 |  |  |  |  | completed | 0 | 0 | 0 | 0
514 | CalPA | Set WMP-41 | CalPA_Set WMP-41 | 1 | CalPA_Set WMP-41_Q1 | a) Please list all distinct risk scores generated by PG&E’s WDRM v4. For example, WDRM v3 generated 17 different risk scores.4 b) For each risk score in part (a), please provide a category or brief description of the type of risk the score represents. c) For each risk score in part (a), please provide a brief explanation of how PG&E intends to use that risk score. d) For each risk score in part (a), please list all PG&E wildfire mitigation initiatives that are informed by that risk score (if PG&E expects to utilize a risk score to inform a mitigation initiative in the future, please so note). e) For each risk score in part (a), please state the most granular level available for that risk score. For example, in WDRM v3, the most granular level available would be the risk scores associated with individual 100m x 100m pixels. f) For each risk score in part (a), please state the granularity at which the risk score is used to inform wildfire mitigation initiatives (e.g. circuit segment, circuit, individual asset, individual miles, etc.). | There are 23 event probability models from WDRM v4 that produce ignition risk values: • Animal – Bird • Animal – Squirrel • Animal – Other • Capacitor Bank • DPD • Fuse • Primary Conductor – Line Slap • Primary Conductor – Wire Down • Primary Conductor – Other • Secondary Conductor • Support Structure - Leaking • Support Structure – Equipment • Switch • Third Party – Balloon • Third Party – Vehicle • Third Party – Other • Transformer – Equipment • Transformer – Leaking • Vegetation – Branch • Vegetation – Trunk • Vegetation – Other • Voltage Regulator • Other Equipment Responses to subparts (b) through (f) of this request are described in the table below. bability Risk Score b) Category / Description c) Intended Use d) Mitigation Initiatives e) Granularity f) Risk Granularity Animal – Bird Ignition risk caused by bird contact Inform mitigation for bird related ignitions TBD* Pixel (100m2 ) Circuit Segment Animal – Squirrel Ignition risk caused by squirrel contact Inform mitigation for squirrel related ignitions TBD* Pixel (100m2 ) Circuit Segment Animal – Other Ignition risk caused by contact other than bird and squirrel Inform mitigation for other animal related ignitions TBD* Pixel (100m2 ) Circuit Segment Capacitor Bank Ignition risk caused by capacitor bank failures Inform mitigation for capacitor bank related ignitions TBD* Asset Asset Dynamic Protective Device (DPD) Ignition risk caused by DPD failures Inform mitigation for DPD related ignitions TBD* Asset Asset Fuse Ignition risk caused by fuse failures Inform mitigation for fuse related ignitions TBD* Asset Asset Primary Conductor – Line Slap Ignition risk caused by primary conductor failures due to line slap Inform mitigation for primary conductor line slap related ignitions TBD* Asset Asset Primary Conductor – Wire Down Ignition risk caused by primary conductor failures due to wire down Inform mitigation for primary conductor wire down related ignitions TBD* Asset Asset Primary Conductor – Other Ignition risk caused by primary conductor failures other than line slap and wire down Inform mitigation for other primary conductor related ignitions TBD* Asset Asset Secondary Conductor Ignition risk caused by secondary conductor failures Inform mitigation for secondary conductor related ignitions TBD* Pixel Circuit Segment Support Structure – Electrical Failure Ignition risk caused by support structure electrical failures Inform mitigation for support structure electrical related ignitions TBD* Asset Asset Support Structure – Equipment Failure Ignition risk caused by support structure equipment (pole and attachment) failures Inform mitigation for support structure equipment related ignitions TBD* Asset Asset Switch Ignition risk caused by switch failures Inform mitigation for switch related ignitions TBD* Asset Asset Third Party – Balloon Ignition risk caused by mylar balloon contact Inform mitigations for balloon related ignitions TBD* Pixel (100m2 ) Circuit Segment Third Party – Vehicle Ignition risk caused by vehicle contact Inform mitigations for vehicle related ignitions TBD* Pixel (100m2 ) Circuit Segment Third Party – Other Ignition risk caused by contact other than balloon and vehicle Inform mitigations for other cause related ignitions TBD* Pixel (100m2 ) Circuit Segment Transformer – Equipment Ignition risk caused by pole mounted transformer equipment failures Inform mitigations for transformer equipment related ignitions TBD* Asset Asset Transformer – Leaking Ignition risk caused by leaking transformers Inform mitigations for leaking transformer related ignitions TBD* Asset Asset Vegetation – Branch Ignition risk caused by tree branch failure Inform mitigations for tree branch failure related ignitions TBD* Pixel (100m2 ) Circuit Segment Vegetation – Trunk Ignition risk caused by tree trunk failure Inform mitigations for tree trunk failure related ignitions TBD* Pixel (100m2 ) Circuit Segment Vegetation – Other Ignition risk caused by vegetation failures other than tree branch and trunk failures Inform mitigations for vegetation related ignitions other than tree trunk and branch TBD* Pixel (100m2 ) Circuit Segment Voltage Regulator Ignition risk caused by voltage regulator and shunt capacitor failures Inform mitigation for voltage regulator related ignitions TBD* Asset Asset Other Equipment Ignition risk from causes not specified by the other 22 event probability models Inform mitigation for other equipment related ignitions not covered by a specific equipment model TBD* Pixel (100m2 ) Circuit Segment *To be determined in 2026-2028 Base WMP. | Holly Wehrman | 2024-04-05 | 2024-04-11 | 2024-04-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_041.zip | 0 | N/A | 6 | Section 6 - Risk Methodology and Assessment | 6.1.2 Summary of Risk Models | B.1.1. WDRM v4 |  | CalPA | Set WMP-41 | 1 | 6 | Mona Hedin | Mandy Knockaert | Richard Anderson | Jon Eric Thalman | Aaron Shapiro | Andy Abranches | Yes | Yes |  |  | Yes | Yes | Yes |  | 2024-04-11 | [16 empty] | 1 | Richard Anderson | Jon Eric Thalman | Mona Hedin | Mandy Knockaert | Aaron Shapiro | 6 |  |  |  |  | completed | 0 | 0 | 0 | 0
512 | CalPA | Set WMP-40 | CalPA_Set WMP-40 | 6 | CalPA_Set WMP-40_Q6 | PG&E states on page 3 of its 2025 WMP update that it is introducing a new evolution of its Wildfire Distribution Risk Model (WDRM), called WDRM v4. It states, “The outputs from the WDRM v4 are expected to inform some risk-prioritized, short-cycle work in 2025 and other risk-prioritized long-cycle work in 2026 and beyond.” a) Is WDRM v4 expected to inform scoping and execution of any undergrounding projects that will be performed in 2025 and 2026? b) If the answer to part (a) is yes, please explain how PG&E intends to report this risk reduction in its System Hardening Accountability Report (SHAR) required by D.23-11-069.6 c) Is WDRM v4 expected to inform scoping and execution of any covered conductor projects that will be performed in 2025 and 2026? d) If the answer to part (c) is yes, please explain how PG&E intends to report this risk reduction in the SHAR. | a. As noted in response to Request 5(c) of this data request, WDRM v4 may begin to inform scoping of undergrounding projects as early as the second half of 2024 for undergrounding projects planned for completion in 2027 and beyond. b. The scope of the SHAR includes System Hardening work completed in the GRC period (2023-2026). Projects in this time period are not currently anticipated to be informed by WDRM v4. In the event projects selected by WDRM v4 do end up being planned for completion during this time period, WDRM v4 information would be included in the SHAR in the existing risk-related fields (i.e., Applicable Risk Model, Risk Reduction %, etc.). c. As noted in response to Request 5(e) of this data request, WDRM v4 may begin to inform the scoping of overhead hardening (covered conductor) projects as early as the second half of 2024 for projects planned for completion in 2027 and beyond. d. Please see the response to subpart (b) above for how PG&E reports this risk reduction in the SHAR. | Miles Gordon | 2024-04-05 | 2024-04-16 | 2024-04-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_040.zip | 0 | N/A | 6 | Section 6 - Risk Methodology and Assessment | 6.1.2 Summary of Risk Models | B.1.1. WDRM v4 |  | CalPA | Set WMP-40 | 6 | 4 | Mona Hedin | Mandy Knockaert | Richard Anderson UG Team Jerry Santos Julie Cerio Lucy Morris Byron Winget Natalie Dawley Michelle Sakamoto | Jon Eric Thalman Megan Ardell | Aaron Shapiro | Andy Abranches Matt Pender | Yes |  | Yes |  | Yes | Yes | Yes |  | 2024-04-16 |  | extension requested | [14 empty] | 6 | Richard Anderson UG Team Jerry Santos Julie Cerio Lucy Morris Byron Winget Natalie Dawley Michelle Sakamoto | Jon Eric Thalman Megan Ardell | Mona Hedin | Mandy Knockaert | Aaron Shapiro | 4 |  |  | DRU13430 |  | completed | 0 | 0 | 0 | 0
511 | CalPA | Set WMP-40 | CalPA_Set WMP-40 | 5 | CalPA_Set WMP-40_Q5 | PG&E states on page 3 of its 2025 WMP update that it is introducing a new evolution of its Wildfire Distribution Risk Model (WDRM), called WDRM v4. It states, “The outputs from the WDRM v4 are expected to inform some risk-prioritized, short-cycle work in 2025 and other risk-prioritized long-cycle work in 2026 and beyond.” a) Please identify each WMP initiative for which WDRM v4 is expected to “inform risk-prioritized short-cycle work in 2025.” b) Please identify each WMP initiative for which WDRM v4 is expected to “inform risk-prioritized long-cycle work in 2026 and beyond.” c) When will WDRM v4 begin to inform the scoping and execution of undergrounding projects? d) When does PG&E expect to begin constructing undergrounding projects that are scoped using WDRM v4? e) When will WDRM v4 begin to inform the scoping and execution of covered conductor projects? f) When does PG&E expect to begin constructing covered conductor projects that are scoped using WDRM v4? | a. At this time, 2025 workplans are still being developed. PG&E cannot say with certainty which WMP initiatives for which WDRM v4 are expected to “inform riskprioritized short-cycle work in 2025.” PG&E’s 2026-2028 WMP will provide details on workplans drawing on the WDRM v4 for insights. b. PG&E cannot say with certainty what long-cycle work it is expected to inform riskprioritized long-cycle work in 2026 and beyond.” PG&E’s 2026-2028 WMP will provide details on workplans drawing on the WDRM v4 for insights. c. WDRM v4 will begin to inform scoping of undergrounding projects as early as the second half of 2024 for undergrounding projects planned for completion in 2027 and beyond. d. For undergrounding projects scoped using WDRM v4, PG&E anticipates that some planning activities in 2025 and preparatory work for civil construction may begin in 2026 for projects to be completed in 2027. e. WDRM v4 will begin to inform scoping of overhead hardening (covered conductor) projects as early as the second half of 2024 for projects expected to be completed in 2027 and beyond. f. For overhead hardening (covered conductor) projects scoped using WDRM v4, PG&E anticipates that some planning activities in 2025 and preparatory work for civil construction may begin in 2026 for projects to be completed in 2027. | Miles Gordon | 2024-04-05 | 2024-04-16 | 2024-04-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_040.zip | 0 | N/A | 6 | Section 6 - Risk Methodology and Assessment | 6.1.2 Summary of Risk Models | B.1.1. WDRM v4 |  | CalPA | Set WMP-40 | 5 | 6 | Mona Hedin | Mandy Knockaert | Richard Anderson UG Team Jerry Santos Julie Cerio Lucy Morris Byron Winget Natalie Dawley Michelle Sakamoto Merih Tekeste | Jon Eric Thalman Megan Ardell | Aaron Shapiro | Andy Abranches Matt Pender | Yes |  | Yes |  | Yes | Yes | Yes |  | 2024-04-16 |  | extension requested | [14 empty] | 5 | Richard Anderson UG Team Jerry Santos Julie Cerio Lucy Morris Byron Winget Natalie Dawley Michelle Sakamoto Merih Tekeste | Jon Eric Thalman Megan Ardell | Mona Hedin | Mandy Knockaert | Aaron Shapiro | 6 |  |  | DRU13430 |  | completed | 0 | 0 | 0 | 0
544 | CalPA | Set WMP-42 | CalPA_Set WMP-42 | 6 | CalPA_Set WMP-42_Q6 | Page 17 of PG&E’s 2025 WMP Update states, “When viewed on a line weighted basis, the relative average risk of each transmission line can be viewed for insights. It should be noted that these mile weighted values will tend to highlight short lines such as taps.” a) Does PG&E plan to correct for the fact that mile weighted values tend to highlight short lines? b)If the answer to part (a) is yes, explain the methods PG&E plans to use. c) If the answer to part (a) is no, explain why not. | a. No, PG&E does not plan to attempt to correct the fact the mile weighted values can tend to highlight shorter lines. b. Not applicable. c. The probability of failure (pf) and risk in the WTRM framework is calculated at the level of each structure. This pf/risk value can then be used to assign an average pf\risk value at the transmission line level which would be average of pf/risk values across all structures on the transmission line. While the model interface includes line level values (average, sum and max) for reference and the granularity of the model at the structure level also enables calculation of mile weighted values, these values are only used for reference. As the note indicates, the values are not always directly actionable without taking into account the fact that any such analysis can result in highlighting lines that are short. During the Asset Management planning process, the values at the structure level are mainly used for making decisions on asset repair/replacement. | Holly Wehrman | 2024-04-09 | 2024-04-12 | 2024-04-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_042.zip | 0 | N/A | 6.2.2.2 | 6.0 Risk Methodology and Assessment | 6.2.2.2 Consequence | B.1.2. WTRM v2 |  | CalPA | Set WMP-42 | 6 | 3 | Mona Hedin | Mandy Knockaert | Jon Eric Thalman Benson Wong James Ash | Jon Eric Thalman | Aaron Shapiro | Andy Abranches | Yes | Yes |  |  |  | Yes | Yes |  | 2024-04-12 | [16 empty] | 6 | Jon Eric Thalman Benson Wong James Ash | Jon Eric Thalman | Mona Hedin | Mandy Knockaert | Aaron Shapiro | 3 |  |  |  |  | completed | 0 | 0 | 0 | 0
543 | CalPA | Set WMP-42 | CalPA_Set WMP-42 | 5 | CalPA_Set WMP-42_Q5 | Page 16 of PG&E’s 2025 WMP Update states, “in the WTRM v2 update, we corrected this overly conservative estimate by applying a remaining strength of 92% (equivalent to Condition Code 2) to reinforced poles, in order to provide more accurate results.” State the basis for applying a remaining strength of 92% to reinforced poles. | The WTRM uses condition codes assigned by an inspector based on ground and visual inspections of the pole. The condition codes range from 1 = no visible damage, to 3 = moderate damage, to 5 = immediate safety concern. The framework estimates the remaining strength from the condition codes using a simple linear relationship between condition codes and remaining strength. The translation line is anchored at two points, condition code = 1 is translated to remaining strength = 100% (no damage) while a condition code = 3 is translated to remaining strength = 67% or 2/3rd. The strength ratio of 2/3rd is based on California General Order 95 which is a threshold for repair or replacement of a component. The two anchor points define the translation and other condition codes are translated either by linear interpolation or linear extrapolation. Based on input from SME workshops, the strength degradation associated with a condition code of 2 has been reduced by half from 1/6th to 1/12th. The consensus feedback from the workshops was that a 1/6 strength reduction was unrealistically conservative for elements that exhibit only cosmetic damage (e.g. light surface corrosion). Condition Code Remaining Strength (%) 1 100 2 92 3 67 4 50 5 33 As noted in the question, the 92% remaining strength was intended to be consistent with a condition code of 2, which is typically used for a less than perfect condition that does not require repair. This was considered slightly conservative for a reinforcement that is as strong as the pole, which was Asset Strategy’s understanding of the intent of pole reinforcements by their vendor. PG&E continues to evaluate this assessment. | Holly Wehrman | 2024-04-09 | 2024-04-12 | 2024-04-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_042.zip | 0 | N/A | 6.2.2.2 | 6.0 Risk Methodology and Assessment | 6.2.2.2 Consequence | B.1.2. WTRM v2 |  | CalPA | Set WMP-42 | 5 | 0 | Mona Hedin | Mandy Knockaert | Jon Eric Thalman Benson Wong James Ash | Jon Eric Thalman | Aaron Shapiro | Andy Abranches | Yes | Yes |  |  |  | Yes | Yes |  | 2024-04-12 | [16 empty] | 5 | Jon Eric Thalman Benson Wong James Ash | Jon Eric Thalman | Mona Hedin | Mandy Knockaert | Aaron Shapiro | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
629 | OEIS | 019 | OEIS_019 | 1 | OEIS_019_Q1 | Regarding PG&E’s response to ACI PG&E-23-26, PG&E states the following in its 2025 WMP Update (p. 132): PG&E is currently finalizing an analysis to understand the tradeoffs between reliability and wildfire risk mitigation when EPSS circuits are enabled. This analysis should be completed by the second quarter of 2024 to be shared in PG&E’s 2024 RAMP filing and will address the portion of the ACI seeking a re-evaluation of PG&E’s EPSS-enablement thresholds. PG&E filed its 2024 RAMP filing on May 15, 2024; is this analysis completed? If yes, what is the format of this analysis that can be provided? | Please see Exhibit 4 Chapter 1: “2024 Risk Assessment and Mitigation Phase Report” of PG&E’s 2024 RAMP Filing for the initial analysis which presents the impact of the current PG&E EPSS enablement threshold. A further analysis is expected to be shared by the end of the second quarter of 2024 on the re-evaluation of PG&E’s EPSS enablement threshold. PG&E’s 2024 RAMP Filing is located at the following link: https://www.cpuc.ca.gov/- /media/cpuc-website/divisions/safety-policy-division/reports/2024-ramp-applicationpge051524. pdf. | Brad Hill | 2024-05-16 | 2024-05-21 | 2024-05-21 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/OEIS_019.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--26 Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI 23-26 Evaluation and Reporting of Safety Impacts Related to EPSS |  | OEIS | 019 | 1 | 0 | Mona Hedin | Saritha Basani | Katherine Hee | Eric Lamoureux | Kenny Lee | Mark Quinlan | Yes | Yes | Yes |  | Yes | Yes | Yes |  | 2024-05-21 | [16 empty] | 1 | Katherine Hee | Eric Lamoureux | Mona Hedin | Saritha Basani | Kenny Lee | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
666 | CPUC - SPD (Safety Policy Division) | 017 | CPUC - SPD (Safety Policy Division)_017 | 6 | CPUC - SPD (Safety Policy Division)_017_Q6 | Provide the analysis referenced in ACI PG&E-23-26 which computes the risk associated with EPSS-enablement thresholds. SPD understands the analysis shows a demonstration of trade-offs between reliability and wildfire risk mitigation effectiveness for each FPI level, as well as inclusion of areas outside the HFTD. SPD already has access to the analysis provided with the RAMP filing, and would like to see the more detailed FPI based analysis. | Please see response to SPD_017-Q005. | Henry Sweat | 2024-06-10 | 2024-06-13 | 2024-06-13 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_017.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--26 Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI 23-26 Evaluation and Reporting of Safety Impacts Related to EPSS |  | CPUC - SPD (Safety Policy Division) | 017 | 6 | 0 | Mona Hedin | Saritha Basani | Katherine Hee/John Birch | Eric Lamoureux | Kenny Lee | Mark Quinlan | Yes | [7 empty] | 2024-06-13 | [16 empty] | 6 | Katherine Hee/John Birch | Eric Lamoureux | Mona Hedin | Saritha Basani | Kenny Lee | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
665 | CPUC - SPD (Safety Policy Division) | 017 | CPUC - SPD (Safety Policy Division)_017 | 5 | CPUC - SPD (Safety Policy Division)_017_Q5 | Compute the additional risk reduced (or increased) due to the changes in criteria. The computation should account for lower probabilities of fires at lower FPI levels. Compute the additional risk induced due to increased (or reduced due to decreased) outages, due to the change in criteria. | PG&E is still completing the requested analysis and will provide the requested change in risk by Monday, July 1, 2024. | Henry Sweat | 2024-06-10 | 2024-06-13 | 2024-06-13 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_017.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--26 Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI 23-26 Evaluation and Reporting of Safety Impacts Related to EPSS |  | CPUC - SPD (Safety Policy Division) | 017 | 5 | 0 | Mona Hedin | Saritha Basani | Katherine Hee/John Birch/Benson Wong | Eric Lamoureux | Kenny Lee | Mark Quinlan | Yes | [7 empty] | 2024-06-13 | [16 empty] | 5 | Katherine Hee/John Birch/Benson Wong | Eric Lamoureux | Mona Hedin | Saritha Basani | Kenny Lee | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
664 | CPUC - SPD (Safety Policy Division) | 017 | CPUC - SPD (Safety Policy Division)_017 | 4 | CPUC - SPD (Safety Policy Division)_017_Q4 | Discuss the reason for the changes. | Please see response to SPD_017-Q001. PG&E continues to observe its EPSS peak season and non-peak season wildfire risk enablement criteria according to risk conditions observed across its service area. Biannually, recommendations are presented by leaders across PG&E to an officer-in-charge for approval to transition to peak season wildfire risk enablement criteria or to non-peak wildfire risk enablement criteria depending on observed field conditions. | Henry Sweat | 2024-06-10 | 2024-06-13 | 2024-06-13 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_017.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--26 Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI 23-26 Evaluation and Reporting of Safety Impacts Related to EPSS |  | CPUC - SPD (Safety Policy Division) | 017 | 4 | 0 | Mona Hedin | Saritha Basani | Katherine Hee/John Birch/Benson Wong | Eric Lamoureux | Kenny Lee | Mark Quinlan | Yes | [7 empty] | 2024-06-13 | [16 empty] | 4 | Katherine Hee/John Birch/Benson Wong | Eric Lamoureux | Mona Hedin | Saritha Basani | Kenny Lee | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
663 | CPUC - SPD (Safety Policy Division) | 017 | CPUC - SPD (Safety Policy Division)_017 | 3 | CPUC - SPD (Safety Policy Division)_017_Q3 | Prepare a table which shows the number of Circuit Mile Days where EPSS is enabled for 2022 and 2023 for the criteria in FIGURE PG&E-8.1.8-2 as compared to the new criteria. Additionally, provide the expected number of Circuit Mile Days where EPSS will be enabled for both criteria for a typical year. | Please see response to SPD_017-Q001. PG&E continues to leverage the same enablement criteria first approved by PG&E’s Wildfire Risk Governance Steering Committee in 2022 and provided in response to Question No. 001. EPSS settings were enabled for approximately 5,960,000 Circuit Mile Days in 2022 and approximately 5,520,000 Circuit Mile Days in 2023. Given EPSS enablement is dependent on the forecasted daily wildfire risk conditions in PG&E’s service area and may vary any given year in accordance with extremity of peak season conditions, an expected number of Circuit Mile Days where EPSS will be enabled is not available. However, based on the prior two years of program utilization, PG&E has averaged approximately 5,740,000 Circuit Mile Days of EPSS settings enablement a year. | Henry Sweat | 2024-06-10 | 2024-06-13 | 2024-06-13 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_017.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--26 Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI 23-26 Evaluation and Reporting of Safety Impacts Related to EPSS |  | CPUC - SPD (Safety Policy Division) | 017 | 3 | 0 | Mona Hedin | Saritha Basani | Katherine Hee/John Birch | Eric Lamoureux | Kenny Lee | Mark Quinlan | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | 2024-06-13 | [16 empty] | 3 | Katherine Hee/John Birch | Eric Lamoureux | Mona Hedin | Saritha Basani | Kenny Lee | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
662 | CPUC - SPD (Safety Policy Division) | 017 | CPUC - SPD (Safety Policy Division)_017 | 2 | CPUC - SPD (Safety Policy Division)_017_Q2 | When did this change take effect? | See response to SPD_017-Q001. The non-peak wildfire risk enablement criteria was approved by the PG&E Wildfire Risk Governance Steering Committee on February 2, 2022, and the peak season wildfire risk enablement criteria was approved on June 6, 2022. | Henry Sweat | 2024-06-10 | 2024-06-13 | 2024-06-13 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_017.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--26 Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI 23-26 Evaluation and Reporting of Safety Impacts Related to EPSS |  | CPUC - SPD (Safety Policy Division) | 017 | 2 | 0 | Mona Hedin | Saritha Basani | Katherine Hee/John Birch | Eric Lamoureux | Kenny Lee | Mark Quinlan | Yes | [7 empty] | 2024-06-13 | [16 empty] | 2 | Katherine Hee/John Birch | Eric Lamoureux | Mona Hedin | Saritha Basani | Kenny Lee | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
661 | CPUC - SPD (Safety Policy Division) | 017 | CPUC - SPD (Safety Policy Division)_017 | 1 | CPUC - SPD (Safety Policy Division)_017_Q1 | SPD understands PG&E has updated its EPSS enablement criteria since publishing FIGURE PG&E-8.1.8-2 in PG&E’s 2023-2025 Wildfire Mitigation Plan per page 133 of PG&E’s 2025 WMP Update. Provide an updated figure similar to FIGURE PG&E-8.1.8-2 and discuss the changes. | PG&E continues to observe two enablement criteria approved by our Wildfire Risk Governance Steering Committee in 2022, one during peak wildfire risk conditions and one during non-peak risk conditions. Included below are the EPSS peak and non-peak wildfire risk condition enablement criteria. Separately, we are in the process of evaluating wildfire risk and reliability tradeoffs when EPSS settings are enabled and anticipate finalizing the analysis by the end of Q2 2024. | Henry Sweat | 2024-06-10 | 2024-06-13 | 2024-06-13 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_017.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--26 Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI 23-26 Evaluation and Reporting of Safety Impacts Related to EPSS |  | CPUC - SPD (Safety Policy Division) | 017 | 1 | 0 | Mona Hedin | Saritha Basani | Katherine Hee/John Birch | Eric Lamoureux | Kenny Lee | Mark Quinlan | Yes |  | Yes | [5 empty] | 2024-06-13 |  |  | j1oz - EPSS enablement criteria graphic | [13 empty] | 1 | Katherine Hee/John Birch | Eric Lamoureux | Mona Hedin | Saritha Basani | Kenny Lee | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
647 | CPUC - SPD (Safety Policy Division) | 016 | CPUC - SPD (Safety Policy Division)_016 | 4 | CPUC - SPD (Safety Policy Division)_016_Q4 | Provide GIS data that show progressive sectionalization of EPSS-enabled circuits: a. Data snapshot of circuits from January 1, 2022 b. Data snapshot of circuits from January 1, 2023 c. Data snapshot of circuits from January 1, 2024 | PG&E is still compiling data and will provide the requested information as soon as possible. | Henry Sweat | 2024-05-30 | 2024-06-04 | 2024-06-04 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_016.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--26 Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI 23-26 Evaluation and Reporting of Safety Impacts Related to EPSS |  | CPUC - SPD (Safety Policy Division) | 016 | 4 | 3 | Mona Hedin | Saritha Basani | Katherine Hee; GIS (Eszter Tompos) | Eric Lamoureux Shawn Holder | Kenny Lee | Mark Quinlan |  | Yes | Yes |  | Yes | Yes |  |  | 2024-06-04 | [16 empty] | 4 | Katherine Hee; GIS (Eszter Tompos) | Eric Lamoureux Shawn Holder | Mona Hedin | Saritha Basani | Kenny Lee | 3 |  |  |  |  | completed | 0 | 0 | 0 | 0
680 | CalPA | Set WMP-50 | CalPA_Set WMP-50 | 10 | CalPA_Set WMP-50_Q10 | Provide an Excel spreadsheet of the following distribution circuits (as rows): SCE REFUGIO 1701, SCE VEGAS 1701, SCE TEJON TIE 1101, SCE TEHACHAPI 1101, SCE MCFARLAND 1101, VALLEY SPRINGS 1101, LAKEWOOD 1103, VASONA 1102, NAPA 1110, PUEBLO 2104, BIG TREES 0402, LOS OSITOS 2101, LAS POSITAS 2103, LAS AROMAS 0401, ORINDA 0401, SPENCE 1101. Include the following information in separate columns: a) Circuit Name b) Circuit ID e) Division (e.g., Los Padres Division)4 f) Date PG&E first activated EPSS settings on any part of the circuit5 g) Total Customers h) Number of CPZs contained on the circuit i) Circuit SAIDI for 2017 j) Circuit SAIDI for 2018 k) Circuit SAIDI for 2019 l) Circuit SAIFI for 2017 m) Circuit SAIFI for 2018 n) Circuit SAIFI for 2019 o) Circuit MAIFI for 2017 p) Circuit MAIFI for 2018 q) Circuit MAIFI for 2019 | Please see “WMP-Discovery2023-2025_DR_CalAdvocates_050-Q008Atch01.xlsx” for the requested information. In addition to the circuits included in the attachment, please see the table below for Circuit ID’s for the Circuits which did not have outages and were not provided in the attachment. Circuit Name Circuit ID SCE Vegas 1701 188881701 SCE Tejon Tie 1101 258191101 SCE McFarland 1101 258111101 Pueblo 2104 043292104 | Amanda Asadi | 2024-06-24 | 2024-07-09 | 2024-07-09 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_050.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--26 Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI 23-26 Evaluation and Reporting of Safety Impacts Related to EPSS |  | CalPA | Set WMP-50 | 10 | 15 | Mona Hedin | Saritha Basani | Tom Huynh | Satvir Nagra | Kenny Lee | Martin Wyspianski | Yes | Yes | Yes | Yes | Yes | Yes |  |  | 2024-07-09 | [16 empty] | 10 | Tom Huynh | Satvir Nagra | Mona Hedin | Saritha Basani | Kenny Lee | 15 |  |  |  |  | completed | 0 | 0 | 0 | 0
679 | CalPA | Set WMP-50 | CalPA_Set WMP-50 | 9 | CalPA_Set WMP-50_Q9 | Provide an Excel table that lists (as rows) each momentary outage that occurred from January 1, 2017 through December 31, 2023 on the following circuits: SCE REFUGIO 1701, SCE VEGAS 1701, SCE TEJON TIE 1101, SCE TEHACHAPI 1101, SCE MCFARLAND 1101 VALLEY SPRINGS 1101, LAKEWOOD 1103, VASONA 1102, NAPA 1110, PUEBLO 2104, BIG TREES 0402, LOS OSITOS 2101, LAS POSITAS 2103, LAS AROMAS 0401, ORINDA 0401, SPENCE 1101. For each outage, the Excel table should include the following information in separate columns: a) Outage ID b) Circuit Name c) Circuit ID d) Division e) Was EPSS enabled on this circuit at the time of the outage? f) When was this circuit made EPSS-capable? g) FNL (First No Light) h) Outage End Day & Time i) CESO (Count of Customers Experiencing Sustained Outages) j) Customer Minutes k) Cause l) Restoration Time (Minutes) | Please see “WMP-Discovery2023-2025_DR_CalAdvocates_050-Q008Atch01.xlsx” for the requested information. Please note, column N indicates if the outage was sustained or momentary. | Amanda Asadi | 2024-06-24 | 2024-07-09 | 2024-07-09 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_050.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--26 Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI 23-26 Evaluation and Reporting of Safety Impacts Related to EPSS |  | CalPA | Set WMP-50 | 9 | 121 | Mona Hedin | Saritha Basani | Tom Huynh | Satvir Nagra | Kenny Lee | Martin Wyspianski | Yes | Yes | Yes | Yes | Yes | Yes |  |  | 2024-07-09 | [16 empty] | 9 | Tom Huynh | Satvir Nagra | Mona Hedin | Saritha Basani | Kenny Lee | 121 |  |  |  |  | completed | 0 | 0 | 0 | 0
678 | CalPA | Set WMP-50 | CalPA_Set WMP-50 | 8 | CalPA_Set WMP-50_Q8 | Provide an Excel table that lists (as rows) each sustained outage that occurred from January 1, 2017 through December 31, 2023 on the following circuits: SCE REFUGIO 1701, SCE VEGAS 1701, SCE TEJON TIE 1101, SCE TEHACHAPI 1101, SCE MCFARLAND 1101, VALLEY SPRINGS 1101, LAKEWOOD 1103, VASONA 1102, NAPA 1110, PUEBLO 2104, BIG TREES 0402, LOS OSITOS 2101, LAS POSITAS 2103, LAS AROMAS 0401, ORINDA 0401, SPENCE 1101. For each outage, the Excel table should include the following information in separate columns: a) Outage ID b) Circuit Name c) Circuit ID d) Division e) Was EPSS enabled on this circuit at the time of the outage? f) When was this circuit made EPSS-capable? g) FNL (First No Light) h) Outage End Day & Time i) CESO (Count of Customers Experiencing Sustained Outages) j) Customer Minutes k) Cause l) Restoration Time (Minutes) | Please see “WMP-Discovery2023-2025_DR_CalAdvocates_050-Q008Atch01.xlsx” for the requested information. Column N indicates if the outage was sustained or momentary. Please note, as the following circuits did not have any outages, they have not been included in the attachment: SCE VEGAS 1701, SCE TEJON TIE 1101, SCE MCFARLAND 1101, PUEBLO 2104. As of July 2, 2024, these circuits have not been made EPSS-capable. | Amanda Asadi | 2024-06-24 | 2024-07-09 | 2024-07-09 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_050.zip | 1 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--26 Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI 23-26 Evaluation and Reporting of Safety Impacts Related to EPSS |  | CalPA | Set WMP-50 | 8 | 12 | Mona Hedin | Saritha Basani | Tom Huynh | Satvir Nagra | Kenny Lee | Martin Wyspianski | Yes | Yes | Yes | Yes | Yes | Yes |  |  | 2024-07-09 | [16 empty] | 8 | Tom Huynh | Satvir Nagra | Mona Hedin | Saritha Basani | Kenny Lee | 12 |  |  |  |  | completed | 0 | 0 | 0 | 0
677 | CalPA | Set WMP-50 | CalPA_Set WMP-50 | 7 | CalPA_Set WMP-50_Q7 | Provide an Excel table that lists (as rows) each momentary outage that occurred from January 1, 2023 through December 31, 2023 on any of the circuits identified in your response to Question 5 of data request CalAdvocates-PGE-2023WMP-34. For each outage, the Excel table should include the following information in separate columns: a) Outage ID b) Circuit Name c) Circuit ID d) Division e) Was EPSS enabled on this circuit at the time of the outage? f) FNL (First No Light) g) Outage End Day & Time h) CESO (Count of Customers Experiencing Sustained Outages) i) Customer Minutes j) Cause k) Restoration Time (Minutes) | Please see “WMP-Discovery2023-2025_DR_CalAdvocates_050-Q006Atch01.xlsx” for the requested information. Please note, column M indicates if the outage was sustained or momentary. | Amanda Asadi | 2024-06-24 | 2024-07-09 | 2024-07-09 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_050.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--26 Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI 23-26 Evaluation and Reporting of Safety Impacts Related to EPSS |  | CalPA | Set WMP-50 | 7 | 11 | Mona Hedin | Saritha Basani | Tom Huynh | Satvir Nagra | Kenny Lee | Martin Wyspianski | Yes | Yes | Yes | Yes | Yes | Yes |  |  | 2024-07-09 | [16 empty] | 7 | Tom Huynh | Satvir Nagra | Mona Hedin | Saritha Basani | Kenny Lee | 11 |  |  |  |  | completed | 0 | 0 | 0 | 0
676 | CalPA | Set WMP-50 | CalPA_Set WMP-50 | 6 | CalPA_Set WMP-50_Q6 | Provide an Excel table that lists (as rows) each sustained outage that occurred from January 1, 2023 through December 31, 2023 on any of the circuits identified in your response to Question 5 of data request CalAdvocates-PGE-2023WMP-34. For each outage, the Excel table should include the following information in separate columns: a) Outage ID b) Circuit Name c) Circuit ID d) Division e) Was EPSS enabled on this circuit at the time of the outage? f) FNL (First No Light) g) Outage End Day & Time h) CESO (Count of Customers Experiencing Sustained Outages) i) Customer Minutes j) Cause k) Restoration Time (Minutes) | Please see “WMP-Discovery2023-2025_DR_CalAdvocates_050-Q006Atch01.xlsx” for the requested information. Please note, column M indicates if the outage was sustained or momentary. | Amanda Asadi | 2024-06-24 | 2024-07-09 | 2024-07-09 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_050.zip | 1 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--26 Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI 23-26 Evaluation and Reporting of Safety Impacts Related to EPSS |  | CalPA | Set WMP-50 | 6 | 11 | Mona Hedin | Saritha Basani | Tom Huynh | Satvir Nagra | Kenny Lee | Martin Wyspianski | Yes | Yes | Yes | Yes | Yes | Yes |  |  | 2024-07-09 | [16 empty] | 6 | Tom Huynh | Satvir Nagra | Mona Hedin | Saritha Basani | Kenny Lee | 11 |  |  |  |  | completed | 0 | 0 | 0 | 0
675 | CalPA | Set WMP-50 | CalPA_Set WMP-50 | 5 | CALPA_Set WMP-50_Q5 | Data request CalAdvocates-PGE-2023WMP-34, Questions 9 and 10, PG&E states that Garberville 1101 and Otter 1102 had Fuse Save Installations “identified as a proactive strategy to both minimize wildfire risk while also providing reliability improvement benefits under EPSS enablement conditions.” a) Please provide an excel sheet of circuits that PG&E identified that might need proactive strategies ahead of EPSS enablement. b) Please provide the criteria PG&E used to determine which circuits might need proactive strategies for reliability improvement under EPSS enablement. | a) Please see “WMP-Discovery2023-2025_DR_CalAdvocates_050-Q005Atch01.xlsx” for a list of EPSS circuits identified for proactive reliability improvement work in 2024. b) Reliability improvement work identified as “proactive” relative to the EPSS program includes vegetation management, animal mitigation work, and sectionalizing work on EPSS capable zones experiencing multiple outages. Circuits and zones are identified for proactive work based on a combination of factors including historic EPSS outage activity, which includes causes of outages, customer impact, in some cases history of animal interaction in the geographic area, and all historical outage activity for sectionalizing work. | Amanda Asadi | 2024-06-24 | 2024-07-19 | 2024-07-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_050.zip | 1 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--26 Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI 23-26 Evaluation and Reporting of Safety Impacts Related to EPSS |  | CalPA | Set WMP-50 | 5 | 2 | Mona Hedin | Saritha Basani | Katherine Hee/Dave Casuncad | Eric Lamoureux | Kenny Lee | Mark Quinlan | [8 empty] | 2024-07-19 |  | kxfk - 7/11 - extension needed to 7/19 due to data gaps. | [14 empty] | 5 | Katherine Hee/Dave Casuncad | Eric Lamoureux | Mona Hedin | Saritha Basani | Kenny Lee | 2 |  |  |  |  | completed | 0 | 0 | 0 | 0
674 | CalPA | Set WMP-50 | CalPA_Set WMP-50 | 4 | CalPA_Set WMP-50_Q4 | Provide an Excel spreadsheet of all distribution circuits in HFTD or High Fire Risk Areas (HFRAs), or crossing HFTD and HFRA boundaries, existing as of January 1, 2024 (as rows) that includes the following information in separate columns: a) Circuit Name b) Circuit ID c) Date PG&E first activated EPSS settings on any part of the circuit3 | Please see “WMP-Discovery2023-2025_DR_CalAdvocates_050-Q004Atch01.xlsx” for the requested information. Please note, circuits scoped for the EPSS program in 2024 are based on primary overhead in HFRA and HFRA Tier 1 Buffer Areas and are not relative to HFTD areas. | Amanda Asadi | 2024-06-24 | 2024-07-09 | 2024-07-09 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_050.zip | 1 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--26 Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI 23-26 Evaluation and Reporting of Safety Impacts Related to EPSS |  | CalPA | Set WMP-50 | 4 | 3 | Mona Hedin | Saritha Basani | Katherine Hee/Chandler Nelson/John Birch | Eric Lamoureux | Kenny Lee | Mark Quinlan | Yes |  | Yes |  |  |  | Yes |  | 2024-07-09 | [16 empty] | 4 | Katherine Hee/Chandler Nelson/John Birch | Eric Lamoureux | Mona Hedin | Saritha Basani | Kenny Lee | 3 |  |  |  |  | completed | 0 | 0 | 0 | 0
673 | CalPA | Set WMP-50 | CalPA_Set WMP-50 | 3 | CalPA_Set WMP-50_Q3 | Data request CalAdvocates-PGE-2023WMP-34, Question 3, Attachments 1 and 2 show claims and complaints received from 5/19/2023 to 12/12/2023. Please provide an Excel sheet of claims and complaints filed by customers related to outages on circuits with EPSS settings enabled at the time of outage that were received in 2021, 2022, 1/1/2023 to 5/18/2023, 12/13/2023 to 12/31/2023. For each claim or complaint, provide the following information in separate columns: a) The Circuit name and ID associated with the complaint; b) The date each complaint or claim was received; c) Description of each complaint or claim; d) Resolution of each complaint or claim; e) Due date of each resolution; f) Actual completion date of each resolution. | Please be advised an attachment to this response contains CONFIDENTIAL information and is being provided pursuant to the accompanying confidentiality declaration. Please see “WMP-Discovery2023-2025_DR_CalAdvocates_050-Q003Atch01.xlsm” and “WMP-Discovery2023-2025_DR_CalAdvocates_050-Q003Atch02CONF.xlsm” for CPUC complaint information and claims information related to EPSS outages. Please note, EPSS related complaints are only tracked through complaints provided to PG&E by the CPUC, which is the data provided in the spreadsheet. Details of the complaint and resolution are in the individual cells in the excel file. Please note, there are no due dates for claims and the date given is the date the claim was closed. Please note that a population of EPSS complaints was inadvertently coded as “service interruption/outage” complaints. As such, PG&E is reviewing all “service interruption/outage” complaints and will provide any additional EPSS complaint data at a later date. | Amanda Asadi | 2024-06-24 | 2024-07-26 | 2024-07-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_050.zip | 2 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--26 Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI 23-26 Evaluation and Reporting of Safety Impacts Related to EPSS |  | CalPA | Set WMP-50 | 3 | 6 | Mona Hedin | Saritha Basani | Patrick Smalley | Christopher Bober/Tracy Maratukulam | Vivian Kim | Mark Quinlan | Yes | Yes | Yes |  | Yes | Yes | Yes |  | 2024-07-26 |  | j1oz - 7/1 - extension granted to 7/11 from engineer kxfk - 7/11 - extension needed to 7/26 due to data gaps. | [14 empty] | 3 | Patrick Smalley | Christopher Bober/Tracy Maratukulam | Mona Hedin | Saritha Basani | Vivian Kim | 6 |  |  |  |  | completed | 0 | 0 | 0 | 0
672 | CalPA | Set WMP-50 | CalPA_Set WMP-50 | 2 | CalPA_Set WMP-50_Q2 | In response to Data request CalAdvocates-PGE-2023WMP-34, Question 1, PG&E states, “no additional action required” for 36 circuits in 2022. Please explain why no additional action was required. | PG&E used the term “no additional action required” in the referenced data request to account for when a review was complete and the previously identified action items were either appropriate or additional actions items were not required due to one of the following reasons upon reviewing the outages and causes: • Outage Frequency (i.e., outages occurred across a long period of time on the circuit) • Cause Type (for example, a 3rd Party - Car Pole outage triggering a MORE review) PG&E would then continue to monitor the circuit for additional outages that may result in new action items as needed. | Amanda Asadi | 2024-06-24 | 2024-07-09 | 2024-07-09 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_050.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--26 Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI 23-26 Evaluation and Reporting of Safety Impacts Related to EPSS |  | CalPA | Set WMP-50 | 2 | 0 | Mona Hedin | Saritha Basani | Tim Bedford | Brienden Realph | Kenny Lee | Mark Quinlan | Yes |  | Yes | Yes | Yes | Yes |  |  | 2024-07-09 | [16 empty] | 2 | Tim Bedford | Brienden Realph | Mona Hedin | Saritha Basani | Kenny Lee | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
668 | CalPA | Set WMP-49 | CalPA_Set WMP-49 | 1 | CalPA_Set WMP-49_Q1 | How did PG&E come up with the 25 random numbers when it decided on the 25 out of 50 fast-trip outages to provide responses to? | PG&E selected the first 25 outages listed in the referenced file “Random Fast-Trip August 2023 Outages.xlsx” to provide the information requested in CalAdvocates_048-Q010. | Tyler Holzschuh | 2024-06-13 | 2024-06-27 | 2024-06-14 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_049.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--26 Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI 23-26 Evaluation and Reporting of Safety Impacts Related to EPSS |  | CalPA | Set WMP-49 | 1 | 0 | Mona Hedin | Saritha Basani | James Tuccillo/Erik Madsen | Eric Lamoureux | Kenny Lee | Mark Quinlan | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | 2024-06-27 | [16 empty] | 1 | James Tuccillo/Erik Madsen | Eric Lamoureux | Mona Hedin | Saritha Basani | Kenny Lee | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
628 | CalPA | Set WMP-48 | CalPA_Set WMP-48 | 10 | CalPA_Set WMP-48_Q10 | For each of the outages in the attached excel spreadsheet named “Random Fast-Trip August 2023 Outages.xlsx”, please provide: a) The protective function that tripped the circuit (e.g. definite time delay ground overcurrent); b) The current threshold of the protective function; c) The time delay of the protective function; d) The maximum load line-current from 2019-2023; e) The maximum unfaulted ground-current from 2019-2023; and f) If on distribution, whether the circuit was three-wire or four-wire. | PG&E objects to the request on the grounds that it is overbroad and unduly burdensome. Notwithstanding and without waiving this objection, PG&E is compiling the requested data for a random selection of 25 of the 50 outages included in “Random Fast-Trip August 2023 Outages.xlsx” and can provide the data by June 5, 2024. Please note, as this requires a manual data pull across multiple systems of record that will take many hours of work, it would be unduly burdensome to provide the information for all of the identified 50 outages. However, should this be an issue, we would be happy to meet and confer with you to discuss this request and our respective positions. | Tyler Holzschuh | 2024-05-16 | 2024-05-31 | 2024-05-31 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_048.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--26 Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI 23-26 Evaluation and Reporting of Safety Impacts Related to EPSS |  | CalPA | Set WMP-48 | 10 | 6 | Mona Hedin | Saritha Basani | Katherine Hee/James Tuccillo | Eric Lamoureux | Kenny Lee | Mark Quinlan | Yes | Yes |  |  |  | Yes | Yes |  | 2024-05-31 | [16 empty] | 10 | Katherine Hee/James Tuccillo | Eric Lamoureux | Mona Hedin | Saritha Basani | Kenny Lee | 6 |  |  |  |  | completed | 0 | 0 | 0 | 0
627 | CalPA | Set WMP-48 | CalPA_Set WMP-48 | 9 | CalPA_Set WMP-48_Q9 | Please provide the number of non-momentary (i.e., sustained) outages that PG&E had on circuits where fast-trip settings were not enabled from January to December 2023, by month. | Please see PG&E’s response to Q008. | Tyler Holzschuh | 2024-05-16 | 2024-05-31 | 2024-05-31 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_048.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--26 Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI 23-26 Evaluation and Reporting of Safety Impacts Related to EPSS |  | CalPA | Set WMP-48 | 9 | 0 | Mona Hedin | Saritha Basani | Katherine Hee Tom Huynh | Eric LamoureuxSatvir Nagra | Kenny Lee | Mark Quinlan /Martin Wyspianski | Yes |  | Yes |  |  | Yes | Yes |  | 2024-05-31 | [16 empty] | 9 | Katherine Hee Tom Huynh | Eric LamoureuxSatvir Nagra | Mona Hedin | Saritha Basani | Kenny Lee | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
626 | CalPA | Set WMP-48 | CalPA_Set WMP-48 | 8 | CalPA_Set WMP-48_Q8 | Please provide the number of momentary outages that PG&E had on circuits where fast-trip settings were not enabled from January to December 2023, by month. | Please see the table below for the requested information. Month # of Momentary Events # of Sustained Events Grand Total JAN 715 4152 4867 FEB 465 4390 4855 MAR 1175 5302 6477 APR 597 6140 6737 MAY 600 6264 6864 JUN 616 6041 6657 JUL 523 5723 6246 AUG 550 7014 7564 SEP 417 6028 6445 OCT 467 6909 7376 NOV 668 5993 6661 DEC 671 5431 6102 Grand Total 7464 69387 76851 | Tyler Holzschuh | 2024-05-16 | 2024-05-31 | 2024-05-31 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_048.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--26 Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI 23-26 Evaluation and Reporting of Safety Impacts Related to EPSS |  | CalPA | Set WMP-48 | 8 | 0 | Mona Hedin | Saritha Basani | Katherine Hee Tom Huynh | Eric Lamoureux Satvir Nagra | Kenny Lee | Mark Quinlan /Martin Wyspianski | Yes | Yes | Yes |  |  | Yes | Yes |  | 2024-05-31 | [16 empty] | 8 | Katherine Hee Tom Huynh | Eric Lamoureux Satvir Nagra | Mona Hedin | Saritha Basani | Kenny Lee | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
625 | CalPA | Set WMP-48 | CalPA_Set WMP-48 | 7 | CalPA_Set WMP-48_Q7 | Please provide the number of circuit-mile-days that PG&E did not activate fast-trip from January to December 2023, by month. | The circuit-mile-days below represent EPSS-scoped High Fire Risk Area miles not enabled with EPSS settings in 2023. Month Not Enabled HFRA Circuit Mile Days January 2023 750,439 February 2023 676,531 March 2023 751,419 April 2023 719,367 May 2023 699,301 June 2023 390,479 July 2023 52,739 August 2023 34,547 September 2023 43,504 October 2023 60,153 November 2023 323,700 December 2023 672,401 Total 5,174,581 | Tyler Holzschuh | 2024-05-16 | 2024-05-31 | 2024-05-31 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_048.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--26 Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI 23-26 Evaluation and Reporting of Safety Impacts Related to EPSS |  | CalPA | Set WMP-48 | 7 | 0 | Mona Hedin | Saritha Basani | Katherine Hee | Eric Lamoureux | Kenny Lee | Jason Regan | Yes | Yes | Yes |  |  | Yes | Yes |  | 2024-05-31 | [16 empty] | 7 | Katherine Hee | Eric Lamoureux | Mona Hedin | Saritha Basani | Kenny Lee | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
624 | CalPA | Set WMP-48 | CalPA_Set WMP-48 | 6 | CalPA_Set WMP-48_Q6 | Please provide the number of circuit-mile-days that PG&E activated fast-trip from January to December 2023, by month. | The circuit-mile-days below represent High Fire Risk Area miles enabled with EPSS settings in 2023. Month Enabled HFRA Circuit Mile Days January 2023 1,096 February 2023 2,275 March 2023 116 April 2023 7,926 May 2023 52,234 June 2023 336,813 July 2023 698,797 August 2023 716,988 September 2023 683,788 October 2023 691,383 November 2023 403,592 December 2023 79,135 Total 3,674,143 | Tyler Holzschuh | 2024-05-16 | 2024-05-31 | 2024-05-31 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_048.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--26 Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI 23-26 Evaluation and Reporting of Safety Impacts Related to EPSS |  | CalPA | Set WMP-48 | 6 | 0 | Mona Hedin | Saritha Basani | Katherine Hee | Eric Lamoureux | Kenny Lee | Mark Quinlan | Yes | Yes |  |  |  | Yes | Yes |  | 2024-05-31 | [16 empty] | 6 | Katherine Hee | Eric Lamoureux | Mona Hedin | Saritha Basani | Kenny Lee | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0
623 | CalPA | Set WMP-48 | CalPA_Set WMP-48 | 5 | CalPA_Set WMP-48_Q5 | Please provide the list of circuits that are directly upstream of PG&E’s distribution lines, including the following information: a) Circuit name; b) Voltage; and c) Whether the circuit is part of the NERC bulk electric system. | Per PG&E’s meeting with the Public Advocates Office (Cal Advocates) on May 24, 2024, PG&E understands this to be a request for a list of transmission lines that traverse PG&E’s HFTD service area irrespective of distribution lines and to provide a model of PG&E’s transmission system. Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_048- Q005Atch01.xlsx” for a list of PG&E’s HFTD transmission lines and their corresponding voltage. Please also see attachment “WMP-Discovery2023- 2025_DR_CalAdvocates_048-Q005Atch02CONF.zip” for documentation showing PG&E’s Transmission Operating Diagrams. Please note that these documents have been designated confidential as they contain Critical Energy Infrastructure Information. Additionally, they have also been designated confidential pursuant to the requirements of the Federal Energy Regulatory Commission. The information being provided will allow Cal Advocates to perform an independent evaluation of PG&E’s transmission lines to determine whether each circuit is part of the NERC Bulk Electric System. | Tyler Holzschuh | 2024-05-16 | 2024-05-31 | 2024-05-31 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_048.zip | 2 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--26 Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI 23-26 Evaluation and Reporting of Safety Impacts Related to EPSS |  | CalPA | Set WMP-48 | 5 | 3 | Mona Hedin | Saritha Basani | Katherine Hee Ben Nie Avineet Pannu | Eric Lamoureux/Davis Erwin | Kenny Lee | Mark Quinlan | Yes | Yes | Yes |  | Yes | Yes |  |  | 2024-05-31 | [16 empty] | 5 | Katherine Hee Ben Nie Avineet Pannu | Eric Lamoureux/Davis Erwin | Mona Hedin | Saritha Basani | Kenny Lee | 3 |  |  |  |  | completed | 0 | 0 | 0 | 0
622 | CalPA | Set WMP-48 | CalPA_Set WMP-48 | 4 | CalPA_Set WMP-48_Q4 | For PG&E’s circuits above 35 kV and classified as part of the NERC bulk electric system please describe, with references to PG&E’s procedures: a) PG&E’s fast-trip line-current thresholds; b) How PG&E’s fast-trip line-current thresholds are calculated from measured circuit values; c) The intentional delays assigned to those line-current thresholds; d) PG&E’s fast-trip ground-current thresholds; e) How PG&E’s fast-trip ground-current thresholds are calculated from measured circuit values; f) The intentional delays assigned to those ground-current thresholds; and g) How the current and delay thresholds differ from non fast-trip settings. | NERC Bulk Electric System transmission lines are excluded from PG&E’s Transmission EPSS program, therefore, PG&E is unable to provide the requested information. | Tyler Holzschuh | 2024-05-16 | 2024-05-31 | 2024-05-31 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_048.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--26 Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI 23-26 Evaluation and Reporting of Safety Impacts Related to EPSS |  | CalPA | Set WMP-48 | 4 | 7 | Mona Hedin | Saritha Basani | Katherine Hee Ben Nie | Eric Lamoureux Davis Erwin | Kenny Lee | Mark Quinlan | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | 2024-05-31 | [16 empty] | 4 | Katherine Hee Ben Nie | Eric Lamoureux Davis Erwin | Mona Hedin | Saritha Basani | Kenny Lee | 7 |  |  |  |  | completed | 0 | 0 | 0 | 0
621 | CalPA | Set WMP-48 | CalPA_Set WMP-48 | 3 | CalPA_Set WMP-48_Q3 | For PG&E’s circuits above 35 kV, but not classified as part of the NERC bulk electric system, please describe, with references to PG&E’s procedures: a) PG&E’s fast-trip line-current thresholds; b) How PG&E’s fast-trip line-current thresholds are calculated from measured circuit values; c) The intentional delays assigned to those line-current thresholds; d) PG&E’s fast-trip ground-current thresholds; e) How PG&E’s fast-trip ground-current thresholds are calculated from measured circuit values; f) The intentional delays assigned to those ground-current thresholds; and g) How the current and delay thresholds differ from non fast-trip settings. | PG&E’s Transmission EPSS (a category of “fast-trip”) settings are applied only on a subset of radial lines that are not classified as NERC BES. The responses below pertain only to the EPSS settings, and do not apply to normal non-EPSS settings. a) Transmission line protection is typically not purely current based. Transmission line protection commonly uses impedance based relays (aka distance relays), for which the trip threshold is not defined in current (amperes), but as an impedance value (ohms). For current based phase and ground overcurrent, Transmission EPSS phase instantaneous overcurrent and ground instantaneous overcurrent thresholds are set based on normal non-EPSS phase time overcurrent pickup and ground time overcurrent pickup thresholds respectively. Preferably, the settings are verified to be greater than 120% of distribution fault current for any tapped banks. However, if this criteria cannot be satisfied, providing instantaneous clearing for 100% of the transmission line is given precedence, and the risk of miscoordination with distribution faults is identified to Operations. For impedance based distance elements, Transmission EPSS phase distance and ground distance thresholds are set based on normal non-EPSS Zone 2 phase distance and Zone 2 ground distance thresholds respectively. These Zone 2 elements are already normally overreaching the end of the line. The adjustment to these distance elements is not the pickup threshold, but rather eliminating the normal time delays used for relay coordination purposes. b) The response here is provided with the interpretation that “calculated” is in reference to how the protection engineer calculates the relay setting thresholds, and not how the protective relay calculates the measured circuit values to compare against the set thresholds. Transmission line relay thresholds for both EPSS and non-EPSS settings are not calculated from measured circuit values, but are based on fault studies performed using a short-circuit model of the power system and by performing short-circuit studies. Relay thresholds also take into account facility ratings to avoid operating below the facility rating. c) Transmission EPSS settings have no intentional time delays. d) See response above to Part a. e) See response above to Part b. f) See response above to Part c. g) Current thresholds and delays (time dials) for phase time overcurrent and ground time overcurrent are identical for EPSS and non-EPSS settings. Current thresholds for phase instantaneous overcurrent and ground instantaneous overcurrent are normally set higher for non-EPSS settings as compared to fast-trip settings for the purpose of relay coordination and selectivity of clearing only insection faults. Delays for the instantaneous overcurrents are zero in both EPSS and non-EPSS settings. Distance element thresholds for phase distance and ground distance are identical for EPSS and non-EPSS settings. Zone 1 distance element time delays are also identical for EPSS and non-EPSS settings. Zone 2 distance element time delays are intentionally set to zero in EPSS settings, while for non-EPSS settings would have a typical value of 20-30 cycles or longer for the purpose of relay coordination. | Tyler Holzschuh | 2024-05-16 | 2024-05-31 | 2024-05-31 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_048.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--26 Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI 23-26 Evaluation and Reporting of Safety Impacts Related to EPSS |  | CalPA | Set WMP-48 | 3 | 7 | Mona Hedin | Saritha Basani | Katherine Hee Ben Nie John Birch Erik Madsen | Eric Lamoureux Davis Erwin | Kenny Lee | Mark Quinlan | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | 2024-05-31 | [16 empty] | 3 | Katherine Hee Ben Nie John Birch Erik Madsen | Eric Lamoureux Davis Erwin | Mona Hedin | Saritha Basani | Kenny Lee | 7 |  |  |  |  | completed | 0 | 0 | 0 | 0
620 | CalPA | Set WMP-48 | CalPA_Set WMP-48 | 2 | CalPA_Set WMP-48_Q2 | For PG&E’s four-wire multi-grounded primary circuits at or below 35 kV please describe, with references to PG&E’s procedures: a) PG&E’s fast-trip line-current thresholds; b) How PG&E’s fast-trip line-current thresholds are calculated from measured circuit values; c) The intentional delays assigned to those line-current thresholds; d) PG&E’s fast-trip ground-current thresholds; e) How PG&E’s fast-trip ground-current thresholds are calculated from measured circuit values; f) The intentional delays assigned to those ground-current thresholds; and g) How the current and delay thresholds differ from non fast-trip settings. | PG&Es most current EPSS protection guidelines are document in TD-1470P-01 Att. 1 “Application Guide Device Profile Settings.” Please see “WMP-Discovery2023- 2025_DR_CalAdvocates_048-Q002.pdf” for a copy of these guidelines. The same criteria applies as stated in Question 1 subpart a). a) The same criteria applies as stated in Question 1 subpart b). b) The same criteria applies as stated in Question 1 subpart c). c) The same criteria applies as stated in Question 1 subpart d) except for SGF, it is not applied in most 4-wire system configurations. d) PG&E’s EPSS 4-wire muti-grounded primary circuit ground overcurrent trip settings are based upon short circuit analysis provided through simulation of the distribution network model. The simulations provide values to set as described in Question 1 section a). Maximum ground current data is obtained through planning forecasts as well as historical SCADA observations. e) The same criteria applies as stated in Question 1 subpart e) other than no SGF delay applies. f) The same criteria applies as state in Question 1 subpart g). | Tyler Holzschuh | 2024-05-16 | 2024-05-31 | 2024-05-31 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_048.zip | 1 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--26 Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI 23-26 Evaluation and Reporting of Safety Impacts Related to EPSS |  | CalPA | Set WMP-48 | 2 | 7 | Mona Hedin | Saritha Basani | James Tuccillo/Eric Madsen | Eric Lamoureux | Kenny Lee | Mark Quinlan | Yes | Yes | Yes |  |  | Yes |  |  | 2024-05-31 | [16 empty] | 2 | James Tuccillo/Eric Madsen | Eric Lamoureux | Mona Hedin | Saritha Basani | Kenny Lee | 7 |  |  |  |  | completed | 0 | 0 | 0 | 0
619 | CalPA | Set WMP-48 | CalPA_Set WMP-48 | 1 | CalPA_Set WMP-48_Q1 | For PG&E’s three-wire uni-grounded primary circuits at or below 35 kV (nominal) please describe, with references to PG&E’s procedures: a) PG&E’s fast-trip (known as Enhanced Powerline Safety Settings, or EPSS) line-current2 thresholds; b) How PG&E’s fast-trip line-current thresholds are calculated from measured circuit values; c) The intentional delays assigned to those line-current thresholds; d) PG&E’s fast-trip ground-current thresholds; e) How PG&E’s fast-trip ground-current thresholds are calculated from measured circuit values; f) The intentional delays assigned to those ground-current thresholds; and g) How the current (both line and ground) and delay thresholds differ from non fast-trip settings. | PG&Es most current EPSS protection guidelines are document in TD-1470P-01 Att. 1 “Application Guide Device Profile Settings”. a) EPSS phase overcurrent settings for line reclosers (LR) and circuit breakers (CB) are set with the following guidelines: Phase time overcurrent (51 element) Phase minimum-to-trip (MTT) ≤ 60% three-phase fault or 70% line-to-line fault based upon simulated short circuit bolted faults at the protection zone end of line. Fuses and other single phase (non-ganged) protective devices are not included as delimiters for the purpose of establishing the protective zone. Set phase MTT greater than 1.2x maximum expected loading. Phase instantaneous/definite time overcurrent (50 element) Phase instantaneous trip setting is set equal to the phase time overcurrent minimum to trip. b) PG&E’s EPSS phase overcurrent trip settings are based upon short circuit analysis provided through simulation of the distribution network model. The simulations provide values to set as described in a). Maximum loading data is obtained through planning forecasts as well as historical SCADA observations. c) For EPSS, phase instantaneous/definite time settings are used to establish coordination delay. The time delay of the furthest protective device is set to 0ms or no intentional delay. Each consecutive source side protective device is set with an additional +0.02 to 0.05s time delay, optimizing for margin. Protective device time delays will not exceed 0.1s or 6 cycles. d) EPSS ground overcurrent settings for line reclosers and circuit breakers are set with the following guidelines: Ground time overcurrent (51N/G element) Ground minimum-to-trip (MTT) ≤ 50% simulated short circuit bolted line to ground fault at the protection zone end of line. Fuses and other single phase (non-ganged) protective devices are not included as delimiters for the purpose of establishing the protective zone. Set ground MTT greater than 1.2x maximum expected normal standing ground current. Ground instantaneous/definite time overcurrent (50N/G element) Phase instantaneous trip setting is set equal to the phase time overcurrent minimum to trip. Sensitive Ground Element (SGF) The sensitive ground element (SGF) for three-wire applications is typically set between 5-15A to provide a low set ground overcurrent element to attempt to detect high impedance ground faults. The SGF setting threshold is also required to be 1.2x the maximum observed standing ground fault current due to system capacitance and configuration. e) PG&E’s EPSS ground overcurrent trip settings are based upon short circuit analysis provided through simulation of the distribution network model. The simulations provide values to set as described in d). f) The ground instantaneous/definite time overcurrent time delay is set the same as the phase delay in section c). For SGF the minimum time delay is typically set from 5-15 seconds with 1-3 seconds of coordination time between devices equipped in series with SGF towards the source. g) Non-EPSS settings operate typically with a time-overcurrent element which may or may not also have an instantaneous or definite time element set. Non-EPSS settings also account for fuses as other non-gang trip device to delimit protective zones thereby reducing the zone of protection. The minimum separation guideline between two LRs or between LR and CB is typically 0.2s. Both EPSS and non-EPSS settings utilize the same principles of end of line fault detection and anticipated load accommodate when setting the MTT thresholds. In addition, settings are designed to protect against equipment damage by limiting I^2T energy as well as arc-flash exposure. | Tyler Holzschuh | 2024-05-16 | 2024-05-31 | 2024-05-31 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_048.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--26 Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI 23-26 Evaluation and Reporting of Safety Impacts Related to EPSS |  | CalPA | Set WMP-48 | 1 | 7 | Mona Hedin | Saritha Basani | James Tuccillo/Eric Madsen | Eric Lamoureux | Kenny Lee | Mark Quinlan | Yes | Yes | Yes |  |  | Yes |  |  | 2024-05-31 | [16 empty] | 1 | James Tuccillo/Eric Madsen | Eric Lamoureux | Mona Hedin | Saritha Basani | Kenny Lee | 7 |  |  |  |  | completed | 0 | 0 | 0 | 0
644 | CPUC - SPD (Safety Policy Division) | 016 | CPUC - SPD (Safety Policy Division)_016 | 1 | CPUC - SPD (Safety Policy Division)_016_Q1 | In response to ACI PG&E-23-13 – Workforce Planning and Resource Allocation to Respond to EPSS Events, Customer Average Interruption Duration Index (CAIDI) metric PG&E indicated: customers on average experiencing EPSS outages of 176 minutes in 2022 and 193 minutes in 2023 (We note that the CAIDI score when excluding Major Event Days (MED) was 183 minutes for 2023). What was the key reason(s) or driver(s), if known, for the increase in CAIDI from 2022 to 2023? | Excluding Major Event Days (MEDs), the increase in CAIDI from 2022 to 2023 was approximately seven minutes. In 2023, the additional implementation of Down Conductor Detection (DCD) resulted in outages that accounted for an increase in EPSS CAIDI of approximately ten minutes. Excluding both MEDs and DCD outages, the EPSS CAIDI in 2023 was approximately 173 minutes. In 2024, the EPSS PMO plans to implement DCD technology firmware upgrades, developed in partnership with our vendor, across devices currently DCD capable in the field in an effort to reduce occurrence of DCD trips where no cause was found after patrol or the outage was related to planned system switching activities. | Henry Sweat | 2024-05-30 | 2024-06-04 | 2024-06-04 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_016.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--13 | ACI 23-13 Workforce Planning and Resource Allocation |  | CPUC - SPD (Safety Policy Division) | 016 | 1 | 0 | Mona Hedin | Saritha Basani | Katherine Hee | Eric Lamoureux | Kenny Lee | Mark Quinlan | Yes | Yes | Yes |  |  | Yes | Yes |  | 2024-06-04 | [16 empty] | 1 | Katherine Hee | Eric Lamoureux | Mona Hedin | Saritha Basani | Kenny Lee | 0 |  |  |  |  | completed | 0 | 0 | 0 | 0