468 | CalPA | Set WMP-30 | CalPA_Set WMP-30 | 4 | CalPA_Set WMP-30_Q4 | The following questions refer to the risk scores generated from WDRM v4. This should be understood to refer to PG&E’s responses to questions 1 and 2 above. Please provide a GIS file that details the risk scores at the same granularity that is currently used to inform wildfire mitigation measures (as discussed in questions 1(f) and 2(f)). This file should contain the following: a) Geometric features detailing the relevant geometry for each risk score. This may be polygons that depict “pixels,” lines that depict circuit segments, points that depict assets, or other geometry that best suits the relevant risk scores. If multiple risk scores share geometry (e.g., multiple risk scores that are used to inform mitigation measures at the circuit segment level), there is no need to include multiple layers that depict the same physical geometry. b) For each geometric feature, please include all relevant risk scores from questions 1(a) and 2(a) as attributes. c) For each geometric feature, include the circuit identification number as an attribute. d) For each geometric feature, include the circuit name as an attribute. e) For each geometric feature, include the circuit segment name as an attribute. f) As needed, include unique identification for each geometric feature (e.g., asset ID, substation name, etc.) | a) - f) As stated in the response to Questions 001 - 003, the WDRM v4 is not currently available. PG&E plans to make the model information available with the 2025 WMP Update. | Holly Wehrman | 2023-10-11 | 2023-10-25 | 2023-10-23 | https://www.pge.com/pge_global/common/pdfs/safety/emergency-preparedness/natural-disaster/wildfires/wildfire-mitigation-plan/reference-docs/2023/CalAdvocates_030.zip | 0 | N/A | 2022 WMP Section 4.5 | Model Metrics and Calculation Methodologies | N/A | N/A
469 | CalPA | Set WMP-30 | CalPA_Set WMP-30 | 5 | CalPA_Set WMP-30_Q5 | The following questions refer to the risk scores generated from WDRM v4. This should be understood to refer to PG&E’s responses to questions 1 and 2 above. Please provide a spreadsheet that lists (as rows) each circuit-segment that is included in the Wildfire Distribution Risk Model v4. This spreadsheet should include, at minimum, the following columns. a) Name or ID number of each circuit segment. b) Circuit name for the circuit that each segment is part of. c) Circuit ID for the circuit that each segment is part of. d) Nominal voltage. e) The pixel count of the circuit segment. (Cal Advocates understands this to be the number of 100m x 100m pixels analyzed by the WDRM v4 along the length of the circuit segment). f) The average risk value(s) associated with each pixel along the circuit segment. (In previous versions of the risk model, this was referred to as the “mean MAVF core risk” or “mean risk”). g) Total circuit-miles on the circuit-segment. h) Total overhead circuit-miles on the circuit-segment. i) Total non-HFTD overhead circuit-miles on the circuit-segment. j) Total Tier 2 overhead circuit-miles on the circuit-segment. k) Total Tier 3 overhead circuit-miles on the circuit-segment. l) Total underground circuit-miles on the circuit-segment. m) Total non-HFTD underground circuit-miles on the circuit-segment. n) Total Tier 2 underground circuit-miles on the circuit-segment. o) Total Tier 3 underground circuit-miles on the circuit-segment. p) Each risk score (each in a separate and labeled column) identified in question 1(a) that is used at the circuit-segment level to inform wildfire mitigation initiatives. (May require multiple columns.) q) Each composite risk score (each in a separate and labeled column) identified in question 2(a) that is used at the circuit-segment level to inform wildfire mitigation initiatives. (May require multiple columns.) | a) - q) As stated in the response to Questions 001 - 004, the WDRM v4 is not currently available. PG&E plans to make the model information available with the 2025 WMP Update. | Holly Wehrman | 2023-10-11 | 2023-10-25 | 2023-10-23 | https://www.pge.com/pge_global/common/pdfs/safety/emergency-preparedness/natural-disaster/wildfires/wildfire-mitigation-plan/reference-docs/2023/CalAdvocates_030.zip | 0 | N/A | 2022 WMP Section 4.5 | Model Metrics and Calculation Methodologies | N/A | N/A
470 | CalPA | Set WMP-30 | CalPA_Set WMP-30 | 6 | CalPA_Set WMP-30_Q6 | The following questions refer to the risk scores generated from WDRM v4. This should be understood to refer to PG&E’s responses to questions 1 and 2 above. a) Has E3 or another entity performed an independent review of the WDRM v4? b) If the answer to part (a) is yes, please provide a copy of any report and output from the independent review. c) If the answer to part (a) is no, does PG&E plan to have E3 or a similar entity perform an independent review of the WDRM v4? d) If the answer to part (c) is no, please explain why not. e) If the answer to part (c) is yes, when does PG&E expect the review to be completed? | a) - e) The WDRM v4 is currently under review by E3. PG&E expects that the E3 review will be completed and available with the 2025 WMP Update. | Holly Wehrman | 2023-10-11 | 2023-10-25 | 2023-10-23 | https://www.pge.com/pge_global/common/pdfs/safety/emergency-preparedness/natural-disaster/wildfires/wildfire-mitigation-plan/reference-docs/2023/CalAdvocates_030.zip | 0 | N/A | 2022 WMP Section 4.5 | Model Metrics and Calculation Methodologies | N/A | N/A
471 | CalPA | Set WMP-30 | CalPA_Set WMP-30 | 7 | CalPA_Set WMP-30_Q7 | The following questions refer to the risk scores generated from WDRM v4. This should be understood to refer to PG&E’s responses to questions 1 and 2 above. a) Has PG&E created a detailed overview document that details the WDRM v4, similar to the “2021 Wildfire Distribution Risk Model Overview” that PG&E submitted following the public workshop held on October 5 and 6, 2021? b) If the answer to part (a) is yes, please provide a copy of the document. c) If the answer to part (a) is no, does PG&E plan to create such a document? d) If the answer to part (c) is no, please explain why not. e) If the answer to part (c) is yes, when does PG&E expect the document to be completed? | a) - e) As stated in the response to Questions 001 - 005, the WDRM v4 is not currently available. PG&E plans to make the model information available with the 2025 WMP Update. Along with this model information, PG&E anticipates preparing a similar document as part of the 2025 WMP Update. | Holly Wehrman | 2023-10-11 | 2023-10-25 | 2023-10-23 | https://www.pge.com/pge_global/common/pdfs/safety/emergency-preparedness/natural-disaster/wildfires/wildfire-mitigation-plan/reference-docs/2023/CalAdvocates_030.zip | 0 | N/A | 2022 WMP Section 4.5 | Model Metrics and Calculation Methodologies | N/A | N/A
472 | CalPA | Set WMP-30 | CalPA_Set WMP-30 | 8 | CalPA_Set WMP-30_Q8 | The following questions refer to the risk scores generated from WDRM v4. This should be understood to refer to PG&E’s responses to questions 1 and 2 above. Page 75 of PG&E’s 2023-2025 Wildfire Mitigation Plan Supplemental Response to Revision Notice, September 27, 2023 states, “When we begin using the WDRM v4 and incorporating it with the WBCA [Wildfire Benefit Cost Analysis], risk ranking and project prioritization will include wildfire risk reduction, reliability benefits, public safety, project costs, long-term savings and other factors that present a more fulsome view into the costs and benefits of an undergrounding project.” a) Does the WDRM v4 include an estimation of reliability benefits, as discussed in the above quote? Please explain if yes. b) Does the WDRM v4 include an estimation of public safety, as discussed in the above quote? Please explain if yes. c) Does the WDRM v4 include an estimation of project costs, as discussed in the above quote? Please explain if yes. | a) - c) The WDRM v4 scope does not include the estimated benefits requested in parts a, b, and c. Reliability benefits, public safety, and project costs will be considered as part of the WBCA and are not part of the WDRM v4. | Holly Wehrman | 2023-10-11 | 2023-10-25 | 2023-10-23 | https://www.pge.com/pge_global/common/pdfs/safety/emergency-preparedness/natural-disaster/wildfires/wildfire-mitigation-plan/reference-docs/2023/CalAdvocates_030.zip | 0 | N/A | 2022 WMP Section 4.5 | Model Metrics and Calculation Methodologies | N/A | N/A
473 | CalPA | Set WMP-31 | CalPA_Set WMP-31 | 1 | CalPA_Set WMP-31_Q1 | The following questions pertain to PG&E’s 2023 - 2025 WMP Revision 3, submitted on September 27, 2023, Section 8.1.7 – Open Work Orders. On page 530 of your 2023 – 2025 WMP R3, PG&E provided a table (Table 8-8-1) showing the total number of past due transmission asset work orders by age and HFTD tier. Please provide an updated version of Table 8-8-1, as of September 30, 2023. Number of Past Due Transmission Asset Work Orders Categorized by Age (through September 30, 2023) HFTD Area 0 – 30 Days 31 – 90 Days 91 – 180 Days 181+ Days Non – HFTD HFTD Tier 2 HFTD Tier 3 | Please see the table below for the requested information. Number of Past Due Transmission Asset Work Orders Categorized by Age (through September 30, 2023) HFTD Area 0 – 30 Days 31 – 90 Days 91 – 180 Days 181+ Days Non – HFTD 1877 3314 3467 16159 HFTD Tier 2 155 550 1765 1149 HFTD Tier 3 60 54 98 835 | Holly Wehrman | 2023-10-12 | 2023-10-26 | 2023-10-25 | https://www.pge.com/pge_global/common/pdfs/safety/emergency-preparedness/natural-disaster/wildfires/wildfire-mitigation-plan/reference-docs/2023/CalAdvocates_031.zip | 0 | N/A | 8.1.7 | Open Work Orders | N/A | N/A
474 | CalPA | Set WMP-31 | CalPA_Set WMP-31 | 2 | CalPA_Set WMP-31_Q2 | The following questions pertain to PG&E’s 2023 - 2025 WMP Revision 3, submitted on September 27, 2023, Section 8.1.7 – Open Work Orders. On page 530 of your 2023 – 2025 WMP R3, PG&E provided a table (Table 8-8-1) showing the total number of past due transmission asset work orders by age and HFTD tier. Please provide a similar table for past due distribution asset work orders by age and HFTD tier, as of September 30, 2023. Number of Past Due Distribution Asset Work Orders Categorized by Age (through September 30, 2023) HFTD Area 0 – 30 Days 31 – 90 Days 91 – 180 Days 181+ Days Non – HFTD HFTD Tier 2 HFTD Tier 3 | Please see the table below for the requested information. Number of Past Due Distribution Asset Work Orders Categorized by Age (through September 30, 2023) HFTD Area 0 – 30 Days 31 – 90 Days 91 – 180 Days 181+ Days Non – HFTD 18,404 38,327 41,357 200,643 HFTD Tier 2 1,353 15,817 25,158 68,061 HFTD Tier 3 230 269 847 60,907 | Holly Wehrman | 2023-10-12 | 2023-10-26 | 2023-10-25 | https://www.pge.com/pge_global/common/pdfs/safety/emergency-preparedness/natural-disaster/wildfires/wildfire-mitigation-plan/reference-docs/2023/CalAdvocates_031.zip | 0 | N/A | 8.1.7 | Open Work Orders | N/A | N/A
475 | CalPA | Set WMP-31 | CalPA_Set WMP-31 | 3 | CalPA_Set WMP-31_Q3 | The following questions pertain to PG&E’s 2023 - 2025 WMP Revision 3, submitted on September 27, 2023, Section 8.1.7 – Open Work Orders. On page 557 of your 2023 – 2025 WMP R3, PG&E stated with regard to distribution asset work orders, “PG&E is unable to provide the number of past due asset work orders, categorized by age, in the HFTD from Q1 2020 through Q3 2022.” a) Please list the reasons why PG&E was unable to provide the number of past due asset work orders, categorized by age, in the HFTD, as stated above. b) Please list any steps PG&E has taken to improve its ability to provide the number of past due asset work orders, categorized by age, in the HFTD. | a) At the time of filing the 2023 – 2025 WMP, PG&E did not have the capability to extract the data at the granularity requested. Therefore, PG&E was unable to provide the number of past due asset work orders and, therefore, utilized the Quarterly Data Report, Table 2, metric 7 as a proxy to generate the number of past due asset work orders. b) Throughout 2023, PG&E has improved its “data” extraction capabilities and is now able to provide this data at the requested granularity. This capability has improved by employing additional data scientists and creating automated scripting possibilities. This semi-automated process will now allow us to pull data more readily, and at the granularity desired. | Holly Wehrman | 2023-10-12 | 2023-10-26 | 2023-10-25 | https://www.pge.com/pge_global/common/pdfs/safety/emergency-preparedness/natural-disaster/wildfires/wildfire-mitigation-plan/reference-docs/2023/CalAdvocates_031.zip | 0 | N/A | 8.1.7 | Open Work Orders | N/A | N/A
476 | CalPA | Set WMP-31 | CalPA_Set WMP-31 | 4 | CalPA_Set WMP-31_Q4 | The following questions pertain to PG&E’s 2023 - 2025 WMP Revision 3, submitted on September 27, 2023, Section 8.1.7 – Open Work Orders. Section 8.1.7.2 – Open Work Orders – Distribution Tags in PG&E’s 2023 – 2025 WMP R3 discusses a subset of open works orders referred to as “ignition-risk” tags. Please provide a table similar to Table 8-8-1 for all past due, ignition-risk, distribution asset work orders by age and HFTD tier, as of September 30, 2023. Number of “Ignition Risk” Past Due Distribution Asset Work Orders Categorized by Age (through September 30, 2023) HFTD Area 0 – 30 Days 31 – 90 Days 91 – 180 Days >181 Days Non - HFTD HFTD Tier 2 HFTD Tier 3 | Please see the table below for the requested information. Number of “Ignition Risk” Past Due Distribution Asset Work Orders Categorized by Age (through September 30, 2023) HFTD Area 0 – 30 Days 31 – 90 Days 91 – 180 Days >181 Days Non - HFTD 33 205 454 2,077 HFTD Tier 2 1,191 1,4826 23,605 60,512 HFTD Tier 3 146 193 753 55,157 | Holly Wehrman | 2023-10-12 | 2023-10-26 | 2023-10-25 | https://www.pge.com/pge_global/common/pdfs/safety/emergency-preparedness/natural-disaster/wildfires/wildfire-mitigation-plan/reference-docs/2023/CalAdvocates_031.zip | 0 | N/A | 8.1.7 | Open Work Orders | N/A | N/A
477 | CPUC - SPD (Safety Policy Division) | 011 | CPUC - SPD (Safety Policy Division)_011 | 1 | CPUC - SPD (Safety Policy Division)_011_Q1 | Provide calculations that justify Table RN-PG&E-23-05-3. Explain specifically how Risk Avoidance over Lifetime Benefit is calculated from Total Risk. (page 85 of PG&E’s 2023-2025 Wildfire Mitigation Plan (WMP) – Supplemental Revision Notice Response) | In Critical Issue RN-PG&E-23-05, PG&E explained that in response to the Commission’s decision in the Risk-Based Decision-Making Framework OIR (RBDMF),1 we are in the process of constructing a benefit/cost model. The model will incorporate several elements of the mitigation selection decision-making process into an analytical model. PG&E calls this the Wildfire Benefit Cost Analysis (WBCA) tool. In RN-PG&E-23-05 PG&E provided an example of the output from the WBCA model for two mitigation alternatives at two circuit segments (Table RN-PG&E-23-05-3). PG&E responded to an Energy Safety Data Request2 asking for more information about the WBCA. In that response, PG&E explained that the WBCA has not been fully developed, approved, or implemented within PG&E. We also explained that the workplan submitted in the 2023-2025 WMP is based on PG&E’s Wildfire Distribution Risk Model (WDRM) and none of the 2023-2026 projects included in the WMP workplan were selected using the WBCA. The WBCA is being developed to support PG&E’s 10-year (SB 884) undergrounding plan and we anticipate finalizing the WBCA for that submission in 2024. We anticipate eventually using the WBCA to inform project selection for PG&E’s long-term undergrounding plan and future WMPs. Because the WBCA is still in development, PG&E is not in position to respond to either of the questions in this data request. | Henry Sweat | 2023-10-12 | 2023-10-17 | 2023-10-17 | https://www.pge.com/pge_global/common/pdfs/safety/emergency-preparedness/natural-disaster/wildfires/wildfire-mitigation-plan/reference-docs/2023/SPD_011.zip | 0 | N/A | 8.1.2.2 | Grid Design and System Hardening | Undergrounding of electric lines and/or equipment | N/A
477 | CPUC - SPD (Safety Policy Division) | 012 | CPUC - SPD (Safety Policy Division)_012 | 1 | CPUC - SPD (Safety Policy Division)_012_Q1 | Provide calculations that justify Table RN-PG&E-23-05-3. Explain specifically how Risk Avoidance over Lifetime Benefit is calculated from Total Risk. (page 85 of PG&E’s 2023-2025 Wildfire Mitigation Plan (WMP) – Supplemental Revision Notice Response) | Please see “WMP-Discovery2023_DR_SPD_012-Q001Atch01.xlsx” for the visual and underlying data. This chart has not been updated. PG&E expects to update this chart in Q2 of 2024 as part of the Risk Assessment and Mitigation Phase (RAMP) filing. Please note, there was a non-material correction in the visual data labels. Both the original and corrected visual data labels are provided in the attachment. | Henry Sweat | 2023-11-13 | 2023-11-15 | 2023-11-14 | https://www.pge.com/content/dam/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_012.zip | 1 | N/A | 8.1.2.2 | Grid Design and System Hardening | Undergrounding of electric lines and/or equipment | N/A
478 | CPUC - SPD (Safety Policy Division) | 011 | CPUC - SPD (Safety Policy Division)_011 | 2 | CPUC - SPD (Safety Policy Division)_011_Q2 | Provide a numerical justification that shows the risk from (outages or other sources) for EPSS compares to benefits of EPSS (less wildfires, others?). SPD would prefer the analysis performed using cost benefit ratios (similar to that shown in Table RN-PG&E-23-05-3). | Please see PG&E’s response to Question 1 of this data request. | Henry Sweat | 2023-10-12 | 2023-10-17 | 2023-10-17 | https://www.pge.com/pge_global/common/pdfs/safety/emergency-preparedness/natural-disaster/wildfires/wildfire-mitigation-plan/reference-docs/2023/SPD_011.zip | 0 | N/A | 8.1.2.2 | Grid Design and System Hardening | Undergrounding of electric lines and/or equipment | N/A
479 | CalPA | Set WMP-32 | CalPA_Set WMP-32 | 1 | CalPA_Set WMP-32_Q1 | Please provide the following data for the years 2020, 2021, 2022, and 2023: a) Number of miles of underground distribution that PG&E installed as part of overhead-to-undergrounding conversion projects for the purposes of wildfire risk reduction. b) Number of miles of overhead distribution PG&E removed as part of the same projects in part (a). | Please see the table below with the data requested for subparts a and b. a) Please see row (a) UG Miles Completed. Included are the miles of underground primary distribution lines installed each year 2020-2022 for the purposes of wildfire risk reduction. The data provided in 2023 is year to date through November 1, 2023. In addition to the miles complete, PG&E also has approximately 200 miles currently in progress (e.g., permit complete, in construction, trench complete, conduit installed, ready for cable pulling). b) Please see row (b) OH Miles Replaced (estimated). Included are the estimated miles of overhead primary distribution lines PG&E has removed as part of undergrounding projects for the purposes of wildfire risk reduction. PG&E historically did not track exactly the overhead miles replaced by each project, therefore, the overhead miles replaced is calculated based on UG Miles Completed using a standard conversion factor for rebuild projects or all other undergrounding projects. For Community rebuild projects (Butte and Greenville) for every 1.57 miles of UG installed, one mile of existing OH lines has been removed; for all other projects, 1.25 miles of UG installed equates to one mile of existing OH removed. 2020 2021 2022 2023 Total a) UG Miles Completed 42.4 73.2 179.8 208.6 503.9 b) OH Miles Replaced (est.) 27.9 53.2 134 158.5 373.5 | Holly Wehrman | 2023-10-31 | 2023-11-14 | 2023-11-14 | https://www.pge.com/content/dam/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_032.zip | 0 | N/A | 7.2.2.1 | Wildfire Mitigation Strategy Development | Projected Overall Risk Reduction | N/A
480 | CalPA | Set WMP-32 | CalPA_Set WMP-32 | 2 | CalPA_Set WMP-32_Q2 | Please provide the same information as requested in Question 1 for undergrounding projects that fall into each of the following categories: a) Rule 20 undergrounding. b) Wildfire rebuild undergrounding. c) Any other undergrounding not included in Question 1 or parts a and b of this question. | Please see the table provided below with the data requested for subparts a – c. a) Please see row (a) Rule 20. Included are the undergrounded miles of primary distribution lines in High Fire Thread Districts (HFTD) and/or High Fire Risk Areas (HFRA) as part of the following programs: • Rule 20A – 100% utility funding • Rule 20B – partial utility funding • Rule 20C – minimal utility funding Note, this data does not include all Rule 20 projects. It includes only those Rule 20 projects that have taken place in the HFTD/HFRA given the impact of these projects on reducing wildfire risk. b) Please see row (b) Wildfire Rebuild. Included are the undergrounded miles of primary distribution lines completed as part of wildfire rebuild. This includes work in our Fire Rebuild Program that are located in an HFTD/HFRA, as well as the Community Rebuild program (i.e., Butte and Greenville). c) Please see row (c) Other. Included are the undergrounded miles of primary distribution lines through PG&E’s targeted undergrounding program, as well as capacity projects and work requested by others located in an HFTD/HFRA. Please note, PG&E previously did not track overhead miles replaced, therefore, the overhead miles replaced is calculated based on UG Miles Completed using a standard conversion factor for rebuild projects or all other undergrounding projects. For WMP-Discovery2023_DR_CalAdvocates_032-Q002 Page 2 Community rebuild projects (Butte and Greenville) for every 1.57 miles of UG installed, one mile of existing OH lines has been removed; for all other projects, 1.25 miles of UG installed equates to one mile of existing OH removed. | Holly Wehrman | 2023-10-31 | 2023-11-14 | 2023-11-14 | https://www.pge.com/content/dam/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_032.zip | 0 | N/A | 8.1.2.2 | Grid Design and System Hardening | Undergrounding of Electric Lines and/or Equipment – Distribution | N/A
481 | CalPA | Set WMP-32 | CalPA_Set WMP-32 | 3 | CalPA_Set WMP-32_Q3 | Please provide copies of all current, sole-source contracts PG&E has executed with other entities with regard to any of the following: a) Suppliers of materials related to distribution undergrounding projects. b) Entities who perform labor related to distribution undergrounding projects. c) Entities who assist PG&E with planning, permitting, environmental review, and other similar non-construction tasks related to distribution undergrounding projects. d) Any other entities who provide goods or services to PG&E in relation to distribution undergrounding projects. | The attachments to this response contain CONFIDENTIAL information and are being provided pursuant to the accompany confidentiality declaration “WMPDiscovery2023_DR_CalAdvocates_032-Q003_Confidentiality Declaration.” a) PG&E does not have a sole-source contract process that mirrors state and federal sole-source contracting law. Instead, PG&E has a direct award process that documents contracts that are awarded over certain dollar thresholds to suppliers that are not preferred suppliers (generally, master services agreement or outline agreement suppliers). PG&E currently uses a Direct Award Documentation (DAD) form to document our direct awards. PG&E identified two direct award contracts that we have executed with entities providing goods and/or services related to system hardening distribution undergrounding projects.1 The population of contracts PG&E reviewed included contracts for work completed between 2020 and 2023 and where the total contract spend during that period was greater than $100,000. The direct award contracts and associated documents that PG&E is providing are: • WMP-Discovery2023_DR_CalAdvocates_032-Q003Atch01CONF.pdf • WMP-Discovery2023_DR_CalAdvocates_032-Q003Atch02CONF.pdf • WMP-Discovery2023_DR_CalAdvocates_032-Q003Atch03CONF.pdf • WMP-Discovery2023_DR_CalAdvocates_032-Q003Atch04CONF.pdf • WMP-Discovery2023_DR_CalAdvocates_032-Q003Atch05CONF.pdf Attachments 01-03 are the Direct Award Documentation and Contract, including Contract Change Order for the first vendor who received a direct award contract. Attachments 04-05 are the Direct Award Documentation and Contract for the second vendor who received a direct award contract. b) See response to part a. c) See response to part a. d) See response to part a. | Holly Wehrman | 2023-10-31 | 2023-12-01 | 2023-12-01 | https://www.pge.com/content/dam/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_032.zip | 5 | N/A | 8.1.2 | Grid Design, Operations, and Maintenance | Grid Design and System Hardening | N/A
482 | CalPA | Set WMP-32 | CalPA_Set WMP-32 | 4 | CalPA_Set WMP-32_Q4 | Describe all vegetation management activities that PG&E typically performs around the following line types. In your responses to parts (b) through (d), please describe if, and in what ways, PG&E’s vegetation management activities for that category meaningful differ compared to your response to part (a): a) Aboveground distribution mains located in HFTD/HFRA. b) Aboveground distribution secondaries located in HFTD/HFRA. c) Aboveground distribution services located in HFTD/HFRA. d) Right-of-way for underground distribution located in HFTD/HFRA. | a) We interpret this question to address Primary Distribution voltages 4kV, 12kV, 17kV and 21kV. The following programs target work on OH facilities: i. Annual Routine Tree Inspection (system-wide all line miles), resulting pruning and tree removals. • Pruning to maintain 18 inches of year-round clearance outside HFTD and HFRA • Pruning to maintain 4 feet of year-round clearance inside HFTD and HFRA and pruning to maintain 4 feet of clearance inside SRA during declared fire season. • Maintenance of Overhang removal in EVM circuit segments completed 2019-2022 • Mitigation up to complete tree removal for hazardous tree conditions identified during these inspections or brought to PG&E’s attention by other inspection programs, customer, or agency notifications. ii. Second Patrol Tree Inspection in HFTD and HFRA, resulting pruning and tree removals. • Second inspections approximately 6 months after Annual Routine Inspections to identify emerging hazardous tree conditions. WMP-Discovery2023_DR_CalAdvocates_032-Q004 Page 2 o Tree Mortality o Priority Tree work based on local or tree specific conditions. o Address tree response (growth) that annual pruning cannot fully mitigate to maintain compliance with Minimum Distance Requirements iii. Vegetation Control (Firebreak maintenance) in SRA/FRA/HFTD and HFRA • All poles supporting equipment not specifically exempted by 14 CCR 1255 • Additional inventory in HFTD and HFRA supporting the same equipment requiring firebreaks in SRA and FRA o These poles are all inventoried and evaluated for risk. ▪ Low risk poles are not maintained unless conditions change to elevated risk. ▪ Solid Blade disconnects and split-bolt only locations are not mitigated with firebreak maintenance. • Work takes place year-round, and majority of inventory is treated at least 1 time per year. b) We interpret this question to address voltages of less than 750 volts on pole-to-pole configurations. The following programs target work on OH facilities: i. Annual Routine Tree Inspection (system wide-all line miles), resulting pruning and tree removals. • Pruning to mitigate strain or abrasion on the assets. • Mitigation up to complete tree removal for hazardous tree conditions identified during these inspections or brought to PG&E’s attention by other inspection programs, customer or agency notifications. c) We interpret this question to address voltages of less than 750 volts on pole-toservice configurations. The following programs target work on OH facilities: i. Mitigation up to complete tree removal for hazardous tree conditions identified during System Inspections (not Vegetation Management program inspections) resulting in EC notifications sent to Vegetation Management for mitigation. ii. Conditions brought to PG&E’s attention by other inspection programs, customer, or agency notifications. iii. Vegetation Management program inspections is not focused on these lines however if inspector notice any conditions need work. d) PG&E does not currently have a Vegetation Management program with UG ROW maintenance in scope | Holly Wehrman | 2023-10-31 | 2023-11-14 | 2023-11-14 | https://www.pge.com/content/dam/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_032.zip | 0 | N/A | 8.2 | Vegetation Management and Inspections | N/A | N/A
483 | CalPA | Set WMP-32 | CalPA_Set WMP-32 | 5 | CalPA_Set WMP-32_Q5 | Please estimate the typical, annual cost per mile of vegetation management activities that PG&E performs around the following line types: a) Aboveground distribution mains located in HFTD/HFRA. b) Aboveground distribution secondaries located in HFTD/HFRA. c) Aboveground distribution services located in HFTD/HFRA. d) Right-of-way for underground distribution located in HFTD/HFRA. | a) Please see table below for Routine and Second Patrol annual average cost per mile of VM Distribution programs based on 2022 annual spend and 2022 actual miles. PG&E tracks costs for the entire VM program and does not break these numbers out by Non-HFTD versus HFTD/HFRA, etc. Please note that annual costs per mile are currently unavailable for TRI, FTI, and VMOM as these programs were introduced in 2023. Program Cost Per Mile Routine $8,650 based on 2022 Second Patrol $2,745 based on 2022 FTI Unavailable TRI Unavailable VMOM Unavailable b) VM activities on aboveground distribution secondaries occur simultaneously with the activities completed for distribution mains. Please see table in part ‘A’ for the average cost per mile for VM activities completed within the Routine and Second Patrol program. WMP-Discovery2023_DR_CalAdvocates_032-Q005 Page 2 c) Please see table in part ‘A’ for any costs associated with VM activities in HFTD/HFRA. d) Not applicable as VM does not conduct inspections on right-of-way (ROW) for underground distribution lines. | Holly Wehrman | 2023-10-31 | 2023-11-14 | 2023-11-14 | https://www.pge.com/content/dam/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_032.zip | 9 | N/A | 8.2 | Vegetation Management and Inspections | N/A | N/A
484 | CalPA | Set WMP-32 | CalPA_Set WMP-32 | 6 | CalPA_Set WMP-32_Q6 | Cal Advocates understands that, in every project to replace overhead bare distribution with covered conductor, PG&E performs pole loading calculations for every pole in the project. a) Is the above characterization correct? Please elaborate if incorrect. b) Does PG&E have a threshold safety factor (or other result from a pole loading calculation) at which it will replace poles in a project? c) If the answer to part (b) is yes, please describe PG&E’s threshold(s). d) If the answer to part (b) is no, please explain how PG&E determines which poles to replace in a project. | a) PG&E performs pole loading calculations for every pole that will be supporting the covered conductor. b) PG&E adheres to the requirements of General Order 95, Rule 44. In addition, for covered conductor projects, we adhere to our fire area design guidance, which is detailed in Chapter 15 of our Electric Design Manual, the relevant portion of which is included as attachment “WMP-Discovery2023_DR_CalAdvocates_032- Q006Atch01.pdf.” c) Please see the response to subpart (b), which explains the guidelines we follow. d) Not applicable, please see the response to subpart (b). | Holly Wehrman | 2023-10-31 | 2023-11-14 | 2023-11-14 | https://www.pge.com/content/dam/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_032.zip | 1 | N/A | 7.2 | Wildfire Mitigation Strategy Development | Wildfire Mitigation Strategy | N/A
485 | CalPA | Set WMP-32 | CalPA_Set WMP-32 | 7 | CalPA_Set WMP-32_Q7 | Please provide the results of all pole loading calculations performed as part of all bare-to-covered conductor replacement projects in 2022 and 2023 (as of October 1, 2023). This should contain the following at minimum: a) Pole IDs. b) Estimated safety factor before conductor replacement (bare conductor). c) Estimated safety factor after conductor replacement (covered conductor). d) Determination of whether the pole needed replacement based on safety factor. e) Whether the pole was actually replaced. | Please reference attachment, “WMP-Discovery2023_DR_CalAdvocates_032- Q007Atch01.xlsx” for the list of pole loading calculations performed as part of covered conductor projects that were constructed in 2022 and have completed the quality verification process. Projects constructed in 2023 are still undergoing quality verification and have not been included in this report. The report contains the following information: 1. The Pole SAP Equipment ID for the in-service poles. 2. The Bending Safety Factor after covered conductor installation. 3. The In-Service Pole Status; options for this data field are as follows: • “Existing” means that the pole did not need to be replaced as a result of covered conductor installation. • “Replaced” means that the pole was replaced as part of the covered conductor installation project. • “New” means that the pole is newly required as part of the covered conductor installation project. A pole did not exist in this location prior to the covered conductor installation project. 4. Pole Material; options for this data field are as follows: WMP-Discovery2023_DR_CalAdvocates_032-Q007 Page 2 • Wood. • Composite. 5. Grade of Construction; options for this data field are as follows: • A. • B. • C. 6. Loadcase; options for this data field are as follows: • GO 95. • NESC. a) This information has been included in the attachment, as described in item 1 above. b) PG&E’s estimating process does not include performing a pole loading calculation of the pole in the configuration prior to covered conductor installation. We model the pole with the covered conductor and equipment for the new project and make a determination as to whether the pole is adequately sized to remain in-service. If a pole replacement is required, the pole loading calculation is performed for the new pole. c) This information has been included in the attachment, as described in item 2 above. d) This information has been included in the attachment, as described in item 3 above. e) This information has been included in the attachment, as described in item 2 above. All replaced poles are noted as “Replaced | Holly Wehrman | 2023-10-31 | 2023-11-14 | 2023-11-14 | https://www.pge.com/content/dam/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_032.zip | 1 | N/A | 7.2 | Wildfire Mitigation Strategy Development | Wildfire Mitigation Strategy | N/A
486 | CalPA | Set WMP-32 | CalPA_Set WMP-32 | 8 | CalPA_Set WMP-32_Q8 | For each year from 2020 through 2023, please provide ten randomly-selected pole loading calculations performed as part of a bare-to-covered conductor replacement project. For these calculations, please provide: a) The full calculation input(s). b) The full calculation output(s). c) Any interpretations associated with the calculation (for example, an engineer’s determination that the calculation demonstrates a pole must be replaced). | a) - c) PG&E is providing the requested ten randomly selected pole loading calculations for covered conductor projects from 2020, 2021, and 2022. Please see attachment “WMP-Discovery2023_DR_CalAdvocates_032- Q008Atch01CONF.zip” for the thirty pole loading calculations provided. Each of these pole loading calculations contains the inputs, outputs, and associated information (interpretations) to identify if the pole is new or existing. Projects constructed in 2023 are still undergoing quality verification and have not been included. | Holly Wehrman | 2023-10-31 | 2023-11-14 | 2023-11-14 | https://www.pge.com/content/dam/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_032.zip | 1 | N/A | 7.2 | Wildfire Mitigation Strategy Development | Wildfire Mitigation Strategy | N/A
487 | OEIS | 015 | OEIS_015 | 1 | OEIS_015_Q1 | Regarding confirmation of 2024/2025 targets. a. PG&E’s 2023-2025 WMP Revision 3 Table 8.1.7-2 (page 555) shows that PG&E expects to close 66,200 backlog distribution ignition risk tags in 2024 and 59,000 backlog distribution ignition risk tags in 2025. PG&E’s targets in Tables 8-3 and RN-PG&E-23-04-2 do not reflect the same expected number of backlog ignition tag closures outlined in Table 8.1.7-2, as these tables show targets of closing 46,000 distribution backlog tags in 2024 and 55,000 distribution backlog tags in 2025. i. Confirm that PG&E intends for its targets to reflect the plan and commitment made in its 2023-2025 WMP Revision 3 Table 8.1.7-2 (page 555). ii. If not, explain the discrepancy between the commitment to close 66,200 backlog distribution ignition risk tags in 2024 and 59,000 backlog distribution ignition risk tags in 2025 (Table 8.1.7-2, page 555) to the targets outlined in Tables 8-3 and RN-PG&E-23-04-2. | ii. The discrepancy between the two tables reflects expected multi-year planning values as compared to the minimum required tags to meet our risk reduction targets. The 46,000 tags represent the minimum amount of tags needed to meet our 68% wildfire risk reduction in the tag backlog, which was set as the target in our initial WMP submission. Given the bundling approach proposed in the subsequent Revision Notice response, we anticipate that we will be able to complete a larger number of tags. This will exceed the quantity and risk reduction targets that were initially set forth in Table 8-3, for both years. Additionally, the population of tags utilized to create the two tables is not identical. The population of tags that is included in writing Table 8.1.7-2 for the Revision Notice response includes some tags created in 2023. These tags were not part of the initial backlog population when the WMP target was written earlier in the year. Thus, Table 8-3 is based on the backlog population at the time of writing the initial 2023 WMP, while Table 8.1.7-2 reflects a more current view of the tag population. | Dakota Smith | 2023-11-03 | 2023-11-08 | 2023-11-08 | https://www.pge.com/content/dam/pge/docs/outages-and-safety/outage-preparedness-and-support/OEIS_015.zip | 0 | N/A | 8.1.7 | Open Work Orders | N/A | N/A
488 | CalPA | Set WMP-33 | CalPA_Set WMP-33 | 1 | CalPA_Set WMP-33_Q1 | Please provide an Excel sheet listing (as rows) each asset work order (or “tag”) that was open as of June 30, 2023, and was a Level A or B tag. For each tag, provide the following information in separate columns: a) Work order ID number b) Equipment type c) HFTD tier d) Asset type: Distribution or transmission e) GO 95 Rule 18 priority level of the tag f) Utility-specific priority level (A or B) g) Date the tag was originally created h) Due date of the original work order i) Most recent date the work order was reinspected or modified (if applicable) j) Due date of the work order after it was reinspected or modified (if applicable) k) Date the work order was completed & closed, if any. Note: parts (a) through (j) should match the QDR for Q2 of 2023. | Please see attachment “WMP-Discovery2023_DR_CalAdvocates_033- Q001Atch01.xlsx” for the requested data. The data in columns A through J of the attachment has been provided from the 2023 Q2 QDR for any tags where the original priority (column F) is A or B, or where the utilityspecific priority level at the end of Q2 is A or B (column M). Two columns, K and L, have been provided for the date the tag was completed and closed. Column K indicates the date the work was completed in the field and column L indicates the date of closure in SAP. Field completion and closure dates were pulled on November 21. | Aaron Louie | 2023-11-09 | 2023-11-28 | 2023-11-28 | https://www.pge.com/content/dam/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_033.zip | 1 | N/A | 8.1.7 | Open Work Orders | N/A | N/A
489 | CalPA | Set WMP-33 | CalPA_Set WMP-33 | 2 | CalPA_Set WMP-33_Q2 | Please provide an Excel sheet listing (as rows) each asset work order (or “tag”) that was open as of September 25, 2023, and was a Level A or B tag. For each tag, provide the following information in separate columns: a) Work order ID number b) Equipment type c) HFTD tier d) Asset type: Distribution or transmission e) GO 95 Rule 18 priority level of the tag f) Utility-specific priority level (A or B) g) Date the tag was originally created h) Due date of the original work order i) Most recent date the work order was reinspected or modified (if applicable) j) Due date of the work order after it was reinspected or modified (if applicable) k) Date the work order was completed & closed, if any. | On November 11, 2023, PG&E confirmed with Cal Advocates that providing data as of September 30, 2023, is sufficient for this response. Please see attachment “WMP-Discovery2023_DR_CalAdvocates_033- Q002Atch01.xlsx” for the requested data. The data in columns A through J of the attachment has been provided from the 2023 Q3 QDR for any tags where the original priority (column F) is A or B, or where the utilityspecific priority level at the end of Q3 is A or B (column M). Two columns, K and L, have been provided for the date the tag was completed and closed. Column K indicates the date the work was completed in the field and column L indicates the date of closure in SAP. Field completion and closure dates were pulled on November 21. | Aaron Louie | 2023-11-09 | 2023-11-28 | 2023-11-28 | https://www.pge.com/content/dam/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_033.zip | 1 | N/A | 8.1.7 | Open Work Orders | N/A | N/A
490 | CalPA | Set WMP-33 | CalPA_Set WMP-33 | 3 | CalPA_Set WMP-33_Q3 | Please provide an Excel sheet listing (as rows) each asset work order (or “tag”) that was open as of November 8, 2023, and was a Level A or B tag. For each tag, provide the following information in separate columns: a) Work order ID number b) Equipment type c) HFTD tier d) Asset type: Distribution or transmission e) GO 95 Rule 18 priority level of the tag f) Utility-specific priority level (A or B) g) Date the tag was originally created h) Due date of the original work order i) Most recent date the work order was reinspected or modified (if applicable) j) Due date of the work order after it was reinspected or modified (if applicable) k) Date the work order was completed & closed, if any. | Please see attachment “WMP-Discovery2023_DR_CalAdvocates_033- Q003Atch01.xlsx” for the requested data. The data provided was calculated using the Quarterly Data Report logic run on November 9, 2023. Since the QDR pulls from a database that lags SAP by one day, the output reflects the data in SAP for November 8, 2023. The data in columns A through J has been provided for tags where the original priority (column F) is A or B, or where the utility-specific priority level on November 8 is A or B (column M). Two columns, K and L, have been provided for the date the tag was completed and closed. Column K indicates the date the work was completed in the field and column L indicates the date of closure in SAP. Field completion and closure dates were pulled on November 21. | Aaron Louie | 2023-11-09 | 2023-11-28 | 2023-11-28 | https://www.pge.com/content/dam/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_033.zip | 1 | N/A | 8.1.7 | Open Work Orders | N/A | N/A
491 | CalPA | Set WMP-34 | CalPA_Set WMP-34 | 1 | CalPA_Set WMP-34_Q1 | The following questions pertain to PG&E’s 2023-2025 WMP Revision 3, submitted on September 27, 2023. Page 1122 of your 2023 WMP R3 discusses the 2022 EPSS Reliability Study’s Multiple Outage Reviews (MOR). Filsinger Energy Partners’ PG&E Independent Safety Monitor Status Update Report, October 6, 2023 (ISM Report 3) also discusses the MOR program at p. 12, stating:5 In 2022, over 200 circuits underwent these in-depth reviews, generating approximately 1,400 action items. This program continued into 2023 with 35 circuits having had a detailed MORE (with several of these circuits being on their second or third review) through early August, generating an additional 135 MORE (sic) action items.” a) Please provide a table or Excel sheet showing the results of each MOR for 2022, including the following, in separate columns: i. The CPZs that underwent review, ii. The result of each CPZ’s review, iii. If the CPZ’s review had action items generated, iv. Details about each action item, if applicable, v. If an action item was not created, provide a brief explanation as to why, vi. The status of each action item, vii. Completion due date of each action item, viii. The date each action item was completed, if applicable, ix. If an action item was not completed by its due date, provide a brief explanation as to why it was not completed on time, b) Please provide a table or Excel sheet showing the results of each MOR for 2023, including the following, in separate columns: i. The CPZs that underwent review, ii. The result of each CPZ’s review, iii. If the CPZ’s review had action items generated, iv. Details about each action item, if applicable, v. If an action item was not created, provide a brief explanation as to why, vi. The status of each action item, vii. Completion due date of each action item, viii. The date each action item was completed, if applicable, and ix. If an action item which was not completed by its due date, provide a brief explanation as to why it was not completed on time, | In the summer of 2022, an initial Multiple Outage Review and Evaluation (MORE) process began, with the objective to examine circuits where there was an increased frequency of customers experiencing EPSS outages. The daily outage review was initiated internally amongst the EPSS Program Operations team, initially targeting two weeks for responses to initiated Action Items at the circuit level. The targeted timeframe was an internal goal for the EPSS Operations team in 2022 and was not an established metric across the PG&E enterprise. As a result, reasonings for delayed completion of Action Items are not readily available as the target timeframe was internal to the EPSS Program Management Office. The MORE process was formalized in 2023 and evolved from a circuit level view to a more targeted device level view with increased maturity. The MORE process has comparatively more details in 2023 than in 2022 due to refinements in technology and processes. This includes the migration of Action Item tracking from a manual process in 2022 to a digital platform in 2023. As a result of the migration to a technology-based tracking system, there are duplicate records for the same actions, as indicated in the attached data. If an Action Item was created in both the digital platform and the manual tracker during the transition period and was marked complete in the digital platform but not the legacy manual tracker, that has been marked accordingly in the attached data. When reviewing circuits or devices for review in 2022 and 2023, the EPSS Operations Team determined whether additional mitigation actions would or would not be initiated from the EPSS Operations Team to improve reliability. This could have been the result of factors including, but not limited to, EPSS outage profiles, ongoing actions by other PG&E teams, external escalations, and known issues with a repeat device or circuit. Please see “WMP-Discovery2023-2025_DR_CalAdvocates_034-Q001Atch01.xlsx” for details regarding questions (i)-(ix) for parts (a) and (b) for 2022 and 2023, respectively. | Justin Hagler | 2023-12-12 | 2024-01-19 | 2024-01-19 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_034.zip | 1 | N/A | 8.1.8.1.1 | Grid Operations and Procedures | Protective Equipment and Device Settings | N/A
492 | CalPA | Set WMP-34 | CalPA_Set WMP-34 | 2 | CalPA_Set WMP-34_Q2 | a) Please explain the criteria for including a CPZ in a MOR for 2022. b) Please explain the criteria for including a CPZ in a MOR for 2023. c) Please explain the criteria for not including a CPZ in a MOR for 2022. d) Please explain the criteria for not including a CPZ in a MOR for 2023. | The criteria for a Multiple Outage Review and Evaluation (MORE) evolved in response to an increased number of customers experiencing outages due to EPSS protection across the system. The MORE process was formalized in 2023 and evolved from a circuit level view to a more targeted device level view with increased maturity. In both years, the primary determinant of circuits and devices being reviewed was the number of EPSS outages. a) For 2022, the outage review process included the following for EPSS circuits: • Number of EPSS Outages (with a minimum of five for the circuit) • Escalations from EPSS Leadership • Escalations from Customer Team • Escalations from Regional VP Team • Circuits by EPSS CEMI 5+ count b) For 2023, the criteria for the MORE process included the following for EPSS devices: • Number of EPSS Outages on a rolling 60-day basis (with a minimum of three in that timespan for the device) • Escalations from EPSS Leadership • Escalations from Customer Team • Escalations from Regional VP Team c) If a circuit did not meet the criteria above in part (a), it was not reviewed as a part of the outage review process in 2022. d) If a device did not meet the criteria above in part (b), it was not reviewed as a part of the MORE process in 2023. | Justin Hagler | 2023-12-12 | 2024-01-19 | 2024-01-19 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_034.zip | 0 | N/A | 2022 WMP Section 7.1 | Wildfire Mitigation Strategy Development | N/A | N/A
493 | CalPA | Set WMP-34 | CalPA_Set WMP-34 | 3 | CalPA_Set WMP-34_Q3 | Regarding circuits with EPSS capabilities: a) Provide a table or Excel sheet of complaints and claims filed by customers related to outages on circuits with EPSS settings enabled at the time of outage. For each item, provide the following information in separate columns: a. The Circuit name and ID associated with the complainant; b. The date each complaint or claim was received; c. Description of each complaint/claim; d. Resolution of each complaint/claim; e. Due date of each resolution; f. Actual completion date of each resolution. b) Provide an updated excel table of “EPSS Outages Monthly Report_20220118.xlsx” provided to SED that includes a column for “CPZ” in the “EPSS Outages – 2021 Season” tab. | a) i-v) Please see “WMP-Discovery2023-2025_DR_CalAdvocates_034-Q003Atch01.xlsx” and “WMP-Discovery2023-2025_DR_CalAdvocates_034-Q003Atch02CONF.xlsx” for CPUC complaint information and claims information related to EPSS. Please note, EPSS related complaints are only tracked through complaints provided to PG&E by the CPUC, which is the data provided in the spreadsheet. Details of the complaint and resolution are in the individual cells in the excel file. Please note, there are no due dates for claims and the date given is the date the claim was closed. We are searching our records for other customer complaints regarding EPSS and will supplement this response if identified. b) Please see “WMP-Discovery2023-2025_DR_CalAdvocates_034-Q003Atch03.xlsx” that includes the requested circuit segment information in column “S”. | Justin Hagler | 2023-12-12 | 2024-01-19 | 2024-01-19 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_034.zip | 3 | N/A | 8.1.8.1.1 | Grid Operations and Procedures | Protective Equipment and Device Settings | N/A
494 | CalPA | Set WMP-34 | CalPA_Set WMP-34 | 4 | CalPA_Set WMP-34_Q4 | PG&E’s 2023 WMP R3, p. 1048, states “Name changes including the absorption of CPZs into others resulting in the original CPZ no longer existing.” Additionally, p. 410, in Table RN-PG&E-23-05-1 (Circuit Segments in the 2022 WMP Undergrounding Workplan but Not Listed in the 2023-2026 Undergrounding Workplan) states, “(a) PG&E often changes circuit segment names when additional segmenting devices are placed on the grid or other grid design changes such as switching occur.” a) Describe PG&E’s circuit segment naming convention when a segmenting device is installed or other grid change occurs (e.g., a segmenting device divides one CPZ into two) and the time period after which the name change(s) would go into effect (e.g., immediately after grid change, end of month, end of fiscal year, etc.) b) Have any of the CPZs with EPSS enabled had a change of name from month to month in the EPSS Monthly Reports to SED, since the first EPSS report was submitted? c) If the answer to part (b) is yes, provide a list of CPZs with previous name(s), current name, date the name change occurred, and the reason for the name change, description of the state of the CPZ (e.g., active or inactive). NOTE: This should include intermediate name changes (e.g., suppose that CPZ A divides into CPZ A and CPZ B in March 2022, but then in March 2023 CPZ B becomes CPZ C such that CPZ B no longer exists). | a) PG&E’s circuit segment naming convention for a Circuit Protection Zone (CPZ) is a concatenation of typically: the five (5) digit Substation ID, four (4) digit Feeder ID, and variable-digit Protective Device ID. Note that while the term ‘CPZ’ typically refers to the segmentation of our primary distribution system using only SCADA enabled (e.g., remote access) devices, differing PG&E programs may commonly use this term to describe the segmentation of the same system based on the specific needs or purpose of their program. For example, the EPSS program defines the CPZs used in their program leveraging only the EPSS-capable devices that are used to enable and disable EPSS settings daily. b) Yes. c) Given the generalized definition of the term ‘Circuit Protection Zone’ described in response a) above, PG&E does not collect, analyze, and retain CPZ name changes at the requested level of granularity. PG&E is able to support CalAdvocates in providing data should specific requests for a geographic area, customer demographic, comparisons between programs, or other purpose be required. | Justin Hagler | 2023-12-12 | 2024-01-22 | 2024-01-22 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_034.zip | 0 | N/A | 8.1.8.1.1 | Grid Operations and Procedures | Protective Equipment and Device Settings | N/A
495 | CalPA | Set WMP-34 | CalPA_Set WMP-34 | 5 | CalPA_Set WMP-34_Q5 | Provide an Excel spreadsheet of all distribution circuits in HFTDs or High Fire Risk Areas (HFRAs), or crossing HFTD and HFRA boundaries, existing as of January 1, 2023 (as rows) that includes the following information in separate columns: a) Circuit Name b) Circuit ID c) City d) County e) Division (e.g., Los Padres Division) 6 f) Date PG&E first activated EPSS settings on any part of the circuit7 g) Total Customers h) Number of CPZs contained on the circuit i) Circuit SAIDI for 2017 j) Circuit SAIDI for 2018 k) Circuit SAIDI for 2019 l) Circuit SAIFI for 2017 m) Circuit SAIFI for 2018 n) Circuit SAIFI for 2019 o) Circuit MAIFI for 2017 p) Circuit MAIFI for 2018 q) Circuit MAIFI for 2019 | Please see “WMP-Discovery2023-2025_DR_CalAdvocates_034-Q005Atch01.xlsx” for sub-parts a-b and e-q. Data for city (sub-part c) and county (sub-part d) are excluded due to circuits passing through multiple cities and counties. Circuits are not individually related to a city or county. For sub-part f, no circuits had EPSS settings in 2017-2019. The first version of EPSS settings was created in 2021. | Justin Hagler | 2023-12-12 | 2024-01-22 | 2024-01-22 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_034.zip | 1 | N/A | 8.1.8.1.1 | Grid Operations and Procedures | Protective Equipment and Device Settings | N/A
496 | CalPA | Set WMP-34 | CalPA_Set WMP-34 | 6 | CalPA_Set WMP-34_Q6 | Please divide the data presented in question 5 into performance quartiles based on SAIDI and SAIFI. (An example table is included below the question’s subparts.) a) Of the distribution circuits listed in response to Question 5, identify, in Excel spreadsheet format, the best performing (i.e., circuits experiencing the least number of sustained outages) 25% circuits by average combined SAIFI for years 2017 to 2019 in each of your divisions. b) Of the distribution circuits listed in response to Question 5, identify in an Excel spreadsheet format the worst performing (i.e., circuits experiencing the most sustained outages) 25% circuits by average combined SAIFI for years 2017 to 2019 in each of your divisions. c) Of the distribution circuits listed in response to Question 5, identify in an Excel spreadsheet format the best performing SAIDI (i.e., circuits experiencing the shortest duration of sustained outages) 25% circuits by average combined for years 2017 to 2019 in each of your divisions. d) Of the distribution circuits listed in response to Question 5, identify in an Excel spreadsheet format the worst performing (i.e., circuits experiencing the longest duration of sustained outages) 25% circuits by average combined SAIDI for years 2017 to 2019 in each of your divisions. Example Table: Question 6, Part a) Division Circuit Name Average SAIFI 2017-2019 Los Padres San Francisco 1101 1.080 Los Padres Los Angeles 1102 1.011 North Valley Sacramento 1103 0.98 | Please see “WMP-Discovery2023-2025_DR_CalAdvocates_034-Q005Atch01.xlsx” for sub-parts a-d. | Justin Hagler | 2023-12-12 | 2024-01-22 | 2024-01-22 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_034.zip | 0 | N/A | 8.1.8.1.1 | Grid Operations and Procedures | Protective Equipment and Device Settings | N/A
497 | CalPA | Set WMP-34 | CalPA_Set WMP-34 | 7 | CalPA_Set WMP-34_Q7 | Provide an Excel table that lists (as rows) each sustained outage that occurred from January 1, 2017 through December 31, 2022 on any of the circuits identified in your response to Question 6. For each outage, the Excel table should include the following information in separate columns: a) Outage ID b) Circuit Name c) Circuit ID d) Division e) Was EPSS enabled on this circuit at the time of the outage? f) When was this circuit made EPSS-capable? g) FNL (First No Light) h) Outage End Day & Time i) CESO (Count of Customers Experiencing Sustained Outages) j) Customer Minutes k) Cause l) Restoration Time (Minutes) | ll sustained outages with information for a-e, and g-l are provided in “WMPDiscovery2023-2025_DR_CalAdvocates_034-Q007Atch01.xlsx.” In regard to sub-part f, the information of when the circuit was first made EPSS capable is provided in “WMPDiscovery2023-2025_DR_CalAdvocates_Q34-Q007Atch02.xlsx.” | Justin Hagler | 2023-12-12 | 2024-01-22 | 2024-01-22 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_034.zip | 2 | N/A | 8.1.8.1.1 | Grid Operations and Procedures | Protective Equipment and Device Settings | N/A
498 | CalPA | Set WMP-34 | CalPA_Set WMP-34 | 8 | CalPA_Set WMP-34_Q8 | Provide an Excel table that lists (as rows) each momentary outage that occurred from January 1, 2017 through December 31, 2022 on any of the circuits identified in your response to Question 6. For each outage, the Excel table should include the following information in separate columns: a) Outage ID b) Circuit Name c) Circuit ID d) Division e) Was EPSS enabled on this circuit at the time of the outage? f) When was this circuit made EPSS-capable? g) FNL (First No Light) h) Outage End Day & Time i) CESO (Count of Customers Experiencing Sustained Outages) j) Customer Minutes k) Cause (if known) l) Was the circuit patrolled in response to the momentary outage? | All momentary outages with information for a-e, and g-l are provided in “WMPDiscovery2023-2025_DR_CalAdvocates_034-Q008Atch01.xlsx.” In regard to sub-part f, the information of when the circuit was first made EPSS enabled is provided in “WMPDiscovery2023-2025_DR_CalAdvocates_034-Q007Atch02.xlsx. | Justin Hagler | 2023-12-12 | 2024-01-22 | 2024-01-22 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_034.zip | 1 | N/A | 8.1.8.1.1 | Grid Operations and Procedures | Protective Equipment and Device Settings | N/A
499 | CalPA | Set WMP-34 | CalPA_Set WMP-34 | 9 | CalPA_Set WMP-34_Q9 | Regarding PG&E’s 2021 Reliability Report, PG&E stated “Base reliability projects have been initiated on Garberville 1101 circuit to minimize the impacts of EPSS… and taking a more surgical approach in applying EPSS settings when the circuit is most at risk.”8 However, PG&E did not report an EPSS outage for Garberville 1101 in 2021.9 PG&E’s first reported outage on Garberville 1101 was on July 24, 2022,10 which was after the 2021 Reliability Report was published. Please explain this discrepancy. | We confirm that Garberville 1101 had no 2021 outages categorized as EPSS outages as reported in PG&E January Monthly Report2 . The proposed base reliability projects (Fuse Saver installations) as stated in PG&E’s Annual Electric Distribution Reliability Report 2021, 1 which was published following the 2021 EPSS pilot effort, and informed by learnings from that pilot, were identified as a proactive strategy to both minimize wildfire risk while also providing reliability improvement benefits under EPSS enablement conditions. | Justin Hagler | 2023-12-12 | 2024-01-19 | 2024-01-19 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_034.zip | 0 | N/A | 8.1.8.1.1 | Grid Operations and Procedures | Protective Equipment and Device Settings | N/A
500 | CalPA | Set WMP-34 | CalPA_Set WMP-34 | 10 | CalPA_Set WMP-34_Q10 | Regarding PG&E’s 2021 Reliability Report, PG&E stated “Base reliability project has been initiated on Otter 1102 circuit to minimize the impacts of EPSS… and taking a more surgical approach in applying EPSS settings when the circuit is most at risk.” 11 However, PG&E did not report an EPSS outage for Otter 1102 in 2021.12 PG&E’s first reported outage on Otter 1102 was on August 19, 2022,13 which was after the 2021 Reliability Report was published. Please explain this discrepancy. | We confirm Otter 1102 had no 2021 outages categorized as EPSS outages as reported in PG&E January Monthly Report2 . The proposed base reliability project (Fuse Saver installation) as stated in PG&E Annual Electric Distribution Reliability Report 2021, which was published following the 2021 EPSS pilot effort and informed by learnings of that pilot, were identified as a proactive strategy to both minimize wildfire risk while also providing reliability improvement benefits under EPSS enablement conditions. | Justin Hagler | 2023-12-12 | 2024-01-19 | 2024-01-19 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_034.zip | 0 | N/A | 8.1.8.1.1 | Grid Operations and Procedures | Protective Equipment and Device Settings | N/A
501 | CalPA | Set WMP-34 | CalPA_Set WMP-34 | 11 | CalPA_Set WMP-34_Q11 | In PG&E’s November 2023 EPSS Monthly report, PG&E reports that there have been 28 outages on EPSS-enabled Transmission lines (T-EPSS) outages in the year to date. a) Are there downstream outages (e.g., to distribution customers that may be served from a substation that may be fed by the transmission line) that result from outages that occur on EPSS-enabled transmission lines? b) Did any of the 28 reported T-EPSS outages in 2023 cause downstream impacts to other transmission or distribution customers? c) If the answer to part (b) is yes, please describe the extent of the downstream impacts. d) If the answer to part (b) is yes, are those downstream outages reported as EPSS outages in PG&E’s monthly EPSS reports or in any other reporting venue? e) If the answer to part (b) is yes, why did PG&E not have a backup or contingency transmission circuit(s) in place to avoid downstream distribution outages? | a) Yes, a Distribution outage may occur as a result of an outage on an EPSS-enabled Transmission line. b) The T-EPSS outages reported in the EPSS Monthly Report represent the outages on Distribution lines that resulted from outages on Transmission lines while EPSS settings were enabled. c) Please see response b) above. d) Please see response b) above. e) Transmission EPSS settings are only enabled on radial transmission lines to reduce impacts on the bulk electrical system. By design, these transmission lines serve as the only normal source for the substation(s) they feed and as such, distribution circuits will be de-energized if an outage is experienced on the transmission circuit. This would be true when there is an outage on those transmission circuits regardless of EPSS enablement. | Justin Hagler | 2023-12-12 | 2024-01-19 | 2024-01-19 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_034.zip | 0 | N/A | 8.1.8.1.1 | Grid Operations and Procedures | Protective Equipment and Device Settings | N/A
502 | CalPA | Set WMP-35 | CalPA_Set WMP-35 | 1 | CalPA_Set WMP-35_Q1 | In Table 9-2 of PG&E’s 2023-2025 WMP R4 submitted January 8th, 2024, PG&E indicates that system hardening is planned for certain frequently de-energized circuits. Please update Table 9-2 by providing the estimated completion year and quarter for each of the mitigation actions listed in the right-most column (“Measures taken, or planned to be taken, to reduce the need for and impact of future PSPSP of circuit”). If the timetable for completion is unknown or undetermined, please so state. | Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_035-Q001Atch01.xlsx” for an updated Table 9-2 as of February 12, 2024. We included the original Table 9-2 of PG&E’s 2023-2025 WMP R4 in columns B to J and appended a new column, column K, with updated information about Measures Taken, or Planned to be Taken, to Reduce the Need for and Impact of Future PSPS of Circuit. New content that has been appended is identified by red text. Additionally, we have added Line Removal work where applicable on some circuits, which was not included in the original Table 9-2; however, was part of PG&E’s GH-01 System Hardening workplan. This attachment corresponds with the version of Table 9-2 located on pages 908-909 of our 2023-2025 WMP R4. Please let us know if you would also like the requested information for the second version of Table 9-2 that starts on page 1509 of our 2023-2025 WMP. | Franky Lao | 2024-02-07 | 2024-02-23 | 2024-02-23 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_035.zip | 1 | N/A | 9.1.2 | Identification of Frequently De-Energized Circuits | N/A | N/A
503 | CalPA | Set WMP-36 | CalPA_Set WMP-36 | 1 | CalPA_Set WMP-36_Q1 | PG&E provided the following table in the response to CalAdvocates-PGE-2023WMP-06 question 5: Please provide an updated table showing actual values for 2023 and forecast values for 2024, with the EVM transitional programs disaggregated into the three initiatives described in PG&E’s response to CalAdvocates-PGE-2023WMP-06, Q5: 1.Tree Removal Inventory 2.Focused Tree Inspections 3.VM for Operational Mitigations. | Please see the updated table below for the requested information. 2023 Actuals (in $1,000s) 2024 Forecast (in $1,000s) Routine $785,446 $694,225 Second Patrol $125,148 $98,112 WMP-Discovery2023-2025_DR_CalAdvocates_036-Q001 VC (Pole Clearing) $22,826 $25,353 Tree Removal Inventory $34,947 $52,153 VM for Operational Mitigations $13,280 $22,872 Focused Tree Inspections in AOC $27,275 $81,342 Total $1,008,922 $974,05 | Franky Lao | 2024-03-08 | 2024-03-29 | 2024-03-29 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_036.zip | 0 | N/A | Vegetation Management | N/A | N/A | N/A
504 | CalPA | Set WMP-36 | CalPA_Set WMP-36 | 2 | CalPA_Set WMP-36_Q2 | Please disaggregate the data in Table 11 of PG&E’s 2023 Q4 QDR such that there is only one Utility Initiative Tracking ID for each row. If this is not possible, please explain why and clarify the methodology for grouping certain tracking IDs. | Please refer to the upcoming 2023 WMP Annual Report on Compliance (ARC) that PG&E is filing with the Office of Energy Infrastructure Safety on April 2, 2024. We will provide Cal Advocates a copy of this document once it is finalized and filed with the Office of Energy Safety. In the 2023 ARC, PG&E provides its 2023 actual expenditure and planned budget by Utility Initiative Tracking ID to the best of its ability. Utility Tracking IDs are tied to the targets and objectives that PG&E has outlined in its 2023-2025 WMP and is a subset of the total investments that PG&E has made to mitigate wildfires. Please note that our 2023 Q4 QDR, Table 11, provides what we consider to be a more complete view of our wildfire prevention and management investments. Furthermore, some targets and objectives have expenditures that are limited to Provider Cost Centers (PCCs), which are the costs associated with the departments or groups that provide services to the greater company. The cost of these services is allocated across multiple workstreams and are not directly charged to specific projects that can be aligned to a specific WMP initiative. For example, an engineering team may be responsible for evaluating and composing reports on different technologies for potential use across the company. One of the technologies they evaluate may contribute to an objective set forth in the WMP; however, the time that team spends on that specific evaluation, as opposed to all the other evaluations they conduct, is not tracked in a fashion that allows for an accurate accounting of expenditures aligned to this report. | Franky Lao | 2024-03-08 | 2024-03-29 | 2024-03-29 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_036.zip | 0 | N/A | QDR | N/A | N/A | N/A
504 | CalPA | Set WMP-36 | CalPA_Set WMP-36 | 2(a) | CalPA_Set WMP-36_Q2(a) | Please disaggregate the data in Table 11 of PG&E’s 2023 Q4 QDR such that there is only one Utility Initiative Tracking ID for each row. If this is not possible, please explain why and clarify the methodology for grouping certain tracking IDs. | Please reference “WMP-Discovery2023-2025_DR_CalAdvocates_036- Q002Supp01Atch01.pdf” for a copy of the 2023 WMP Annual Report on Compliance (ARC) and please reference “WMP-Discovery2023-2025_DR_CalAdvocates_036- Q002Supp01Atch02.xlsx” for associated attachments to the ARC. | Franky Lao | 2024-03-08 | 2024-04-09 | 2024-04-09 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_036.zip | 2 | N/A | QDR | N/A | N/A | N/A
505 | CalPA | Set WMP-36 | CalPA_Set WMP-36 | 3 | CalPA_Set WMP-36_Q3 | Table 7 of PG&E’s 2023 Q4 QDR does not reflect the planned or actual net addition or removal values reported in Table 8. a) Please explain this discrepancy. b) Is Table 7 or Table 8 accurate? | a) The data used in Table 7 is extracted from PG&E’s GIS systems, and other critical databases.The data in PG&E’s GIS systems are also utilized for the submission of the Spatial Quarterly Data Report. Per the Data Guidelines, Table 7 breaks down utility equipment and customer counts across multiple service area designations. Table 8 provides a summary of projected and actual additions or removals of equipment in their service territory across service area designations. PG&E interprets Table 8 as the Quarterly Net Change in system year-over-year. For example, the calculation for Q4 2023’s metric uses the difference between Q4 2023 and Q4 2022 to obtain the value. b) Table 7 and Table 8 are both accurate, and Table 8 is formulaically derived from Table 7. | Franky Lao | 2024-03-08 | 2024-03-29 | 2024-03-29 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_036.zip | 0 | N/A | QDR | N/A | N/A | N/A
506 | CalPA | Set WMP-36 | CalPA_Set WMP-36 | 4 | CalPA_Set WMP-36_Q4 | Table 9 of PG&E’s 2023 Q4 QDR reports on the utility’s infrastructure upgrades. a) Please provide clarification on how PG&E interprets and uses the term “utility infrastructure upgrades”. b) Per data guidelines version 3.2, these values should be “Numeric ≥ 0, or blank”. Please explain the negative values reported for metric number 1.d.3.c.i in Q3 2023 and Q4 2023. | a) For our 2023 QDR submissions, the term “utility infrastructure upgrades” encompasses all work performed under GH-01, specifically: overhead conductor hardening, undergrounding, and line removal. Additional details about this work can be found in WMP commitment GH-01, System Hardening, in Section 8.2.1.2 of our 2023-2025 WMP (pages 396-399). b) The negative values reported were a mathematical error. Upon review of the calculation and associated method used to report the data reported in Table 9, we corrected the quarterly data reported as Metric Type 1 Number of Overhead Circuit Miles Planned for Upgrade. Please see the updated Table 9 below, with the corrections incorporated into the Table 9 template. This data included below is the cumulative, year-to-date System Hardening miles completed by quarter based on GH-01 WMP target commitment. PG&E will submit a corrected QDR to Energy Safety’s QDR docket. | Franky Lao | 2024-03-08 | 2024-03-29 | 2024-03-29 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_036.zip | 0 | N/A | QDR | N/A | N/A | N/A
507 | CalPA | Set WMP-40 | CalPA_Set WMP-40 | 1 | CalPA_Set WMP-40_Q1 | PG&E states on page 23 of its 2025 WMP Update regarding its workplan for undergrounding and covered conductor projects: PG&E is currently refining our workplans for both overhead hardening and undergrounding projects through the end of the GRC period (2026) to account for the direction provided in D.23-11-069. As we update the workplan, we continue the approach described in the Base 2023-2025 WMP of intentionally building additional miles into the workplan to account for unforeseen delays to individual projects such as property access, weather, permitting, land rights acquisition, materials, or other constraints. Thus, some of the projects included in this workplan may not be completed in the 2023 to 2026 timeframe. Generally, PG&E will continue working on these projects until they can be completed. Finally, additional projects may be identified and added to the workplan going forward for potential completion between 2023 and 2026. a) Please identify PG&E’s intended cost recovery venue for the abovementioned undergrounding projects not completed in the 2023-26 timeframe. b) Please identify PG&E’s intended cost recovery venue for the abovementioned overhead hardening projects not completed in the 2023-26 timeframe. c) Please identify PG&E’s intended cost recovery venue for the abovementioned “additional projects” that may be identified and added to the workplan. | a. The cost recovery venue for undergrounding projects depends on the year in which the project becomes operational (i.e. is electrified). Any undergrounding project made operational in 2023-2026 will be recovered through PG&E’s 2023 General Rate Case (GRC) via the Wildfire Mitigation Balancing Account (WMBA). PG&E plans to submit its SB 884 10-Year Undergrounding Plan with a currently anticipated program launch date of January 1, 2027 and proposes that any undergrounding project that is operational on or after January 1, 2027 would be recovered through PG&E’s SB 884 10-Year Undergrounding Plan. While PG&E’s intent is to launch the SB 884 undergrounding program in 2027, PG&E is currently awaiting the SB 884 10-Year Plan guidelines from Energy Safety. Based on the review timeline of the legislation (i.e., nine-month review by Energy Safety, two months for electric utilities to submit to the CPUC, and nine-month review by CPUC), if final guidelines are issued mid-year 2024, the earliest we could possibly receive approval for our SB 884 Plan and cost recovery would be in mid2026. Thus, PG&E anticipates our Plan period would begin January 1, 2027 – meaning that projects included in our SB 884 Plan would begin to be electrified in 2027. The Plan launch in January 2027 assumes Energy Safety and the CPUC approve our Plan and cost recovery without requiring significant changes to our planned program. Furthermore, given the typical undergrounding project lifecycle of approximately two or more years, electrifying projects in 2027 will require project readiness work in 2025 and 2026. Thus, PG&E would begin incurring costs in 2025 and 2026 for projects that will become used and useful in the SB 884 Plan period of 2027 and beyond. PG&E’s cost recovery application will include these costs for readiness work for projects that become operative during the SB 884 Plan period. b. Any overhead hardening projects not fully completed in the 2023-2026 GRC timeframe will continue to be recovered through PG&E’s next GRC period via the WMBA. c. Please see the responses to subparts (a) and (b) for the requested information. | Miles Gordon | 2024-04-05 | 2024-04-10 | 2024-04-10 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_040.zip | 0 | N/A | 8.1.2 | Section 8.1.2 - Grid Design and System Hardening | 8.1.2.2 Undergrounding of electric lines and/or equipment | 2.1.1.2 GH-04 Undergrounding
508 | CalPA | Set WMP-40 | CalPA_Set WMP-40 | 2 | CalPA_Set WMP-40_Q2 | PG&E states on page 23 of its 2025 WMP Update regarding its workplan for undergrounding projects: PG&E is currently refining our workplans for both overhead hardening and undergrounding projects through the end of the GRC period (2026) to account for the direction provided in D.23-11-069. Additionally, PG&E’s Base 2023-2025 WMP R5 at page 408 states annual undergrounding mileage targets or forecasts: 350 miles in 2023, 250 miles in 2024, 330 miles in 2025, and 440 miles in 2026. With respect to undergrounding projects specifically: a) D.23-11-069 sets annual risk reduction targets to be achieved by undergrounding.4 In the 2023-2025 WMP period as a whole, does PG&E currently expect to fall short of, meet, or exceed the risk reduction target established in the GRC proceeding? b) According to PG&E’s current workplan, what is the amount of risk reduction that PG&E expects to achieve in 2024 due to undergrounding projects? c) How does your answer to part (b) compare to the risk reduction target established in D.23-11-069? d) According to PG&E’s current workplan, what is the amount of risk reduction that PG&E expects to achieve in 2025 due to undergrounding projects? e) How does your answer to part (d) compare to the risk reduction target established in D.23-11-069? f) Does PG&E anticipate completing additional undergrounding mileage in 2023-2026 beyond the GRC-authorized 1,230 undergrounding miles? g) If yes, please state the number of miles and PG&E’s intended cost recovery venue for said miles. | a. PG&E intends to meet the cumulative system hardening risk reduction requirement of 18% by 2026, using the risk reduction methodology described in Advice Letter 7150-E-A. b. Based on the workplan as of February 22, 2024, and using the GRC risk reduction methodology described in Advice Letter 7150-E-A, the 2024 target-informed risk reduction for undergrounding projects is currently forecasted to be approximately 1.6%. Using the WMP risk reduction method (risk reduction based on WDRM v3 only), the target-informed anticipated risk reduction for undergrounding projects currently forecasted for completion in 2024 is approximately 1.5%. Note: these values only include projects in Maintenance Activity Type (MAT) codes 08W and 3UG. c. Annual risk reduction forecasts established in D.23-11-069 are cumulative for the GRC period (2023-2026). Risk reduction forecasts for specific mitigation types were not established. The response to subpart (b) includes the undergrounding contribution to the GRC System Hardening cumulative risk reduction target (to be achieved by 2026) noted above and shown in the table below. System Hardening GRC Risk Reduction Targets (per D.23-11-069, OP 23) Date 12/31/2023 12/31/2024 12/31/2025 12/31/2026 Overall Target: 2023-2026 Cumulative Risk Reduction Target 2% 5% 10% 18% 18% For all system hardening work, including overhead covered conductor, underground and line removal, the 2024 cumulative risk reduction target established in D.23-11- 069 is 5% for 2023-2024. Based on the system hardening workplan as of February 22, 2024 and using the GRC risk reduction methodology described in Advice Letter 7150-E-A, PG&E’s current forecasted cumulative risk reduction for system hardening in 2023-2024 is 4.7% (MAT codes 3UG and 08W only). The actual risk reduction values of completed system hardening work are expected to meet the overall cumulative target of 18% by 2026. Note, as described in the 2023 WMP ACI 22-16, the workplans purposefully build in additional miles compared to the proposed targets at that time to account for the fact that project dependencies and construction issues may arise and delay some projects. Therefore, the cumulative mileage and risk reduction associated with the workplan are currently overstated as compared to what would be accomplished in accordance with the target. To account for this, the risk reduction reported in this response has been proportionately adjusted to align the anticipated risk reduction with the target miles. d. The system hardening workplan associated with years 2025 and 2026 is currently combined, as the projects associated with each year are still being finalized. Based on the workplan as of February 22, 2024 and using the GRC risk reduction methodology described in Advice Letter 7150-E-A, the 2025-2026 target-informed risk reduction for undergrounding projects is currently forecasted to be approximately 8.3%. Using the WMP risk reduction method (risk reduction based on WDRM v3 only), the target-informed anticipated risk reduction for undergrounding projects currently forecasted for completion in 2025-2026 is approximately 8.4%. Note: these values only include projects in MAT codes 08W and 3UG. e. As mentioned in subpart (c), risk reduction targets established in D.23-11-069 are cumulative for the GRC period (2023-2026). Risk reduction targets for specific mitigation types were not established. The response to sub-part d includes the undergrounding contribution to the GRC System Hardening cumulative risk reduction target noted above and shown in the table below. System Hardening GRC Risk Reduction Targets (per D.23-11-069, OP 23) Date 12/31/2023 12/31/2024 12/31/2025 12/31/2026 Overall Target: 2023-2026 Cumulative Risk Reduction Target 2% 5% 10% 18% 18% For all system hardening work, including overhead covered conductor, underground and line removal, the 2025 cumulative risk reduction target established in D-23-11- 069 is 10% for 2023-2025, and 18% for 2023-2026. Based on the system hardening workplan as of February 22, 2024 and using the GRC risk reduction methodology described in Advice Letter 7150-E-A, PG&E’s current forecasted cumulative risk reduction for system hardening in 2025-2026 and 2023-2026 is 13.7% and 18.4%, respectively (MAT codes 3UG and 08W only). Note, as described in the 2023 WMP ACI 22-16, the workplans purposefully build in additional miles compared to the proposed targets at that time to account for the fact that project dependencies and construction issues may arise and delay some projects. Therefore, the cumulative mileage and risk reduction associated with the workplan are currently overstated as compared to what would be accomplished in accordance with the target. To account for this, the risk reduction reported in this response has been proportionately adjusted to align the anticipated risk reduction with the target miles. f. PG&E does not currently anticipate materially exceeding the 1,230 miles of undergrounding targeted in the 2023 GRC decision. PG&E intends to align with the authorized 2023 GRC system hardening cost cap of $4.723 billion and 18% cumulative risk reduction target. PG&E may continue to complete undergrounding work beyond the 1,230 miles if those miles are within authorized costs. PG&E would count those miles as contributing to the four-year cumulative risk reduction requirement. g. If undergrounding miles are completed beyond the 1,230 estimated miles but are within the authorized costs and contribute to the risk reduction requirements, PG&E will recover costs in the GRC Wildfire Mitigation Balancing Account (WMBA). | Miles Gordon | 2024-04-05 | 2024-04-10 | 2024-04-10 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_040.zip | 0 | N/A | 8 | Section 8.1.2 - Grid Design and System Hardening | 8.1.2.2 Undergrounding of electric lines and/or equipment | 2.1.1.2 GH-04 Undergrounding
509 | CalPA | Set WMP-40 | CalPA_Set WMP-40 | 3 | CalPA_Set WMP-40_Q3 | PG&E states on page 23 of its 2025 WMP Update regarding its workplan for covered conductor projects: PG&E is currently refining our workplans for both overhead hardening and undergrounding projects through the end of the GRC period (2026) to account for the direction provided in D.23-11-069. With respect to covered conductor projects specifically: a) D.23-11-069 sets annual risk reduction targets to be achieved by installing covered conductor. In the 2023-2025 WMP period as a whole, does PG&E currently expect to fall short of, meet, or exceed the risk reduction target established in the GRC proceeding? b) According to PG&E’s current workplan, what is the amount of risk reduction that PG&E expects to achieve in 2024 due to covered conductor projects? c) How does your answer to part (b) compare to the risk reduction target established in D.23-11-069? d) According to PG&E’s current workplan, what is the amount of risk reduction that PG&E expects to achieve in 2025 due to covered conductor projects? e) How does your answer to part (d) compare to the risk reduction target established in D.23-11-069? f) Does PG&E anticipate completing additional covered conductor mileage in 2023-2026 beyond the GRC-authorized 778 covered conductor miles? g) If yes, please state the number of miles and PG&E’s intended cost recovery venue for said miles. | a. PG&E intends to meet the cumulative system hardening risk reduction requirement of 18% by 2026 using the risk reduction methodology described in Advice Letter 7150-E-A. b. Based on the workplan as of February 22, 2024 and referencing the GRC risk reduction methodology described in Advice Letter 7150-E-A, the 2024 targetinformed risk reduction for overhead hardening projects is currently forecasted to be approximately 0.6%. Using the WMP risk reduction method (risk reduction based on WDRM v3 only), the target-informed anticipated risk reduction for overhead hardening projects currently forecasted for completion in 2024 is approximately 0.1%. Note: these values only include projects in Maintenance Activity Type (MAT) codes 08W and 3UG. c. Annual risk reduction forecasts established in D.23-11-069 are cumulative for the GRC period (2023-2026). Risk reduction forecasts for specific mitigation types were not established. The response to subpart (b) includes the overhead hardening contribution to the GRC System Hardening cumulative risk reduction target noted above and shown in the table below. System Hardening GRC Risk Reduction Targets (per D.23-11-069, OP 23) Date 12/31/2023 12/31/2024 12/31/2025 12/31/2026 Overall Target: 2023-2026 Cumulative Risk Reduction Target 2% 5% 10% 18% 18% For all system hardening work, including overhead covered conductor, underground and line removal, the 2024 cumulative risk reduction target established in D.23-11- 069 is 5% for 2023-2024. Based on the system hardening workplan as of February 22, 2024 and using the GRC risk reduction methodology described in Advice Letter 7150-E-A, PG&E’s current forecasted cumulative risk reduction for system hardening in 2023-2024 is 4.7% (MAT codes 3UG and 08W only). The actual risk reduction values of completed system hardening work is expected to meet the overall cumulative target of 18% by 2026. Note, as described in the 2023 WMP ACI 22-16, the workplans purposefully build in additional miles compared to the proposed targets at that time to account for the fact that project dependencies and construction issues may arise and delay some projects. Therefore, the cumulative mileage and risk reduction associated with the workplan are currently overstated as compared to what would be accomplished in accordance with the target. To account for this, the risk reduction reported in this response has been proportionately adjusted to align the anticipated risk reduction with the target miles. d. The system hardening workplan associated with years 2025 and 2026 is currently combined, as the projects associated with each year are still being finalized. Based on the workplan as of February 22, 2024 and referencing the GRC risk reduction methodology described in Advice Letter 7150-E-A, the 2025-2026 target-informed risk reduction for overhead hardening projects is currently forecasted to be approximately 5.0% Using the WMP risk reduction method (risk reduction based on WDRM v3 only), the target-informed anticipated risk reduction for overhead hardening projects currently forecasted for completion in 2025-2026 is approximately 4.3%. Note: these values only include projects in MAT codes 08W and 3UG. e. As mentioned in subpart (c), risk reduction targets established in D.23-11-069 are cumulative for the GRC period (2023-2026). Risk reduction targets for specific mitigation types were not established. The response to subpart (d) includes the overhead hardening contribution to the GRC System Hardening cumulative risk reduction target noted above and shown in the table below. System Hardening GRC Risk Reduction Targets (per D.23-11-069, OP 23) Date 12/31/2023 12/31/2024 12/31/2025 12/31/2026 Overall Target: 2023-2026 Cumulative Risk Reduction Target 2% 5% 10% 18% 18% For all system hardening work, including overhead covered conductor, underground and line removal, the 2025 cumulative risk reduction target established in D.23-11- 069 is 10% for 2023-2025, and 18% for 2023-2026. Based on the system hardening workplan as of February 22, 2024 and using the GRC risk reduction methodology described in Advice Letter 7150-E-A, PG&E’s current forecasted cumulative risk reduction for system hardening in 2025-2026 and 2023-2026 is 13.7% and 18.4%, respectively (MAT codes 3UG and 08W only). Note, as described in the 2023 WMP ACI 22-16, the workplans purposefully build in additional miles compared to the proposed targets at that time to account for the fact that project dependencies and construction issues may arise and delay some projects. Therefore, the cumulative mileage and risk reduction associated with the workplan are currently overstated as compared to what would be accomplished in accordance with the target. To account for this, the risk reduction reported in this response has been proportionately adjusted to align the anticipated risk reduction with the target miles. f. Please see the response to CalAdvocates_040_Q002, subpart (f), PG&E has the same position as it relates to Overhead Hardening target miles as articulated in the response to Q2 (f) for undergrounding. g. Please see the response to CalAdvocates_040_Q002, subpart (g) PG&E has the same position as it relates to Overhead Hardening target miles as articulated in the response to Q2 (g) for undergrounding. | Miles Gordon | 2024-04-05 | 2024-04-10 | 2024-04-10 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_040.zip | 0 | N/A | 8 | Section 8.1.2 - Grid Design and System Hardening | 8.1.2.1 Covered Conductor Installation – Distribution | 2.1.4.1 GH-11 Traditional Overhead Hardening Conductor
510 | CalPA | Set WMP-40 | CalPA_Set WMP-40 | 4 | CalPA_Set WMP-40_Q4 | PG&E states on page 25 of its 2025 WMP Update: “PG&E proposes to add a 2025 target (System Hardening – Transmission Conductor Segment Replacement (GH-11)) to perform conductor segment replacement on two transmission lines.” a) Was the abovementioned work requested and authorized in PG&E’s Test Year 2023 GRC? b) If yes, please provide the exhibit and page number in PG&E’s Test Year 2023 GRC testimony that discusses this work, as well as the relevant Major Activity Type (MAT) code or codes. c) If yes, please provide the final authorized funding amount for this program as set forth in D.23-11-069, with a citation to the relevant pages of that decision.5 | a) No. System Hardening - Transmission Conductor Segment Replacement was not forecast or authorized in the 2023 General Rate Case (GRC). b) Not applicable, please see the response to subpart (a). c) Not applicable, please see the response to subpart (a). | Miles Gordon | 2024-04-05 | 2024-04-10 | 2024-04-10 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_040.zip | 0 | N/A | 8 | Section 8.1.2 - Grid Design and System Hardening | 8.1.2.5.1 Traditional Overhead Hardening – Transmission Conductor | 2.1.4.1 GH-11 Traditional Overhead Hardening Conductor
511 | CalPA | Set WMP-40 | CalPA_Set WMP-40 | 5 | CalPA_Set WMP-40_Q5 | PG&E states on page 3 of its 2025 WMP update that it is introducing a new evolution of its Wildfire Distribution Risk Model (WDRM), called WDRM v4. It states, “The outputs from the WDRM v4 are expected to inform some risk-prioritized, short-cycle work in 2025 and other risk-prioritized long-cycle work in 2026 and beyond.” a) Please identify each WMP initiative for which WDRM v4 is expected to “inform risk-prioritized short-cycle work in 2025.” b) Please identify each WMP initiative for which WDRM v4 is expected to “inform risk-prioritized long-cycle work in 2026 and beyond.” c) When will WDRM v4 begin to inform the scoping and execution of undergrounding projects? d) When does PG&E expect to begin constructing undergrounding projects that are scoped using WDRM v4? e) When will WDRM v4 begin to inform the scoping and execution of covered conductor projects? f) When does PG&E expect to begin constructing covered conductor projects that are scoped using WDRM v4? | a. At this time, 2025 workplans are still being developed. PG&E cannot say with certainty which WMP initiatives for which WDRM v4 are expected to “inform riskprioritized short-cycle work in 2025.” PG&E’s 2026-2028 WMP will provide details on workplans drawing on the WDRM v4 for insights. b. PG&E cannot say with certainty what long-cycle work it is expected to inform riskprioritized long-cycle work in 2026 and beyond.” PG&E’s 2026-2028 WMP will provide details on workplans drawing on the WDRM v4 for insights. c. WDRM v4 will begin to inform scoping of undergrounding projects as early as the second half of 2024 for undergrounding projects planned for completion in 2027 and beyond. d. For undergrounding projects scoped using WDRM v4, PG&E anticipates that some planning activities in 2025 and preparatory work for civil construction may begin in 2026 for projects to be completed in 2027. e. WDRM v4 will begin to inform scoping of overhead hardening (covered conductor) projects as early as the second half of 2024 for projects expected to be completed in 2027 and beyond. f. For overhead hardening (covered conductor) projects scoped using WDRM v4, PG&E anticipates that some planning activities in 2025 and preparatory work for civil construction may begin in 2026 for projects to be completed in 2027. | Miles Gordon | 2024-04-05 | 2024-04-16 | 2024-04-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_040.zip | 0 | N/A | 6 | Section 6 - Risk Methodology and Assessment | 6.1.2 Summary of Risk Models | B.1.1. WDRM v4
512 | CalPA | Set WMP-40 | CalPA_Set WMP-40 | 6 | CalPA_Set WMP-40_Q6 | PG&E states on page 3 of its 2025 WMP update that it is introducing a new evolution of its Wildfire Distribution Risk Model (WDRM), called WDRM v4. It states, “The outputs from the WDRM v4 are expected to inform some risk-prioritized, short-cycle work in 2025 and other risk-prioritized long-cycle work in 2026 and beyond.” a) Is WDRM v4 expected to inform scoping and execution of any undergrounding projects that will be performed in 2025 and 2026? b) If the answer to part (a) is yes, please explain how PG&E intends to report this risk reduction in its System Hardening Accountability Report (SHAR) required by D.23-11-069.6 c) Is WDRM v4 expected to inform scoping and execution of any covered conductor projects that will be performed in 2025 and 2026? d) If the answer to part (c) is yes, please explain how PG&E intends to report this risk reduction in the SHAR. | a. As noted in response to Request 5(c) of this data request, WDRM v4 may begin to inform scoping of undergrounding projects as early as the second half of 2024 for undergrounding projects planned for completion in 2027 and beyond. b. The scope of the SHAR includes System Hardening work completed in the GRC period (2023-2026). Projects in this time period are not currently anticipated to be informed by WDRM v4. In the event projects selected by WDRM v4 do end up being planned for completion during this time period, WDRM v4 information would be included in the SHAR in the existing risk-related fields (i.e., Applicable Risk Model, Risk Reduction %, etc.). c. As noted in response to Request 5(e) of this data request, WDRM v4 may begin to inform the scoping of overhead hardening (covered conductor) projects as early as the second half of 2024 for projects planned for completion in 2027 and beyond. d. Please see the response to subpart (b) above for how PG&E reports this risk reduction in the SHAR. | Miles Gordon | 2024-04-05 | 2024-04-16 | 2024-04-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_040.zip | 0 | N/A | 6 | Section 6 - Risk Methodology and Assessment | 6.1.2 Summary of Risk Models | B.1.1. WDRM v4
513 | CalPA | Set WMP-40 | CalPA_Set WMP-40 | 7 | CalPA_Set WMP-40_Q7 | PG&E states on page 51 of its 2025 WMP Update that, in response to ACI PG&E-23-05 – Updating Grid Hardening Decision Making, “PG&E is developing a WBCA [Wildfire Benefit Cost Analysis] tool to incorporate cost effectiveness components, reliability considerations, and location-specific mitigation effectiveness calculations.” PG&E further states that undergrounding projects “scoped with the WBCA in 2024 and 2025 will likely have a completion date in 2027 or later.” a) Will the WBCA tool be used to scope any projects that will be tracked in the System Hardening Accountability Report required by D.23-11-069? 7 b) If the answer to part (a) is yes, please explain how this will be identified in the SHAR. c) If the answer to part (a) is yes, please identify any changes to the SHAR template (e.g. adding fields) that would need to be made to include the necessary information to track such projects. d) Does PG&E expect to request any changes to the SHAR to facilitate tracking projects scoped using the WBCA? Please explain your response. | a. No, the System Hardening Accountability Report (SHAR) required by D.23-11-069 will only include projects completed in the GRC period (2023 – 2026). Project details will not be included for projects that will be completed in 2027 and beyond. At this time, we are intending for projects selected using the WBCA tool in accordance with SB 884 to be completed in 2027 and beyond. In the event projects selected using the WBCA are planned for completion during the GRC time period (2023-2026), these projects will be tracked in the SHAR as required by D.23-11-069. b. Not applicable, please see the response to subpart (a) above. c. Not applicable, please see the response to subpart (a) above. d. No, please see the response to sub-part (a) above for the requested explanation. | Miles Gordon | 2024-04-05 | 2024-04-10 | 2024-04-10 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_040.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--05 – Updating Grid Hardening Decision Making | ACI 23-05 Updating Grid Hardening Decision Making
514 | CalPA | Set WMP-41 | CalPA_Set WMP-41 | 1 | CalPA_Set WMP-41_Q1 | a) Please list all distinct risk scores generated by PG&E’s WDRM v4. For example, WDRM v3 generated 17 different risk scores.4 b) For each risk score in part (a), please provide a category or brief description of the type of risk the score represents. c) For each risk score in part (a), please provide a brief explanation of how PG&E intends to use that risk score. d) For each risk score in part (a), please list all PG&E wildfire mitigation initiatives that are informed by that risk score (if PG&E expects to utilize a risk score to inform a mitigation initiative in the future, please so note). e) For each risk score in part (a), please state the most granular level available for that risk score. For example, in WDRM v3, the most granular level available would be the risk scores associated with individual 100m x 100m pixels. f) For each risk score in part (a), please state the granularity at which the risk score is used to inform wildfire mitigation initiatives (e.g. circuit segment, circuit, individual asset, individual miles, etc.). | There are 23 event probability models from WDRM v4 that produce ignition risk values: • Animal – Bird • Animal – Squirrel • Animal – Other • Capacitor Bank • DPD • Fuse • Primary Conductor – Line Slap • Primary Conductor – Wire Down • Primary Conductor – Other • Secondary Conductor • Support Structure - Leaking • Support Structure – Equipment • Switch • Third Party – Balloon • Third Party – Vehicle • Third Party – Other • Transformer – Equipment • Transformer – Leaking • Vegetation – Branch • Vegetation – Trunk • Vegetation – Other • Voltage Regulator • Other Equipment Responses to subparts (b) through (f) of this request are described in the table below. bability Risk Score b) Category / Description c) Intended Use d) Mitigation Initiatives e) Granularity f) Risk Granularity Animal – Bird Ignition risk caused by bird contact Inform mitigation for bird related ignitions TBD* Pixel (100m2 ) Circuit Segment Animal – Squirrel Ignition risk caused by squirrel contact Inform mitigation for squirrel related ignitions TBD* Pixel (100m2 ) Circuit Segment Animal – Other Ignition risk caused by contact other than bird and squirrel Inform mitigation for other animal related ignitions TBD* Pixel (100m2 ) Circuit Segment Capacitor Bank Ignition risk caused by capacitor bank failures Inform mitigation for capacitor bank related ignitions TBD* Asset Asset Dynamic Protective Device (DPD) Ignition risk caused by DPD failures Inform mitigation for DPD related ignitions TBD* Asset Asset Fuse Ignition risk caused by fuse failures Inform mitigation for fuse related ignitions TBD* Asset Asset Primary Conductor – Line Slap Ignition risk caused by primary conductor failures due to line slap Inform mitigation for primary conductor line slap related ignitions TBD* Asset Asset Primary Conductor – Wire Down Ignition risk caused by primary conductor failures due to wire down Inform mitigation for primary conductor wire down related ignitions TBD* Asset Asset Primary Conductor – Other Ignition risk caused by primary conductor failures other than line slap and wire down Inform mitigation for other primary conductor related ignitions TBD* Asset Asset Secondary Conductor Ignition risk caused by secondary conductor failures Inform mitigation for secondary conductor related ignitions TBD* Pixel Circuit Segment Support Structure – Electrical Failure Ignition risk caused by support structure electrical failures Inform mitigation for support structure electrical related ignitions TBD* Asset Asset Support Structure – Equipment Failure Ignition risk caused by support structure equipment (pole and attachment) failures Inform mitigation for support structure equipment related ignitions TBD* Asset Asset Switch Ignition risk caused by switch failures Inform mitigation for switch related ignitions TBD* Asset Asset Third Party – Balloon Ignition risk caused by mylar balloon contact Inform mitigations for balloon related ignitions TBD* Pixel (100m2 ) Circuit Segment Third Party – Vehicle Ignition risk caused by vehicle contact Inform mitigations for vehicle related ignitions TBD* Pixel (100m2 ) Circuit Segment Third Party – Other Ignition risk caused by contact other than balloon and vehicle Inform mitigations for other cause related ignitions TBD* Pixel (100m2 ) Circuit Segment Transformer – Equipment Ignition risk caused by pole mounted transformer equipment failures Inform mitigations for transformer equipment related ignitions TBD* Asset Asset Transformer – Leaking Ignition risk caused by leaking transformers Inform mitigations for leaking transformer related ignitions TBD* Asset Asset Vegetation – Branch Ignition risk caused by tree branch failure Inform mitigations for tree branch failure related ignitions TBD* Pixel (100m2 ) Circuit Segment Vegetation – Trunk Ignition risk caused by tree trunk failure Inform mitigations for tree trunk failure related ignitions TBD* Pixel (100m2 ) Circuit Segment Vegetation – Other Ignition risk caused by vegetation failures other than tree branch and trunk failures Inform mitigations for vegetation related ignitions other than tree trunk and branch TBD* Pixel (100m2 ) Circuit Segment Voltage Regulator Ignition risk caused by voltage regulator and shunt capacitor failures Inform mitigation for voltage regulator related ignitions TBD* Asset Asset Other Equipment Ignition risk from causes not specified by the other 22 event probability models Inform mitigation for other equipment related ignitions not covered by a specific equipment model TBD* Pixel (100m2 ) Circuit Segment *To be determined in 2026-2028 Base WMP. | Holly Wehrman | 2024-04-05 | 2024-04-11 | 2024-04-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_041.zip | 0 | N/A | 6 | Section 6 - Risk Methodology and Assessment | 6.1.2 Summary of Risk Models | B.1.1. WDRM v4
515 | CalPA | Set WMP-41 | CalPA_Set WMP-41 | 2 | CalPA_Set WMP-41_Q2 | a) Please list all composite (or aggregate) risk scores generated by PG&E’s WDRM v4. For example, WDRM v3 generated five composite risk scores. b) For each risk score in part (a), please provide a category or brief description of the type of risk the score represents. c) For each risk score in part (a), please provide a brief explanation of how PG&E intends to use that risk score. d) For each risk score in part (a), please list all PG&E wildfire mitigation initiatives that are informed by that risk score (if PG&E expects to utilize a risk score to inform a mitigation initiative in the future, please so note). e) For each risk score in part (a), please state the most granular level available for that risk score. f) For each risk score in part (a), please state the granularity at which the risk score is used to inform wildfire mitigation initiatives (e.g. circuit segment, circuit, individual asset, individual miles, etc.). | There are three composite risk scores available from WDRM v4 at a circuit segment level that produce ignition risk values: • All (Total Risk); • System Hardening; and • Vegetation. Responses to parts (b) through (f) of this request are described in the table below. a) Composite Risk Score b) Category / Description c) Intended Use d) Mitigation Initiatives e) Granularity f) Risk Granularity All Composite All 23 event risk drivers Inform on total system risk TBD* Asset and Pixel (100m2 ) Circuit Segment System Hardening Composite 21 event risk drivers that System Hardening mitigation addresses, excludes: •Support Structure – Electrical •Transformer – Leaking Inform System Hardening prioritization System Hardening Asset and Pixel (100m2 ) Circuit Segment Vegetation 3 event risk drivers that vegetation mitigation addresses, includes: •Vegetation – Branch •Vegetation – Trunk •Vegetation – Other Inform mitigation aimed at reducing vegetation related ignitions TBD* Pixel (100m2 ) Circuit Segment *To be determined in 2026-2028 Base WMP. | Holly Wehrman | 2024-04-05 | 2024-04-11 | 2024-04-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_041.zip | 0 | N/A | 6 | Section 6 - Risk Methodology and Assessment | 6.1.2 Summary of Risk Models | B.1.1. WDRM v4
516 | CalPA | Set WMP-41 | CalPA_Set WMP-41 | 3 | CalPA_Set WMP-41_Q3 | Questions 3 and 4 refer to the risk scores generated from WDRM v4. This should be understood to refer to PG&E’s responses to questions 1 and 2 above. If PG&E possesses geospatial data that is not in the specific format requested in questions 3 and 4, but that PG&E believes substantially contains the information requested in questions 3 and 4, please contact the originators to discuss the format of your responses. Question 3 Please provide a GIS file that details the most granular level (as discussed in questions 1(e) and 2(e)) available for each risk score identified in questions 1(a) and 2(a). This file should contain the following: a) Geometric features detailing the most granular level available for each risk score. This may be polygons that depict “pixels,” lines that depict circuit segments, points that depict assets, or other geometry that best suits the relevant risk scores. If multiple risk scores share geometry (e.g., multiple risk scores that are calculated at the “pixel” level), there is no need to include multiple layers that depict the same physical geometry. b) For each geometric feature, please include all relevant risk scores from questions 1(a) and 2(a) as attributes. | a) Please see “WMP-Discovery2023-2025_DR_CalAdvocates_041- Q003Atch01CONF.zip” for GIS files which include the combined pixel-based models (Vegetation, Animal, Third Party, Secondary Conductor, and Other Equipment), and individual Asset Equipment models. Please note, Asset Equipment model results are referenced to point geometry locations, while the pixel-model results are referenced to 100m-by-100m square grid pixel locations that overlay the PG&E service territory. When converting PG&E native data sets into GIS format, the original model column names were unfortunately truncated to 10-character lengths for GIS Field names. This truncation made identifying contributing model results in composite files difficult. Therefore, more descriptive Field names were substituted for the truncated versions. A companion Excel workbook, “WMP-Discovery2023- 2025_DR_CalAdvocates_041-Q003Atch02.xlsx,” has been provided with GIS File specific tabs to cross-reference the substituted Field names to the original model result. b) Please see the answer to subpart a) above. | Holly Wehrman | 2024-04-05 | 2024-04-29 | 2024-04-29 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_041.zip | 2 | N/A | 6 | Section 6 - Risk Methodology and Assessment | 6.1.2 Summary of Risk Models | B.1.1. WDRM v4
517 | CalPA | Set WMP-41 | CalPA_Set WMP-41 | 4 | CalPA_Set WMP-41_Q4 | Please provide a GIS file that details the risk scores at the same granularity that is currently used to inform wildfire mitigation measures (as discussed in questions 1(f) and 2(f)). This file should contain the following: a) Geometric features detailing the relevant geometry for each risk score. This may be polygons that depict “pixels,” lines that depict circuit segments, points that depict assets, or other geometry that best suits the relevant risk scores. If multiple risk scores share geometry (e.g., multiple risk scores that are used to inform mitigation measures at the circuit segment level), there is no need to include multiple layers that depict the same physical geometry. b) For each geometric feature, please include all relevant risk scores from questions 1(a) and 2(a) as attributes. c) For each geometric feature, include the circuit identification number as an attribute. d) For each geometric feature, include the circuit name as an attribute. e) For each geometric feature, include the circuit segment name as an attribute. f) As needed, include unique identification for each geometric feature (e.g., asset ID, substation name, etc.) | Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_041- Q003Atch01CONF.zip” for the requested System Hardening and Vegetation Management composite models. | Holly Wehrman | 2024-04-05 | 2024-04-29 | 2024-04-29 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_041.zip | 0 | N/A | 6 | Section 6 - Risk Methodology and Assessment | 6.1.2 Summary of Risk Models | B.1.1. WDRM v4
518 | CalPA | Set WMP-41 | CalPA_Set WMP-41 | 5 | CalPA_Set WMP-41_Q5 | Question 5 refers to the risk scores generated from WDRM v4. This should be understood to refer to PG&E’s responses to questions 1 and 2 above. Please provide a spreadsheet that lists (as rows) each circuit-segment that is included in the Wildfire Distribution Risk Model v4. This spreadsheet should include, at minimum, the following columns. a) Name or ID number of each circuit segment. b) Circuit name for the circuit that each segment is part of. c) Circuit ID for the circuit that each segment is part of. d) Nominal voltage. e) The pixel count of the circuit segment (as applicable, e.g., for pixel-based sub-models). f) The average risk value(s) associated with each pixel along the circuit segment (as applicable, e.g., for pixel-based sub-models). g) The asset count of the circuit segment (as applicable, e.g., for asset-based sub-models).5 h) The risk value(s) associated with each asset along the circuit segment (as applicable, e.g., for asset-based sub-models).5 i) The risk per line mile of the circuit-segment (as applicable). j) Total circuit-miles on the circuit-segment. k) Total overhead circuit-miles on the circuit-segment. l) Total non-HFTD overhead circuit-miles on the circuit-segment. m) Total Tier 2 overhead circuit-miles on the circuit-segment. n) Total Tier 3 overhead circuit-miles on the circuit-segment. o) Total underground circuit-miles on the circuit-segment. p) Total non-HFTD underground circuit-miles on the circuit-segment. q) Total Tier 2 underground circuit-miles on the circuit-segment. r) Total Tier 3 underground circuit-miles on the circuit-segment. s) A separate, labeled column for each risk score identified in question 1(a) that is used at the circuit-segment level to inform wildfire mitigation initiatives. (May require multiple columns.) t) A separate, labeled column for each composite risk score identified in question 2(a) that is used at the circuit-segment level to inform wildfire mitigation initiatives. (May require multiple columns.) | a) - t) Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_041- Q005Atch01.xlsx” for the requested information. ATTACHMENT: WMP-Discovery2023-2025_DR_CalAdvocates_041-Q005Atch01.xlsx | Holly Wehrman | 2024-04-05 | 2024-04-11 | 2024-04-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_041.zip | 1 | N/A | 6 | Section 6 - Risk Methodology and Assessment | 6.1.2 Summary of Risk Models | B.1.1. WDRM v4
519 | CalPA | Set WMP-41 | CalPA_Set WMP-41 | 6 | CalPA_Set WMP-41_Q6 | Pages 9-11 of PG&E’s 2025 WMP Update discuss version 4 of PG&E’s Wildfire Consequence Model. Please provide a GIS file that details the most granular level available for the Wildfire Consequence Model, version 4. This file should contain the following: a) Geometric features detailing the most granular level available for consequence (it is Cal Advocates’ understanding that the consequence model uses “pixels”). b) For each geometric feature, please include all relevant consequence values (if there are multiple) as attributes. | Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_041- Q003Atch01CONF.zip” for a GIS file containing for the requested Wildfire Consequence (WFC) v4 model pixel results. | Holly Wehrman | 2024-04-05 | 2024-04-29 | 2024-04-29 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_041.zip | 0 | N/A | 6 | Section 6 - Risk Methodology and Assessment | 6.1.2 Summary of Risk Models | B.1.1. WDRM v4
520 | CalPA | Set WMP-41 | CalPA_Set WMP-41 | 7 | CalPA_Set WMP-41_Q7 | Please provide a GIS file that details the most granular level available for the Wildfire Consequence Model version used in the WDRM v3. This file should contain the following: a) Geometric features detailing the most granular level available for consequence (it is Cal Advocates’ understanding that the consequence model uses “pixels”). b) For each geometric feature, please include all relevant consequence values (if there are multiple) as attributes. | Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_041- Q003Atch01CONF.zip” for a GIS file containing the requested Wildfire Consequence (WFC) v3.4 model pixel results. | Holly Wehrman | 2024-04-05 | 2024-04-29 | 2024-04-29 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_041.zip | 0 | N/A | 6 | Section 6 - Risk Methodology and Assessment | 6.1.2 Summary of Risk Models | B.1.1. WDRM v4
521 | CalPA | Set WMP-41 | CalPA_Set WMP-41 | 8 | CalPA_Set WMP-41_Q8 | a) Has E3 or another entity completed an independent review of the WDRM v4? b) If the answer to part (a) is yes, please provide a copy of any reports and outputs from the independent review. c) If the answer to part (a) is no, when does PG&E expect the review to be completed? | a) E3 is currently conducting an independent review of the WDRM v4. b) The E3 review is scheduled to be available by the end of Q2 2024. c) Please see the response to subpart (b) above. | Holly Wehrman | 2024-04-05 | 2024-04-11 | 2024-04-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_041.zip | 0 | N/A | 6 | Section 6 - Risk Methodology and Assessment | 6.1.2 Summary of Risk Models | B.1.1. WDRM v4
522 | CalPA | Set WMP-41 | CalPA_Set WMP-41 | 9 | CalPA_Set WMP-41_Q9 | a) Has PG&E created a detailed overview document that details the WDRM v4, similar to the “2021 Wildfire Distribution Risk Model Overview” that PG&E submitted following the public workshop held on October 5 and 6, 2021? b) If the answer to part (a) is yes, please provide a copy of the document. c) If the answer to part (a) is no, does PG&E plan to create such a document? d) If the answer to part (c) is no, please explain why not. e) If the answer to part (c) is yes, when does PG&E expect the document to be completed? | a) PG&E is currently creating the detailed overview documentation for the WDRM v4. It is scheduled to be available by the end of Q2 2024. b) Not applicable, please see the response to subpart (a) above. c) Not applicable, please see the response to subpart (a) above. d) Not applicable, please see the response to subpart (a) above. e) Please see the response to subpart (a) above. | Holly Wehrman | 2024-04-05 | 2024-04-11 | 2024-04-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_041.zip | 0 | N/A | 6 | Section 6 - Risk Methodology and Assessment | 6.1.2 Summary of Risk Models | B.1.1. WDRM v4
523 | MGRA | Data Request No. 9 | MGRA_Data Request No. 9 | 1 | MGRA_Data Request No. 9_Q1 | Table PG&E-B.1.1-2 Event Probability Model Predictive Performance In the table, predictive ability for drivers of ignitions from Primary Conductor (Other, Wire Down) fare relatively poorly compared to regular attributes. Explain why this is so. | This is a topic of current study. The wire-down model addresses primary wire-down ignitions due to equipment failures and not vegetation related failures. Current investigations are focused on the fact that most failure events occur in coastal areas and ignitions do not follow the same pattern. Work is ongoing to improve the model’s ability to represent this spatial pattern | Joseph Mitchell | 2024-04-08 | 2024-04-11 | 2024-04-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_009.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--25 Fire Potential Index (FPI) and Ignition Probability Weather (IPW) Enhancements | ACI 23-25 Fire Potential Index and Ignition Probability Weather Enhancements
524 | MGRA | Data Request No. 9 | MGRA_Data Request No. 9 | 2 | MGRA_Data Request No. 9_Q2 | Please provide information available on the introduction of “an assessment of dry wind conditions for predicting areas of high consequence”. | As indicated on page 10 of the 2025 PG&E WMP Update, one of the key updates to the v4 Wildfire Consequence (WFC) model is the addition of an analog for Red Flag conditions. Red Flag conditions are correlated with fire outcomes. However, due to inconsistencies with the way Red Flag conditions are forecast and reported, a proxy for Red Flag conditions has been developed that is consistent across the territory. The WFC model uses one of the definitions for Red Flag conditions found in Northern California and estimates the so-called “dry wind” conditions from PG&E historic meteorology data. Dry wind conditions enter as a partition in the baseline consequence model, similar to the way the risk bowtie uses Red Flag warnings. Like Red Flag warnings, dry wind remains correlated with severe fire outcomes. However, the additional explanatory power of dry wind over the predicted destructive condition has proven to be more modest. | Joseph Mitchell | 2024-04-08 | 2024-04-11 | 2024-04-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_009.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--25 Fire Potential Index (FPI) and Ignition Probability Weather (IPW) Enhancements | ACI 23-25 Fire Potential Index and Ignition Probability Weather Enhancements
525 | MGRA | Data Request No. 9 | MGRA_Data Request No. 9 | 3 | MGRA_Data Request No. 9_Q3 | Will this “dry wind” consequence assessment also be couple to driver weather days also characterized by high winds? | PG&E interprets this question to be requesting whether the dry wind definition corresponds to days with drier weather and higher winds. In this case, yes, the dry wind definition is based on relative humidity being lower than a threshold and the wind speed being higher than a threshold. In this way, it does serve to identify dry and windy days. | Joseph Mitchell | 2024-04-08 | 2024-04-11 | 2024-04-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_009.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--25 Fire Potential Index (FPI) and Ignition Probability Weather (IPW) Enhancements | ACI 23-25 Fire Potential Index and Ignition Probability Weather Enhancements
526 | MGRA | Data Request No. 9 | MGRA_Data Request No. 9 | 4 | MGRA_Data Request No. 9_Q4 | Will the “dry wind” weather days be associated with a probability driver also correlated with “dry wind” weather days and if howso. | PG&E interprets this question to ask whether the dry wind days data, used in the development of Wildfire Consequence, is directly used in the development of the probability of ignition sub models. If so, the response is: no, but the same source meteorological wind and humidity observations used in the development of the dry wind days in the wildfire consequence model are used in the development of the probability of ignition sub-models. | Joseph Mitchell | 2024-04-08 | 2024-04-11 | 2024-04-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_009.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--25 Fire Potential Index (FPI) and Ignition Probability Weather (IPW) Enhancements | ACI 23-25 Fire Potential Index and Ignition Probability Weather Enhancements
527 | MGRA | Data Request No. 9 | MGRA_Data Request No. 9 | 5 | MGRA_Data Request No. 9_Q5 | PS-07: Reduce PSPS Impacts to Customers (Section 9.1.5) For the 22k to 13k reduction in customers exposed to PSPS events, how much of the reduction is due to 1) undergrounding 2) Motorized Switch Operations (MSOs), and 3) other factors. | All of the reduction from 22k to 13k is attributed to undergrounding. As mentioned in section B.2.1.1.3 of the 2025 WMP, the number of undergrounding miles for 2025 was adjusted from 550 miles to 330 miles, therefore the reduction in customer events mitigated corresponds proportionally to the decrease in undergrounding miles completed. No customer events mitigated from Motorized Switch Operations (MSO) replacements are expected in 2025 as the program is expected to be completed in 2024. | Joseph Mitchell | 2024-04-08 | 2024-04-11 | 2024-04-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_009.zip | 0 | N/A | 9.1.5 | 9.0 Public Safety Power Shutoff | 9.1.5 Performance Metrics Identified by the Electrical Corporation | 2.1.1.3 PS-07: Reduce PSPS Impacts to Customers
528 | MGRA | Data Request No. 9 | MGRA_Data Request No. 9 | 6 | MGRA_Data Request No. 9_Q6 | Explain how MSO reduces PSPS incidence. | For clarification, Motorized Switch Operator (MSO) devices do not reduce “PSPS incidence,” but rather the scope of customer impact during a PSPS event. While MSO devices were intended to serve as a sectionalizing device, PG&E identified MSO devices as an ignition risk when operated while energized due to the chance of arc flashes. As a result, MSO devices are not operated while energized, but must first be de-energized before they can be operated. If an MSO device is selected for a PSPS event, the next upstream non-MSO device must first be used to temporarily de-energize the MSO device, so that the MSO device can be operated while de-energized. The non-MSO device is closed to energize up to the now-open MSO device. This procedure eliminates the ignition risk from the MSO device but results in a short duration PSPS outage for the customers located between the MSO device and the upstream device. If the MSO device is replaced with a non-MSO device such as reclosers, subsurface equipment, and other vacuum switch equipment approved for current usage, these short duration outage customers will no longer experience any outage during the PSPS event because the replacement devices can be opened directly without needing to utilize an upstream device. | Joseph Mitchell | 2024-04-08 | 2024-04-11 | 2024-04-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_009.zip | 0 | N/A | 9.1.5 | 9.0 Public Safety Power Shutoff | 9.1.5 Performance Metrics Identified by the Electrical Corporation | 2.1.1.3 PS-07: Reduce PSPS Impacts to Customers
529 | MGRA | Data Request No. 9 | MGRA_Data Request No. 9 | 7 | MGRA_Data Request No. 9_Q7 | Does MSO also allow for EPSS to be enabled as a function of weather conditions? | Motor Switch Operator (MSO) devices are not capable of fault protection and therefore are not part of EPSS. As part of the MSO initiative in the WMP, these units are being replaced with either a line recloser, an automated switch, or a manual switch. If the line recloser option is selected, those replaced devices will have EPSS capability and be enabled during EPSS weather conditions. | Joseph Mitchell | 2024-04-08 | 2024-04-11 | 2024-04-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_009.zip | 0 | N/A | 8.1.8.1.1 | 8.1.8 Grid Operations and Procedures | 8.1.8.1.1 Protective Equipment and Device Settings | 2.1.1.3 PS-07: Reduce PSPS Impacts to Customers
530 | MGRA | Data Request No. 9 | MGRA_Data Request No. 9 | 8 | MGRA_Data Request No. 9_Q8 | If not, is EPSS enabled based on weather conditions and if so how? | Yes, EPSS is enabled and disabled based on forecasted weather conditions. EPSS settings are enabled or disabled based on criteria approved by our Wildfire Risk Governance Steering Committee. This criteria is based on 2km-by-2km model outputs from our Fire Potential Index (FPI) model. PG&E’s FPI model is trained to identify localized wildfire risk based on a variety of key risk indicators derived from fire science as well as lessons learned from previous catastrophic wildfires. | Joseph Mitchell | 2024-04-08 | 2024-04-11 | 2024-04-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_009.zip | 0 | N/A | 8.1.8.1.1 | 8.1.8 Grid Operations and Procedures | 8.1.8.1.1 Protective Equipment and Device Settings | 2.1.1.3 PS-07: Reduce PSPS Impacts to Customers
531 | MGRA | Data Request No. 9 | MGRA_Data Request No. 9 | 9 | MGRA_Data Request No. 9_Q9 | Table ACI-PG&E-23-05-3: Ignition mitigation effectiveness For Alt 4 – Covered conductor + EPSS, effectiveness is rated at 78.2%. Alt 9 includes CC + EPSS, but also REFCL and DCD and shows an effectiveness of 65%. How is it possible that adding additional mitigations reduces the effectiveness? If this calculation is in error please provide a corrected value. Perform this as a circuit analysis, not a substation analysis, assuming all circuits are REFCL enabled. | The reported blended average effectiveness for Alt 9 was based on a study focused on a specific subset of circuits where REFCL could be utilized. This same Alt 9 analysis cannot be performed assuming all circuits are REFCL enabled. The REFCL analysis was applied to substations that met the following requirements: • Single voltage 3 wire 12 kV substation; • Minimum of 20 OH miles in HFTD; • Less than 50% of circuit UG; and • Less than 20% of circuit past autobanks. The effectiveness of the other mitigation types (CC Overhead, EPSS, DCD) on the Alt 9 population is less in comparison to that of the full population in the Alt 4 study. Therefore, the overall blended average effectiveness of Alt 9 is lower than Alt 4. | Joseph Mitchell | 2024-04-08 | 2024-04-11 | 2024-04-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_009.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--25 Fire Potential Index (FPI) and Ignition Probability Weather (IPW) Enhancements | ACI 23-25 Fire Potential Index and Ignition Probability Weather Enhancements
532 | MGRA | Data Request No. 9 | MGRA_Data Request No. 9 | 10 | MGRA_Data Request No. 9_Q10 | Please provide the above table ACI-PG&E-23-05-3 under the assumption that Covered Conductor wildfire ignition reduction effectiveness is 85.0%, not 66.4%. | This is not feasible to provide based on the methodology of PG&E’s study. Mitigation effectiveness cannot be predetermined (i.e. 85% overall wildfire ignition reduction effectiveness is not an input). Rather, the average effectiveness value of 66.4% is the result of assessing the aggregated mitigation effectiveness against more the 2,000 modes of failure, each with an effectiveness ranging from 0% to 100%. Much of the benefits of covered conductor overlap the benefits of the operational mitigations, such as EPSS. Because of that, we chose a more granular analysis of outage causes to assign effectiveness to differentiate the multiple combined mitigations so as not to “double count” benefits. | Joseph Mitchell | 2024-04-08 | 2024-04-11 | 2024-04-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_009.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--25 Fire Potential Index (FPI) and Ignition Probability Weather (IPW) Enhancements | ACI 23-25 Fire Potential Index and Ignition Probability Weather Enhancements
533 | MGRA | Data Request No. 9 | MGRA_Data Request No. 9 | 11 | MGRA_Data Request No. 9_Q11 | p. 57 - Non-Underground Mitigations “This consideration of location-specific benefits and risks is consistent with the prior decision-tree approach we used to select projects and mitigations for completion in 2023 to 2025.” In what ways does the new calculation differ from the previous decision-tree based analysis and in what ways does it differ? | PG&E objects to this question on the grounds that it is vague and ambiguous, including that the repetition of the statement “in what ways does [it] differ” may imply that the intent of the question may have not been fully articulated. Nonetheless, PG&E interprets the question as asking for clarity on the difference between the Wildfire Benefit Cost Analysis (WBCA), which we interpret to be the “new calculation” referenced in the question, and the tools used to select system hardening projects prior to the WBCA tool. We have, therefore, answered based on that understanding of the question. PG&E’s system hardening program starts by using a model to determine where (which circuit segments) we should complete wildfire system hardening work. Once a circuit segment is selected, PG&E’s Grid Design engineers use a decision tree to evaluate the sections of that circuit segment to determine the right mitigation approach along the circuit segment. The primary element that has changed over the last few years is the “model” used to select the majority of circuit segments to then be scoped for hardening, for example: • Projects selected using PG&E’s Wildfire Distribution Risk Model (WDRM) v2 identified work located in the top 20% circuit segments, selected solely based on wildfire risk scores, and • Projects selected using WDRM v3 incorporated feasibility factors in combination with wildfire risk scores to create a Wildfire Feasibility Effectiveness (WFE) score. Going forward, the WBCA is an analytical framework that will compute the total lifetime costs and total lifetime benefits of different mitigations, and combinations of mitigations, at the circuit segment level. As discussed in our 2025 WMP update, the WBCA tool incorporates wildfire risk, as well as reliability, public safety, and cost efficiency in accordance with the requirements of SB 884. Reliability and public safety are new inputs to the selection process that is used by the WBCA which informs the selection of hardening projects from these additional inputs. The cost efficiency data incorporated into WBCA is more comprehensive than the feasibility score used in WFE. Cost efficiency accounts for benefits associated with wildfire, public safety, and reliability risk reduction, as well as costs associated with vegetation management, lifecycle maintenance costs/operating expenses of various mitigations. Cost efficiency also includes the upfront capital installation costs which were previously incorporated into the WFE score. Once a project is selected for hardening using the appropriate model as described above, the decision tree was/is used to assess circuit segment factors along the length of the segment to: (a) incorporate the reality that all conditions are not uniform along the length of a circuit segment and different approaches may be necessary within a single circuit segment; and (b) account for additional factors not fully captured by the model used to select projects. These factors include: (1) tree fall-in risk; (2) ingress/egress risk; and (3) PSPS mitigation (see PG&E’s 2023-2025 Base WMP R5 at page 430). In summary, the decision tree approach used by our Grid Engineers to scope hardening projects is very similar from 2023-2025 and into the future. What is changing is our analytical “model” being used to select which circuit segments to harden as the WBCA tool represents a meaningful step forward, incorporating additional inputs (as described above) from the WDRM v2 or WDRM v3/WFE models that were used in the past to select nearly all of the 2023-2025 projects. | Joseph Mitchell | 2024-04-08 | 2024-04-11 | 2024-04-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_009.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--25 Fire Potential Index (FPI) and Ignition Probability Weather (IPW) Enhancements | ACI 23-25 Fire Potential Index and Ignition Probability Weather Enhancements
534 | MGRA | Data Request No. 9 | MGRA_Data Request No. 9 | 12 | MGRA_Data Request No. 9_Q12 | Table ACE PG&E-23-06-01 Please provide the slides presented at these workshops, redacted for any confidential material. | Please reference the table below for presentation materials for the workshops identified. Workshop Title Attachment Name Kickoff and Corrosion Testing Date: May 3, 2023 WMP-Discovery2023-2025_DR_MGRA_009-Q012Atch01.pdf Aging Susceptibility Date: June 12, 2023 WMP-Discovery2023-2025_DR_MGRA_009-Q012Atch02.pdf New Technologies Date: July 17, 2023 WMP-Discovery2023-2025_DR_MGRA_009-Q012Atch03.pdf Maintenance and Inspections Date: July 24, 2023 WMP-Discovery2023-2025_DR_MGRA_009-Q012Atch04.pdf Effectiveness Testing Date: August 7, 2023 WMP-Discovery2023-2025_DR_MGRA_009-Q012Atch05.pdf Workshop Title Attachment Name New Technologies – EFD Date: September 20, 2023 WMP-Discovery2023-2025_DR_MGRA_009-Q012Atch06.pdf New Technologies Date: November 8, 2023 WMP-Discovery2023-2025_DR_MGRA_009-Q012Atch07.pdf | Joseph Mitchell | 2024-04-08 | 2024-04-11 | 2024-04-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_009.zip | 7 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23-06 – Continuation of Grid Hardening Joint Studies | ACI 23-06 Continuation of Grid Hardening Joint Studies
535 | MGRA | Data Request No. 9 | MGRA_Data Request No. 9 | 13 | MGRA_Data Request No. 9_Q13 | Early Fault Detection/Distribution Fault Anticipation Are EFD circuits being deployed on circuits that are being scoped for undergrounding? | PG&E has avoided selecting circuits/circuit segments with known undergrounding schedules for Early Fault Detection (EFD) deployment. | Joseph Mitchell | 2024-04-08 | 2024-04-11 | 2024-04-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_009.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23-07 – Deployment of New Technologies | ACI 23-07 – Deployment of New Technologies
536 | MGRA | Data Request No. 9 | MGRA_Data Request No. 9 | 14 | MGRA_Data Request No. 9_Q14 | What would be the final year that a circuit will be undergrounded that might potentially be implemented with an EFD? | Not applicable, please see the response to Question No. 13 for an explanation. | Joseph Mitchell | 2024-04-08 | 2024-04-11 | 2024-04-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_009.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23-07 – Deployment of New Technologies | ACI 23-07 – Deployment of New Technologies
537 | MGRA | Data Request No. 9 | MGRA_Data Request No. 9 | 15 | MGRA_Data Request No. 9_Q15 | Please provide a list of reportable ignitions for the last two years including the following additional attributes: a. rating system at the time of the ignition (R0, R1, R2, etc) b. whether circuit was implemented with active DCD c. whether circuit was implemented with active EPSS d. whether PSPS was activated anywhere on the system. | Please see attachment “WMP-Discovery2023-2025_DR_MGRA_009-Q015Atch01.xlsx” for the requested information. Please note that for subpart (a), PG&E produces Fire Potential Index (FPI) ratings only for circuits with a Fire Index Area (FIA). | Joseph Mitchell | 2024-04-08 | 2024-04-11 | 2024-04-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_009.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--25 Fire Potential Index (FPI) and Ignition Probability Weather (IPW) Enhancements | ACI 23-25 Fire Potential Index and Ignition Probability Weather Enhancements
538 | MGRA | Data Request No. 9 | MGRA_Data Request No. 9 | 16 | MGRA_Data Request No. 9_Q16 | Please provide a list of outages for the last two years including the following additional attributes: a. rating system at the time of the outage (R0, R1, R2, etc) b. whether circuit was implemented with active DCD c. whether circuit was implemented with active EPSS | Please see attachment “WMP-Discovery2023-2025_DR_MGRA_009-Q016Atch01.xlsx” for the requested information. | Joseph Mitchell | 2024-04-08 | 2024-04-17 | 2024-04-17 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_009.zip | 1 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--25 Fire Potential Index (FPI) and Ignition Probability Weather (IPW) Enhancements | ACI 23-25 Fire Potential Index and Ignition Probability Weather Enhancements
539 | CalPA | Set WMP-42 | CalPA_Set WMP-42 | 1 | CalPA_Set WMP-42_Q1 | Page 10 of PG&E’s 2025 WMP Update states that, for version 4 of PG&E’s Wildfire Consequence Model, PG&E increased the fire simulation time from eight to 24 hours. a) List the reasons why PG&E chose to increase the fire simulation time to 24 hours. b) Is PG&E aware of any potential detrimental effects associated with increasing the fire simulation time from eight to 24 hours? c) If the answer to part (b) is yes, list any such potential detrimental effects. d) What has PG&E done so far to validate the accuracy of 24-hour fire simulations? | a) There were two main drivers for evaluating and eventually utilizing longer fire simulations: 1. Expert consensus. Interveners and the E3 model validation for the WDRM v3 model recommended moving to longer simulation times to capture fire impacts. 2. As outlined in more detail in the response to Request No. 002, there is a slightly more robust relationship between simulation acreage and actual acreage burned in historic fires. b) No. c) Not applicable, please see the response to subpart (b) above. d) As outlined in the response to Request No. 002, there is a slightly more robust relationship between simulation acreage and acreage burned in historic fires. | Holly Wehrman | 2024-04-09 | 2024-04-12 | 2024-04-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_042.zip | 0 | N/A | 6.2.2.2 | 6.0 Risk Methodology and Assessment | 6.2.2.2 Consequence | B.1.1. WDRM v4
540 | CalPA | Set WMP-42 | CalPA_Set WMP-42 | 2 | CalPA_Set WMP-42_Q2 | Page 1021 of PG&E’s 2023-2025 WMP R4 states, in response to ACI PG&E-22-05, In general, 24-hour simulations result in higher impacts as simulated fires are more likely to reach highly populated areas despite decreasing reliability on the weather forecasts as time progresses, and unknown suppression effectiveness over time. Sensitivity analysis is continuing, and PG&E will be able to provide results in 2023 that quantify the effectiveness of shorter versus longer simulation durations. a) Describe the result of the sensitivity analysis discussed above. b) Provide any written results, reports, or other output of the sensitivity analysis discussed above. | a) PG&E ran comparisons of both 24-hour and 8-hour simulations for historical fires in the VIIRS dataset (fires detected from space in California above latitude 35.5, not restricted to fire season). The plot below is a comparison between actual acreage burned measured via satellite (y axis) against simulated acreage burned by Technosylva (x axis) for 24-hour and 8-hour simulations. Every dot represents a historic fire and a paired Technosylva simulation. The correlation between acres burned and Technosylva simulated acres burned is slight. Please see below for the output of this analysis. By binning the simulation acreage (x) values and averaging the historical acres (y) burned per bin, we can discern a more nuanced relationship. See below. The trend in the orange dots (24-hr simulation) is smoother than the trend in the blue dots (8-hr) especially where the y-axis predictions rise above the blue line. WFC takes this to mean that 24-hr TS simulations >1000 acres are more reliably predictive of larger historical fires. This is the primary support for utilizing 24-hour simulations in the WFC. b) Please see response to subpart a) above. | Holly Wehrman | 2024-04-09 | 2024-04-12 | 2024-04-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_042.zip | 0 | N/A | 6.2.2.2 | 6.0 Risk Methodology and Assessment | 6.2.2.2 Consequence | B.1.1. WDRM v4
541 | CalPA | Set WMP-42 | CalPA_Set WMP-42 | 3 | CalPA_Set WMP-42_Q3 | Page 7 of PG&E’s 2025 WMP Update states, with regard to PG&E’s distribution event probability models, “Significant efforts were made to improve asset, ignitions, and outage data quality.” List and explain the significant efforts discussed above. | As mentioned on page 7 of PG&E’s 2025 WMP, the following is a more detailed list of specific data quality improvements that are a result of the continuous effort to improve the quality and utilization of model data for assets, ignitions, and outages. Asset data quality improvements included: • Tracing asset failures and asset history back in time to identify the asset that failed and its characteristics. • Gathering asset information related to causal pathways as recommended by Subject Matter Experts (SMEs). o For support structures, this included: • Incorporating pole remaining strength as a feature in the model. o For primary conductors, this included: • Gathering distribution load flow software outputs. • Shifting conductor material and size types from categorical model inputs to continuous model inputs (i.e. conductor diameter, conductor strength, and conductor weight). • Using LiDAR data and splice observations where available in HFTD areas. • Incorporating Finite Element Analysis (FEA) model developed by the Applied Technology Services (ATS) team that assessed fault current and wind-driven line slap scenarios. • Including open tags. o For dynamic protective devices, fuses, switches, capacitor banks, and voltage regulators: • Gathering asset attributes as captured in EDGIS over time (2016-2022). • Including open tags. o Creating methodologies to estimate asset age when missing. • Reporting asset data quality issues to the Asset Knowledge Management team to resolve. Ignition data quality improvements were primarily focused on: • Enhancing wildfire ignition data for use in the wildfire consequence model. • Reporting data quality issues back to the Ignitions Investigation team to resolve. Outage data quality improvements included: • Improving the incorporating vegetation outage report latitude & longitude locations to improve outage fault locations. • Utilizing latitude & longitude locations from notification repair records where available to improve outage fault locations. • Assigning historical equipment failure-caused outages to the equipment ID of the asset that failed. • Working with Distribution Asset Strategy to help improve field personnel reporting of outages. • Shifting to a data pipeline that updates daily to categorize emergent outages to the appropriate model. • Developing 100% unit test coverage of data pipeline supporting functions to enhance reliability of the data. | Holly Wehrman | 2024-04-09 | 2024-04-12 | 2024-04-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_042.zip | 0 | N/A | 6.2.2.2 | 6.0 Risk Methodology and Assessment | 6.2.2.2 Consequence | B.1.1. WDRM v4
542 | CalPA | Set WMP-42 | CalPA_Set WMP-42 | 4 | CalPA_Set WMP-42_Q4 | Table PG&E-B.1.1-1 on page 8 of PG&E’s 2025 WMP Update indicates that WDRM v4 includes wind direction in its vegetation models. a) Describe how wind direction is incorporated in the vegetation models in WDRM v4. b) List the data sources that PG&E uses to incorporate wind direction into its risk model. c) Describe the benefits of incorporating wind direction into the risk model. | The basis for incorporating wind direction comes from the paper “Towards Simulation and Risk Assessment of Weather-Related Outages” by Rui Yao found here: https://web.eecs.utk.edu/~kaisun/papers/2018-TSG_Yao_Weather.pdf Within this paper, a probability density function is defined (equation 14) which quantifies the probability per angle that anything from a spatial location, in this case a tree’s location, will project itself into a conductor given the conductor’s normal vector and direction of the wind. This probability density is integrated along the conductor, via the angle, to calculate the total probability of strike given a wind’s direction, the tree’s location, and the location of the conductor segment. Due to the unavailability of LiDAR for the distribution system, Planet’s canopy height raster (Fall 2020) is used, the snapshot of the distribution grid (v4) and an average distribution line height of 8 meters to determine which of the pixels within the canopy height raster which can fall into a conductor and, approximately, which pixels kinematically have a chance of branches/debris from the tree falling into a conductor. For wind vectors, Meteorology’s POMMS system is used. The data is in 2 km by 2 km cells and communicates the wind vector components at 10m and the roughness length to easily calculate speeds at heights other than 10m. This data occurs in one-hour intervals and covers the years 2015 to 2021. Only the fire season and wind speeds above 6.7 meters per second is considered. Please note that the value 6.7 m/s was the value that the odds of a tree falling in a storm are equal to a tree falling not in a storm studied in the paper. The covariate calculation is as follows: The grid is divided into segments of 5 meters in length. For each 5-meter segment, and for each strike tree for that segment, the total probability along that 5-meter segment is calculated for all one-hour intervals of wind speeds greater than 6.7 m/s. All calculated probabilities are summed over that time for each tree-segment pair. A second quantity is calculated by weighting each hourly probability by the increased odds of wind damage during the storm by turning the log-odds (equation 13) into a probability, then multiply by the directional probability and finally multiplying by the inverse distance from the vegetation pixel to the 5-meter segment before summing over time. The total wind direction index is then found for each 5-meter segment by summing over all trees that influence it. Finally, each 5-meter segment is assigned to a pixel of the 100-meter-by100-meter resolution raster used in the WDRM and all segment’s indices found within a single pixel are summed. Two more indices are formed by taking the above two quantities and dividing by the total number of trees within the 100-meter pixel for a total of four new wind directional covariates. Wind is a vector quantity and has magnitude and direction. Magnitude has been present in the WDRM before but has been a low-value covariate. The reason for this is that higher speeds don’t necessarily mean higher risk when the wind direction is pointing away from an asset and the tree is oriented in location which is not impactful to the line. | Holly Wehrman | 2024-04-09 | 2024-04-12 | 2024-04-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_042.zip | 0 | N/A | 6.2.1 | 6.0 Risk Methodology and Assessment | 6.2.1 Risk and Risk Component Identification | B.1.1. WDRM v4
543 | CalPA | Set WMP-42 | CalPA_Set WMP-42 | 5 | CalPA_Set WMP-42_Q5 | Page 16 of PG&E’s 2025 WMP Update states, “in the WTRM v2 update, we corrected this overly conservative estimate by applying a remaining strength of 92% (equivalent to Condition Code 2) to reinforced poles, in order to provide more accurate results.” State the basis for applying a remaining strength of 92% to reinforced poles. | The WTRM uses condition codes assigned by an inspector based on ground and visual inspections of the pole. The condition codes range from 1 = no visible damage, to 3 = moderate damage, to 5 = immediate safety concern. The framework estimates the remaining strength from the condition codes using a simple linear relationship between condition codes and remaining strength. The translation line is anchored at two points, condition code = 1 is translated to remaining strength = 100% (no damage) while a condition code = 3 is translated to remaining strength = 67% or 2/3rd. The strength ratio of 2/3rd is based on California General Order 95 which is a threshold for repair or replacement of a component. The two anchor points define the translation and other condition codes are translated either by linear interpolation or linear extrapolation. Based on input from SME workshops, the strength degradation associated with a condition code of 2 has been reduced by half from 1/6th to 1/12th. The consensus feedback from the workshops was that a 1/6 strength reduction was unrealistically conservative for elements that exhibit only cosmetic damage (e.g. light surface corrosion). Condition Code Remaining Strength (%) 1 100 2 92 3 67 4 50 5 33 As noted in the question, the 92% remaining strength was intended to be consistent with a condition code of 2, which is typically used for a less than perfect condition that does not require repair. This was considered slightly conservative for a reinforcement that is as strong as the pole, which was Asset Strategy’s understanding of the intent of pole reinforcements by their vendor. PG&E continues to evaluate this assessment. | Holly Wehrman | 2024-04-09 | 2024-04-12 | 2024-04-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_042.zip | 0 | N/A | 6.2.2.2 | 6.0 Risk Methodology and Assessment | 6.2.2.2 Consequence | B.1.2. WTRM v2
544 | CalPA | Set WMP-42 | CalPA_Set WMP-42 | 6 | CalPA_Set WMP-42_Q6 | Page 17 of PG&E’s 2025 WMP Update states, “When viewed on a line weighted basis, the relative average risk of each transmission line can be viewed for insights. It should be noted that these mile weighted values will tend to highlight short lines such as taps.” a) Does PG&E plan to correct for the fact that mile weighted values tend to highlight short lines? b)If the answer to part (a) is yes, explain the methods PG&E plans to use. c) If the answer to part (a) is no, explain why not. | a. No, PG&E does not plan to attempt to correct the fact the mile weighted values can tend to highlight shorter lines. b. Not applicable. c. The probability of failure (pf) and risk in the WTRM framework is calculated at the level of each structure. This pf/risk value can then be used to assign an average pf\risk value at the transmission line level which would be average of pf/risk values across all structures on the transmission line. While the model interface includes line level values (average, sum and max) for reference and the granularity of the model at the structure level also enables calculation of mile weighted values, these values are only used for reference. As the note indicates, the values are not always directly actionable without taking into account the fact that any such analysis can result in highlighting lines that are short. During the Asset Management planning process, the values at the structure level are mainly used for making decisions on asset repair/replacement. | Holly Wehrman | 2024-04-09 | 2024-04-12 | 2024-04-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_042.zip | 0 | N/A | 6.2.2.2 | 6.0 Risk Methodology and Assessment | 6.2.2.2 Consequence | B.1.2. WTRM v2
545 | CalPA | Set WMP-42 | CalPA_Set WMP-42 | 7 | CalPA_Set WMP-42_Q7 | Page 24 of PG&E’s 2025 WMP Update states that PG&E is adjusting target PS-07 (Reduce PSPS Impacts to Customers) in 2025 downward by 40% to account for a 40% decrease in underground miles. Does PG&E expect a similar reduction in the number of EPSS customer events mitigated in 2025? Explain your answer. | While PG&E anticipates EPSS outage volume would reduce commensurately with reduced overhead line exposure, specific EPSS-related outage targets specifically considering reduced UG work have not been calculated. As risk is the primary driver of PG&E’s approach to selecting sites to underground, it is possible portions of a circuit versus the entire circuit may be scoped for undergrounding. As such, portions of the circuit remaining in High Fire Risk Areas (HFRAs) and EPSS buffer areas may continue to be protected by EPSS-capable devices and would be enabled when criteria are met. It is possible a fault may occur downstream of one of these devices when enabled, resulting in an outage impacting downstream customers, regardless of undergrounding status. If undergrounding were to replace all HFRA and EPSS buffer overhead line exposure of a circuit, the circuit would be removed from EPSS scope which would significantly reduce EPSS enablement. Opportunities for full undergrounding continue to be evaluated during project scoping, focusing on undergrounding in areas where it can be most beneficial in reducing wildfire risk as well as PSPS and EPSS impact reduction for customers and critical facilities. | Holly Wehrman | 2024-04-09 | 2024-04-12 | 2024-04-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_042.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--14 Effectiveness Analysis for EPSS Including Implementation of DCD | ACI 23-14 Effectiveness Analysis for EPSS
546 | CalPA | Set WMP-42 | CalPA_Set WMP-42 | 8 | CalPA_Set WMP-42_Q8 | Page 29 of PG&E’s 2025 WMP Update states that PG&E’s 2025 forecast capital expenditure associated with covered conductor installation will increase by a factor of 5.8, from $41.4 million to $241.6 million. The updated Table PG&E-8.1.2-1 on page 402 of PG&E’s 2023-2025 WMP R5 redline indicates that, in 2025, the mileage associated with covered conductor installation will increase by a factor of 4, from 50 miles to 200 miles. Please explain why PG&E’s capital forecast for 2025 will increase by a factor of 5.8 while the mileage will increase by a factor of 4. | The primary driver for the capital expenditure increase ratio being larger than the mileage increase ratio is the allocation of future year readiness costs. For any given year, the budget allocation includes costs for the current year construction costs and readiness/planning costs (Scoping, Design, Permitting, Pre-Construction activities) for future year projects. For the original 2025 capital forecast in the 2023 WMP, approximately $35.7 million was allocated for 2025 construction costs and $5.7 million for future year readiness. For the updated 2025 capital forecast, approximately $184.6 million was allocated for 2025 construction costs and $57.1 million for future year readiness. The significant increase in future year readiness cost between the original and updated forecast is due to the 2026 mileage differences (50 miles in the original 2023 WMP and 348 miles in the update). The secondary driver for the capital expenditure increase ratio being larger than the mileage increase ratio is the change in the unit cost assumption. In the 2023 WMP, the OH unit costs used in the capital forecast model was $0.83 million/mile which was based on completed 2021 and 2022 projects. For the update, the unit cost was updated to $1.00 million/mile based on completed 2023 projects. | Holly Wehrman | 2024-04-09 | 2024-04-12 | 2024-04-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_042.zip | 0 | N/A | 4.3 | 4.0 Overview of WMP | 4.3 Proposed Expenditures | 2.3 Expenditures
547 | CalPA | Set WMP-42 | CalPA_Set WMP-42 | 9 | CalPA_Set WMP-42_Q9 | In comparison to PG&E’s WDRM v3, does WDRM v4: a) Move 10 percent or more of ignition risk into or out of the top ignition risk circuits, segments, or spans? If yes, please provide the data in the format of Table 1-1 in section 1.1.1 of the 2025 Wildfire Mitigation Plan Update Guidelines for both WDRM v3 and v4. b) Move 10 percent or more of PSPS risk into or out of the top PSPS risk circuits, segments, or spans? If yes, please provide the data in the format of Table 1-2 in section 1.1.1 of the 2025 Wildfire Mitigation Plan Update Guidelines for both WDRM v3 and v4. | PG&E clarifies that the referenced Table1-1 in Section 1.1.1 was not provided in the 2025 update, as directed by the Office of Energy and Infrastructure Safety (OEIS) since it is not intended to be operationalized in 2025. Furthermore, the requested data pertains to the WDRM v4 which was recently approved for use in developing workplans that will be described in PG&E’s 2026-2028 WMP. As such the requested data were not used in the development of workplans described in PG&E’s 2025 WMP update. a. Yes, 10 percent or more of WDRM v3 circuit segments move out of the top 10 percent of circuit segments in WDRM v4 when prioritizing by average circuit segment wildfire risk. Please reference “WMP-Discovery2023- 2025_DR_CalAdvocates_042-Q009Atch01.xlsx” for the requested data. b. The PSPS model is separate from the WDRM and has not been updated since PG&E’s 2024 WMP. As such the population of top 10 percent of PSPS risk has not changed. ATTACHMENT: WMP-Discovery2023-2025_DR_CalAdvocates_042-Q009Atch01.xlsx | Holly Wehrman | 2024-04-09 | 2024-04-12 | 2024-04-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_042.zip | 1 | N/A | 6.2.1 | 6.0 Risk Methodology and Assessment | 6.2.1 Risk and Risk Component Identification | B.1.1. WDRM v4
548 | CalPA | Set WMP-43 | CalPA_Set WMP-43 | 1 | CalPA_Set WMP-43_Q1 | There does not appear to be an option of covered conductor with both EPSS and DCD. a) Did PG&E consider an alternative that consists of covered conductor with EPSS and DCD? b) If the answer to part (a) is yes, why is this option not included as one of the possible alternatives in the WBCA? c) If the answer to part (a) is no, why not? | a) Yes, PG&E did consider an alternative option consisting of covered conductor with both EPSS and DCD, which is provided in Table ACI-PG&E-23-05-3 as, “Alt. 4 – Covered conductor (CC) Overhead with EPSS.” Please note, this option is not labeled in the table as DCD enabled; however, all EPSS options include DCD. b) Please see the response to subpart (a). The Alt. 4 option referenced above is included in one of the possible alternatives in the WBCA. c) Please see the response to subpart (a). | Holly Wehrman | 2024-04-12 | 2024-04-17 | 2024-04-17 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_043.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--05 – Updating Grid Hardening Decision Making | ACI 23-05 Updating Grid Hardening Decision Making
549 | CalPA | Set WMP-43 | CalPA_Set WMP-43 | 2 | CalPA_Set WMP-43_Q2 | The blended average effectiveness for alternative 9 (REFCL with covered conductor, EPSS, and DCD) is lower than alternative 4 (covered conductor with EPSS). a) Why does the effectiveness for alternative 9 appear lower than alternative 4, although alternative 9 appears to include more mitigation techniques? | The reported blended average effectiveness for Alt 9 was based on a study focused on a specific subset of circuits and associated substations where REFCL could be utilized. Please see the response to Request No. 6 for details on this study. The effectiveness of Alternative 9 is less in comparison to that of the full population in the Alternative 4 study primarily due to the following reasons: (1) Different study periods were used to determine the outages addressed by each alternative based on data availability (2017 – 2020 for Alt. 9 REFCL and 2015- 2022 for Alt. 4), and (2) The Alt 9 effectiveness results were based on 133 substations vs. 435 substations (that were split into CPZ’s) studied in Alt 4. The blend of outages and mitigations assessed for each alternative resulted in different overall effectiveness values. | Holly Wehrman | 2024-04-12 | 2024-04-17 | 2024-04-17 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_043.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--05 – Updating Grid Hardening Decision Making | ACI 23-05 Updating Grid Hardening Decision Making
550 | CalPA | Set WMP-43 | CalPA_Set WMP-43 | 3 | CalPA_Set WMP-43_Q3 | List the assumptions unique to each of the ten alternatives. | The assumptions for each of the 10 alternatives are as follows. Alt. 1 – Baseline There are no assumed savings or ignition reduction in the Baseline scenario. Alt. 2 – Underground Primary All primary overhead outages for lines that are undergrounded are mitigated, 100% of ignition risk is reduced. Secondary/service conductor phase-to-phase outage ignition reduction is significant, however, there is still a chance for contact failure. Secondary/service conductor phase-to-ground ignition reduction is less than average. No additional ignition risk reduction is achieved via enhanced settings. Alt. 3 – Underground All All primary and secondary overhead outages for lines that are undergrounded are mitigated, 100% of ignition risk is reduced. No additional ignition risk reduction is achieved via enhanced settings. Alt. 4 – Covered Conductor (CC) Overhead with EPSS and DCD Phase-to-phase outage ignition risk is mostly reduced, but overhead construction still leaves potential for ignition. Phase-on-ground and line-to-ground outage ignition reduction was less than average (40%). Splice/jumper failure ignition risk is mostly reduced, but overhead construction still leaves potential for ignition. Pole/crossarm failure ignition risk reduction is significant, but there is still a chance for contact failure. Secondary/service conductor phase-to-phase outage ignition risk reduction is significant but there is still a chance for contact failure. Secondary/service conductor phase-to-ground outage ignition risk reduction was less than average. Additional ignition risk mitigation is achieved via enhanced settings. Alt. 5 – Bare Conductor Rebuild with EPSS and DCD Replacing overhead conductor, including removing splices & replacing jumpers, reduced most of the risk of those conductor ignition types, however, there is still potential for ignition. There is no phase-to-phase and phase-to-ground outage ignition reduction. Additional ignition risk mitigation is achieved via enhanced settings. Alt. 6 – Line Removal with Remote Grid All primary overhead outages are mitigated, there are no overhead ignition events. Secondary/service conductor phase-to-phase outage ignition risk reduction is significant, however, there is still a chance for contact failure. Secondary/service conductor phase-to-ground ignition risk reduction is less than average. There are no additional ignition reductions achieved via enhanced settings. Alt. 7 – EPSS including downed conductor detection (DCD)/Partial Voltage (with bare conductor) Phase-to-phase outage ignition risk is mostly reduced, but overhead construction still leaves potential for ignition. Phase-on-ground and line-to-ground outage ignition reduction was less than average (40%). No effectiveness savings for secondary/service. Alt. 8 – EPSS and PSPS (with bare conductor) The analysis for alternative 8 varies from the prior 7 alternatives due to the inclusion of PSPS. This is because unplanned outages cannot occur simultaneously to pro-active PSPS de-energization. Instead, alternative 7 was used as the basis for step 1 of the analysis to establish the effectiveness of bare conductor with EPSS as 60.4%. Subsequently, the observed effectiveness of PSPS, 78%, was added as an incremental reduction to the residual risk post-alternative 7. The resulting calculation is shown below: Effectiveness = 60.4% + 78% x (100%-60.4%) = 91.3% Alt. 9 – Rapid Earth Fault Current Limiter (REFCL), CC Overhead, EPSS and DCD REFCL only mitigates risk for phase to ground faults. REFCL Transient Outage (90%) – Transient type faults that the three second delay would prevent from impacting the system. Savings also applied to unknown cause outages with line-to-ground fault targets. Additionally, with instantaneous setting enabled REFCL Single Line to Ground 80% effective, REFCL Double Line to Ground faults 65% effective. Additionally, please see the response to Request No. 6 for additional details of high-level bank screening assumptions. Covered Conductor Rebuild – New The analysis for Covered Conductor Rebuild – New mirrors the baseline assumptions of Alternative 4 without considering EPSS/DCD | Holly Wehrman | 2024-04-12 | 2024-04-17 | 2024-04-17 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_043.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--05 – Updating Grid Hardening Decision Making | ACI 23-05 Updating Grid Hardening Decision Making
551 | CalPA | Set WMP-43 | CalPA_Set WMP-43 | 4 | CalPA_Set WMP-43_Q4 | The table notes, “All of these effectiveness values represent a blended average effectiveness at the circuit segment level with the exception of ‘Alt. 9 – REFCL, CC Overhead, EPSS and DCD’ which is a substation effectiveness score. Not all substations are capable of having REFCL applied, and it cannot be isolated to a circuit segment only.” a) Explain the difference in “substation effectiveness score” and “blended average effectiveness at the circuit segment level.” b) Does alternative nine assume that, for circuits where REFCL cannot be applied to the substation, there are no mitigations applied? c) If the answer to part (b) is yes, state the basis for this assumption. d) Describe how PG&E would implement alternative 9 on circuits served by substations where REFCL could be applied. e) Describe how PG&E would implement alternative 9 on circuits served by substations where REFCL could not be applied. | a) “Substation effectiveness score” starts with a pass/fail preliminary review. All requirements for REFCL must be met to pass. The preliminary screening requirements are: o Single voltage 3 wire 12 kV substation; o Minimum of 20 OH miles in HFTD; o No Autotransformer located inside the substation; o The total charging current not exceeding 167 Amps for each Distribution Transformer Bank in a substation; and o Less than 20% of circuit mileage past autotransformers outside of the substation Blended average effectiveness refers to the average effectiveness of REFCL based on weather days with instantaneous off/on. b) For substations where REFCL cannot be applied due to technical feasibility, we excluded these from the study all together. Therefore, Alternative 9 only shows effectiveness on substations that met the high-level requirements for REFCL implementation. c) The substations that were excluded were not included in the base dataset for the REFCL effectiveness calculation. d) To implement REFCL on these circuits, additional engineering review of the substation layout would be performed to ensure adequate room for installation of the REFCL equipment and review of substation and distribution equipment ratings to identify necessary upgrades to allow for REFCL operation. REFCL would be applied independently of other mitigations. Additional CPZ level review would be needed to determine which segments should receive covered conductor and which should include underground in a blend such that we don’t compromise REFCL. e) PG&E would not implement alternative 9 on substations that do not meet the preliminary review for REFCL requirements. These substations would be evaluated for Alternatives 1-8. | Holly Wehrman | 2024-04-12 | 2024-04-26 | 2024-04-17 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_043.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--05 – Updating Grid Hardening Decision Making | ACI 23-05 Updating Grid Hardening Decision Making
552 | CalPA | Set WMP-43 | CalPA_Set WMP-43 | 5 | CalPA_Set WMP-43_Q5 | Alternative 8 is the only alternative that appears to include PSPS. a) Is PSPS considered in any of the other alternatives? b) Why is the effectiveness for alternative 8 higher than similar alternatives that appear to include more mitigation techniques? c) If the answer to part (a) is no, why not? | a) No, PSPS is not considered in any of the other alternatives. b) This effectiveness value was calculated in a different manner from others in the study. For alternative 8, the observed effectiveness of PSPS (78%) was applied to the residual risk post-alternative 7. This resulted in an effectiveness of: 60.4% + 78% x (100%-60.4%) = 91.3%. With the exception of alternatives 8 & 9, each effectiveness value was calculated based on each mitigation’s expected effectiveness in preventing an ignition resulting from over 2,000 unplanned failure modes (outage types) captured in PG&E’s historical HFTD outage dataset between 2015 and 2022. The study for PSPS cannot be completed in this same manner because an unplanned outage cannot occur simultaneously to pro-active PSPS de-energization. | Holly Wehrman | 2024-04-12 | 2024-04-17 | 2024-04-17 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_043.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--05 – Updating Grid Hardening Decision Making | ACI 23-05 Updating Grid Hardening Decision Making
553 | CalPA | Set WMP-43 | CalPA_Set WMP-43 | 6 | CalPA_Set WMP-43_Q6 | The table notes, “Not all substations are capable of having REFCL applied, and it cannot be isolated to a circuit segment only.” a) How many substations does PG&E have that serve circuit segments within its HFTD/HFRA? b) How many of the substations in your response to part (a) are not capable of having REFCL applied? c) Provide a list of the substations in part (b). For each substation, state the reasons why REFCL cannot be applied. d) If PG&E has not conducted the analysis necessary to respond to parts (b) and (c) in full, please explain why not. | a) Approximately 435 distribution substations serve circuit segments within HFTD/HFRA. b) After preliminary screening, 302 of these distribution substations are not feasible for REFCL deployment. c) Please see attachment WMP-Discovery2023-2025_DR_CalAdvocates_043- Q006Atch01.xlsx, which includes a list of all substations within an HFTD/HFRA (column A). Column B (Pass/Fail) denotes if the substation meets (Pass) or does not meet (Fail) the requirements where REFCL can or cannot be applied. Substations that are categorized as not feasible (Fail) in the analysis are due to one or a combination of the following reasons below: • Column C (kV): Connected circuits are not 12 kV; • Column D (3 Wire or 4 Wire): Substations have 4-wire multi-grounded distribution circuits connected to the substation or a mix of connections. • Column E (HFTD Miles): Total HFTD/HFRA circuit miles is less than twenty miles; • Column F (Auto in the Sub): Autotransformer located inside the substation. • Column G (Field Auto Analysis): Circuit mileage downstream of autotransformers is greater than twenty percent; and • Column I (Coil Charge Amps): The total charging current exceeds 167 Amps, for each Distribution Substation bank (number of banks per substation outlined in Column H). The Coil Charge Amps are calculated as an alternative way to measure the proportion of a circuit underground (less than 50% of circuit is underground). d) Not applicable, please see the responses provided in subparts (b) and (c) above. | Holly Wehrman | 2024-04-12 | 2024-04-26 | 2024-04-17 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_043.zip | 1 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--05 – Updating Grid Hardening Decision Making | ACI 23-05 Updating Grid Hardening Decision Making
554 | CalPA | Set WMP-43 | CalPA_Set WMP-43 | 7 | CalPA_Set WMP-43_Q7 | The table lists the assumption, “Mitigation effectiveness for other Environmental caused outages: None for Overhead and All for Underground.” State the basis for this assumption. | The referenced table should not have reflected “None for Overhead and All for Underground” for mitigation effectiveness for other environmental caused outages. Some outage combinations did have a savings assigned in the final study, these were mostly related to overhead transformer equipment failures where enhanced safety settings or overhead hardening would mitigate risk. The environmental/external basic cause is assigned to an outage during a significant weather or environmental event. Overhead construction would still be susceptible to earthquakes, erosion, lightning and ice events. The enhanced safety settings and overhead hardening would still apply for transformer and equipment failure related outages and reduce the chance of an ignition for some environmental/external outages. | Holly Wehrman | 2024-04-12 | 2024-04-26 | 2024-04-17 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_043.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--05 – Updating Grid Hardening Decision Making | ACI 23-05 Updating Grid Hardening Decision Making
555 | CalPA | Set WMP-43 | CalPA_Set WMP-43 | 8 | CalPA_Set WMP-43_Q8 | The table lists the assumption, “Analysis assumes no Overhead degradation for life of the asset.” a) State the basis for this assumption. b) Does PG&E have plans to include overhead degradation of assets in its mitigation effective analysis in the future? c) How does the WBCA consider benefits and costs over the lifetime of the asset if the analysis assumes no overhead degradation? | a) PG&E chose to consistently assume no degradation of assets in each effectiveness calculation. Given that the book life of overhead versus underground assets is comparable, a degradation factor was not considered necessary within the analysis. b) PG&E does not currently have plans to integrate degradation of assets into effectiveness analyses. c) The net present value of installation costs plus expected lifetime operations and maintenance costs are considered in the WBCA. Similarly, the net present value of risk reduction benefits is considered over the expected life of the asset. | Holly Wehrman | 2024-04-12 | 2024-04-17 | 2024-04-17 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_043.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--05 – Updating Grid Hardening Decision Making | ACI 23-05 Updating Grid Hardening Decision Making
556 | CalPA | Set WMP-43 | CalPA_Set WMP-43 | 9 | CalPA_Set WMP-43_Q9 | The table lists the assumption, “EPSS and DCD are only active when conditions are greater than R1.” a) State the basis for this assumption. b) Are weather events an applicable attribute in the outage combinations used in PG&E’s mitigation effectiveness assessments? c) Please provide a list of all applicable attributes to be used in outage combinations. | a) EPSS and DCD settings are not engaged in the system when the FPI rating is R1, which forms the basis for this assumption. However, the calculations behind engaging EPSS are complex and, for more information, please see our Base 2023- 2025 WMP, R5 (April 2, 2024) on page numbers 570-571 and our 2022 Revised WMP (July 26, 2022) on page numbers 848-852.1 b) No, a specific weather attribute is not directly included in the outage combination analysis. c) For alternative 1-9, each considered the basic cause, supplemental cause, failed/involved equipment, and equipment condition. Additionally, Alt 9 considered the type of outage i.e., phase-to-phase, single line-to-ground, and double line-toground to distinguish REFCL’s impact as it has a specific effectiveness for each fault type. The FPI rating was considered in the analysis to distinguish when specific setting configurations would be enabled for REFCL. | Holly Wehrman | 2024-04-12 | 2024-04-17 | 2024-04-17 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_043.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--05 – Updating Grid Hardening Decision Making | ACI 23-05 Updating Grid Hardening Decision Making
557 | CalPA | Set WMP-43 | CalPA_Set WMP-43 | 10 | CalPA_Set WMP-43_Q10 | Page 66 of PG&E’s 2025 WMP Update states, “The Joint Utilities have met monthly in 2023 to discuss the results of recorded and estimated effectiveness for covered conductor.” a) Provide the results of recorded effectiveness for covered conductor that were discussed in 2023 for each of the Joint Utilities. b) Provide the results of estimated effectiveness for covered conductor that were discussed in 2023 for each of the Joint Utilities. c) List any other findings from the monthly meetings in 2023 noted above. | a) Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_043- Q010Atch01.pdf” for the Joint IOU Covered Conductor Working Group Report, which includes the results of recorded and estimated effectiveness for covered conductors discussed during 2023 monthly Joint Utility meetings. b) Please see the response to subpart (a) for the requested information. c) PG&E is not aware of additional findings outside of those in the Joint IOU Covered Conductor Working Group Report, identified in subpart (a). | Holly Wehrman | 2024-04-12 | 2024-04-17 | 2024-04-17 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_043.zip | 1 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23-06 – Continuation of Grid Hardening Joint Studies | ACI 23-06 Continuation of Grid Hardening Joint Studies
557 | CalPA | Set WMP-43 | CalPA_Set WMP-43 | 10(s) | CalPA_Set WMP-43_Q10(s) | Cal Advocates requested results of meetings held in 2023 regarding the effectiveness for covered conductor. PG&E’s response appears to be identical to the Joint IOU CC report from its 2023-2025 Base WMP (2023-03-27_PGE_2023_WMP_R0_Appendix D ACI PG&E-22-11_Atch01.pdf, provided to OEIS March 2023), and does not include results of meetings held in 2023. • Please verify whether PG&E possesses documents responsive to question 10 that include the results of recorded and estimated effectiveness for covered conductor based on meetings held in 2023. • If yes, please provide those in response to this data request. | Per the supplemental request from Holly Wehrman requested on April 19, 2024: Cal Advocates requested results of meetings held in 2023 regarding the effectiveness for covered conductor. PG&E’s response appears to be identical to the Joint IOU CC report from its 2023-2025 Base WMP (2023-03- 27_PGE_2023_WMP_R0_Appendix D ACI PG&E-22-11_Atch01.pdf, provided to OEIS March 2023), and does not include results of meetings held in 2023. • Please verify whether PG&E possesses documents responsive to question 10 that include the results of recorded and estimated effectiveness for covered conductor based on meetings held in 2023. • If yes, please provide those in response to this data request. PG&E responds as follows: PG&E included the results of the covered conductor working group in the 2023-2025 WMP Update located on pages 64-67 of the PDF. PG&E does not possess materials in addition to what was provided in the 2025 WMP Update. a) Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_043- Q010Atch01.pdf” for the Joint IOU Covered Conductor Working Group Report, which includes the results of recorded and estimated effectiveness for covered conductors discussed during 2023 monthly Joint Utility meetings. b) Please see the response to subpart (a) for the requested information. c) PG&E is not aware of additional findings outside of those in the Joint IOU Covered Conductor Working Group Report, identified in subpart (a). | Holly Wehrman | 2024-04-19 | 2024-04-24 | 2024-04-24 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_043.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23-06 – Continuation of Grid Hardening Joint Studies | ACI 23-06 Continuation of Grid Hardening Joint Studies
558 | CalPA | Set WMP-43 | CalPA_Set WMP-43 | 11 | CalPA_Set WMP-43_Q11 | Pages 66-67 of PG&E’s 2025 WMP Update list three workshops the Joint Utilities held with Energy Safety: June 2023 Distribution Fault Anticipation, July 2023 Early Fault Detection, August 2023 REFCL. a) Provide a copy of any materials prepared by PG&E for each of the three workshops. b) Provide a copy of any reports, minutes, recordings, or other output of the three workshops. c) List any findings from each of the three workshops. d) List any action items PG&E took on from each of the three workshops. | a) Please see the table below for presentation materials for the workshops identified. Workshop Date & Title Attachment Name June 2023 Distribution Fault Anticipation (DFA) WMP-Discovery2023-2025_DR_CalAdvocates_043- Q011Atch01.pdf WMP-Discovery2023-2025_DR_CalAdvocates_043- Q011Atch02.pdf July 2023 Early Fault Detection (EFD) WMP-Discovery2023-2025_DR_CalAdvocates_043- Q011Atch03.pdf August 2023 Rapid Earth Fault Current Limiter (REFCL) WMP-Discovery2023-2025_DR_CalAdvocates_043- Q011Atch04.pdf b) No reports, minutes, recordings were taken or prepared at the referenced workshops. Please see the response to subpart (a) for the presentation materials from the workshops. c) The findings from the workshops are as follows: 1) For the June 2023 DFA workshop, SCE and SDG&E are finding similar successes using this technology as PG&E. SDG&E is using a different system, however, are able to find precursors to underground elbow failures. 2) For the July 2023 EFD workshop, SCE is finding similar successes using this technology as PG&E and is also using this technology on transmission lines. 3) For the August 2023 REFCL workshop, we did not have any specific takeaways or findings. d) PG&E’s action item from these workshops is to continue the discussions and collaboration about uses of EFD and DFA, and implement our WMP commitments on these technologies. We are also still evaluating the usage of REFCL to determine the potential value it could add to our system, if any. | Holly Wehrman | 2024-04-12 | 2024-04-17 | 2024-04-17 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_043.zip | 4 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23-06 – Continuation of Grid Hardening Joint Studies | ACI 23-06 Continuation of Grid Hardening Joint Studies
558 | CalPA | Set WMP-43 | CalPA_Set WMP-43 | 11(s) | CalPA_Set WMP-43_Q11(s) | In response to part (b), PG&E stated, “No reports, minutes, recordings were taken or prepared at the referenced workshops”; however, Slide 6 of attachment 2 lists “meeting minutes” under “next steps.” • Please verify whether PG&E possesses any meeting minutes associated with the workshops discussed in question 11. • If yes, please provide those in response to this data request. | Per the supplemental request from Holly Wehrman requested on April 19, 2024: In response to part (b), PG&E stated, “No reports, minutes, recordings were taken or prepared at the referenced workshops”; however, Slide 6 of attachment 2 lists “meeting minutes” under “next steps.” • Please verify whether PG&E possesses any meeting minutes associated with the workshops discussed in question 11. • If yes, please provide those in response to this data request. PG&E responds as follows: Southern California Edison (SCE) hosts this workgroup and maintains the workshop materials. The “Next Steps” included in “WMP-Discovery2023- 2025_DR_CalAdvocates_043-Q011Atch02.pdf” were to create Meeting Minutes, however, SCE did not end up creating the referenced minutes. a) Please see the table below for presentation materials for the workshops identified. Workshop Date & Title Attachment Name June 2023 Distribution Fault Anticipation (DFA) WMP-Discovery2023-2025_DR_CalAdvocates_043- Q011Atch01.pdf WMP-Discovery2023-2025_DR_CalAdvocates_043- Q011Atch02.pdf July 2023 Early Fault Detection (EFD) WMP-Discovery2023-2025_DR_CalAdvocates_043- Q011Atch03.pdf August 2023 Rapid Earth Fault Current Limiter (REFCL) WMP-Discovery2023-2025_DR_CalAdvocates_043- Q011Atch04.pdf b) No reports, minutes, recordings were taken or prepared at the referenced workshops. Please see the response to subpart (a) for the presentation materials from the workshops. c) The findings from the workshops are as follows: 1) For the June 2023 DFA workshop, SCE and SDG&E are finding similar successes using this technology as PG&E. SDG&E is using a different system, however, are able to find precursors to underground elbow failures. 2) For the July 2023 EFD workshop, SCE is finding similar successes using this technology as PG&E and is also using this technology on transmission lines. 3) For the August 2023 REFCL workshop, we did not have any specific takeaways or findings. d) PG&E’s action item from these workshops is to continue the discussions and collaboration about uses of EFD and DFA, and implement our WMP commitments on these technologies. We are also still evaluating the usage of REFCL to determine the potential value it could add to our system, if any. | Holly Wehrman | 2024-04-19 | 2024-04-24 | 2024-04-24 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_043.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23-06 – Continuation of Grid Hardening Joint Studies | ACI 23-06 Continuation of Grid Hardening Joint Studies
559 | CalPA | Set WMP-43 | CalPA_Set WMP-43 | 12 | CalPA_Set WMP-43_Q12 | Page 67 of PG&E’s 2025 WMP Update states, “In 2023, the utilities discussed the unit costs of CC and undergrounding and compared, at a high level, the different cost drivers.” a) Provide the unit costs of covered conductor that were discussed in 2023 for each of the Joint Utilities. b) Provide the unit costs of undergrounding that were discussed in 2023 for each of the Joint Utilities. c) Describe the cost drivers that were discussed in 2023 for each of the Joint Utilities. d) List any other findings from the monthly meetings in 2023 noted above. | a) Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_043- Q010Atch01.pdf” for the Joint IOU Covered Conductor Working Group discussion, which includes the requested cost information. The section discussing covered conductor costs begins on page 39. b) Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_043- Q010Atch01.pdf” for the Joint IOU Covered Conductor Working Group discussion, which includes the requested cost information. The section discussing undergrounding costs begins on page 40. c) Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_043- Q010Atch01.pdf” for the Joint IOU Covered Conductor Working Group discussion, which includes the requested cost information. The section discussing cost drivers begins on page 39. d) Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_043- Q010Atch01.pdf” for the Joint IOU Covered Conductor Working Group discussion, which includes the findings from the monthly meetings. | Holly Wehrman | 2024-04-12 | 2024-04-17 | 2024-04-17 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_043.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23-06 – Continuation of Grid Hardening Joint Studies | ACI 23-06 Continuation of Grid Hardening Joint Studies
559 | CalPA | Set WMP-43 | CalPA_Set WMP-43 | 12(s) | CalPA_Set WMP-43_Q12(s) | Cal Advocates requested results of meetings held in 2023 regarding the unit costs and cost drivers of covered conductor and undergrounding. PG&E’s response refers to the attachment to Question 10 which, as noted above, does not discuss results from 2023 meetings. • Please verify whether PG&E possesses documents responsive to question 12 that include the unit costs and cost drivers of covered conductor and undergrounding based on meetings held in 2023. • If yes, please provide those in response to this data request. | Per the supplemental request from Holly Wehrman requested on April 19, 2024: Cal Advocates requested results of meetings held in 2023 regarding the unit costs and cost drivers of covered conductor and undergrounding. PG&E’s response refers to the attachment to Question 10 which, as noted above, does not discuss results from 2023 meetings. • Please verify whether PG&E possesses documents responsive to question 12 that include the unit costs and cost drivers of covered conductor and undergrounding based on meetings held in 2023. • If yes, please provide those in response to this data request.. PG&E responds as follows: PG&E does not possess materials in addition to what was provided in the 2025 WMP Update. a) Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_043- Q010Atch01.pdf” for the Joint IOU Covered Conductor Working Group discussion, which includes the requested cost information. The section discussing covered conductor costs begins on page 39. b) Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_043- Q010Atch01.pdf” for the Joint IOU Covered Conductor Working Group discussion, which includes the requested cost information. The section discussing undergrounding costs begins on page 40. c) Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_043- Q010Atch01.pdf” for the Joint IOU Covered Conductor Working Group discussion, which includes the requested cost information. The section discussing cost drivers begins on page 39. d) Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_043- Q010Atch01.pdf” for the Joint IOU Covered Conductor Working Group discussion, which includes the findings from the monthly meetings. | Holly Wehrman | 2024-04-19 | 2024-04-24 | 2024-04-24 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_043.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23-06 – Continuation of Grid Hardening Joint Studies | ACI 23-06 Continuation of Grid Hardening Joint Studies
560 | CalPA | Set WMP-43 | CalPA_Set WMP-43 | 13 | CalPA_Set WMP-43_Q13 | Page 68 of PG&E’s 2025 WMP Update states, with regard to the REFCL pilot at the Calistoga substation, “Although we are committed to continuing this demonstration project, several factors have caused delays in commissioning this program, including equipment failure, extended lead time of equipment, and the need to procure additional equipment to further stabilize the system.” a) List and describe each equipment failure that occurred during 2021, 2022, or 2023 and delayed the commissioning of the program. b) List and describe each instance of extended lead time that occurred during 2021, 2022, or 2023 and delayed the commissioning of the program. c) List and describe PG&E’s current needs to procure additional equipment to further stabilize the system. d) When does PG&E currently anticipate receiving actionable results from the REFCL pilot at the Calistoga substation? e) List each of the efforts PG&E made in 2023 to accelerate the REFCL pilot at the Calistoga substation. f) List each of the efforts PG&E plans to make in 2024 to accelerate the REFCL pilot at the Calistoga substation. g) List each of the efforts PG&E plans to make in 2025 to accelerate the REFCL pilot at the Calistoga substation. | a) Three equipment failures that occurred during 2021 and 2022 delayed the commissioning of the program: 1) In 2021, a substation voltage regulator failure occurred during a test program; 2) In 2022, a substation grounding transformer failure occurred; and 3) In 2022, a GFN RCC failure occurred. b) Three instances of extended lead time occurred during 2021 and 2022 that delayed the commissioning of the program: 1) In 2021 — mobile test resistor for fault testing; 2) In 2021 — replacement substation voltage regulators; and 3) In 2022 — replacement of grounding transformer and RCC. c) PG&E has procured a damping resistor to reduce high standing neutral voltage to stabilize the operation of the REFCL system. At this time, we have no plans to procure additional equipment. d) PG&E currently anticipates receiving actionable results from the REFCL pilot at the Calistoga substation at the end of 2024. e) In order to accelerate the REFCL pilot at the Calistoga substation in 2023, PG&E worked with the supplier to design and supply a damping resistor to reduce neutral voltage. This was necessary due to PG&E observing high standing neutral voltage which could not be reduced even with balancing the ground currents. This forced PG&E to temporarily disable REFCL and work with the supplier for the resistor installation in order to move the project forward. f) In order to accelerate the REFCL pilot in 2024, PG&E is installing and testing the damping resistor to allow the REFCL system to be put back into service. g) PG&E cannot, at this time, identify discrete efforts that it will make in 2025 to accelerate the REFCL pilot because the 2025 workplan is dependent on the results of the work in 2024, which are still unknown. | Holly Wehrman | 2024-04-12 | 2024-04-17 | 2024-04-17 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_043.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23-07 – Deployment of New Technologies | ACI 23-07 – Deployment of New Technologies
561 | CalPA | Set WMP-43 | CalPA_Set WMP-43 | 14 | CalPA_Set WMP-43_Q14 | Page 69 of PG&E’s 2025 WMP Update states, “As of December 2023, PG&E moved beyond pilot and into production of these technologies, having deployed EFD technology on 103 locations over 6 distribution circuits and DFA technology at 79 substations.” a) State the approximate number of circuit miles on which EFD is currently active. b) State the approximate number of circuit miles on which DFA is currently active. c) Describe PG&E’s standards and criteria for determining where to install EFD technology. d) Describe PG&E’s standards and criteria for determining where to install DFA technology. e) Please describe the results of the pilot program mentioned in the quote above, which prompted PG&E to move into production and deployment of these technologies in December 2023. f) Provide any reports, analyses, or other documentation of the results of the pilot program. | a) PG&E currently has 321 circuit miles currently active for EFD. b) PG&E currently has 7,536 circuit miles currently active for DFA. c) EFD circuit/location selection criteria are based on highest HFRA/HFTD risk score, reliable cellular coverage availability, and areas that are not significantly included in our near-term undergrounding effort. d) DFA circuit/location selection criteria are based on highest HFRA/HFTD risk score, reliability impacted customers (CEMI 2), areas highly-impacted by EPSS, and reliable cellular coverage availability. e) Please see the EPIC 2.34 report for the results of the EFD/DFA pilot program, which is available at the following link: https://www.pge.com/assets/pge/docs/about/corporate-responsibility-andsustainability/PGE-EPIC-Project-2.34.pdf. PG&E spent 2022 and 2023 operationalizing these technologies. This operationalizing work included: (1) developing install standards (2022); (2) working to get materials standardized and established between suppliers and PG&E sourcing (2022); (3) developing streamlined alert analysis (2023); and (4) developing investigation workflows (2023). f) Please see the EPIC 2.34 report, a link to which is provided in response to subpart (e) above, for a report and analyses of the EFD/DFA pilot program. | Holly Wehrman | 2024-04-12 | 2024-04-17 | 2024-04-17 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_043.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23-07 – Deployment of New Technologies | ACI 23-07 – Deployment of New Technologies
562 | CalPA | Set WMP-43 | CalPA_Set WMP-43 | 15 | CalPA_Set WMP-43_Q15 | Table ACI-PG&E-23-09-1 on page 75 of PG&E’s 2025 WMP Update lists the number of HFTD structures in each consequence level from E&S to Medium. a) Provide an updated version of this table with additional rows to show the structures with a consequence rank lower than Medium. b) Please provide an updated version of this table (including the additional rows from part (a)) that lists structures in the HFTD/HFRA (not only the HFTD). c) Explain the methodology PG&E used to segregate its plat maps by consequence rank. d) Provide any procedures, reports, analyses, or other documentation to support your response to part (c). | a) Please see below for an updated Table ACI-PG&E-23-09-1. Consequence Rank All HFTD/HFRA Structures Eyes-on-Risk (EOR) Risk/Structure E&S 11,464 10.60% 9.2 x 10-6 E&S – Tier 3 2,874 2.80% 9.7 x 10-6 E&S – Tier 2/HFRA 8,590 7.70% 9.0 x 10-6 High 68,481 37.80% 5.5 x 10-6 High – Tier 3 27,697 15.60% 5.6 x 10-6 High – Tier 2/HFRA 40,784 22.20% 5.4 x 10-6 Medium 93,218 27.40% 2.9 x 10-6 Medium – Tier 3 33,408 10.00% 3.0 x 10-6 Medium – Tier 2/HFRA 59,810 17.40% 2.9 x 10-6 Low 485,488 24.30% 0.5 x 10-6 Low – Tier 3 138,965 8.50% 0.6 x 10-6 Low – Tier 2/HFRA 346,523 15.80% 0.5 x 10-6 b) Table ACI-PG&E-23-09-1 includes HFTD/HFRA structures in its Tier 2 counts and should have been labeled as such to begin with. PG&E has corrected the labels in the table above. c) PG&E uses WDRM v3 to create the maps, which provides wildfire consequence scores at the structure level. For HFTD and HFRA areas, these consequence scores are the basis for plat map consequence scores and inspection frequencies. The WDRM v3 risk model calculates wildfire probabilities of ignition, consequence, and risk scores for structures in the overhead distribution system in areas of PG&E’s service territory. d) Please see “Section 4 – Source Data” in attachment WMP-Discovery2023- 2025_DR_CalAdvocates_043-Q015Atch01.pdf” for the requested procedure. | Holly Wehrman | 2024-04-12 | 2024-04-17 | 2024-04-17 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_043.zip | 1 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23-09 – Decrease in Detailed Distribution Inspections | ACI 23-09 – Decrease in Detailed Distribution Inspections
563 | CalPA | Set WMP-43 | CalPA_Set WMP-43 | 16 | CalPA_Set WMP-43_Q16 | Table ACI-PG&E-23-09-1 on page 75 of PG&E’s 2025 WMP Update lists the number of HFTD structures in each consequence level from E&S to Medium. a) Has PG&E used the WDRM v4 to re-rank its structures and plat maps? If no, explain why not. b) If the answer to part (a) is no, does PG&E plan to use the WDRM v4 to re-rank its structures and plat maps? If no, explain why not. c) If the answer to either parts (a) or (b) is yes, does PG&E plan to adjust its detailed inspection program to use the updated plat map ranking? If no, explain why not. d) If the answer to part (c) is yes, will PG&E use the same inspection frequencies for the updated plat map ranking? If no, explain why not. e) If the answer to part (c) is yes, when does PG&E plan to adjust its detailed inspection program to use the updated plat map ranking? | a) Yes, PG&E has used WDRM v4 to see how its structures and plat maps would rank under the new modeling. b) Not applicable, please see the response to subpart (a) above. c) Yes, PG&E plans to adjust its detailed inspection program to use the updated plat map ranking that incorporates WDRV v4. d) Yes, PG&E currently plans to use the same inspection frequencies for the updated plat map ranking. e) PG&E currently plans to adjust its detailed inspection program to use the updated plat map ranking in 2025. | Holly Wehrman | 2024-04-12 | 2024-04-17 | 2024-04-17 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_043.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23-09 – Decrease in Detailed Distribution Inspections | ACI 23-09 – Decrease in Detailed Distribution Inspections
564 | CalPA | Set WMP-43 | CalPA_Set WMP-43 | 17 | CalPA_Set WMP-43_Q17 | Page 76 of PG&E’s 2025 WMP Update states, Inspecting high consequence assets annually by ground would increase both the eyes-on-risk and the cost of the inspection plan relative to inspecting these assets every other year. PG&E calculates that approximately 37,000 additional inspections would need to be performed annually at a cost of roughly $4.3 million. Similarly, inspecting medium consequence structures every other year would result in 15,000 more inspections at an additional annual cost of $1.7 million. a) What would be the annual cost of performing approximately 37,000 additional detailed aerial inspections of high consequence assets? b) What would be the annual cost of performing approximately 15,000 additional detailed aerial inspections of medium consequence assets? c) What would be the estimated benefit, in dollars, of inspecting high consequence assets annually? d) What would be the estimated benefit, in dollars, of inspecting medium consequence assets annually? | a) The annual cost of performing approximately 37,000 additional detailed aerial inspections of high consequence assets is roughly $5.5 million. b) The annual cost of performing approximately 15,000 additional detailed aerial inspections of medium consequence assets is roughly $2.25 million. c) PG&E does not quantify the estimated benefit, in dollars, of inspecting high or medium consequence assets annually. The main benefit of additional inspections is identifying additional maintenance needs, but PG&E does not have a standardized approach to calculating a dollar benefit associated with identifying additional notifications, as PG&E treats inspections as a foundational program that supports PG&E’s maintenance program. As noted in our 2025 WMP Update, additional inspection finds do not mitigate risk unless maintenance work is actually performed. d) Please see the response to subpart (c) above for the requested explanation. | Holly Wehrman | 2024-04-12 | 2024-04-17 | 2024-04-17 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_043.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23-09 – Decrease in Detailed Distribution Inspections | ACI 23-09 – Decrease in Detailed Distribution Inspections
565 | MGRA | Data Request No. 10 | MGRA_Data Request No. 10 | 1 | MGRA_Data Request No. 10_Q1 | Please provide a spreadsheet listing (as rows) of every undergrounding project completed during the period of January 1, 2023, through December 31, 2023, including non-WMP projects. For each project, please provide the following information (as columns): a) Project ID number or other identifier b) Circuit ID c) ID of each circuit segment that was entirely undergrounded in the project d) ID of each circuit segment that was partially undergrounded in the project e) Total overhead circuit-miles removed f) Total circuit-miles of underground conductor installed g) Total miles of trenching required h) Total electric costs of the project (i.e., costs attributed to your electric facilities), including costs for planning, design, permitting, and construction i) Total number of customers served by the project j) Total number of minutes of PSPS experienced by the project circuit segments since 2019. | Please see attachment “WMP-Discovery2023-2025_DR_MGRA_010-Q001Atch01.xlsx,” worksheet “Q1 a-h”, for a list of PG&E’s system hardening projects with undergrounding miles—as well as the Community Rebuild undergrounding miles— completed in 2023. Descriptions of the included fields are as follows: a) In worksheet “Q1 a-h”, please see column A (Order). b) In worksheet “Q1 a-h”, please see column B (Circuit ID), also included are the following related fields: • Column C (Circuit Name); • Column D (Circuit Protection Zone (CPZ)). c) Not applicable. To date, no circuit segment (referred to as a CPZ in this response) has been fully undergrounded. When PG&E undergrounds a CPZ, 100% of the pre-existing overhead circuitry is not replaced because one or more of the following reasons may be applicable: • Hardening applied to a CPZ can be a hybrid of mitigation methods (overhead hardening, undergrounding, line removal). • There are portions of the CPZ in locations that are infeasible to replace with underground circuitry (e.g. water crossings). • Hardening a CPZ may be split into multiple sub-projects, each focused on different portions of the CPZ. Various project specific constraints (e.g. permits) lead to multi-year hardening of a whole CPZ. d) Please see the response to subpart (c). All circuit segments (referred to as a CPZ in this response) identified in this response are considered partially undergrounded; therefore, that field is not included in the attachment. e) PG&E interprets the request for “Total overhead circuit-miles removed” as the distance of existing overhead infrastructure that was replaced with underground infrastructure in an undergrounding project. This information is not provided in this response because PG&E currently does not have complete tabular data to provide the total overhead circuit-miles removed relating to the undergrounding project. This information is actively being consolidated and will be available in PG&E’s System Hardening Accountability Report in accordance with the requirements of GRC 23-11-069 (OP 20–23). f) In worksheet “Q1 a-h”, please see column T (UG – 2023 Complete). This includes the undergrounding miles completed in 2023. In worksheet “Q1 a-h”, please see column L (Total Planned UG Miles). This includes the sum of all undergrounding miles planned for the project for all years, including 2023 miles completed and pre- and post-2023, where applicable. Also provided is mileage for our other system hardening methods (overhead hardening and line removal). g) Trenching length data is not currently captured; therefore, that field is not provided in the attachment. h) In worksheet “Q1 a-h”, please see column AA (Total Estimated Actual Cost). PG&E interprets “electric costs” as project costs associated with starting and completing an electric undergrounding project; therefore, both incurred and forecasted costs for the project are included. i) In worksheet “Q1 i-j,” please see column B (Customer Count – April 2024). PG&E does not currently have a complete mapping of customer counts by undergrounding order (job). PG&E is proving the number of customers associated with a CPZ as of April 2024 where undergrounding work has taken place in 2023. Note, the customers reported by CPZ are not representative of the customers impacted by a specific undergrounding project. j) In worksheet “Q1 i-j,” please see columns C and D. PSPS minutes are measured at the customer level, but PG&E does not currently have a completed mapping of customers to undergrounding orders (jobs). PG&E is providing two measures associated with total number of minutes of PSPS experienced by the project CPZs since 2019 where undergrounding work has taken place in 2023: 1. The minutes reported in column C (Sum of PSPS Minutes for Average Customer Outage on CPZ) is a total of the average customer outage duration from events in 2019-2023. 2. The minutes reported in column D (Sum of PSPS Minutes for Maximum Event Duration on CPZ) is a total from events in 2019-2023, measuring the duration from the beginning of the first outage start and concluding with the last outage end. PG&E points out that the minutes reported in column C may be less than the minutes reported in column D for the following reasons: • Some customers may experience multiple short-duration outages within the same PSPS event, such as microgrid switching. Column C reports the duration as the sum of these multiple outage durations, while column D calculates the time period between the earliest outage start (among these multiple outages) and the last outage end. • Customers located on the same CPZ may be restored at different times. This results in the average outage duration reported, in column C, being lower than the duration reported in column D (which uses the restoration time of the last customer as the end time). Note, the PSPS minutes reported by CPZ is not representative of the outages on a specific portion of that CPZ that is in scope of a specific undergrounding project. | Joseph Mitchell | 2024-04-12 | 2024-04-17 | 2024-04-17 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_010.zip | 1 | N/A | 8 | Section 8.1.2 - Grid Design and System Hardening | 8.1.2.2 Undergrounding of electric lines and/or equipment | 2.1.1.2 GH-04 Undergrounding
566 | MGRA | Data Request No. 10 | MGRA_Data Request No. 10 | 2 | MGRA_Data Request No. 10_Q2 | Please provide a spreadsheet listing (as rows) of every planned undergrounding projected to be fully or partially completed by the end of 2025. This includes work currently underway, completed in 2024, or to be performed in 2024. a) Order number b) Program c) Circuit ID number d) Circuit-segment name or ID number (if the project affects more than one circuitsegment, please identify each one) e) Relevant wildfire risk score(s) from the wildfire risk model that you are using to estimate distribution risk in your 2025 WMP Update filing f) The expected or actual start date of the project g) The expected completion date of the project h) Length (in circuit miles) of underground conductor to be installed prior to the end of 2025 j) Length (in circuit miles) of overhead conductor to be permanently removed prior to the end 2025 and replaced by underground conductor (note that this may differ slightly from the previous section due to differing overhead and underground routes) k) Length (in circuit miles) of overhead conductor to be permanently removed in 2025 and not replaced with covered conductor or undergrounded) l) Total number of customers served by the project m) Total number of minutes of PSPS experienced by the project circuit segments since 2019. | Please see attachment “WMP-Discovery2023-2025_DR_MGRA_010-Q002Atch01.xlsx”, worksheet “Q2 a-k” for a list of PG&E’s forecasted undergrounding projects for 2024-2026. Please note that the forecasted miles for 2025 and 2026 have been combined in this report as the projects associated with each of these years are still being finalized. A description of the included fields is as follows: a) In worksheet “Q2 a-k”, please see column A (Order). b) In worksheet “Q2 a-k”, please see column B (Category). c) In worksheet “Q2 a-k”, please see column C (Circuit ID) and column D (Circuit Name). d) In worksheet “Q2 a-k”, please see column E (Circuit Protection Zone (CPZ)). e) In worksheet “Q2 a-k”, please see column H (Applicable Risk Score) and column G (Applicable Risk Model). f) In worksheet “Q2 a-k”, please see column I (Est. Construction Start Date). This date represents the estimated date construction will be initiated on the project, recognizing there are additional phases prior to the construction start (e.g., planning, design, estimating, permitting). g) In worksheet “Q2 a-k”, please see column J (Est. Project End Date). The year included represents when the newly installed undergrounded lines are planned for electrification and the project is considered complete. Since the key criteria for reporting miles as complete is not the construction end date, but the fire risk safety audit completion and electric energization, please note that a project can have a construction end dates at the end of year, but may be associated with the following year given they passed the fire risk safety audit in the later year. This dynamic is common within the year as well. h) In worksheet “Q2 a-k”, please see column M (Total Planned UG Miles). The sum of all undergrounding miles planned for the project for 2024-2026. As noted above the, forecasted miles for 2025 and 2026 have been combined in this report. i) [Noting that this Data Request skipped subpart (i) and, therefore, no response is included.] j) PG&E interprets the data requested as the distance of existing overhead infrastructure that was replaced with underground infrastructure in an undergrounding project. This information is not provided in this response because PG&E currently does not have complete tabular data to provide the total overhead circuit-miles removed relating to the undergrounding project. k) In worksheet “Q2 a-k”, please see column N (Total Planned Removal Miles). This includes the sum of all Line Removal miles planned for the project for 2024-2026. WMP-Discovery2023-2025_DR_MGRA_010-Q002 Page 3 As noted above, the, forecasted miles for 2025 and 2026 have been combined in this report. l) In worksheet “Q2 l-m,” please see column B for data, and see the response to MGRA 010-Question 001 subpart i of this data request for an explanation. m) In worksheet “Q2 l-m,” please see columns C and D for data. Additionally, please see the response to Request No. 1, subpart (j) of this data request for a further explanation. | Joseph Mitchell | 2024-04-12 | 2024-04-17 | 2024-04-17 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_010.zip | 1 | N/A | 8 | Section 8.1.2 - Grid Design and System Hardening | 8.1.2.2 Undergrounding of electric lines and/or equipment | 2.1.1.2 GH-04 Undergrounding
567 | MGRA | Data Request No. 10 | MGRA_Data Request No. 10 | 3 | MGRA_Data Request No. 10_Q3 | Are DCD algorithms based on prevailing weather conditions? If so, please describe how sensitivity of DCD is adjusted according to weather. | The Downed Conductor Detection (DCD) algorithm and corresponding protective function element is directly tied to EPSS enablement criteria. No additional weather or enablement criteria is applied when enabling DCD. | Joseph Mitchell | 2024-04-12 | 2024-04-17 | 2024-04-17 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_010.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--14 Effectiveness Analysis for EPSS Including Implementation of DCD | ACI 23-14 Effectiveness Analysis for EPSS
568 | MGRA | Data Request No. 10 | MGRA_Data Request No. 10 | 4 | MGRA_Data Request No. 10_Q4 | During todays (April 8th) meet and confer, the ADMS technology was mentioned that could allow much faster switching of fast trip configurations. Please describe ADMS and for what mitigations it could be used, and how much it might help to improve the false trip rate. | Advanced Distribution Management System (ADMS) is an operating platform where supervisory control and data acquisition (SCADA), the real-time system network model, and other operational applications are used to monitor and control the grid. The EPSS application within ADMS currently being developed will be used to streamline the routine enablement and disablement of EPSS devices as an operational mitigation to current manual practices. The ADMS EPSS application will not directly impact the way EPSS performs as a protective function and therefore will not have an effect on the false trip rate. | Joseph Mitchell | 2024-04-12 | 2024-04-17 | 2024-04-17 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_010.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--14 Effectiveness Analysis for EPSS Including Implementation of DCD | ACI 23-14 Effectiveness Analysis for EPSS
569 | MGRA | Data Request No. 10 | MGRA_Data Request No. 10 | 5 | MGRA_Data Request No. 10_Q5 | Please provide the 2022 and 2023 EPSS reliability studies referred to on p. 8 and p. 12 of TN13808_20240402T112956_20240402_PGE_2025_WMPUpdate_R0_ACI2315_ Atch01.pdf. | For the narrative associated with PG&E’s 2022 EPSS Reliability Study, please reference pdf page 1120 at the following link: https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/pge-wmp-r4-010824.pdf Please also reference “WMP-Discovery2023-2025_DR_MGRA_010-Q005Atch01.xlsx” for the 2022 EPSS Reliability Study. For PG&E’s 2023 EPSS Reliability Study, please reference the following attachments: • WMP-Discovery2023-2025_DR_MGRA_010-Q005Atch02.pdf • WMP-Discovery2023-2025_DR_MGRA_010-Q005Atch03.xlsx | Joseph Mitchell | 2024-04-12 | 2024-04-17 | 2024-04-17 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_010.zip | 3 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--14 Effectiveness Analysis for EPSS Including Implementation of DCD | ACI 23-14 Effectiveness Analysis for EPSS
570 | MGRA | Data Request No. 10 | MGRA_Data Request No. 10 | 6 | MGRA_Data Request No. 10_Q6 | As per discussions in the April 8th meet and confer, please provide distribution unplanned outage data for the 2023 calendar year in any format required to remove transmission data or any other confidential information. This can be unrelated to the format required by the Spatial Quarterly Data Report. | Please see attachment “WMP-Discovery2023-2025_DR_MGRA_010-Q006Atch01.xlsx” for the requested information. | Joseph Mitchell | 2024-04-12 | 2024-04-17 | 2024-04-17 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_010.zip | 1 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--14 Effectiveness Analysis for EPSS Including Implementation of DCD | ACI 23-14 Effectiveness Analysis for EPSS
571 | CalPA | Set WMP-44 | CalPA_Set WMP-44 | 1 | CalPA_Set WMP-44_Q1 | Page 52 of PG&E’s 2025 WMP Update states: We assessed the effectiveness of each of the mitigation alternatives against more than 2,200 outage combinations that have occurred in PG&E’s HFTD during wildfire season. PG&E SMEs reviewed each of the outage combinations…and assigned an effectiveness rating for each mitigation at preventing each outage combination. a) How many SMEs were involved in reviewing outage combinations and assigning effectiveness ratings? b) Please describe the methods used by PG&E SMEs to review outage combinations and assign effectiveness ratings. c) Do the 2,200 outage combinations represent a specific time period? Please explain your answer. d) Do the 2,200 outage combinations include outage combinations that occurred in PG&E’s HFRA but not in the HFTD? Please explain your answer. | a) For the initial qualitative assessment, experts in the Electric Distribution Engineering, EPSS, Remote Grid, Electric Distribution Reliability and REFCL teams were engaged with the Grid Design team. Three experts on the Design team reviewed the data from Grid Design. In addition, several data analysts were included in the calculations of the effectiveness. b) The following steps were taken to review outage combinations and determine effectiveness ratings: • Outages were initially reviewed by similar outage (or outage cause) types, for example splice failure, vegetation, bird, etc.; • Reviewed line by line to confirm accuracy; and • Methodology checked and confirmed by additional Grid Design SME’s. c) The outage cause, equipment outage combinations were based on the 2015-2022 study period’s outage history in the HFTD. d) No, the study that was produced for the WMP was a snapshot of the HFTD information only. There is currently no tool that can pull HFRA information for each outage; the existing tool was only designed to perform spatial analysis on HFTD layer and information. | Holly Wehrman | 2024-04-15 | 2024-04-18 | 2024-04-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_044.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--05 – Updating Grid Hardening Decision Making | ACI 23-05 Updating Grid Hardening Decision Making
572 | CalPA | Set WMP-44 | CalPA_Set WMP-44 | 2 | CalPA_Set WMP-44_Q2 | Page 54 of PG&E’s 2025 WMP Update states, “To determine circuit segment-level mitigation effectiveness, the WBCA will adjust for the outage combinations likely to occur on a given circuit segment, their estimated frequency, and their contribution to overall risk on the circuit segment.” a) Please describe the methods used in the WBCA to adjust for the outage combinations likely to occur on a given circuit segment. b) Please describe the methods used in the WBCA to adjust for the estimated frequency of outage combinations on a given circuit segment. c) Please describe the methods used in the WBCA to adjust for the contribution of outage combinations to overall risk on a given circuit segment. | a) As stated on pp. 51-52 of PG&E’s 2025 WMP Update, “outage combinations”, refers to “potential ignition(s) resulting from particular combinations of unplanned outage events and equipment attributes”. The likely “outage combinations” on a given circuit segment are based on the fifteen unique probability of ignition risk subdrivers output from Version 3 of the Wildfire Distribution Risk Model (WDRM v3). These include: • Vegetation (Branch); • Vegetation (Trunk); • Vegetation (other); • Animal (Bird); • Animal (Squirrel); • Animal (other); • Third Party (Balloon); • Third Party (Vehicle); • Third Party (other); • Primary Conductor; • Secondary Conductor; • Equipment (Support Structure); • Equipment (Transformer); • Equipment (Voltage Control); and • Equipment (other). b) As described above, each circuit segment has a unique likelihood of an outage and ignition based on the 15 subdrivers from WDRM v3. In the WBCA, based on the mitigation effectiveness of associated with each individual subdriver, the residual frequency on a given circuit segment can be computed. As a hypothetical example, the mitigation effectiveness for a program is 50% for vegetation (branch) and 60% for equipment (support structure). Circuit segment #1 has a vegetation (branch) subdriver frequency of 0.2 and equipment (support structure) subdriver of 0.8. Circuit segment #2 has a vegetation (branch) subdriver frequency of 0.5 and equipment (support structure) subdriver of 0.5. The resulting mitigation frequency for CS #1 is (0.2)*(1-50%) + (0.8)*(1-60%) = 0.42 frequency or 58% effective while CS #2 mitigation frequency is (0.5)*(1-50%) + (0.5)*(1-60%) = 0.45 or 55% effective. As a result, even though the circuit segments start with the same baseline frequency, due to the difference in the frequency of the individual 15 subdrivers and its associated mitigation effectiveness, the resulting change in frequency is different for each circuit segment. c) Similar to the response to part b, each circuit segment has a unique risk based on the 15 subdrivers from WDRM v3. In the WBCA, based on the mitigation effectiveness of associated with each individual subdriver, the residual risk on a given circuit segment can be computed. As a hypothetical example, the mitigation effectiveness for a program is 50% for vegetation (branch) and 60% for equipment (support structure). Circuit segment #1 has a vegetation (branch) subdriver risk 2 and equipment (support structure) subdriver of 8. Circuit segment #2 has a vegetation (branch) subdriver risk of 5 and equipment (support structure) subdriver of 5. The resulting mitigation risk for CS #1 is (2)*(1-50%) + (8)*(1-60%) = 4.2 risk or 58% effective while CS #2 mitigation frequency is (5)*(1-50%) + (5)*(1-60%) = 4.5 or 55% effective. As a result, even though the circuit segments start with the same baseline risk, due to the difference in the risk of the individual 15 subdrivers and its associated mitigation effectiveness, the resulting change in risk is different for each circuit segment. | Holly Wehrman | 2024-04-15 | 2024-04-18 | 2024-04-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_044.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--05 – Updating Grid Hardening Decision Making | ACI 23-05 Updating Grid Hardening Decision Making
573 | CalPA | Set WMP-44 | CalPA_Set WMP-44 | 3 | CalPA_Set WMP-44_Q3 | Page 54 of PG&E’s 2025 WMP Update states, “To determine circuit segment-level mitigation effectiveness, the WBCA will adjust for the outage combinations likely to occur on a given circuit segment, their estimated frequency, and their contribution to overall risk on the circuit segment.” a) Will the WBCA adjust for outage combinations on a scale smaller than a circuit segment? For example, a very long circuit segment may not have uniform outage characteristics along its entire length. b) If the answer to part (a) is yes, please explain the methods and criteria PG&E plans to use to adjust the WBCA for outage combinations on a scale smaller than a circuit segment. c) If the answer to part (a) is no, please explain why not. | a) The WBCA will not adjust for outage combinations on a scale smaller than a circuit segment. b) Not applicable, please see the response to subpart (a) above. c) Outputs from the Wildfire Distribution Risk Model (WDRM) are aggregated to the circuit segment level as the best model view for system hardening work. While individual pixel level data is available, the circuit segment view has less noise than the pixel level output. As such, the mean probability of ignition for each sub-driver, as output from WDRM, is assumed to be uniform across an entire circuit segment. Accordingly, the risks from individual sub-driver “outage combinations” are assumed to be uniform across that circuit segment as well. | Holly Wehrman | 2024-04-15 | 2024-04-18 | 2024-04-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_044.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--05 – Updating Grid Hardening Decision Making | ACI 23-05 Updating Grid Hardening Decision Making
574 | CalPA | Set WMP-44 | CalPA_Set WMP-44 | 4 | CalPA_Set WMP-44_Q4 | Page 56 of PG&E’s 2025 WMP Update discusses Undergrounding versus Overhead Hardening. Undergrounding is stated to have greater total permanent risk reduction, but it takes longer and costs more to install. a) Has PG&E conducted an analysis of its transmission and distribution system to determine the estimated remaining useful life of its assets? b) If the answer to part (a) is yes, does PG&E consider the remaining life of assets when evaluating benefits of overhead hardening, which is faster to deploy? c) If the answer to part (a) is yes, please provide any applicable analysis relevant to the condition of PG&E’s transmission and distribution system assets. | a) No, the Wildfire Transmission Risk Model (WTRM) and Wildfire Distribution Risk Model (WDRM) incorporate age, in addition to other parameters, to assess risk based on the probability of an asset failure leading to an ignition occurring and the consequence of a wildfire if it were to occur. The model helps determine whether assets may require mitigation response. For example, an asset with high wildfire risk may drive the response of a detailed inspection, which could then result in the need to replace or repair the asset. The age of the asset when it requires replacement pinpoints the end of its useful life. Therefore, while the WTRM and WDRM help determine what assets are most likely to fail, they do not specifically predict the date an asset will fail, i.e. its “useful life.” b) Not applicable, please see the response to subpart (a) above. c) Not applicable, please see the response to subpart (a) above. | Holly Wehrman | 2024-04-15 | 2024-04-18 | 2024-04-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_044.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--05 – Updating Grid Hardening Decision Making | ACI 23-05 Updating Grid Hardening Decision Making
575 | CalPA | Set WMP-44 | CalPA_Set WMP-44 | 5 | CalPA_Set WMP-44_Q5 | Page 57 of PG&E’s 2025 WMP Update states, “Regarding cost effectiveness scores, the undergrounding projects in PG&E’s current workplan were previously selected using a methodology (WDRM V2 and V3) that did not incorporate cost effectiveness scores for individual projects. Therefore, cost effectiveness scores are not available.” a) Define the term “undergrounding project” in the above statement. b) Has PG&E used the outputs from WDRM v4 to calculate the cost effectiveness scores for the undergrounding projects in PG&E’s current workplan? c) If the answer to part (b) is yes, please provide the cost effectiveness scores for all projects in PG&E’s current undergrounding workplan. d) If the answer to part (b) is no, explain why not. e) Does PG&E plan to use the outputs from WDRM v4 to calculate the cost effectiveness scores for the undergrounding projects in PG&E’s current workplan? f) If the answer to part (e) is yes, when does PG&E anticipate completing this analysis? g) If the answer to part (e) is no, explain why not. | a) As stated in PG&E’s Comments on CPUC Safety Policy Division staff’s original proposed guidelines for the SB 884 program (September 27, 2023), PG&E defines a “project” at the circuit segment level (also referred to as circuit protection zone (CPZ)) because our current risk model measures risk at the circuit segment level and does not have more granular risk detail. When projects are scoped and planned for near-term completion (generally within 3 to 4 years), we create sub-projects, or jobs, which will reflect portions of a CPZ. PG&E identifies jobs based on mileage, diversity of risk ranking, dependencies (e.g., easements, environmental permitting issues) and constructability. As the risk models are periodically updated and released, projects may be added to the workplan, reprioritized, or removed. b) No, WDRM v4 has not been used for the current workplan. c) Not applicable, please see the response to subpart (b) above. d) WDRM v2 and v3 were applicable for the current workplan. WDRM v4 analysis is intended to be applied to the workplan for projects that will be completed starting from 2027. PG&E does not currently anticipate completing any projects selected with WDRM v4 in the 2023 GRC period. It is possible, but unlikely, that some of these projects may be completed prior to 2027 based on the timing to complete and construct the project in relation to all other projects in the current workplan. e) No, the current workplan uses WDRM v2 and v3 only. WDRM v4 analysis is intended to be applied to the workplan from 2027. f) Not applicable, please see the response to subpart (e) above. g) Per the requirements of SB-884, PG&E is developing the Wildfire Benefit Cost Analysis (WBCA) tool to evaluate the costs and benefits of undergrounding and other alternative mitigations. PG&E intends to use the outputs of WDRM v4 in the WBCA, which is intended to be applied to the workplan for projects completed starting in 2027. | Holly Wehrman | 2024-04-15 | 2024-04-18 | 2024-04-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_044.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--05 – Updating Grid Hardening Decision Making | ACI 23-05 Updating Grid Hardening Decision Making
576 | CalPA | Set WMP-44 | CalPA_Set WMP-44 | 6 | CalPA_Set WMP-44_Q6 | Figure ACI-PG&E-23-02-1 on page 40 of PG&E’s 2025 WMP Update states, “When considering the overall Wildfire Risk with EPSS and PSPS, this is still ~3x of Distribution Overhead.” a) Define the phrase “Distribution Overhead” in this context. b) Please state the significance of the “~3x” ratio of “overall Wildfire Risk with EPSS and PSPS” compared to “Distribution Overhead.” | a) “Distribution Overhead” in this context refers to the reliability risks associated with PG&E’s “Failure of Electric Distribution Overhead Assets” risk, excluding EPSS and PSPS outages, from its forthcoming 2024 RAMP Report. This risk was previewed in the February 7, 2024 CPUC-hosted PG&E 2024 RAMP (pre-filing) workshop #1. b) The significance of this statement is to emphasize that Wildfire Risk is still the primary focus of system hardening mitigations, rather than reliability risks. | Holly Wehrman | 2024-04-15 | 2024-04-18 | 2024-04-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_044.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23-02 – PSPS and Wildfire Risk Trade-Off Transparency | ACI PG&E-23-02 – PSPS and Wildfire Risk Trade-Off Transparency
577 | CalPA | Set WMP-44 | CalPA_Set WMP-44 | 7 | CalPA_Set WMP-44_Q7 | Figure ACI-PG&E-23-02-1 on page 40 of PG&E’s 2025 WMP Update indicates that wildfire risk is approximately $20,668 million, and PSPS and EPSS combined reduce the wildfire risk by approximately $16.359 million. a) Are the $20,668 million wildfire risk and the $16.359 million risk reduction estimates annual values? Please explain if no. b) Do the $20,668 million wildfire risk and the $16.359 million risk reduction estimates apply to PG&E’s entire service territory? Please explain if no. | a) The $20,668 million wildfire risk and respective $16,359 million risk reduction are both annual values. b) The $20,668 million wildfire risk and respective $16,359 million risk reduction apply to PG&E’s entire service territory, but this risk is densely focused within the HFTD and HFRA. | Holly Wehrman | 2024-04-15 | 2024-04-18 | 2024-04-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_044.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23-02 – PSPS and Wildfire Risk Trade-Off Transparency | ACI PG&E-23-02 – PSPS and Wildfire Risk Trade-Off Transparency
578 | CalPA | Set WMP-44 | CalPA_Set WMP-44 | 8 | CalPA_Set WMP-44_Q8 | Figure ACI-PG&E-23-02-1 on page 40 of PG&E’s 2025 WMP Update indicates that wildfire risk is approximately $20,668 million, and PSPS and EPSS combined reduce the wildfire risk by approximately $16.359 million. a) Has PG&E estimated the incremental wildfire risk reduction (in dollars) attributed to widescale deployment of REFCL? Please provide this estimate if yes. b) If the answer to part (a) is no, why has PG&E not conducted that analysis? c) Has PG&E estimated the incremental risk increase attributed to widescale deployment of REFCL? Please provide this estimate if yes. d) If the answer to part (c) is no, why has PG&E not conducted that analysis? e) Has PG&E estimated the incremental lifetime expenditure attributed to widescale deployment of REFCL? Please provide this estimate if yes. f) If the answer to part (e) is no, why has PG&E not conducted that analysis? | a) No, PG&E has not estimated the incremental wildfire risk reduction (in dollars) attributed to widescale deployment of REFCL. b) This study has not been conducted because REFCL cannot be deployed widescale on PG&E’s electric assets. REFCL can only be applied to substations that meet the following minimum requirements: • Single voltage 3-wire 12 kV substation; • At least 20 overhead miles in HFTD; • Less than 50% of circuit underground; • Less than 20% of circuit past autobanks; and • Sufficient physical space to deploy equipment. c) PG&E has not estimated the incremental risk increase attributed to widescale deployment of REFCL. d) Please see the response to subpart (b) above, as the reasoning is the same. e) PG&E has not estimated the incremental lifetime expenditure attributed to widescale deployment of REFCL. f) Please see the response to subpart (b) above, as the reasoning is the same. | Holly Wehrman | 2024-04-15 | 2024-04-18 | 2024-04-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_044.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23-02 – PSPS and Wildfire Risk Trade-Off Transparency | ACI PG&E-23-02 – PSPS and Wildfire Risk Trade-Off Transparency
579 | CalPA | Set WMP-44 | CalPA_Set WMP-44 | 9 | CalPA_Set WMP-44_Q9 | Page 88 of PG&E’s 2025 WMP Update states, “CPUC reportable fire ignitions on EPSS enabled circuits were reduced by approximately 72% relative to the three-year historical average.” a) Please provide copies of any reports, analysis, or other documentation to support PG&E’s statement quoted above. b) Are EPSS outages with DCD-enablement distinguishable in the EPSS monthly reports served by PG&E? c) If the answer to part (b) is yes, please state how such outages are distinguishable. d) If the answer to part (b) is no, does PG&E plan to make such outages distinguishable in future EPSS monthly reports? | a) Please see the below presentation that supports the ignition reduction effectiveness calculation referenced on page 88 of PG&E’s 2025 Wildfire Mitigation Plan Update. b) No, outages on DCD-enabled devices are not currently identified separately in the EPSS monthly reports provided to SED. c) Not applicable, please see the response to subpart (b) above. d) No, PG&E does not currently plan to differentiate outages on DCD-enabled devices in future EPSS monthly reports. | Holly Wehrman | 2024-04-15 | 2024-04-18 | 2024-04-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_044.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--14 Effectiveness Analysis for EPSS Including Implementation of DCD | ACI 23-14 Effectiveness Analysis for EPSS
580 | CalPA | Set WMP-44 | CalPA_Set WMP-44 | 10 | CalPA_Set WMP-44_Q10 | The following table is from PG&E’s 2022 Annual Electric Reliability Report, page 12: a) Please provide an updated version of this table with an additional row for 2023. b) If PG&E is unable to provide any of the requested data from part (a), please provide a reason for each data point. c) If PG&E is unable to provide any of the requested data from part (a), please provide an estimate of when this data will be available. | a) An updated version of the requested table is not currently available, as described in subpart (b) below. b) PG&E publishes the Annual Electric Reliability Report each July for the prior year. The referenced table will be included in the 2023 Annual Electric Reliability Report, which is tentatively scheduled to be published in July 2024 at the following link: https://www.pge.com/en/about/pge-systems/electric-systems/electric-reliabilityreports.html. c) Please see the response to subpart (b) above. | Holly Wehrman | 2024-04-15 | 2024-04-18 | 2024-04-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_044.zip | 0 | N/A | N/A | N/A | N/A | N/A
581 | CalPA | Set WMP-44 | CalPA_Set WMP-44 | 11 | CalPA_Set WMP-44_Q11 | Page 97 of PG&E’s 2025 WMP Update states: The 2023 FTI [focused tree inspection] program explored enhanced inspection practices and evaluated improvements to situational awareness to further inform and guide clearance recommendations. Based on results of the program, PG&E is moving forward with executing 1,500 miles of work in 2024.” a) Please describe the results of the program on which PG&E is basing the decision to move forward with executing 1,500 miles of work in 2024. b) Provide any available reports, analyses, or other documentation of the results of the program. | a) The 2023 pilot performed inspections in Areas of Concern (AOC) in Butte, Calaveras, Napa, and El Dorado counties. Inspections utilized Tree Risk Assessment Qualified (TRAQ) arborists exclusively to identify trees to be worked and followed the Distribution Inspection Procedure guidance of Level 1 & Level 2 visual inspections. PG&E also performed 100% Quality Control field review on all miles post-inspection. The pilot yielded 7,170 trees identified for work across approximately 260 miles. In 2024, the program is being expanded to 1,500 miles; the AOCs represent where our distribution system is most likely to see higher rates of tree failures during wildfire season or winter storms. The objective of the program is to reduce vegetation-caused outages and ignitions from occurring in these areas where there is highest potential for such outages and ignitions. To that end, in 2024, a Level 2 visual assessment will be performed on all strike potential trees within the 1,500 miles. TRAQ arborists will continue to be the only inspectors performing inspections. PG&E based its decision to move forward with executing 1,500 miles of FTI work based on internal and external factors that supported program development or maturity. The FTI program was initiated in response to RN-22-09 which committed PG&E to benchmark with other utilities to define best practices and mitigations for hazard tree mitigation, evaluate appropriate inspection intervals and inspection levels. This resulted in PG&E developing its first version of Vegetation Management specific Areas of Concern (AOCs) and a series of commitments to mature the program to more holistic application by 2025. While PG&E was piloting the Focused Tree Inspection program in 2023, RN-23-07 was issued and assigned “Remedy b” which mandated that PG&E create “a plan to fully implement (beyond the pilot) and mature Focused Tree Inspections during the WMP cycle”. This directive required PG&E to continue forward with FTI in advance of completion of the FTI program pilot. In addition to the two revision notices, the FTI program also created responses to address 2023-2025 WMP Decision ACI(s)1 as well as, WMP Maturity Survey questions2. These responses prompted further advancement of the FTI program while it was still in its initial phases of development. Initial mileage targets for the FTI program were higher than the 1,500 miles committed in the 2024 WMP targets. Internal target setting decisions were made based on the operational realities resulting from the initial pilot, as well as the increased rigor and expectations to further enhance a program that focused on hazard tree identification, developing more specific guidance on thresholds for Level 2 inspections as well as continue working to bolster Annual and Second patrol Vegetation Management programs in the HFTD for thorough wildfire mitigation of hazard trees. Footnotes 1. ACI references from 202302025 WMP Decision: PG&E-23-15. Implementation of Focused Tree Inspections and Addressing the Risk from Hazard Trees. PG&E-23- 19. Continued Progression of Vegetation Management Maturity. PG&E-23-21. Identification of High-Risk Species for Focused Tree Inspections 2. 04.01.02.Q01 - Does the vegetation database include all vegetation within the right of the way and within strike of the potential assets? 04.02.02.Q01- Do the measured parameters and procedures applied during vegetation inspections enable identifying higher risk areas and vegetation? 04.02.04.Q04 - Is the relative risk reduction and cost of vegetation inspections considered in strategy development? 04.03.02.Q01- Does the electrical corporation proactively trim trees based on predictive modeling results (such as species-specific vegetative growth and limb, trunk, or root failure rates)? 07.05.01.Q06 - Does the electrical corporation cooperate or participate in best practice sharing through comparing vegetation inspection, management, treatment procedures, training, and lessons learned with other electrical corporations? b) Please see the table below for the results of the 2023 FTI pilot program: | Holly Wehrman | 2024-04-15 | 2024-04-18 | 2024-04-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_044.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23-19 – Continued Progression of Vegetation Management Maturity | ACI 23-19 Continued Progresion of Vegatation Management Maturity
582 | CalPA | Set WMP-44 | CalPA_Set WMP-44 | 12 | CalPA_Set WMP-44_Q12 | Table ACI-PG&E-23-23-1 on page 112 of PG&E’s 2025 WMP Update includes the following entry: a) Explain why the last calibration date of this weather station was recorded as 9/1/2022, over three months after the site was destroyed on May 21, 2022. b) Provide any records of the calibration on 9/1/2022. c) When did PG&E become aware that the site had been destroyed? d) When does PG&E plan to replace the destroyed site? | a) The September 1, 2022, date, was the scheduled due date for the calibration and recorded by erroneously due to a data pull error. The actual date for the last calibration was August 4, 2021. b) Please see response to subpart A. The September 1, 2022, date was recorded in error. c) PG&E first became aware of an issue with this weather station around June 6, 2022. PG&E was able to confirm the site had been destroyed during the 2022 scheduled calibration on July 29, 2022. d) PG&E is currently working on reinstalling this station. | Holly Wehrman | 2024-04-15 | 2024-04-18 | 2024-04-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_044.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23-23 – Weather Station Maintenance and Calibration | ACI PG&E-23-23 – Weather Station Maintenance and Calibration
583 | CalPA | Set WMP-44 | CalPA_Set WMP-44 | 13 | CalPA_Set WMP-44_Q13 | Table ACI-PG&E-23-23-1 on page 113 of PG&E’s 2025 WMP Update includes the following entry: a) Explain why the last calibration date of this weather station was recorded as 11/1/2022, over one month after the station was removed on September 17, 2022. b) Provide any records of the calibration on 11/1/2022. c) When did PG&E become aware that the station had been removed? d) When does PG&E plan to relocate the station? | a) This calibration date was recorded erroneously due to a data pull error. This station has never been calibrated as it was removed on July 19, 2021, due to a pole replacement and then asked to be relocated due to shading. This station was originally installed in August 2020. b) There is no proof of calibration since the station was installed for under 12 months. c) The station was scheduled by PG&E to be removed due to a pole replacement on July 19, 2021. d) PG&E is currently working on reinstalling this station. | Holly Wehrman | 2024-04-15 | 2024-04-18 | 2024-04-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_044.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23-23 – Weather Station Maintenance and Calibration | ACI PG&E-23-23 – Weather Station Maintenance and Calibration
584 | CalPA | Set WMP-45 | CalPA_Set WMP-45 | 1 | CalPA_Set WMP-45_Q1 | Regarding its usage of Wildfire Distribution Risk Model (WDRM) v4 in scoping covered conductor and undergrounding projects, and the reflection of such in its System Hardening Accountability Report required by D.23-11-069,4 PG&E states the following in response to Question 6 of data request CalAdvocates-PGE-2025WMP-04: The scope of the SHAR [System Hardening Accountability Report] includes System Hardening work completed in the GRC period (2023-2026). Projects in this time period are not currently anticipated to be informed by WDRM v4. In the event projects selected by WDRM v4 do end up being planned for completion during this time period, WDRM v4 information would be included in the SHAR in the existing risk-related fields (i.e., Applicable Risk Model, Risk Reduction %, etc.). a) In the event projects selected with WDRM v4 do end up being planned for completion in the GRC period, how will PG&E show that it is meeting the risk reduction targets outlined in D.23-11-069?5 b) In the event projects selected with WDRM v4 do end up being planned for completion in the GRC period, will PG&E file a Petition for Modification (PFM) of D.23-11-069 to reflect usage of WDRM V4? Please explain your answer. c) In the event projects selected with WDRM v4 do end up being planned for completion in the GRC period, will PG&E submit an advice letter to modify the SHAR template to reflect usage of WDRM v4? Please explain your answer. d) In the event projects selected with WDRM v4 do end up being planned for completion in the GRC period, will PG&E use different means (other than a PFM of D.23-11-069 or an advice letter) to modify the SHAR reporting requirements or SHAR template contents? Please explain your answer. | a) PG&E does not anticipate completing any projects selected with WDRM V4 in the 2023 GRC period. As noted in response to question CalAdvocates 040-Q006, WDRM v4 may begin to inform scoping of undergrounding projects as early as the second half of 2024 for undergrounding projects planned for completion in 2027 and beyond. It is possible, but unlikely, that some of these projects may be completed prior to 2027. Were this to take place, we would follow the logic and methodology described in Advice Letter 7150-E-A. Specifically, where the excel templates for the baseline sheet for forecasted risk reduction (Table 1) and the completed sheet for completed project risk reduction (Table 2) currently include rows for WDRM 2 and WDRM 3 and their summed totals, we would add a new row for WDRM 4 and include those values in the summed totals. b) If PG&E were to complete in the 2023 GRC period any projects selected with WDRM V4, we would not file a PFM of D.23-11-069 because no modification of the decision would be necessary. As written, the decision recognizes the evolving nature of risk models and explicitly allows for the use of “any other future version” of WDRM beyond V2 and V3.3 c) In the unlikely event PG&E selects projects with WDRM V4 for completion in the 2023 GRC period, WDRM v4 information would be included in the SHAR in the existing risk-related fields (i.e., Applicable Risk Model, Risk Reduction %, etc.). If there are other additional substantial changes needed to the template, PG&E would work with SPD staff who, per D.23-11-069, have ministerial authority to adjust the requirements for the SHAR report.4 d) Yes. Please see response to sub-part c above. | Holly Wehrman | 2024-04-15 | 2024-04-18 | 2024-04-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_045.zip | 0 | N/A | 6.2.2.2 | 6.0 Risk Methodology and Assessment | 6.2.2.2 Consequence | B.1.1. WDRM v4
585 | MGRA | Data Request No. 11 | MGRA_Data Request No. 11 | 1 | MGRA_Data Request No. 11_Q1 | Please provide non-confidential versions of any responses to Cal Advocates data requests if the responses to Cal Advocates are confidential. | PG&E objects to this request on the grounds that it seeks to impose a continuing discovery obligation on PG&E. Continuing discovery obligations are not permitted under California law. Biles v. Exxon Mobile Corp., 124 Cal.App.4th 1315, 1328 (2004); Code Civ. Proc. § 2030.060(g). Additionally, PG&E objects to this request on the grounds that it is overbroad and unduly burdensome. PG&E receives an enormous volume of data requests in the window of time between submitting its WMP and the deadline to submit public comments. This burden is exacerbated by the default three business day turnaround period for all responses. Imposing this continuous discovery obligation on PG&E during this period is not tenable. Furthermore, any effort to provide the requested information would be further exacerbated because MGRA has refused to sign a confidentiality or non-disclosure agreement, and providing this information would require manually redacting all confidential information from each response. PG&E notes that the Public Advocates Office is a government agency that has broad statutory authority that exceeds this single regulatory proceeding and allows the Public Advocates Office to obtain information that exceeds what MGRA, as a private organization, would be able to obtain through this proceeding. Lastly, MGRA may obtain non-confidential versions of PG&E responses to Cal Advocates data requests at the following website: https://www.pge.com/en/outagesand-safety/safety/community-wildfire-safety-program.html#accordion-6b52828ca7-itema47a0617be. If you would like to discuss this request and our response, please do not hesitate to reach out as we are happy to meet and confer on this issue. | Joseph Mitchell | 2024-04-16 | 2024-04-19 | 2024-04-19 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_011.zip | 0 | N/A | 6.2.1 | 6.0 Risk Methodology and Assessment | 6.2.1 Risk and Risk Component Identification | 1. Signficant Updates to Risk Models (WDRM v4 & WTRM v2)
586 | MGRA | Data Request No. 11 | MGRA_Data Request No. 11 | 2 | MGRA_Data Request No. 11_Q2 | Please provide a non-confidential version of documentation containing a description of WDRM v4, including testing and validation. | PG&E objects to this request on the grounds that it is overbroad and unduly burdensome to provide what can be interpreted as all “documentation containing a description of WDRM v4.” Gathering and providing all “documentation containing a description of WDRM v4” could take many weeks of work and require reviewing many thousands of documents. PG&E also objects to this request on the grounds that it is vague and ambiguous as to what is included in all “documentation containing a description of WDRM v4.” PG&E further objects to this request insofar as it seeks information protected by the attorney-client privilege and attorney work product privilege. PG&E also objects to the request on the grounds that it exceeds the scope of this regulatory proceeding, as PG&E’s 2025 WMP notes that WDRM v4 has not yet been used for any wildfire mitigation work. Notwithstanding and without waiving these objections, PG&E responds as follows: we anticipate that WDRM v4 model documentation, including a validation report, will be available by the end of Q2 2024. | Joseph Mitchell | 2024-04-16 | 2024-04-19 | 2024-04-19 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_011.zip | 0 | N/A | 6.2.1 | 6.0 Risk Methodology and Assessment | 6.2.1 Risk and Risk Component Identification | 1. Signficant Updates to Risk Models (WDRM v4 & WTRM v2)
587 | MGRA | Data Request No. 11 | MGRA_Data Request No. 11 | 3 | MGRA_Data Request No. 11_Q3 | If E3 or another consulting group has analyzed WDRM v4, please provide a nonconfidential version of its report. | E3 is currently conducting an independent review of the WDRM v4, which is scheduled to be available by the end of Q2 2024. | Joseph Mitchell | 2024-04-16 | 2024-04-19 | 2024-04-19 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_011.zip | 0 | N/A | 6.2.1 | 6.0 Risk Methodology and Assessment | 6.2.1 Risk and Risk Component Identification | 1. Signficant Updates to Risk Models (WDRM v4 & WTRM v2)
588 | CalPA | Set WMP-46 | CalPA_Set WMP-46 | 1 | CalPA_Set WMP-46_Q1 | Regarding Attachment “2024-04-02_PGE_2025_WMP-Update _R0_ACI-23-26_Atch01_CONF.xlsx” of PG&E’s 2025 WMP Update: a) Please provide a description or definition of each column in both worksheets. b) Please state the basis for using $1.615/minute as the conversion factor for column T (impact_community_values) in the “Outage Data” worksheet. c) The range of data for column U (2023_percentage_epss_enabled) in the “CPZ Data” worksheet is 0-99%. Please clarify the time scale this is applicable for. For example, is this 0-99% of the calendar year? d) Please clarify what the data reported in column V (2023_epss_protected_circuit_mile_days) of the “CPZ Data” worksheet represents. | a) Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_046- Q001Atch01.xlsx” for the requested information. b) As originally requested as part of ACI PG&E-22-32, the “impact on community values, including intangibles (e.g. livelihood)” of EPSS was measured using PG&E’s preliminary monetized value of attributes for Electric Reliability of $3.23 as presented in PG&E’s February 7, 2024, Pre-RAMP CPUC Workshop filing. For the purposes of this calculation, the estimated incremental impact from EPSS settings being enabled was assumed to be double the number of customer outage minutes per outage. As such, the total number of interruption minutes was multiplied by the monetized value of attributes for Electric Reliability divided by two to represent the incremental impact of EPSS. c) Column U, “2023_percentage_epss_enabled”, in the “CPZ Data” tab referenced reflects the number of days in 2023 in which a circuit was enabled with EPSS reflected as a percentage of the 2023 calendar year. d) Column V, “2023_epss_protected_circuit_mile_days”, in the “CPZ Data” tab referenced reflects the number of days in 2023 in which a circuit was enabled with EPSS multiplied by the circuit miles. | Holly Wehrman | 2024-04-17 | 2024-04-22 | 2024-04-22 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_046.zip | 1 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23-06 – Continuation of Grid Hardening Joint Studies | ACI 23-06 Continuation of Grid Hardening Joint Studies
589 | CalPA | Set WMP-46 | CalPA_Set WMP-46 | 2 | CalPA_Set WMP-46_Q2 | PG&E’s Community Wildfire Safety Program website4 includes two procedures related to infrared (IR) inspections: TD-1001P-14 and TD-2022P-01. a) Please describe the circumstances in which PG&E utilizes the TD-1001P-14 procedure. b) Please describe the circumstances in which PG&E utilizes the TD-2022P-01 procedure. c) Please provide copies of all current bulletins or job aids associated with TD-1001P-14 that direct inspectors on how to perform IR inspections. d) Please provide copies of all current bulletins or job aids associated with TD-2022P-01 that direct inspectors on how to perform IR inspections. e) Please provide copies of all prior revisions of TD-1001P-14, including bulletins or job aids associated with those prior revisions. f) Please provide copies of all prior revisions of TD-2022P-01, including bulletins or job aids associated with those prior revisions. g) Please identify all procedures (including associated bulletins or job aids) related to infrared inspections of distribution infrastructure that were in effect during 2023. h) Please provide copies of each document responsive to part (g) that has not been provided in response to previous parts of this question. i) Please identify all procedures (including associated bulletins or job aids) related to infrared inspections of distribution infrastructure that were in effect during 2020. j) Please provide copies of each document responsive to part (i) that has not been provided in response to previous parts of this question. k) Please identify all procedures (including associated bulletins or job aids) related to infrared inspections of distribution infrastructure that were in effect during 2017. l) Please provide copies of each document responsive to part (k) that has not been provided in response to previous parts of this question. m) Please identify all procedures (including associated bulletins or job aids) related to infrared inspections of distribution infrastructure that were in effect during 2014. n) Please provide copies of each document responsive to part (m) that has not been provided in response to previous parts of this question. | a) PG&E performs infrared inspections on overhead transmission lines in accordance with the frequency defined in TD-8123P-100 “Transmission Patrols and Enhanced Inspection Frequency Guidelines” and inspection method requirements defined in TD-1001P-14 “Infrared (IR) Inspection Procedures”. Please see attachment “WMPDiscovery2023-2025_DR_CalAdvocates_046-Q002Atch01CONF.pdf” for a copy of TD-8123P-100, Revision (Rev.) 1, and attachment “WMP-Discovery2023- 2025_DR_CalAdvocates_046-Q002Atch02CONF.pdf” for a copy of TD-1001P-14, Rev 4. b) PG&E performs infrared inspections on overhead and underground electric distribution facilities in accordance with inspection method requirements defined in with TD-2022P-01 Rev 2 “Infrared (IR) Inspections of Electric Distribution Facilities” and TD-2305M Electric Distribution Preventative Maintenance Manual, available on PG&E’s website at the following link: https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparednessand-support/TD-2305M.pdf. Please see attachment “WMP-Discovery2023- 2025_DR_CalAdvocates_046-Q002Atch03CONF.pdf” for the current version of procedure TD-2022P-01 (Rev 2). c) Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_046- Q002Atch04.pdf” for the current Rev 2 of TD-1001M-JA19 “Evaluating Conditions from Infrared (IR) Inspections in Transmission Lines.” d) Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_046- Q002Atch05CONF.pdf" for TD-2305M-JA03, Rev 4, for the Underground Inspection Job Aid associated with TD-2022P-01. e) Please see the following for table for prior revisions of TD-1001P-14 and its associated Job Aid (JA)19. Procedure Name Attachment Name TD-1001P-14, Rev 0 Published August 2020 WMP-Discovery2023-2025_DR_CalAdvocates_046-Q002Atch06CONF.pdf TD-1001P-14, Rev 1 Published April 2021 WMP-Discovery2023-2025_DR_CalAdvocates_046-Q002Atch07CONF.pdf TD-1001P-14, Rev 2 Published December 2021 WMP-Discovery2023-2025_DR_CalAdvocates_046-Q002Atch08CONF.pdf TD-1001P-14, Rev 3 Published December 2022 WMP-Discovery2023-2025_DR_CalAdvocates_046-Q002Atch09CONF.pdf TD-1001P-14, Rev 4 Published April 2024 WMP-Discovery2023-2025_DR_CalAdvocates_046-Q002Atch10CONF.pdf TD-1001M-JA19 Rev 0 Effective March 2020 WMP-Discovery2023-2025_DR_CalAdvocates_046-Q002Atch11.pdf TD-1001M-JA19 Rev 1 Effective April 2021 WMP-Discovery2023-2025_DR_CalAdvocates_046-Q002Atch12.pdf Procedure Name Attachment Name TD-1001M-JA19 Rev 2 Effective February 2023 WMP-Discovery2023-2025_DR_CalAdvocates_046-Q002Atch04.pdf f) Please see the following for table for prior revisions of TD-2022P-01 and its associated Job Aid (JA) 03. Procedure Name Attachment Name TD-2022P-01 Rev 0 Published December 2013 WMP-Discovery2023-2025_DR_CalAdvocates_046-Q002Atch13CONF.pdf TD-2022P-01 Rev 1 Published May 2018 WMP-Discovery2023-2025_DR_CalAdvocates_046-Q002Atch14CONF.pdf TD-2022P-01 Rev 2 Published December 2023 WMP-Discovery2023-2025_DR_CalAdvocates_046-Q002Atch03.pdf TD 2305M-JA03, Rev 2* Published October 2012 WMP-Discovery2023-2025_DR_CalAdvocates_046-Q002Atch15.pdf TD 2305M-JA03, Rev 3 Published March 2013 WMP-Discovery2023-2025_DR_CalAdvocates_046-Q002Atch16CONF.pdf TD 2305M-JA03, Rev 2.3 Published July 2015 WMP-Discovery2023-2025_DR_CalAdvocates_046-Q002Atch17.pdf TD 2305M-JA03, Rev 3 Published January 2020 WMP-Discovery2023-2025_DR_CalAdvocates_046-Q002Atch18CONF.pdf TD 2305M-JA03, Rev 4 Effective August 2022 WMP-Discovery2023-2025_DR_CalAdvocates_046-Q002Atch05CONF.pdf *Despite a reasonable search of available records, PG&E was unable to locate revisions to 2305M-JA03 prior to 2012. g) Please see “WMP-Discovery2023-2025_DR_CalAdvocates_046- Q002Atch06CONF.pdf “ for the procedure and “WMP-Discovery2023- 2025_DR_CalAdvocates_046-Q002Atch14CONF.pdf” for the JA in effect during 2023. h) Please see the attachments identified in response to subpart (g) and included with this response. i) Please see “WMP-Discovery2023-2025_DR_CalAdvocates_046-Q002Atch04.pdf” for the procedure and “WMP-Discovery2023-2025_DR_CalAdvocates_046- Q002Atch18CONF.pdf” for the JA in effect during 2020. j) Please see the attachment identified in response to subpart (i) and included with this response. k) Please see “WMP-Discovery2023-2025_DR_CalAdvocates_046- Q002Atch13CONF.pdf” for PG&E’s procedure specific to infrared inspections or distribution infrastructure that was in effect in 2017 and “WMP-Discovery2023- 2025_DR_CalAdvocates_046-Q002Atch17.pdf” for the JA in effect during 2017. l) Please see the attachment identified in response to subpart (k) and included with this response. m) Please see and “WMP-Discovery2023-2025_DR_CalAdvocates_046- Q002Atch13CONF.pdf” for the procedure and “WMP-Discovery2023- 2025_DR_CalAdvocates_046-Q002Atch17.pdf" for the JA in effect during 2014. n) Please see the attachments identified in response to subpart (m) and included with this response. | Holly Wehrman | 2024-04-17 | 2024-04-22 | 2024-04-22 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_046.zip | 18 | N/A | 8.1.3.1.4 | 8.0 Wildfire Mitigations | 8.1.3.1.4 Infrared Inspection | ACI 23-09 – Decrease in Detailed Distribution Inspections
590 | CalPA | Set WMP-46 | CalPA_Set WMP-46 | 3 | CalPA_Set WMP-46_Q3 | In response to data request CalAdvocates-PGE-2025WMP-03, question 1, PG&E provided attachment “WMP-Discovery2023-2025_DR_CalAdvocates_039-Q001Atch01.xlsx” The following questions refer to the tab “2023 QASI Distribution YTD Raw”. a) 47 entries have “Yes” for ObservationOrNonconf (column J) and “None” for FindingPriority (column P). Please explain the circumstances under which there would be findings with no priority assigned. b) Please explain what an entry of “OTR” in SpeccFinding (column Q) means. | a) Circumstances that would have a “Yes” for ObservationOrNonconf (column J) would include findings that may or may not require a tag to be written. The majority of the 47 entries listed are photo discrepancies that are not assigned any priority (FindingPriority column P). Additional examples would include documentation errors, for example, previous tags created in error or existing tags requiring additional information and Third Party notifications. The remainder of the 47 entries are data entry errors that should have been labeled “CritAtt” or “Re-Insp”” as E or F tags were created. These will be used for training and improvement examples. b) Column Q “OTR” is the entry for any “other” type of finding that is not identified as “Bprty”, “CritAtt”, “Emerg”, or “Re-Insp”. It also identifies any inspection that has multiple findings associated with the asset. | Holly Wehrman | 2024-04-17 | 2024-04-25 | 2024-04-25 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_046.zip | 0 | N/A | 8.1.6 | Section 8.1.6 - Quality Assurance and Quality Control | 8.1.6.1 Quality Assurance (QA) | N/A
591 | CalPA | Set WMP-46 | CalPA_Set WMP-46 | 4 | CalPA_Set WMP-46_Q4 | In response to data request CalAdvocates-PGE-2025WMP-03, question 1, PG&E provided attachment “WMP-Discovery2023-2025_DR_CalAdvocates_039-Q001Atch02.xlsx”. The following questions refer to the tab “2023 QASI Transmission YTD Raw”: a) Seven entries have a QC Date (column D) that is earlier than the Inspection Date (column F). For each such entry, explain why this is the case. b) Please define “QC Date” (column D). c) Please define “QA Completion Date” (column C). d) Does PG&E have a standard for the maximum amount of time that is allowable between an inspection and the QC date? e) If the answer to part (d) is yes, what is the maximum amount of time that is allowable between an inspection and the QC date? f) If the answer to part (d) is yes, please provide any relevant procedures, specifications, job aids, bulletins, or other documentation to support your answer. g) If the answer to part (d) is no, why not? h) Does PG&E have a standard for the maximum amount of time that is allowable between an inspection and the QA completion date? i) If the answer to part (h) is yes, what is the maximum amount of time that is allowable between an inspection and the QA completion date? j) If the answer to part (h) is yes, please provide any relevant procedures, specifications, job aids, bulletins, or other documentation to support your answer. k) If the answer to part (h) is no, why not? | a) The inspection date should be earlier than the QC date. The referenced entries were errors which occurred for specific instances when a reinspection was performed. In these instances, the system of record automatically updated the original inspection date to the reinspection date. PG&E has since corrected this automated error in its system. b) “QC Date” (column D) refers to the date that the QC inspection was completed. c) "QA Completion Date” is the date that the Subject Matter Expert completes the review process and submits the record to the database as approved/accurate/complete. d) No, PG&E does not have a standard for the maximum amount of time that is allowable between the completion of the QC inspection and the start of the QA inspection. Generally, QA will inspect the asset three to six weeks after the completion of the QC inspection and the majority of the QA inspections are completed in this time frame. Times will vary due to the review and verification process conducted by QC for each individual asset assessment. e) Not applicable, please see the response to subpart (d) above. f) Not applicable, please see the response to subpart (d) above. g) Please see the response to subpart (d) for the requested explanation. h) PG&E does not have a standard for the maximum amount of time allowable between the QA inspection start and the QA completion date. Generally, the time from sample availability to audit completion is seven days and the majority of the QA inspections are completed in this timeframe. Occasionally, additional time is required for review and alignment which is done as rapidly as possible and is usually completed within an additional seven days. i) Not applicable, please see the response to subpart (h) above. j) Not applicable, please see the response to subpart (h) above. k) Please see response to subpart (h) for the requested explanation. | Holly Wehrman | 2024-04-17 | 2024-04-25 | 2024-04-25 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_046.zip | 0 | N/A | 8.1.6 | Section 8.1.6 - Quality Assurance and Quality Control | 8.1.6.1 Quality Assurance (QA) | N/A
592 | CalPA | Set WMP-46 | CalPA_Set WMP-46 | 5 | CalPA_Set WMP-46_Q5 | In response to data request CalAdvocates-PGE-2025WMP-03, question 1, PG&E provided attachment “WMP-Discovery2023-2025_DR_CalAdvocates_039-Q001Atch03.xlsx”. The following questions refer to the tab “Routine”: a) Please define “QC Date” (column R). b) Please define “QV Date” (column P). c) Does PG&E have a standard for the maximum amount of time that is allowable between an inspection and the QC date? d) If the answer to part (c) is yes, what is the maximum amount of time that is allowable between an inspection and the QC date? e) If the answer to part (c) is yes, please provide any relevant procedures, specifications, job aids, bulletins, or other documentation to support your answer. f) If the answer to part (c) is no, why not? g) Does PG&E have a standard for the maximum amount of time that is allowable between an inspection and the QV date? h) If the answer to part (g) is yes, what is the maximum amount of time that is allowable between an inspection and the QV date? i) If the answer to part (g) is yes, please provide any relevant procedures, specifications, job aids, bulletins, or other documentation to support your answer. j) If the answer to part (g) is no, why not? | An attachment to this response contains CONFIDENTIAL information provided pursuant to the accompanying confidentiality declaration. a) “QC Date” is the date when the QC Specialist completed the review. b) “QV Date” is the date the Quality Assurance-Performance (QA-P) auditor completed the review. c) Yes, PG&E has a standard for the maximum amount of time that is allowable between an inspection and the QC date. d) A QC review should occur before the next routine Vegetation Management (VM) Execution routine inspection. e) Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_046- Q005Atch01CONF.pdf” for PG&E’s Quality Control Vegetation Management Business Process Document. f) Not applicable, please see the response to subpart (c) above. g) No, PG&E does not have a standard for the maximum amount of time that is allowable between an inspection and the QV date. h) Not applicable, please see the response to subpart (g) above. i) Not applicable, please see the response to subpart (g) above. j) The QV (QA) date is dependent on QC date, which is consequently dependent on work Execution date. Inspections past the next routine cycle would be excluded prior to QA sampling as a result of the QC exclusion process. QA-P is currently performing its reviews within 30 days of QC completion. | Holly Wehrman | 2024-04-17 | 2024-04-25 | 2024-04-25 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_046.zip | 1 | N/A | 8.1.6 | Section 8.1.6 - Quality Assurance and Quality Control | 8.1.6.1 Quality Assurance (QA) | N/A
593 | CalPA | Set WMP-46 | CalPA_Set WMP-46 | 6 | CalPA_Set WMP-46_Q6 | In response to data request CalAdvocates-PGE-2025WMP-03, question 1, PG&E provided attachment “WMP-Discovery2023-2025_DR_CalAdvocates_039-Q001Atch03.xlsx”. The following questions refer to the tab “Transmission”: a) Please define “QC Date” (column S). b) Please define “QV Date” (column Q). c) Does PG&E have a standard for the maximum amount of time that is allowable between an inspection and the QC date? d) If the answer to part (c) is yes, what is the maximum amount of time that is allowable between an inspection and the QC date? e) If the answer to part (c) is yes, please provide any relevant procedures, specifications, job aids, bulletins, or other documentation to support your answer. f) If the answer to part (c) is no, why not? g) Does PG&E have a standard for the maximum amount of time that is allowable between an inspection and the QV date? h) If the answer to part (g) is yes, what is the maximum amount of time that is allowable between an inspection and the QV date? i) If the answer to part (g) is yes, please provide any relevant procedures, specifications, job aids, bulletins, or other documentation to support your answer. j) If the answer to part (g) is no, why not? | Please see the responses to Question No. 005, subparts (a) to (j), which also apply to this request and provide the information sought. | Holly Wehrman | 2024-04-17 | 2024-04-25 | 2024-04-25 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_046.zip | 0 | N/A | 8.1.6 | Section 8.1.6 - Quality Assurance and Quality Control | 8.1.6.1 Quality Assurance (QA) | N/A
594 | CalPA | Set WMP-46 | CalPA_Set WMP-46 | 7 | CalPA_Set WMP-46_Q7 | In response to data request CalAdvocates-PGE-2025WMP-03, question 1, PG&E provided attachment “WMP-Discovery2023-2025_DR_CalAdvocates_039-Q001Atch03.xlsx”. The following questions refer to the tab “Pole Clearing”: a) Please define “QC Date” (column P). b) Please define “QV Date” (column N). c) Does PG&E have a standard for the maximum amount of time that is allowable between an inspection and the QC date? d) If the answer to part (c) is yes, what is the maximum amount of time that is allowable between an inspection and the QC date? e) If the answer to part (c) is yes, please provide any relevant procedures, specifications, job aids, bulletins, or other documentation to support your answer. f) If the answer to part (c) is no, why not? g) Does PG&E have a standard for the maximum amount of time that is allowable between an inspection and the QV date? h) If the answer to part (g) is yes, what is the maximum amount of time that is allowable between an inspection and the QV date? i) If the answer to part (g) is yes, please provide any relevant procedures, specifications, job aids, bulletins, or other documentation to support your answer. j) If the answer to part (g) is no, why not? | Please see the responses to Question No. 005, subparts (a) to (j), which also apply to this request and provide the information sought. | Holly Wehrman | 2024-04-17 | 2024-04-25 | 2024-04-25 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_046.zip | 0 | N/A | 8.1.6 | Section 8.1.6 - Quality Assurance and Quality Control | 8.1.6.1 Quality Assurance (QA) | N/A
595 | CalPA | Set WMP-46 | CalPA_Set WMP-46 | 8 | CalPA_Set WMP-46_Q8 | In response to data request CalAdvocates-PGE-2025WMP-03, question 1, PG&E provided attachment “WMP-Discovery2023-2025_DR_CalAdvocates_039-Q001Atch08.xlsx”. The following questions refer to the tab “2023 SI Transmission Desktop QC”: a) Please explain what an entry of “Photos are not adequate per compliance training” in Discrepancy Code Description (column I) means. b) If photos are not adequate per compliance training, is it possible to complete QC for that inspection? Explain why or why not. c) Please provide any relevant procedures, specifications, job aids, bulletins, or other documentation to support your answer to part (b). d) If photos are not adequate per compliance training, what actions do QC personnel take to complete QC? e) Please provide any relevant procedures, specifications, job aids, bulletins, or other documentation to support your answer to part (d). | An attachment to this response contains CONFIDENTIAL information provided pursuant to the accompanying confidentiality declaration. a) The referenced entry represented when the photos provided do not meet the guidance specified in the Transmission Ground New Inspector Training. b) If photos are not adequate, it is possible to complete QC for that inspection through a desktop review which verifies inspection results of attributes that can be validated from the available compliant photographs on the inspection record. A Field review is also completed at the asset location to assesses the conditions in real time as well as utilizing the photographs from the original inspection record. c) Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_046- Q008Atch01CONF.pdf” for PG&E’s Transmission Ground New Inspector Training. d) Desktop QC will document all inspection photograph discrepancies on the QC record for tracking and trending. QC will complete review of all available sections/attributes of the inspection record where compliant photographs were available. QC will discontinue review and recommend a reinspection of the asset as a follow up if: (1) the structure number is not visible in inspection record in any section of the inspection and QC cannot confirm inspector was at the correct location; or (2) there are no photos of insulators, or all photos of insulators appear to be from a different structure. e) PG&E does not have a formal standard for the process outlined in subpart (d). | Holly Wehrman | 2024-04-17 | 2024-04-25 | 2024-04-25 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_046.zip | 1 | N/A | 8.1.6 | Section 8.1.6 - Quality Assurance and Quality Control | 8.1.6.1 Quality Assurance (QA) | N/A
596 | CalPA | Set WMP-46 | CalPA_Set WMP-46 | 9 | CalPA_Set WMP-46_Q9 | In response to data request CalAdvocates-PGE-2025WMP-03, question 1, PG&E provided attachment “WMP-Discovery2023-2025_DR_CalAdvocates_039-Q006Atch01.xlsx,” which relates to asset inspections in 2023. Line 8 indicates that, out of 133 transmission intrusive pole inspections reviewed by desktop QC, 108 failed QC review. Line 9 indicates that, out of 149 transmission intrusive pole inspections reviewed by field QC, 134 failed QC review. a) Has PG&E made any changes to its intrusive inspection practices for transmission pole inspections as a result of the high QC failure rates? b) If the answer to part (a) is yes, describe the changes PG&E has made. c) Provide any relevant procedures, specifications, job aids, bulletins, or other documentation to support your answer to part (b). d) If the answer to part (a) is no, state why not. e) Has PG&E made any changes to its QC review process for intrusive inspections of transmission poles as a result of the high QC failure rates? f) If the answer to part (e) is yes, describe the changes PG&E has made. g) Provide any relevant procedures, specifications, job aids, bulletins, or other documentation to support your answer to part (f). h) If the answer to part (e) is no, state why not. i) Please describe any other actions PG&E took as a result of the high QC failure rates in 2023 noted above. j) What were the primary reasons for transmission intrusive pole inspections to fail desktop QC review in 2023? k) What were the primary reasons for transmission intrusive pole inspections to fail field QC review in 2023? | a) Yes, PG&E is in the process of updating Utility Procedure TD-2325P-01, which provides instruction for intrusively inspective, testing, restoring, reinforcing, treating, and reusing wood poles. As part of this procedure revision, PG&E is addressing potential inspection quality concerns. Please see the response to subpart (j) for additional information regarding the referenced “failure” rates. b) Please see the response to subpart (a) for the requested information. c) We are still in the process of finalizing Revision 4 of TD-2325P-01 and will provide a copy when it is finalized. As of this response, we do not have a specific date for when we expect it to be finalized. d) Not applicable, please see the response to subpart (a). e) Yes, please see the response to subpart (a). f) Please see the response to subpart (a). g) The revised procedures are still being drafted, please see response to subpart (c). h) Not applicable, please see the response to subpart (e). i) Another action that PG&E took was to grow its Pole Test and Treat Program to include a field team and dedicated staff to mitigate quality findings. j) The “failure” rate indicated in the referenced spreadsheet does not represent a failed inspection. PG&E marks “failed” during the QC review process if an inspector did not accurately identify a checklist attribute. k) Please see the response to subpart (j) above. | Holly Wehrman | 2024-04-17 | 2024-04-25 | 2024-04-25 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_046.zip | 0 | N/A | 8.1.6 | Section 8.1.6 - Quality Assurance and Quality Control | 8.1.6.1 Quality Assurance (QA) | N/A
597 | CalPA | Set WMP-46 | CalPA_Set WMP-46 | 10 | CalPA_Set WMP-46_Q10 | In response to data request CalAdvocates-PGE-2025WMP-03, question 1, PG&E provided attachment “WMP-Discovery2023-2025_DR_CalAdvocates_039-Q006Atch01.xlsx,” which relates to asset inspections in 2023. Line 16 indicates that, out of 2820 distribution intrusive pole inspections reviewed by desktop QC, 1672 failed QC review. Line 17 indicates that, out of 1491 distribution intrusive pole inspections reviewed by field QC, 1021 failed QC review. a) Has PG&E made any changes to its intrusive inspection practices for distribution pole inspections as a result of the high QC failure rates? b) If the answer to part (a) is yes, describe the changes PG&E has made. c) Provide any relevant procedures, specifications, job aids, bulletins, or other documentation to support your answer to part (b). d) If the answer to part (a) is no, state why not. e) Has PG&E made any changes to its QC review process for intrusive inspections of distribution poles as a result of the high QC failure rates? f) If the answer to part (e) is yes, describe the changes PG&E has made. g) Provide any relevant procedures, specifications, job aids, bulletins, or other documentation to support your answer to part (f). h) If the answer to part (e) is no, state why not. i) Please describe any other actions PG&E took as a result of the high QC failure rates in 2023 noted above. j) What were the primary reasons for distribution intrusive pole inspections to fail desktop QC review in 2023? k) What were the primary reasons for distribution intrusive pole inspections to fail field QC review in 2023? | Please see the responses to Question No. 009, subparts (a) to (k), which also apply to this request and provide the information sought. | Holly Wehrman | 2024-04-17 | 2024-04-25 | 2024-04-25 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_046.zip | 0 | N/A | 8.1.6 | Section 8.1.6 - Quality Assurance and Quality Control | 8.1.6.1 Quality Assurance (QA) | N/A
598 | OEIS | 016 | OEIS_016 | 1 | OEIS_016_Q1 | Q01. Regarding PG&E’s Response to PG&E-23-15 a. In PG&E’s response to PG&E-23-15, it says that “the following information will be digitally recorded for trees prescribed for removal.”1 i. Did PG&E “enhance the One VM application for Routine, and Second Patrol to include capability to capture factors for prescribing trees for removal” by its target completion date of 1/31/2024?2 (1) If not, explain the reason for the delay and provide an updated target completion date for inclusion of this capability in One VM. ii. Provide the One VM form that “capture[s] factors for prescribing trees for removal.” iii. Is PG&E on track to “Enhance the application for the Vegetation Management for Operational Mitigations (VMOM) - VMPI2 - and Tree Removal Inventory (TRI) - Field Maps - program to include capability to capture factors for prescribing trees for removal” by its target completion date of 11/15/2024?3 (1) If not, explain the reason for the delay and provide an updated target completion date for this planned enhancement. b. In PG&E’s response to PG&E-23-15, it says that “PG&E will be making digital record enhancements to FTI potential strike trees.”4 i. Did PG&E “Enhance record keeping practices for the Focused Tree Inspection program (FTI) by creating records of all potential strike trees inspected using a digitized Tree Risk Assessment form” by it target completion date of 3/31/2024?5 (1) If not, explain the reason for the delay and provide an updated timeline for inclusion of this capability in One VM. ii. Provide PG&E’s digitized Tree Risk Assessment form. | a. i. Yes, PG&E completed our enhancement of the One VM application for Routine and Second Patrol to include capabilities to capture factors for prescribing trees for removal by January 31, 2024. • Please see the 5 Minute Meeting “WMP-Discovery2023- 2025_DR_OEIS_016-Q001Atch01CONF.pdf” delivered to VM personnel via VM Program Communications on January 31, 2024, that calls out the requirement to document reasons for removals within system of record. • Please see Utility Bulletin TD-7102P-01-B036 “WMP-Discovery2023- 2025_DR_OEIS_016-Q001Atch02CONF.pdf” referenced in the 5MM published on January 30, 2024 with an effective date of January 30, 2024 that provides instructions on how to document ‘reasons for removal’ within One VM. ii. Please note, PG&E believes the use of ‘form’ here is incorrect. One VM is an application and the enhancement referenced above was completed within the One VM mobile application utilized by our VM personnel. Please see screenshots below showing that this field is now available within the One VM application. Please see “WMP-Discovery2023-2025_DR_OEIS_016-Q001Atch03.pdf” for additional examples of the ’Removal Reason’ field in the One VM application. iii. Yes, PG&E is still on track to enhance VMOM and TRI program to include the capability to capture factors for prescribing trees for removal by November 15, 2024. Please note, since this objective was written, the timeline of programs to be onboarded onto the One VM platform has changed, and by the time this objective is due, both the VMOM and TRI programs will be integrated into the One VM platform, and no longer utilizing VMPI2 or Field Maps. The One VM application already captures factors for prescribing trees for removal, so the objective intent will still be met. b. i. Yes, PG&E completed the digitization of the TRAQ form on March 25, 2024, however, based upon feedback from both the Operational Observer and Energy Safety, PG&E’s operational approach to FTI was changed to only fill out a TRAQ form on trees prescribed for work. Filling out TRAQ forms on inventory only trees required excessive use of limited TRAQ certified resources, which did not meet the intent of the program. A level 2 inspection will still be performed on all strike potential trees. All strike potential trees between January 1, 2024 to April 8, 2024 will have a record with a Paper TRAQ form attached. On April 8, 2024, PG&E readjusted our approach for FTI and requires a level 2 inspection and a paper TRAQ form to be attached to records with assigned prescriptions. Records marked ‘no work’ will receive a level 2 inspection and TRAQ forms are not required to be attached. With this change, new enhancements are required for us to utilize the digital TRAQ form in One VM. We expect to implement the use of the digitized TRAQ forms in Q3 2024. ii. Please see “WMP-Discovery2023-2025_DR_OEIS_016- Q001Atch04CONF.pdf” for an example of the PG&E digitized Tree Risk Assessment form housed within the One VM application. | Brad Hill | 2024-04-22 | 2024-04-25 | 2024-04-25 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/OEIS_016.zip | 4 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--15 Implementation of Focused Tree Inspections and Addressing the Risk from Hazard Trees | ACI 23-15 Implementation of Focused Tree Inspections and Addressing the Risk from Hazard Trees
598 | OEIS | 016 | OEIS_016 | 1(a) | OEIS_016_Q1(a) | Q01. Regarding PG&E’s Response to PG&E-23-15 a. In PG&E’s response to PG&E-23-15, it says that “the following information will be digitally recorded for trees prescribed for removal.”1 i. Did PG&E “enhance the One VM application for Routine, and Second Patrol to include capability to capture factors for prescribing trees for removal” by its target completion date of 1/31/2024?2 (1) If not, explain the reason for the delay and provide an updated target completion date for inclusion of this capability in One VM. ii. Provide the One VM form that “capture[s] factors for prescribing trees for removal.” iii. Is PG&E on track to “Enhance the application for the Vegetation Management for Operational Mitigations (VMOM) - VMPI2 - and Tree Removal Inventory (TRI) - Field Maps - program to include capability to capture factors for prescribing trees for removal” by its target completion date of 11/15/2024?3 (1) If not, explain the reason for the delay and provide an updated target completion date for this planned enhancement. b. In PG&E’s response to PG&E-23-15, it says that “PG&E will be making digital record enhancements to FTI potential strike trees.”4 i. Did PG&E “Enhance record keeping practices for the Focused Tree Inspection program (FTI) by creating records of all potential strike trees inspected using a digitized Tree Risk Assessment form” by it target completion date of 3/31/2024?5 (1) If not, explain the reason for the delay and provide an updated timeline for inclusion of this capability in One VM. ii. Provide PG&E’s digitized Tree Risk Assessment form. | a. i. Yes, PG&E completed our enhancement of the One VM application for Routine and Second Patrol to include capabilities to capture factors for prescribing trees for removal by January 31, 2024. • Please see the 5 Minute Meeting “WMP-Discovery2023- 2025_DR_OEIS_016-Q001Atch01CONF.pdf” delivered to VM personnel via VM Program Communications on January 31, 2024, that calls out the requirement to document reasons for removals within system of record. • Please see Utility Bulletin TD-7102P-01-B036 “WMP-Discovery2023- 2025_DR_OEIS_016-Q001Atch02CONF.pdf” referenced in the 5MM published on January 30, 2024 with an effective date of January 30, 2024 that provides instructions on how to document ‘reasons for removal’ within One VM. ii. Please note, PG&E believes the use of ‘form’ here is incorrect. One VM is an application and the enhancement referenced above was completed within the One VM mobile application utilized by our VM personnel. Please see screenshots below showing that this field is now available within the One VM application. Please see “WMP-Discovery2023-2025_DR_OEIS_016-Q001Atch03.pdf” for additional examples of the ’Removal Reason’ field in the One VM application. 5 PG&E’s 2023-2025 WMP Update (Rev. #4, January 8, 2024), p. 648 (https://efiling.energysafety.ca.gov/eFiling/Getfile.aspx?fileid=56145&shareable=true, accessed April 17,2024). WildfireMitigationPlansDiscovery2023_DR_OEIS_016-Q001Rev01 Page 3 iii. Yes, PG&E is still on track to enhance VMOM and TRI program to include the capability to capture factors for prescribing trees for removal by November 15, 2024. Please note, since this objective was written, the timeline of programs to be onboarded onto the One VM platform has changed, and by the time this objective is due, both the VMOM and TRI programs will be integrated into the One VM platform, and no longer utilizing VMPI2 or Field Maps. The One VM application already captures factors for prescribing trees for removal, so the objective intent will still be met. b. i. Yes, PG&E completed the digitization of the TRAQ form on March 25, 2024. New enhancements are required for us to utilize the digital TRAQ form in One VM. We expect to implement the use of the digitized TRAQ forms in Q3 2024. As the program has matured, PG&E’s operational approach to FTI was changed to have inspectors fill out a TRAQ form only on those trees likely to fail (either trunk or branch) within the next 15 months and which are accordingly prescribed work. Filling out TRAQ forms on inventory-only, no-work trees or on trees only requiring trimming to maintain routine radial compliance required excessive use of limited TRAQ-certified resources, which did not meet the intent of the program. A level 2 inspection will still be performed on all strike-potential trees, and a record including tree locations and confirmation of the level 2 inspection will be recorded in One VM. All strike-potential trees between January 1, 2024 to April 8, 2024, regardless of whether tree work was prescribed, will have a record with a fully complete paper TRAQ form attached. After April 8, 2024, all strike-potential trees will have a level 2 inspection and a paper TRAQ form will also be attached to records with assigned prescriptions meeting the criteria of likelihood of failure in the next 15 months. For all strike-potential trees that are not prescribed tree work, a record including tree locations and confirmation of the level 2 inspection will be recorded in One VM. ii. Please see “WMP-Discovery2023-2025_DR_OEIS_016- Q001Atch04CONF.pdf” for an example of the PG&E digitized Tree Risk Assessment form housed within the One VM application. | Brad Hill | 2024-04-22 | 2024-06-21 | 2024-06-21 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/OEIS_016.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--15 Implementation of Focused Tree Inspections and Addressing the Risk from Hazard Trees | ACI 23-15 Implementation of Focused Tree Inspections and Addressing the Risk from Hazard Trees
599 | OEIS | 016 | OEIS_016 | 2 | OEIS_016_Q2 | Q02. Regarding PG&E’s Quarterly Targets for Routine Patrol In PG&E’s 2025 WMP Update, PG&E sets quarterly targets for Routine Patrol – Distribution (VM-16); 2023 and 2024 targets are included for reference: PG&E’s Routine Patrol Targets by Year in Circuit Miles6 Year End of Q2 End of Q3 End of Year 2023 41,761 61,806 79,000 2024 39,325 58,988 78,650 2025 31,280 50,830 78,200 %△ 2023-2025 -28.7% -19.5% -1% While PG&E’s end of year target has remained relatively constant from 2023 to 2025, the end of Q2 and end of Q3 targets have decreased year-over-year. a. Why have PG&E’s end of Q2 and end of Q3 targets for routine patrol decreased year-over-year since 2023? b. What percentage of PG&E’s end of Q2 and end of Q3 2025 targets will be completed within the HFTD? c. How will PG&E ensure that the HFTD and other high fire risk areas are inspected in a timely manner to mitigate wildfire risk before and during wildfire season? | a. The targets were reduced in Q2 and Q3 in subsequent years to provide the operations team with greater flexibility during the course of the year. PG&E anticipated slowdowns due to the change in software platform, incorporating other planned vegetation program inspections into the routine patrol where possible, and changes to other VM programs that would impact our routine work. The weather and other external factors can also cause delays in the inspection schedule. b. Approximately 50% of the Q2 end mileage is located in HFTD, and approximately 45% of the Q3 end mileage is located in HFTD. c. PG&E has designed its program through the routine and second patrols to patrol the entire HFTD/HFRA portions of the system twice a year. Once in the first half and once in the second half. Or, in other words, once in the routine patrol and once in the second patrol. | Brad Hill | 2024-04-22 | 2024-04-25 | 2024-04-25 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/OEIS_016.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23-09 – Decrease in Detailed Distribution Inspections | ACI 23-09 – Decrease in Detailed Distribution Inspections
600 | OEIS | 016 | OEIS_016 | 3(s2) | OEIS_016_Q3(s2) | Q03. Regarding PG&E’s Adjustments to its WDRM In its 2025 WMP Update, PG&E discusses the changes made between its Wildfire Distribution Risk Model (WDRM) Version 3 (V3) to Version 4 (V4). Based off those changes, provide: a. An updated version of Table 6-5 from its 2023-2025 WMP based on any changes made to the top risk circuit segments between V3 and V4. b. An updated version of Table 7-2 from its 2023-2025 WMP based on any changes made to the top risk circuit segments between V3 and V4. c. An updated version of Table 6-5 from its 2023-2025 WMP based on any changes made to the top risk circuit segments between V3 and V4. d. An updated version of Figure 7-1 from its 2023-2025 WMP based on any changes made to the top risk circuit segments between V3 and V4. e. An updated version of Table 7-4 from its 2023-2025 WMP based on any changes made to the top risk circuit segments between V3 and V4. f. A graph demonstrating the overlayed risk scores between V3 and V4, similar to the graph provided in Data Request OEIS-PG&E-22-016 Question 17 showing the difference in output between V2 and V3. | d. Please see attachment “WMP-Discovery2023-2025_DR_OEIS_016- Q003Supp02Atch01.pdf” for the updated version of Figure 7-1 from PG&E’s 2023- 2025 Wildfire Mitigation Plan. e. Please see attachment “WMP-Discovery2023-2025_DR_OEIS_016- Q003Supp02Atch02.pdf” for a graph of the requested information. | Brad Hill | 2024-04-22 | 2024-11-08 | 2024-11-04 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/OEIS_016.zip | 2 | N/A | 6.1.2 | Section 6 - Risk Methodology and Assessment | 6.1.2 Summary of Risk Models | B.1.1. WDRM v4
600 | OEIS | 016 | OEIS_016 | 3 | OEIS_016_Q3 | Q03. Regarding PG&E’s Adjustments to its WDRM In its 2025 WMP Update, PG&E discusses the changes made between its Wildfire Distribution Risk Model (WDRM) Version 3 (V3) to Version 4 (V4). Based off those changes, provide: a. An updated version of Table 6-5 from its 2023-2025 WMP based on any changes made to the top risk circuit segments between V3 and V4. b. An updated version of Table 7-2 from its 2023-2025 WMP based on any changes made to the top risk circuit segments between V3 and V4. c. An updated version of Table 6-5 from its 2023-2025 WMP based on any changes made to the top risk circuit segments between V3 and V4. d. An updated version of Figure 7-1 from its 2023-2025 WMP based on any changes made to the top risk circuit segments between V3 and V4. e. An updated version of Table 7-4 from its 2023-2025 WMP based on any changes made to the top risk circuit segments between V3 and V4. f. A graph demonstrating the overlayed risk scores between V3 and V4, similar to the graph provided in Data Request OEIS-PG&E-22-016 Question 17 showing the difference in output between V2 and V3. | PG&E released WDRM v4 for use in January of 2024 and is currently evaluating associated work plans in future years anticipated to be described in PG&E’s 2026 WMP. Much of the analysis for the tables and figures requested in parts (a) through (f) below are included in this work and are underway. As this analysis only recently started and is still ongoing, parts (a) through (d) and (f) will require more time and part (e) will not be available until later in 2024. Please let us know if you would like to meet and confer to discuss this request, the work that needs to be done to create the requested information, and why the information is not currently available. a. The information being requested is under development and anticipated to be available around May 8, 2024. b. The information being requested is under development and anticipated to be available around May 8, 2024. c. The information being requested is under development and anticipated to be available around May 8, 2024. d. The information being requested is under development and anticipated to be available around May 8, 2024. PG&E will provide this information once it is available. However, we anticipate this analysis taking several months to complete as the WDRM v4 model was only recently released. We will provide this information once it is available. | Brad Hill | 2024-04-22 | 2024-04-25 | 2024-04-25 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/OEIS_016.zip | 0 | N/A | 6 | Section 6 - Risk Methodology and Assessment | 6.1.2 Summary of Risk Models | B.1.1. WDRM v4
600 | OEIS | 016 | OEIS_016 | 3(s) | OEIS_016_Q3(s) | Q03. Regarding PG&E’s Adjustments to its WDRM In its 2025 WMP Update, PG&E discusses the changes made between its Wildfire Distribution Risk Model (WDRM) Version 3 (V3) to Version 4 (V4). Based off those changes, provide: a. An updated version of Table 6-5 from its 2023-2025 WMP based on any changes made to the top risk circuit segments between V3 and V4. b. An updated version of Table 7-2 from its 2023-2025 WMP based on any changes made to the top risk circuit segments between V3 and V4. c. An updated version of Table 6-5 from its 2023-2025 WMP based on any changes made to the top risk circuit segments between V3 and V4. d. An updated version of Figure 7-1 from its 2023-2025 WMP based on any changes made to the top risk circuit segments between V3 and V4. e. An updated version of Table 7-4 from its 2023-2025 WMP based on any changes made to the top risk circuit segments between V3 and V4. f. A graph demonstrating the overlayed risk scores between V3 and V4, similar to the graph provided in Data Request OEIS-PG&E-22-016 Question 17 showing the difference in output between V2 and V3. | ANSWER 003 SUPPLEMENTAL 01 a. Please see worksheet “OEIS 016 Q03a” in attachment “WMP-Discovery2023- 2025_DR_OEIS_016-Q003Supp01Atch01.xlsx” for the requested information. b. Please see worksheet “OEIS 016 Q03b” in attachment “WMP-Discovery2023- 2025_DR_OEIS_016-Q003Supp01Atch01.xlsx” for the requested information. c. Please see worksheet “OEIS 016 Q03a” in attachment “WMP-Discovery2023- 2025_DR_OEIS_016-Q003Supp01Atch01.xlsx” for the requested information. d. PG&E would like to amend the response submitted on April 25, 2024, to note that the requested information is unable to be provided by May 8, 2024. Once PG&E started analyzing this request, PG&E realized two weeks was an underestimated WildfireMitigationPlansDiscovery2023_DR_OEIS_016-Q003Supp01 Page 2 time period to produce this analysis. As with the response to subpart e., PG&E will provide this information once it is available. However, anticipates the analysis taking several months to complete as the WDRM v4 model was only recently released. This information will be provided once it is available. e. PG&E will provide this information once it is available. However, PG&E anticipates this analysis taking several months to complete as the WDRM v4 model was only recently released. PG&E will provide this information once it is available. f. Please see worksheet “OEIS 016 Q03f” in attachment “WMP-Discovery2023- 2025_DR_OEIS_016-Q003Supp01Atch01.xlsx” for the requested information. ANSWER 003 PG&E released WDRM v4 for use in January of 2024 and is currently evaluating associated work plans in future years anticipated to be described in PG&E’s 2026 WMP. Much of the analysis for the tables and figures requested in parts (a) through (f) below are included in this work and are underway. As this analysis only recently started and is still ongoing, parts (a) through (d) and (f) will require more time and part (e) will not be available until later in 2024. Please let us know if you would like to meet and confer to discuss this request, the work that needs to be done to create the requested information, and why the information is not currently available. a. The information being requested is under development and anticipated to be available around May 8, 2024. b. The information being requested is under development and anticipated to be available around May 8, 2024. c. The information being requested is under development and anticipated to be available around May 8, 2024. d. The information being requested is under development and anticipated to be available around May 8, 2024. PG&E will provide this information once it is available. However, we anticipate this analysis taking several months to complete as the WDRM v4 model was only recently released. We will provide this information once it is available. | Brad Hill | 2024-04-22 | 2024-05-08 | 2024-05-08 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/OEIS_016.zip | 1 | N/A | 6.1.2 | Section 6 - Risk Methodology and Assessment | 6.1.2 Summary of Risk Models | B.1.1. WDRM v4
601 | MGRA | Data Request No. 12 | MGRA_Data Request No. 12 | 1 | MGRA_Data Request No. 12_Q1 | Please provide an Excel spreadsheet giving the mapping between PG&E weather station IDs and IDs used by Synoptic for the PG&E mesonet if these IDs are different. | PG&E weather station identification numbers (ID) directly correspond to Synoptic weather station IDs. However, Synoptic allows less characters for their IDs. PG&E slightly alters their 8-digit weather IDs to accommodate this character limit by removing the first digit of PG&E’s ID. For example, PG&E weather station with Synoptic ID "PG868" reflects PG&E weather station “PGE-1868” and Synoptic ID “608PG” reflects “PGE-2608”. | Joseph Mitchell | 2024-04-25 | 2024-04-30 | 2024-04-29 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_012.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23-23 – Weather Station Maintenance and Calibration | ACI PG&E-23-23 – Weather Station Maintenance and Calibration
602 | Green Power Institute (GPI) | 003 | Green Power Institute (GPI)_003 | 1 | Green Power Institute (GPI)_003_Q1 | Please provide any PG&E slides, meeting materials, and meeting minutes generated for and/or presented at the two Joint IOU working sessions held in 2023 to “discuss the different types of programs and practices each IOU has in place for disposing and recycling woody debris and vegetation [1].” [1] SDG&E 2025 WMP Update, April 2, 2024, pp. 52-53 | Attachments to this response contain CONFIDENTIAL information provided pursuant to the acaccompanying confidentiality declaration. Please see the following meeting invitations with agendas/questions and meeting notes for the two joint IOU working sessions held in 2023 regarding wood management. Please note, there were no other materials used by PG&E during these meetings. • June 2023 Joint IOU Working Session Attachment Name Description WMP-Discovery2023-2025_DR_GPI_003- Q001Atch01CONF.pdf June 2023_Joint IOU Fuel Management Recycling Practices Meeting Invitation WMP-Discovery2023-2025_DR_GPI_003- Q001Atch02CONF.pdf June 2023_Follow up Email “RE Meeting Notes Joint IOU Fuel Management Recycling Practices” WMP-Discovery2023-2025_DR_GPI_003- Q001Atch03CONF.pdf June 2023_Attachment to Follow up Email – “SCE Meeting Minutes FM Recycling Disposal_2023-06-20” • August 2023 Joint IOU Working Session Attachment Name Description WMP-Discovery2023-2025_DR_GPI_003- Q001Atch04CONF.pdf July 2023_Joint IOU Wood Management Practices Follow-Up Meeting Invitation WMP-Discovery2023-2025_DR_GPI_003- Q001Atch05CONF.pdf August 2023_Follow up Email “FW Joint IOU Wood Management Practices Follow-Up” WMP-Discovery2023-2025_DR_GPI_003- Q001Atch06CONF.pdf August 2023_Attachment to Follow up Email – “Joint IOU Wood Management Meeting Notes” | Zoe Harrold | 2024-04-26 | 2024-05-01 | 2024-05-01 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/GPI_003.zip | 6 | N/A | 8 | Section 8.2 - Vegetation Management and Inspections | 8.2.3 Vegetation and Fuels Management | N/A
603 | Green Power Institute (GPI) | 003 | Green Power Institute (GPI)_003 | 2 | Green Power Institute (GPI)_003_Q2 | Please provide any PG&E slides, meeting materials, and meeting minutes generated for and/or presented at the Joint IOU meeting held in 2023 to “discuss each utility’s respective fuels management programs and began initial collaboration on a possible scoping study on best practices and efficacy of fuels management [2].” [2] SDG&E 2025 WMP Update, April 2, 2024, pp. 52-53 | Attachments to this response contain CONFIDENTIAL information provided pursuant to the acaccompanying confidentiality declaration. Joint IOU discussions to review and evaluate utility fuel management programs were coordinated within a working group that had already been established to support ongoing efforts to develop and establish the Cal Poly San Luis Obispo Wildland-Urban Interface (WUI) Fire Institute. The WUI Fire Institute conducts research, training and education geared towards creating more fire-resistant communities. In October 2023, the utility stakeholders began collaboration on fuel management programs analysis. Each utility contributed to the development of an initial survey, drafting questions, soliciting responses and conducting reviews. Please see attached emails and meeting invites from October 2023 through December 2023 outlined in the table below. Attachment Name Description WMP-Discovery2023-2025_DR_GPI_003- Q002Atch01CONF.pdf Emails re: IOU Engagement with the WUI FIRE Institute WMP-Discovery2023-2025_DR_GPI_003- Q002Atch02CONF.pdf Meeting invite and Agenda re: IOU WUI Research Coordination - Fuel Clearing and Modification Study WMP-Discovery2023-2025_DR_GPI_003- Q002Atch03CONF.pdf Emails re: IOU Meeting Notes/Survey Responses WMP-Discovery2023-2025_DR_GPI_003- Q002Atch04CONF.pdf Emails re: IOU Meeting Notes/Survey Responses WMP-Discovery2023-2025_DR_GPI_003- Q002Atch05CONF.pdf Problem Statement Drafts re: IOU WUI Research Coordination - Fuel Clearing and Modification Study While the IOUs continued to work together to develop a research project request, the Cal Poly WUI Fire Institute formalized and hired a director. The IOUs requested a meeting with the WUI Fire Institute in March 2024, but the meeting did not take place until April 29, 2024, due to scheduling conflicts. The meeting with SCE, SDG&E, PG&E and Cal Poly WUI Fire Institute leadership was intended to finalize the research project request and initiate WUI Fire Institute evaluation. Efforts will continue to refine the research project proposal through 2024 to define a phased scope and delivery schedule. Please see attached emails and meeting invites from April 2024 outlined in the table below. Attachment Name Description WMP-Discovery2023-2025_DR_GPI_003- Q002Atch06CONF.pdf Meeting invite re: WUI Research Request for Fuels Management WMP-Discovery2023-2025_DR_GPI_003- Q002Atch07CONF.pdf Emails re: IOU Questionnaire Follow-Up WMP-Discovery2023-2025_DR_GPI_003- Q002Atch08CONF.pdf Meeting follow-up re: Fuels Management References | Zoe Harrold | 2024-04-26 | 2024-05-01 | 2024-05-01 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/GPI_003.zip | 8 | N/A | 8 | Section 8.2 - Vegetation Management and Inspections | 8.2.3 Vegetation and Fuels Management | N/A
604 | Green Power Institute (GPI) | 003 | Green Power Institute (GPI)_003 | 3 | Green Power Institute (GPI)_003_Q3 | Please provide a summary of any developments since the 2023 meeting and working sessions towards initiating a Joint IOU scoping study on best practices and efficacy of fuels management, including but not limited to planned topics for inclusion in the scoping study. | Please see response to Question 002 for supporting communications, meeting invites and draft research project proposal attachments for the requested information from April 2024. | Zoe Harrold | 2024-04-26 | 2024-05-01 | 2024-05-01 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/GPI_003.zip | 0 | N/A | 8 | Section 8.2 - Vegetation Management and Inspections | 8.2.3 Vegetation and Fuels Management | N/A
605 | OEIS | 017 | OEIS_017 | 1 | OEIS_017_Q1 | Regarding the Joint Utility Covered Conductor Effectiveness Weekly Meetings PG&Es 2025 Update mentions that it participated in weekly meetings with utilities in 2023 “to benchmark and share information regarding covered conductor effectiveness.” (p. 48, response to PG&E-23-04 “Cross-Utility Collaboration on Best Practices for Inclusion of Climate Change Forecasts in Consequence Modeling, Inclusion of Community Vulnerability in Consequence Modeling, and Utility Vegetation Management for Wildfire Safety”). Please explain the following: 1. Which utilities were present at these weekly meetings. 2. The first month these meetings began. 3. If these meetings were in response to a specific Area of Continued Improvement. a. If so, please state which Area of Continued Improvement. b. If not, please state what directive these meetings were in response to. | Southern California Edison (SCE) hosted the Joint Utility Covered Conductor Effectiveness Weekly meetings. Thus, PG&E reached out to SCE to confirm the information provided in response to Question No. 001. 1. SCE confirmed that participants to the referenced meetings included San Diego Gas & Electric (SDG&E), SCE, PacifiCorp, PG&E, Liberty Utilities, and Bear Valley Electric Service, Inc. 2. The meetings began in April 2023. 3. Yes, these meetings were conducted in response to Area of Continued Improvement (ACI) ACI PG&E-22--11 Covered Conductor Effectiveness Lessons Learned as well as PG&E-23-06 Continuation of Grid Hardening Joint Studies (see pages 62-67 of PG&E’s 2025 WMP Update). | Brad Hill | 2024-04-29 | 2024-05-02 | 2024-05-02 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/OEIS_017.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--04 | ACI 23-04 Cross-Utility Collaboration on Best Practicies
606 | OEIS | 017 | OEIS_017 | 2 | OEIS_017_Q2 | Regarding the Utility Undergrounding Working Group Meetings PG&Es 2025 Update mentions that “Lastly, the utilities also developed an undergrounding working group to discuss lessons learned and the challenges associated with undergrounding.” (p. 48, response to PG&E-23-04 “Cross-Utility Collaboration on Best Practices for Inclusion of Climate Change Forecasts in Consequence Modeling, Inclusion of Community Vulnerability in Consequence Modeling, and Utility Vegetation Management for Wildfire Safety”). Please explain the following: 1. Which utilities were present at these working group meetings. 2. The general duration of these meetings: a. Are these monthly, weekly, or quarterly meetings? Please specify. 3. If these meetings were in response to a specific Area of Continued Improvement a. If so, please state which Area of Continued Improvement. b. If not, please state what directive these meetings were in response to. | 1. The Joint Investor-Owned Utility (IOU) meetings are held with SDG&E and Southern California Edison (SCE). 2. a. Starting in October 2023, the meeting cadence was monthly. However, in 2024, our cadence has changed to quarterly as agreed upon by members from participating utilities. 3. a. No, these meetings were not in response to a specific Area of Continued Improvement (ACI). b. During the Joint IOU meetings, we discuss (and continue to discuss) a series of topics such as Customer Engagement Strategies, Vegetation Management, Undergrounding Project Cycle Times, Cost, and Innovative Technologies, among other items. Additionally, PG&E has participated in and will continue to participate in utility workshops hosted by entities such as Electric Power Research Institute (EPRI), where we have an opportunity to share best practices and learn from other utilities. Topics discussed during the most recent EPRI workshop included: • Excavation / Burial / Installation • Easements / Joint Use • New Equipment / Components / Tools • Customers / Community Engagement • Underground Commissioning, Maintenance and Operations | Brad Hill | 2024-04-29 | 2024-05-02 | 2024-05-02 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/OEIS_017.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--04 | ACI 23-04 Cross-Utility Collaboration on Best Practicies
607 | OEIS | 017 | OEIS_017 | 3 | OEIS_017_Q3 | Regarding the Standing Joint Utility Monthly Meetings PG&Es 2025 Update mentions that “Furthermore, as described above, PG&E, SCE, and SDG&E developed standing monthly Joint Utility meetings, creating a forum to keep one another updated and discuss wildfire topics.” (p. 48, response to PG&E-23-04 “Cross-Utility Collaboration on Best Practices for Inclusion of Climate Change Forecasts in Consequence Modeling, Inclusion of Community Vulnerability in Consequence Modeling, and Utility Vegetation Management for Wildfire Safety”). Please provide the following: 1. Provide the following information about these standing monthly joint utility sessions. a. Each working session’s date, time, and host organization. b. The agenda for each working session. 2. Does PG&E plan to continue these sessions in the future? 3. Are there any plans to include Bear Valley, Liberty, or PacifiCorp in these meetings? a. If yes, please state any past or future attempts to include these utilities. | 1. PG&E, SCE and SDG&E held six Joint Utility meetings to discuss wildfire topics between January and April in 2024. Each utility rotates to host two monthly meetings, one in-person and one virtually. In-person meetings are typically held over two days. Virtual meetings are typically held on one day. Each meeting is approximately four hours in duration. a. The working session dates, time and host organization are as follows: January in-person meetings hosted by SCE: January 10, 2024, 12:00 p.m. – 4:30 p.m. January 11, 2024, 8:00 a.m. – 12:00 p.m. February virtual meeting hosted by SCE: February 9, 2024, 8:00 a.m. – 12:00 p.m. March in-person meetings hosted by PG&E: March 13, 2024, 12:00 p.m. – 4:00 p.m. March 14, 2024, 8:00 a.m. – 12:00 p.m. April virtual meeting hosted by PG&E: April 12, 2024, 8:00 a.m. – 12:00 p.m. b. Please see the table below for the agendas for the monthly working sessions: Meeting Attachment Name January in-person meetings hosted by SCE WMP-Discovery2023-2025_DR_OEIS_017- Q003Atch01CONF.pdf February virtual meeting hosted by SCE WMP-Discovery2023-2025_DR_OEIS_017- Q003Atch02CONF.pdf March in-person meetings hosted by PG&E WMP-Discovery2023-2025_DR_OEIS_017- Q003Atch03CONF.pdf April virtual meeting hosted by PG&E WMP-Discovery2023-2025_DR_OEIS_017- Q003Atch04CONF.pdf 2. Yes, PG&E plans to continue these sessions in the future. 3. PG&E, SCE and SDG&E collectively extended the invitation to Bear Valley, Liberty and PacifiCorp to join these meetings. On January 11th , Bear Valley and PacifiCorp participated in the Joint Utility meeting. Bear Valley also participated in the March 13th and 14th meetings. | Brad Hill | 2024-04-29 | 2024-05-02 | 2024-05-02 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/OEIS_017.zip | 4 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--04 | ACI 23-04 Cross-Utility Collaboration on Best Practicies
608 | OEIS | 017 | OEIS_017 | 4 | OEIS_017_Q4 | Regarding the Joint Utility Monthly Meetings on the WMP PG&Es 2025 Update mentions that “The Joint Utilities conduct a monthly meeting that discusses many areas of the WMP in depth. PG&E, Southern California Edison Company (SCE), and SDG&E each take turns leading the meetings. Topics for these meetings generally cover mitigation strategy and implementation, regulatory developments, and knowledge sharing.” (p. 47, response to PG&E-23-04 “Cross-Utility Collaboration on Best Practices for Inclusion of Climate Change Forecasts in Consequence Modeling, Inclusion of Community Vulnerability in Consequence Modeling, and Utility Vegetation Management for Wildfire Safety”). 1. Are these meetings in response to a specific Area of Continued Improvement? a. If so, please state which Area of Continued Improvement. b. If not, please state what directive these meetings were in response to. 2. Are these monthly meetings the same as the Joint Utility meetings mentioned on page 48 of PG&Es 2025 Update (“Furthermore, as described above, PG&E, SCE, and SDG&E developed standing monthly Joint Utility meetings, creating a forum to keep one another updated and discuss wildfire topics.”)? a. If yes, please confirm in your response. b. If not, please describe how they are different. | 1. No, these meetings are not in response to a specific Area of Continued Improvement. a. Not applicable, please see the response to subpart (1). b. These meetings were not in response to any directive. Following the joint utility collaboration and benchmarking on the 2023-2025 Maturity Survey in 2022 and 2023, the Joint IOUs decided to continue meeting regularly to discuss wildfire topics as the process of sharing best practices and talking through issues was beneficial. Please see attachment “WMP-Discovery2023-2025_DR_OEIS_017- Q004Atch01CONF.pdf” for the Meeting Charter that describes the purpose, scope, membership, and logistics for the meetings. 2. Yes, these meetings are the same as the Joint Utility meetings mentioned on page 48 of PG&E’s 2025 WMP Update. a. Please see the response to subpart (2) above. b. Not applicable, please see the response to subpart (2) above. | Brad Hill | 2024-04-29 | 2024-05-02 | 2024-05-02 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/OEIS_017.zip | 1 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--04 | ACI 23-04 Cross-Utility Collaboration on Best Practicies
609 | MGRA | Data Request No. 13 | MGRA_Data Request No. 13 | 1 | MGRA_Data Request No. 13_Q1 | The PG&E response supplied to MGRA in WMP-Discovery2023- 2025_DR_MGRA_009-Q015Atch01-IngitionsAT was incomplete and nonresponsive because: a. It contained on ID that could be crossed-referenced to PG&E’s reported ignition data base. b. It contained only ignition date, not ignition time, which makes it impossible to distinguish them, since many ignitions often occur on the same day. The existing response therefore has not been made usable for any potential investigation regarding cause or whether and is of limited utility. Please provide an updated version containing standard ignition IDs and times. | PG&E objects to, and disagrees with, the categorization of its responses to the referenced data requests as being “incomplete and non-responsive.” PG&E notes that the requesting party could have participated in the meet and confer process—as the parties have done multiple times in the past—if it was unhappy with the responses provided and PG&E would have done its best to accommodate the requesting party. a. PG&E objects to subpart (a) on the grounds that it is vague, ambiguous, and confusing. PG&E interprets this subpart as requesting clarification regarding the index number that was included in Column A of “WMP-Discovery2023- 2025_DR_MGRA_009-Q015Atch01.xlsx.” Please note, the index number is the unique identifier for the event in PG&E’s ignitions database. The index number represents the year the ignition occurred and its unique identification number (ID). For example, Index “20220142” represents a year 2022 ignition with the unique id of 0142. b. Please see attachment “WMP-Discovery2023-2025_DR_MGRA_013- Q001Atch01.xlsx” for an updated spreadsheet which includes the time the ignition was reported in Column “C.” Please note, PG&E is unable to confirm the exact start time of an ignition, however, is providing the timestamp for when the first responder reported the incident. | Joseph Mitchell | 2024-04-30 | 2024-05-03 | 2024-05-01 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_013.zip | 1 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--25 Fire Potential Index (FPI) and Ignition Probability Weather (IPW) Enhancements | ACI 23-25 Fire Potential Index and Ignition Probability Weather Enhancements
610 | CalPA | Set WMP-47 | CalPA_Set WMP-47 | 1 | CalPA_Set WMP-47_Q1 | The attached spreadsheet (filename “CalAdvocates-PGE-2025WMP-11Q1ATTCH_CONF.xlsx”) contains a subset of PG&E’s 2024-2026 system hardening workplan as provided in response to Cal Advocates data request CalAdvocates-PGE-2025WMP-01 Question 8. Specifically it contains 30 undergrounding projects that were scoped using Wildfire Distribution Risk Model (WDRM) v2, 30 undergrounding projects that were scoped using Wildfire Distribution Risk Model v3, and 51 projects in locations with a mix of v2 and v3 basis. a) For all projects scoped using WDRM v2 (in the tab labeled “v2 projects”), please provide the total risk reduction percentage (similar to Column AN) for these projects using WDRM v4 in a working Excel spreadsheet (i.e., with links, formulae, source data, etc.). b) For all projects scoped using WDRM v3 (in the tab labeled “v3 projects”), please provide the total risk reduction percentage (similar to Column AN) for these projects using WDRM v4 in a working Excel spreadsheet (i.e., with links, formulae, source data, etc.). c) For all projects in the tab “v2 and v3 mix”, please provide the total risk reduction percentage (similar to Column AN) for these projects using WDRM v4 in a working Excel spreadsheet (i.e., with links, formulae, source data, etc.). | PG&E objects to each of the three subparts of this request on the grounds that they are overly burdensome because it would involve multiple months of work to obtain the requested analysis. Given that the model was only recently released, work in implementing the model is ongoing and still in the early stages. PG&E cannot provide the requested information as PG&E does not currently have WDRM v4 risk reduction calculations available for the 2023-2026 System Hardening workplan specific to the job level. WMP-Discovery2023-2025_DR_CalAdvocates_047-Q001 Page 2 PG&E notes that each version of the WDRM has statistical validity and each iteration does not invalidate the results of preceding models. In other words, retroactively applying a newer model to a portfolio scoped with prior models does not impact the viability of the previously derived results. Please do not hesitate to reach out if you would like to meet and confer about this request as we would be happy to further discuss this issue with you. | Miles Gordon | 2024-04-20 | 2024-05-03 | 2024-05-03 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_047.zip | 0 | N/A | 8.1.2.5 | System Hardening | N/A | 2.1.4.1 GH-11 Traditional Overhead Hardening Conductor
611 | MGRA | Data Request No. 14 | MGRA_Data Request No. 14 | 1 | MGRA_Data Request No. 14_Q1 | The excel spreadsheet WMP-Discovery2023-2025_DR_MGRA_013- Q001Atch01.xlsx contains 11 ignitions in which the circuit was activated with DCD, while only four occurred in the HFTD. PG&E’s WMP Update says that only two ignitions occurred. Please explain this apparent discrepancy. | PG&E’s previous response includes 11 ignition events where Downed Conductor Detection (DCD) technology was enabled at the time of ignition. In two cases out of the 11 ignitions, including corresponding index numbers 20230692 and 20231247N, the fault associated with the ignition was detected by DCD and resulted in an outage. Note that the other nine incidents are not faults that DCD is designed to catch. | Joseph Mitchell | 2024-05-02 | 2024-05-07 | 2024-05-07 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_014.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--25 Fire Potential Index (FPI) and Ignition Probability Weather (IPW) Enhancements | ACI 23-25 Fire Potential Index and Ignition Probability Weather Enhancements
612 | MGRA | Data Request No. 14 | MGRA_Data Request No. 14 | 2 | MGRA_Data Request No. 14_Q2 | Were any of the verified ignitions on DCD-enabled circuits associated with wiredowns? If so provide the wire-down identifier from PG&E’s GIS data, since PG&E included no time data in its wire down data set. | Yes, out of the 11 ignitions that occurred where Downed Conductor Detection (DCD) was enabled on the upstream protective device at the time of the ignition, six ignitions involved one or more primary conductors down. Please see Column A in attachment “WMP-Discovery2023-2025_DR_MGRA_013-Q001Atch01.xlsx” with the following corresponding index numbers for these instances: 20230627; 20230636; 20230716; 20230899; 20230973; and 20231247N. | Joseph Mitchell | 2024-05-02 | 2024-05-07 | 2024-05-07 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_014.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--25 Fire Potential Index (FPI) and Ignition Probability Weather (IPW) Enhancements | ACI 23-25 Fire Potential Index and Ignition Probability Weather Enhancements
613 | MGRA | Data Request No. 14 | MGRA_Data Request No. 14 | 3 | MGRA_Data Request No. 14_Q3 | Please provide the full cause (as reported to the CPUC) for the ignitions that occurred on the DCD-enabled circuits. | Please see the table below for the full cause, as reported to the CPUC, for ignitions that occurred on the DCD-enabled circuits. Index Date Time HFTD Suspected Cause Failure driver Failure sub-driver Asset Type 20230627 7/2/2023 22:12 Non-HFTD Equipment - PG&E All types of equipment / facility failure Splice/ Clamp/ Connector Primary 20230636 7/4/2023 4:40 Non-HFTD Vegetation Contact from Object Contact - Vegetation Primary 20230676 7/10/2023 21:27 Tier 2 Equipment - PG&E All types of equipment / facility failure Transformer failure Primary 20230692 7/14/2023 4:40 Tier 2 Vegetation Contact from Object Contact - Vegetation Primary 20230716 7/16/2023 20:21 Non-HFTD Vandalism Vandalism Vandalism Primary 20230784 7/27/2023 10:43 Non-HFTD Equipment - PG&E All types of equipment / facility failure Capacitor bank failure Primary 20230842 8/6/2023 10:58 Non-HFTD Contact - 3rd Party Contact from Object Contact - Balloon Primary WMP-Discovery2023-2025_DR_MGRA_014-Q003 Page 2 Index Date Time HFTD Suspected Cause Failure driver Failure sub-driver Asset Type 20230899 8/17/2023 19:37 Non-HFTD Vegetation Contact from Object Contact - Vegetation Primary 20230973 8/29/2023 16:55 Tier 2 Contact - 2nd Party Contact from Object Contact - Vegetation Primary 20231096 9/27/2023 20:09 Non-HFTD Vegetation Contact from Object Contact - Vegetation Primary 20231247N 11/4/2023 13:50 Tier 2 Contact - 3rd Party Contact from Object Contact - Vehicle Primary | Joseph Mitchell | 2024-05-02 | 2024-05-07 | 2024-05-07 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_014.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--25 Fire Potential Index (FPI) and Ignition Probability Weather (IPW) Enhancements | ACI 23-25 Fire Potential Index and Ignition Probability Weather Enhancements
614 | MGRA | Data Request No. 14 | MGRA_Data Request No. 14 | 4 | MGRA_Data Request No. 14_Q4 | Please provide detailed cause information for the 17 “near miss” events that PG&E claims may have been averted by DCD activation, as well as outage dates and times. | Please see the below table for a list of the 17 potentially avoided ignitions PG&E observed in 2023 for which the outage fault was detected by DCD technology. Outages FNL End_Date Cause 23-0087355 6/29/2023 19:34 6/30/2023 10:59 Equipment Failure/Involved 23-0087372 6/29/2023 21:43 6/30/2023 11:28 Vegetation 23-0090190 7/9/2023 2:02 7/9/2023 13:43 Vegetation 23-0090168 7/8/2023 20:52 7/9/2023 19:30 Equipment Failure/Involved 23-0099878 8/3/2023 3:34 8/3/2023 7:59 Equipment Failure/Involved 23-0104635 8/15/2023 13:49 8/15/2023 17:07 Vegetation 23-0108800 8/24/2023 18:00 8/25/2023 13:37 Vegetation 23-0119701 9/22/2023 10:27 9/22/2023 17:12 Vegetation 23-0121348 9/27/2023 8:36 9/27/2023 16:25 Equipment Failure/Involved 23-0126506 10/10/2023 11:38 10/10/2023 22:26 Equipment Failure/Involved 23-0128272 10/14/2023 9:14 10/14/2023 10:07 Animal 23-0128164 10/13/2023 15:55 10/14/2023 17:42 Vegetation 23-0131224 10/23/2023 9:20 10/23/2023 11:53 Vegetation 23-0131619 10/24/2023 3:58 10/24/2023 17:11 Equipment Failure/Involved 23-0133597 10/28/2023 17:43 10/29/2023 9:06 Vegetation 23-0133715 10/29/2023 14:22 10/29/2023 20:44 Equipment Failure/Involved 23-0147117 12/12/2023 16:43 12/12/2023 17:53 Animal | Joseph Mitchell | 2024-05-02 | 2024-05-07 | 2024-05-07 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_014.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--25 Fire Potential Index (FPI) and Ignition Probability Weather (IPW) Enhancements | ACI 23-25 Fire Potential Index and Ignition Probability Weather Enhancements
615 | MGRA | Data Request No. 14 | MGRA_Data Request No. 14 | 5 | MGRA_Data Request No. 14_Q5 | How many “false” DCD signals were received that resulted in outages in 2023? What were the number of customers and customer minutes affected? | In 2023, a total of 252 DCD outage events occurred where either: (1) no identifiable visual fault condition could be found following a patrol; or (2) the event was related to planned switching activities. The 252 outages affected 269,307 customers for a total of 55,305,653 total customer interruption minutes. For events where no obvious visual fault condition could be found following a patrol, it is likely—after reviewing event data—that in a portion of these cases, a transient high impedance ground fault occurred but the problem was not identifiable during the visual patrol due to a self-correcting temporary condition (e.g., a branch touching the line and then subsequently falling to ground). In other cases, there may be an explainable nonfault system disturbance that may have led to the DCD event. Therefore, to clarify, PG&E does not consider this category of event generically to be “false” signals. | Joseph Mitchell | 2024-05-02 | 2024-05-13 | 2024-05-13 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_014.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--25 Fire Potential Index (FPI) and Ignition Probability Weather (IPW) Enhancements | ACI 23-25 Fire Potential Index and Ignition Probability Weather Enhancements
616 | OEIS | 018 | OEIS_018 | 1 | OEIS_018_Q1 | Regarding FTI Inventory Only Trees In response to Data Request OEIS-P-WMP_2024-PG&E-001, Question 1(b)(i), PG&E stated that “PG&E’s operational approach to FTI was changed to only fill out a TRAQ form on trees prescribed for work.” PG&E describes these trees that are inspected but not prescribed work “inventory only trees.” a. What information does PG&E record in One VM for inventory only trees? b. Provide screenshots of One VM showing the fields inspectors must populate for inventory only trees. | a. Please see “WMP-Discovery2023-2025_DR_OEIS_018-Q001Atch01.xlsx” for a data dictionary for the information we record in One VM for inventory-only trees. Each tab describes the fields populated in One VM and their potential domain values, as follows: • The “VegPoint” tab contains the list of attributes inspectors populate for vegetation points within the One VM application. • The “VM-Prescriptions-c” tab contains the workflow for capturing vegetation details and assigned prescriptions within the One VM application. • The “DV-WorkCode” tab contains the list of all prescription codes available within the One VM application. Please note, these fields are populated by inspectors for both ‘inventory-only’ trees and for trees that require work. b. Please see pages 4-8 of “WMP-Discovery2023-2025_DR_OEIS_018- Q001Atch02.pdf” for screenshots of the fields completed by inspectors when populating ‘inventory only’ tree entries. Please note, the ‘inventory only’ vegetation point is completed once ‘no work needed’ is selected in the drop-down menu for the ”Prescription Action” field in step 13. All subsequent steps would only be for trees prescribed for work. | Brad Hill | 2024-05-03 | 2024-05-08 | 2024-05-08 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/OEIS_018.zip | 2 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23-19 – Continued Progression of Vegetation Management Maturity | ACI 23-19 Continued Progresion of Vegatation Management Maturity
617 | OEIS | 018 | OEIS_018 | 2 | OEIS_018_Q2 | Regarding Back-Up Batteries Completed in 2023: In its WMP Update, PG&E states that it completed 4,700 units of new or replacement portable and permanent batteries (PS-06). a. Provide, in tabular format, a list of accounts that received a battery in 2023, including: i. Whether the battery was new or a replacement. ii. Whether that battery was portable or permanent. iii. Whether | Please see attachment “WMP-Discovery2023-2025_DR_OEIS_018- Q002Atch01CONF.xlsx” for the requested information. Note that all batteries received by customers through the Portable Battery Program or the Disability Disaster Access & Resources program in 2023 were fully subsidized. | Brad Hill | 2024-05-03 | 2024-05-08 | 2024-05-08 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/OEIS_018.zip | 1 | N/A | 8.5.3 | 8.0 Wildfire Mitigations | 8.5.3 Engagement with Access and Functional Needs Populations | 2.1.2 PS-06: Provide 12,000 cumulative new or replacement portable batteries
618 | CPUC - SPD (Safety Policy Division) | 013 | CPUC - SPD (Safety Policy Division)_013 | 1 | CPUC - SPD (Safety Policy Division)_013_Q1 | I’m looking for the following documents: Data Request: CalAdvocates_039-Q014 (CalAdvocates-PGE2025WMP-03) Data Request Date: March 22, 2024 PG&E Date of Response to Data Request: April 5, 2024 PG&E Document No. or Title: WMP-Discovery2023-2025_DR_CalAdvocates_039-Q014Atch01CONF.xlsx WMP-Discovery2023-2025_DR_CalAdvocates_039-Q014Atch02CONF.xlsx WMP-Discovery2023-2025_DR_CalAdvocates_039-Q014Atch03CONF.xlsx WMP-Discovery2023-2025_DR_CalAdvocates_039-Q014Atch04CONF.xlsx | Please see the following files for the requested information. Please note, these attachments were provided as pdf files and not excel files. • WMP-Discovery2023-2025_DR_CalAdvocates_039-Q014Rev01Atch01CONF.pdf • WMP-Discovery2023-2025_DR_CalAdvocates_039-Q014Rev01Atch02CONF.pdf • WMP-Discovery2023-2025_DR_CalAdvocates_039-Q014Rev01Atch03CONF.pdf • WMP-Discovery2023-2025_DR_CalAdvocates_039-Q014Atch04CONF.pdf While reviewing your request, PG&E identified confidential information that was erroneously left unmarked in Attachments 01-03, submitted to The Public Advocates Office (CalAdvocates) on April 5, 2024. PG&E has amended its response to CalAdvocates and is providing the updated, amended, Attachments 01-03. | Henry Sweat | 2024-05-14 | 2024-05-22 | 2024-05-16 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_013.zip | 4 | N/A | 8 | Section 8.3 - Situational Awareness and Forecasting | 8.3.4.1 Existing Ignition Detection Sensors and Systems | ACI 23-25 Fire Potential Index and Ignition Probability Weather Enhancements
619 | CalPA | Set WMP-48 | CalPA_Set WMP-48 | 1 | CalPA_Set WMP-48_Q1 | For PG&E’s three-wire uni-grounded primary circuits at or below 35 kV (nominal) please describe, with references to PG&E’s procedures: a) PG&E’s fast-trip (known as Enhanced Powerline Safety Settings, or EPSS) line-current2 thresholds; b) How PG&E’s fast-trip line-current thresholds are calculated from measured circuit values; c) The intentional delays assigned to those line-current thresholds; d) PG&E’s fast-trip ground-current thresholds; e) How PG&E’s fast-trip ground-current thresholds are calculated from measured circuit values; f) The intentional delays assigned to those ground-current thresholds; and g) How the current (both line and ground) and delay thresholds differ from non fast-trip settings. | PG&Es most current EPSS protection guidelines are document in TD-1470P-01 Att. 1 “Application Guide Device Profile Settings”. a) EPSS phase overcurrent settings for line reclosers (LR) and circuit breakers (CB) are set with the following guidelines: Phase time overcurrent (51 element) Phase minimum-to-trip (MTT) ≤ 60% three-phase fault or 70% line-to-line fault based upon simulated short circuit bolted faults at the protection zone end of line. Fuses and other single phase (non-ganged) protective devices are not included as delimiters for the purpose of establishing the protective zone. Set phase MTT greater than 1.2x maximum expected loading. Phase instantaneous/definite time overcurrent (50 element) Phase instantaneous trip setting is set equal to the phase time overcurrent minimum to trip. b) PG&E’s EPSS phase overcurrent trip settings are based upon short circuit analysis provided through simulation of the distribution network model. The simulations provide values to set as described in a). Maximum loading data is obtained through planning forecasts as well as historical SCADA observations. c) For EPSS, phase instantaneous/definite time settings are used to establish coordination delay. The time delay of the furthest protective device is set to 0ms or no intentional delay. Each consecutive source side protective device is set with an additional +0.02 to 0.05s time delay, optimizing for margin. Protective device time delays will not exceed 0.1s or 6 cycles. d) EPSS ground overcurrent settings for line reclosers and circuit breakers are set with the following guidelines: Ground time overcurrent (51N/G element) Ground minimum-to-trip (MTT) ≤ 50% simulated short circuit bolted line to ground fault at the protection zone end of line. Fuses and other single phase (non-ganged) protective devices are not included as delimiters for the purpose of establishing the protective zone. Set ground MTT greater than 1.2x maximum expected normal standing ground current. Ground instantaneous/definite time overcurrent (50N/G element) Phase instantaneous trip setting is set equal to the phase time overcurrent minimum to trip. Sensitive Ground Element (SGF) The sensitive ground element (SGF) for three-wire applications is typically set between 5-15A to provide a low set ground overcurrent element to attempt to detect high impedance ground faults. The SGF setting threshold is also required to be 1.2x the maximum observed standing ground fault current due to system capacitance and configuration. e) PG&E’s EPSS ground overcurrent trip settings are based upon short circuit analysis provided through simulation of the distribution network model. The simulations provide values to set as described in d). f) The ground instantaneous/definite time overcurrent time delay is set the same as the phase delay in section c). For SGF the minimum time delay is typically set from 5-15 seconds with 1-3 seconds of coordination time between devices equipped in series with SGF towards the source. g) Non-EPSS settings operate typically with a time-overcurrent element which may or may not also have an instantaneous or definite time element set. Non-EPSS settings also account for fuses as other non-gang trip device to delimit protective zones thereby reducing the zone of protection. The minimum separation guideline between two LRs or between LR and CB is typically 0.2s. Both EPSS and non-EPSS settings utilize the same principles of end of line fault detection and anticipated load accommodate when setting the MTT thresholds. In addition, settings are designed to protect against equipment damage by limiting I^2T energy as well as arc-flash exposure. | Tyler Holzschuh | 2024-05-16 | 2024-05-31 | 2024-05-31 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_048.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--26 Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI 23-26 Evaluation and Reporting of Safety Impacts Related to EPSS
620 | CalPA | Set WMP-48 | CalPA_Set WMP-48 | 2 | CalPA_Set WMP-48_Q2 | For PG&E’s four-wire multi-grounded primary circuits at or below 35 kV please describe, with references to PG&E’s procedures: a) PG&E’s fast-trip line-current thresholds; b) How PG&E’s fast-trip line-current thresholds are calculated from measured circuit values; c) The intentional delays assigned to those line-current thresholds; d) PG&E’s fast-trip ground-current thresholds; e) How PG&E’s fast-trip ground-current thresholds are calculated from measured circuit values; f) The intentional delays assigned to those ground-current thresholds; and g) How the current and delay thresholds differ from non fast-trip settings. | PG&Es most current EPSS protection guidelines are document in TD-1470P-01 Att. 1 “Application Guide Device Profile Settings.” Please see “WMP-Discovery2023- 2025_DR_CalAdvocates_048-Q002.pdf” for a copy of these guidelines. The same criteria applies as stated in Question 1 subpart a). a) The same criteria applies as stated in Question 1 subpart b). b) The same criteria applies as stated in Question 1 subpart c). c) The same criteria applies as stated in Question 1 subpart d) except for SGF, it is not applied in most 4-wire system configurations. d) PG&E’s EPSS 4-wire muti-grounded primary circuit ground overcurrent trip settings are based upon short circuit analysis provided through simulation of the distribution network model. The simulations provide values to set as described in Question 1 section a). Maximum ground current data is obtained through planning forecasts as well as historical SCADA observations. e) The same criteria applies as stated in Question 1 subpart e) other than no SGF delay applies. f) The same criteria applies as state in Question 1 subpart g). | Tyler Holzschuh | 2024-05-16 | 2024-05-31 | 2024-05-31 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_048.zip | 1 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--26 Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI 23-26 Evaluation and Reporting of Safety Impacts Related to EPSS
621 | CalPA | Set WMP-48 | CalPA_Set WMP-48 | 3 | CalPA_Set WMP-48_Q3 | For PG&E’s circuits above 35 kV, but not classified as part of the NERC bulk electric system, please describe, with references to PG&E’s procedures: a) PG&E’s fast-trip line-current thresholds; b) How PG&E’s fast-trip line-current thresholds are calculated from measured circuit values; c) The intentional delays assigned to those line-current thresholds; d) PG&E’s fast-trip ground-current thresholds; e) How PG&E’s fast-trip ground-current thresholds are calculated from measured circuit values; f) The intentional delays assigned to those ground-current thresholds; and g) How the current and delay thresholds differ from non fast-trip settings. | PG&E’s Transmission EPSS (a category of “fast-trip”) settings are applied only on a subset of radial lines that are not classified as NERC BES. The responses below pertain only to the EPSS settings, and do not apply to normal non-EPSS settings. a) Transmission line protection is typically not purely current based. Transmission line protection commonly uses impedance based relays (aka distance relays), for which the trip threshold is not defined in current (amperes), but as an impedance value (ohms). For current based phase and ground overcurrent, Transmission EPSS phase instantaneous overcurrent and ground instantaneous overcurrent thresholds are set based on normal non-EPSS phase time overcurrent pickup and ground time overcurrent pickup thresholds respectively. Preferably, the settings are verified to be greater than 120% of distribution fault current for any tapped banks. However, if this criteria cannot be satisfied, providing instantaneous clearing for 100% of the transmission line is given precedence, and the risk of miscoordination with distribution faults is identified to Operations. For impedance based distance elements, Transmission EPSS phase distance and ground distance thresholds are set based on normal non-EPSS Zone 2 phase distance and Zone 2 ground distance thresholds respectively. These Zone 2 elements are already normally overreaching the end of the line. The adjustment to these distance elements is not the pickup threshold, but rather eliminating the normal time delays used for relay coordination purposes. b) The response here is provided with the interpretation that “calculated” is in reference to how the protection engineer calculates the relay setting thresholds, and not how the protective relay calculates the measured circuit values to compare against the set thresholds. Transmission line relay thresholds for both EPSS and non-EPSS settings are not calculated from measured circuit values, but are based on fault studies performed using a short-circuit model of the power system and by performing short-circuit studies. Relay thresholds also take into account facility ratings to avoid operating below the facility rating. c) Transmission EPSS settings have no intentional time delays. d) See response above to Part a. e) See response above to Part b. f) See response above to Part c. g) Current thresholds and delays (time dials) for phase time overcurrent and ground time overcurrent are identical for EPSS and non-EPSS settings. Current thresholds for phase instantaneous overcurrent and ground instantaneous overcurrent are normally set higher for non-EPSS settings as compared to fast-trip settings for the purpose of relay coordination and selectivity of clearing only insection faults. Delays for the instantaneous overcurrents are zero in both EPSS and non-EPSS settings. Distance element thresholds for phase distance and ground distance are identical for EPSS and non-EPSS settings. Zone 1 distance element time delays are also identical for EPSS and non-EPSS settings. Zone 2 distance element time delays are intentionally set to zero in EPSS settings, while for non-EPSS settings would have a typical value of 20-30 cycles or longer for the purpose of relay coordination. | Tyler Holzschuh | 2024-05-16 | 2024-05-31 | 2024-05-31 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_048.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--26 Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI 23-26 Evaluation and Reporting of Safety Impacts Related to EPSS
622 | CalPA | Set WMP-48 | CalPA_Set WMP-48 | 4 | CalPA_Set WMP-48_Q4 | For PG&E’s circuits above 35 kV and classified as part of the NERC bulk electric system please describe, with references to PG&E’s procedures: a) PG&E’s fast-trip line-current thresholds; b) How PG&E’s fast-trip line-current thresholds are calculated from measured circuit values; c) The intentional delays assigned to those line-current thresholds; d) PG&E’s fast-trip ground-current thresholds; e) How PG&E’s fast-trip ground-current thresholds are calculated from measured circuit values; f) The intentional delays assigned to those ground-current thresholds; and g) How the current and delay thresholds differ from non fast-trip settings. | NERC Bulk Electric System transmission lines are excluded from PG&E’s Transmission EPSS program, therefore, PG&E is unable to provide the requested information. | Tyler Holzschuh | 2024-05-16 | 2024-05-31 | 2024-05-31 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_048.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--26 Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI 23-26 Evaluation and Reporting of Safety Impacts Related to EPSS
623 | CalPA | Set WMP-48 | CalPA_Set WMP-48 | 5 | CalPA_Set WMP-48_Q5 | Please provide the list of circuits that are directly upstream of PG&E’s distribution lines, including the following information: a) Circuit name; b) Voltage; and c) Whether the circuit is part of the NERC bulk electric system. | Per PG&E’s meeting with the Public Advocates Office (Cal Advocates) on May 24, 2024, PG&E understands this to be a request for a list of transmission lines that traverse PG&E’s HFTD service area irrespective of distribution lines and to provide a model of PG&E’s transmission system. Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_048- Q005Atch01.xlsx” for a list of PG&E’s HFTD transmission lines and their corresponding voltage. Please also see attachment “WMP-Discovery2023- 2025_DR_CalAdvocates_048-Q005Atch02CONF.zip” for documentation showing PG&E’s Transmission Operating Diagrams. Please note that these documents have been designated confidential as they contain Critical Energy Infrastructure Information. Additionally, they have also been designated confidential pursuant to the requirements of the Federal Energy Regulatory Commission. The information being provided will allow Cal Advocates to perform an independent evaluation of PG&E’s transmission lines to determine whether each circuit is part of the NERC Bulk Electric System. | Tyler Holzschuh | 2024-05-16 | 2024-05-31 | 2024-05-31 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_048.zip | 2 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--26 Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI 23-26 Evaluation and Reporting of Safety Impacts Related to EPSS
624 | CalPA | Set WMP-48 | CalPA_Set WMP-48 | 6 | CalPA_Set WMP-48_Q6 | Please provide the number of circuit-mile-days that PG&E activated fast-trip from January to December 2023, by month. | The circuit-mile-days below represent High Fire Risk Area miles enabled with EPSS settings in 2023. Month Enabled HFRA Circuit Mile Days January 2023 1,096 February 2023 2,275 March 2023 116 April 2023 7,926 May 2023 52,234 June 2023 336,813 July 2023 698,797 August 2023 716,988 September 2023 683,788 October 2023 691,383 November 2023 403,592 December 2023 79,135 Total 3,674,143 | Tyler Holzschuh | 2024-05-16 | 2024-05-31 | 2024-05-31 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_048.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--26 Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI 23-26 Evaluation and Reporting of Safety Impacts Related to EPSS
625 | CalPA | Set WMP-48 | CalPA_Set WMP-48 | 7 | CalPA_Set WMP-48_Q7 | Please provide the number of circuit-mile-days that PG&E did not activate fast-trip from January to December 2023, by month. | The circuit-mile-days below represent EPSS-scoped High Fire Risk Area miles not enabled with EPSS settings in 2023. Month Not Enabled HFRA Circuit Mile Days January 2023 750,439 February 2023 676,531 March 2023 751,419 April 2023 719,367 May 2023 699,301 June 2023 390,479 July 2023 52,739 August 2023 34,547 September 2023 43,504 October 2023 60,153 November 2023 323,700 December 2023 672,401 Total 5,174,581 | Tyler Holzschuh | 2024-05-16 | 2024-05-31 | 2024-05-31 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_048.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--26 Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI 23-26 Evaluation and Reporting of Safety Impacts Related to EPSS
626 | CalPA | Set WMP-48 | CalPA_Set WMP-48 | 8 | CalPA_Set WMP-48_Q8 | Please provide the number of momentary outages that PG&E had on circuits where fast-trip settings were not enabled from January to December 2023, by month. | Please see the table below for the requested information. Month # of Momentary Events # of Sustained Events Grand Total JAN 715 4152 4867 FEB 465 4390 4855 MAR 1175 5302 6477 APR 597 6140 6737 MAY 600 6264 6864 JUN 616 6041 6657 JUL 523 5723 6246 AUG 550 7014 7564 SEP 417 6028 6445 OCT 467 6909 7376 NOV 668 5993 6661 DEC 671 5431 6102 Grand Total 7464 69387 76851 | Tyler Holzschuh | 2024-05-16 | 2024-05-31 | 2024-05-31 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_048.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--26 Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI 23-26 Evaluation and Reporting of Safety Impacts Related to EPSS
627 | CalPA | Set WMP-48 | CalPA_Set WMP-48 | 9 | CalPA_Set WMP-48_Q9 | Please provide the number of non-momentary (i.e., sustained) outages that PG&E had on circuits where fast-trip settings were not enabled from January to December 2023, by month. | Please see PG&E’s response to Q008. | Tyler Holzschuh | 2024-05-16 | 2024-05-31 | 2024-05-31 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_048.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--26 Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI 23-26 Evaluation and Reporting of Safety Impacts Related to EPSS
628 | CalPA | Set WMP-48 | CalPA_Set WMP-48 | 10 | CalPA_Set WMP-48_Q10 | For each of the outages in the attached excel spreadsheet named “Random Fast-Trip August 2023 Outages.xlsx”, please provide: a) The protective function that tripped the circuit (e.g. definite time delay ground overcurrent); b) The current threshold of the protective function; c) The time delay of the protective function; d) The maximum load line-current from 2019-2023; e) The maximum unfaulted ground-current from 2019-2023; and f) If on distribution, whether the circuit was three-wire or four-wire. | PG&E objects to the request on the grounds that it is overbroad and unduly burdensome. Notwithstanding and without waiving this objection, PG&E is compiling the requested data for a random selection of 25 of the 50 outages included in “Random Fast-Trip August 2023 Outages.xlsx” and can provide the data by June 5, 2024. Please note, as this requires a manual data pull across multiple systems of record that will take many hours of work, it would be unduly burdensome to provide the information for all of the identified 50 outages. However, should this be an issue, we would be happy to meet and confer with you to discuss this request and our respective positions. | Tyler Holzschuh | 2024-05-16 | 2024-05-31 | 2024-05-31 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_048.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--26 Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI 23-26 Evaluation and Reporting of Safety Impacts Related to EPSS
628 | CALPA | Set WMP-48 | CALPA_Set WMP-48 | 10(s) | CALPA_Set WMP-48_Q10(s) | For each of the outages in the attached excel spreadsheet named “Random Fast-Trip August 2023 Outages.xlsx”, please provide: a) The protective function that tripped the circuit (e.g. definite time delay ground overcurrent); b) The current threshold of the protective function; c) The time delay of the protective function; d) The maximum load line-current from 2019-2023; e) The maximum unfaulted ground-current from 2019-2023; and f) If on distribution, whether the circuit was three-wire or four-wire. | ANSWER 010 SUPPLEMENTAL 01 Please see “WMP-Discovery2023-2025_DR_CalAdvocates_048- Q010Supp01Atch01.xlsx” for the requested information on 25 of the outages included in the referenced “Random Fast-Trip August 2023 Outages.xlsx.” ANSWER 010 PG&E objects to the request on the grounds that it is overbroad and unduly burdensome. Notwithstanding and without waiving this objection, PG&E is compiling the requested data for a random selection of 25 of the 50 outages included in “Random Fast-Trip August 2023 Outages.xlsx” and can provide the data by June 5, 2024. Please note, as this requires a manual data pull across multiple systems of record that will take many hours of work, it would be unduly burdensome to provide the information for all of the identified 50 outages. However, should this be an issue, we would be happy to meet and confer with you to discuss this request and our respective positions. | Tyler Holzschuh | 2024-05-16 | 2024-06-05 | 2024-06-05 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_048.zip | 1 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--26 Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI 23-26 Evaluation and Reporting of Safety Impacts Related to EPSS
629 | OEIS | 019 | OEIS_019 | 1 | OEIS_019_Q1 | Regarding PG&E’s response to ACI PG&E-23-26, PG&E states the following in its 2025 WMP Update (p. 132): PG&E is currently finalizing an analysis to understand the tradeoffs between reliability and wildfire risk mitigation when EPSS circuits are enabled. This analysis should be completed by the second quarter of 2024 to be shared in PG&E’s 2024 RAMP filing and will address the portion of the ACI seeking a re-evaluation of PG&E’s EPSS-enablement thresholds. PG&E filed its 2024 RAMP filing on May 15, 2024; is this analysis completed? If yes, what is the format of this analysis that can be provided? | Please see Exhibit 4 Chapter 1: “2024 Risk Assessment and Mitigation Phase Report” of PG&E’s 2024 RAMP Filing for the initial analysis which presents the impact of the current PG&E EPSS enablement threshold. A further analysis is expected to be shared by the end of the second quarter of 2024 on the re-evaluation of PG&E’s EPSS enablement threshold. PG&E’s 2024 RAMP Filing is located at the following link: https://www.cpuc.ca.gov/- /media/cpuc-website/divisions/safety-policy-division/reports/2024-ramp-applicationpge051524. pdf. | Brad Hill | 2024-05-16 | 2024-05-21 | 2024-05-21 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/OEIS_019.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--26 Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI 23-26 Evaluation and Reporting of Safety Impacts Related to EPSS
630 | OEIS | 019 | OEIS_019 | 2 | OEIS_019_Q2 | WMP-Discovery2023- 2025_DR_OEIS_016-Q003Supp01Atch01.xlsx, attached to Data Request OEIS_016-Q003, only shows 14 circuit segments, whereas the original Tables 6-5 and 7-2 in the 2023-2025 WMP have 41 circuit segments listed. a. Provide the number of circuit segments used to determine the top 5% for both the original tables (V3) and the updated tables (V4). b. Provide the overall utility risk score used to determine the top 5% for both the original tables (V3) and the updated tables (V4). | a. PG&E used the following number of circuit segments to determine the top 5% for the referenced version(v)3 and v4 WDRM model: • WDRM v3 – 11,171 circuit segments, risk ranked by total utility risk summary. • WDRM v4 – 11,482 circuit segments, risk ranked by total utility risk summary. b. PG&E used the following utility risk scores to determine the top 5% for the referenced (v)3 and v4 WDRM model: • WDRM v3 + Public Safety Power Shutoff (PSPS): 25,146.54. • WDRM v4 + PSPS: 25,103.75. | Brad Hill | 2024-05-16 | 2024-05-21 | 2024-05-21 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/OEIS_019.zip | 0 | N/A | 6.1.2 | Section 6 - Risk Methodology and Assessment | 6.1.2 Summary of Risk Models | B.1.1. WDRM v4
631 | OEIS | 020 | OEIS_020 | 1 | OEIS_020_Q1 | Regarding PG&E’s 2025 Workplan: a. In table 8.1.2-2 of PG&E’s 2023-2025 WMP, PG&E provides a table detailing the number of miles it plans to underground in 2023-2026 in the top 20% Risk ranked circuits, other high-risk circuits, and for all other undergrounding programs.1 i. Please provide this table with the 2025 column updated to reflect PG&E’s 2025 workplan. If the 2025 workplan has not been finalized, please update the table with the current 2025 workplan as of receipt of this data request. ii. Please provide a table outlining PG&E’s 2025 covered conductor workplan including the number of miles in the top 20% risk ranked circuit segments, other high-risk (if applicable), and other covered conductor programs. If the 2025 workplan has not been finalized, please update the table with the current 2025 workplan as of receipt of this data request. b. In table RN-PG&E-05-2 of PG&E’s 2023-2025 WMP, PG&E provides the number of undergrounding miles planned and percentage of portfolio in the top 20% WFE, WDRM v2, WDRM v3, and WDRM v2 + WDRM v3.2 i. Please provide this table with the 2025 row updated to reflect PG&E’s 2025 workplan. If the 2025 workplan has not been finalized, please update the table with the current 2025 workplan as of receipt of this data request. ii. Please provide this table for PG&E’s 2025 covered conductor workplan. If the 2025 workplan has not been finalized, please update the table with the current 2025 workplan as of receipt of this data request. | a. Based on the context of the question, PG&E believes the cited table in this request (8.1.2-2) is a typo, and the intended referenced table is PG&E-8.1.2-3: PG&E Undergrounding Workplan 2023-2026. For transparency, PG&E is providing an updated table 8.1.2-3 for 2023-2026 of our system hardening and undergrounding workplan data from our system of record, Distribution Operations Tool (DOT), as of May 21, 2024. Note, the total miles in 2025 is currently showing as oversubscribed compared to the target. PG&E is finalizing the planned end dates -- many of which will shift their end date into 2026, which is currently showing as undersubscribed in our system of record. For the requested updates to this table, please see the following tables below: i. Table 1: PG&E Undergrounding Workplan 2023-2026. This table incorporates updated miles for 2023 through 2026 from PG&E’s GH–04 undergrounding portfolio as of May 21, 2024. ii. Table 2: PG&E Overhead Hardening Workplan 2023-2026. This table incorporates overhead hardening miles which contribute to PG&E’s GH-01 system hardening portfolio as of May 21, 2024. b. For the requested updates to RN-PG&E-05-02 see the following tables below: i. Table 3: PG&E Undergrounding Workplan Top 20% Risk Comparison. This table incorporates updated miles for 2023 through 2026 from PG&E’s GH-04 undergrounding portfolio as of May 21, 2024. ii. Table 4: PG&E Overhead Hardening Workplan Top 20% Risk Comparison. This table summarizes overhead hardening miles from PG&E’s GH-01 system hardening portfolio as of May 21, 2024. | Brad Hill | 2024-05-17 | 2024-05-24 | 2024-05-24 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/OEIS_020.zip | 0 | N/A | 9 | Section 8.1.2 - Grid Design and System Hardening | 8.1.2.2 Undergrounding of electric lines and/or equipment | 2.1.1.2 GH-04 Undergrounding
632 | CPUC - SPD (Safety Policy Division) | 014 | CPUC - SPD (Safety Policy Division)_014 | 1 | CPUC - SPD (Safety Policy Division)_014_Q1 | Provide the last 100 created Priority A tags and associated inspection report. Include all photos from tags or inspection report. a. A minimum of 50 tags must be identified during inspections. b. A minimum of 50 tags must be from the HFTD. c. If the 100 latest created tags do not meet the criteria from a) and b), supplement the request with the latest created tags for a) and b) until all requirements are met. SPD expects the maximum number of tags to be submitted to be 200. | PG&E understands this to be requesting tags related to overhead (OH) inspections. Please note, as tags can be created outside of inspections, not all tags have associated inspection reports. a. Please see “WMP-Discovery2023-2025_DR_SPD_014-Q001Atch01CONF.zip” for 41 Priority A tags and 41 associated inspection reports. b. Please see “WMP-Discovery2023-2025_DR_SPD_014-Q001Atch02CONF.zip” for 50 Priority B tags that were located in HFTD. c. Please see “WMP-Discovery2023-2025_DR_SPD_014-Q001Atch03CONF.zip” for nine additional tags to satisfy subpart (c) of this request. | Henry Sweat | 2024-05-14 | 2024-05-31 | 2024-05-31 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_014.zip | 3 | N/A | 8 | 8.0 Wildfire Mitigations | 8.1.3 Asset Inspections | N/A
632 | CPUC - SPD (Safety Policy Division) | 014 | CPUC - SPD (Safety Policy Division)_014 | 1(s) | CPUC - SPD (Safety Policy Division)_014_Q1(s) | Provide the last 100 created Priority A tags and associated inspection report. Include all photos from tags or inspection report. a. A minimum of 50 tags must be identified during inspections. b. A minimum of 50 tags must be from the HFTD. c. If the 100 latest created tags do not meet the criteria from a) and b), supplement the request with the latest created tags for a) and b) until all requirements are met. SPD expects the maximum number of tags to be submitted to be 200. | PG&E has prepared the following response after discussing this request with the Safety Policy Division on Monday, June 10, 2024. Please see the table below for attachments, including 50 of each Priority A, X, and B tags and their and associated aerial inspection reports. We experienced unexpected technical difficulties in downloading the requested images taken during the inspections. We will provide these images as soon as possible. Attachment Name Description WMP-Discovery2023-2025_DR_SPD_014-Q001Supp01Atch01CONF.zip Priority A tags and aerial inspection reports WMP-Discovery2023-2025_DR_SPD_014-Q001Supp01Atch02CONF.zip Priority X tags and aerial inspection reports WMP-Discovery2023-2025_DR_SPD_014-Q001Supp01Atch03CONF.zip Priority B tags and aerial inspection reports | Henry Sweat | 2024-05-14 | 2024-06-20 | 2024-06-17 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_014.zip | 3 | N/A | 8 | 8.0 Wildfire Mitigations | 8.1.3 Asset Inspections | N/A
632 | CPUC - SPD (Safety Policy Division) | 014 | CPUC - SPD (Safety Policy Division)_014 | 1(s2) | CPUC - SPD (Safety Policy Division)_014_Q1(s2) | Provide the last 100 created Priority A tags and associated inspection report. Include all photos from tags or inspection report. a. A minimum of 50 tags must be identified during inspections. b. A minimum of 50 tags must be from the HFTD. c. If the 100 latest created tags do not meet the criteria from a) and b), supplement the request with the latest created tags for a) and b) until all requirements are met. SPD expects the maximum number of tags to be submitted to be 200. | Please see “WMP-Discovery2023-2025_DR_SPD_014-Q001Supp02Atch01CONF.zip” for the requested images associated with tag and inspection reports provided with SPD_014-Q001Supp01. We apologize for the delay in providing these images. Please also see the table below for notification numbers and equipment IDs associated with the requested images. The images provided have been named with their corresponding SAP Equipment ID number. SAP Equipment ID Notification Number Priority 100024942 128813801 A 100107796 128811808 A 100441232 128906979 A 100513731 128896582 A 100653473 128713925 A 100775289 128650119 A 100794135 128713748 A 100994052 128778250 A 101026683 128719583 A 101032604 129038899 A 101243247 128719712 A 101245649 128683445 A 101252851 128721517 A 101253218 128697918 A 101253373 128771884 A SAP Equipment ID Notification Number Priority 101255449 128782674 A 101260495 128781416 A 101262321 128721667 A 101371602 128730574 A 101444500 128730976 A 101850863 128722955 A 101895524 128693170 A 102148709 128702317 A 102153741 128776776 A 102167548 128749107 A 102181338 129029152 A 102203361 128775585 A 102316302 128691356 A 103012646 128727232 A 103604571 128752175 A 103607781 129030471 A 103798031 128719140 A 103806605 128965557 A 103869296 128806239 A 103922865 128707532 A 103926013 128726492 A 103963998 128731658 A 103966034 128665620 A 104006749 128782537 A 104014660 128718892 A 104032460 128806443 A 104038435 128707017 A 104064182 128897406 A 104073139 128992508 A 104073318 128838348 A 104085394 128721955 A 104088372 128776997 A 104113883 128719954 A 104119131 128790489 A 104134538 128916103 A 100010258 129039588 B 100021957 129039622 B 100026335 129039608 B 100090984 129039627 B 100091130 129039628 B 100093269 129039629 B 100112024 129039646 B 100334684 129039647 B 100334717 129039652 B 100334846 129039648 B 100334933 129039649 B SAP Equipment ID Notification Number Priority 100334950 129039653 B 100401003 129039654 B 100401059 129039663 B 100441234 129039665 B 100483807 129039666 B 101047877 129039658 B 101065374 129039659 B 101066003 129039670 B 101066113 129039671 B 101066115 129039680 B 101072799 129039673 B 101076423 129039634 B 101076469 129039684 B 101077180 129039685 B 101087117 129039688 B 101087425 129039690 B 101087429 129039636 B 101087439 129039691 B 101088012 129039692 B 101263512 129039694 B 101291261 129039707 B 101472535 129039709 B 101472767 129039710 B 101473346 129039711 B 102183419 129039675 B 102183518 129039676 B 102183520 129039677 B 102261188 129039724 B 102287252 129039732 B 102292118 129039715 B 102292122 129039716 B 102351571 129039735 B 103332724 129039741 B 103349040 129039719 B 103383764 129039750 B 103675694 129039744 B 103774994 129039745 B 103856790 129039765 B 104189498 129039785 B 100012024 129024186 X 100012295 129011081 X 100039148 129051439 X 100068021 129053442 X 100076278 129037187 X 100090913 129018640 X 100093251 128983150 X WMP-Discovery2023-2025_DR_SPD_014-Q001Supp02 Page 4 SAP Equipment ID Notification Number Priority 100097093 128841009 X 100100640 129050892 X 100108232 128904598 X 100608882 128887796 X 100746552 128839212 X 101030144 128912106 X 101030362 128839943 X 101066652 128838652 X 101077124 129017918 X 101087318 128930062 X 101087590 128839163 X 101088019 128941566 X 101252662 129028341 X 101252852 128906811 X 101256940 129028800 X 101257714 129028634 X 101340681 128920126 X 101478938 129037020 X 101889216 128778112 X 102160597 128827121 X 102161339 128820663 X 102166060 128882069 X 102182595 128954114 X 102183489 129029862 X 102209755 128775205 X 102216155 128882152 X 102250278 129052674 X 102351276 128887622 X 103144392 129036806 X 103188144 129028188 X 103218110 129057685 X 103275979 128780922 X 103763197 128840539 X 103901662 129038853 X 103950216 128799691 X 103979412 128949446 X 104001820 129019972 X 104002236 128897828 X 104009699 129018972 X 104039249 129023523 X 104068768 128887711 X 104075989 128884081 X 104148611 129019477 X | Henry Sweat | 2024-05-14 | 2024-06-21 | 2024-06-21 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_014.zip | 1 | N/A | 8 | 8.0 Wildfire Mitigations | 8.1.3 Asset Inspections | N/A
633 | CPUC - SPD (Safety Policy Division) | 014 | CPUC - SPD (Safety Policy Division)_014 | 2 | CPUC - SPD (Safety Policy Division)_014_Q2 | Provide the last 100 created Priority X work orders and associated inspection report. Include all photos from work orders or inspection report. a. A minimum of 50 tags must be identified during inspections. b. A minimum of 50 tags must be from the HFTD. c. If the 100 latest created tags do not meet the criteria from a) and b), supplement the request with the latest created tags for a) and b) until all requirements are met. SPD expects the maximum number of tags to be submitted to be 200. | PG&E understands this to be requesting tags related to overhead (OH) inspections. Please note, as tags can be created outside of inspections, not all tags have associated inspection reports. a. Please see “WMP-Discovery2023-2025_DR_SPD_014-Q002Atch01CONF.zip” for 45 Priority X tags and 44 associated inspection reports. Please note, tags 128778454 and 128778509 were created during the same inspection and are associated with inspection report “OHI_100311564_CONF.pdf” located within the referenced zip folder. b. Please see “WMP-Discovery2023-2025_DR_SPD_014-Q002Atch02CONF.zip” for 48 Priority X tags that were located in HFTD. c. Please see “WMP-Discovery2023-2025_DR_SPD_014-Q002Atch03CONF.zip” for seven additional Priority X tags to satisfy this subpart (c) of this request. | Henry Sweat | 2024-05-14 | 2024-05-31 | 2024-05-31 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_014.zip | 3 | N/A | 8 | 8.0 Wildfire Mitigations | 8.1.3 Asset Inspections | N/A
634 | CPUC - SPD (Safety Policy Division) | 014 | CPUC - SPD (Safety Policy Division)_014 | 3 | CPUC - SPD (Safety Policy Division)_014_Q3 | Provide the last 100 created Priority B work orders and associated inspection report. Include all photos from work orders or inspection report. a. A minimum of 50 tags must be identified during inspections. b. A minimum of 50 tags must be from the HFTD. c. If the 100 latest created tags do not meet the criteria from a) and b), supplement the request with the latest created tags for a) and b) until all requirements are met. SPD expects the maximum number of tags to be submitted to be 200. | PG&E understands this to be requesting tags related to overhead (OH) inspections. Please note, as tags can be created outside of inspections, not all tags have associated inspection reports. a. Please see “WMP-Discovery2023-2025_DR_SPD_014-Q003Atch01CONF.zip” for 50 Priority B tags that were identified during inspections and their associated inspection reports. b. Please see “WMP-Discovery2023-2025_DR_SPD_014-Q003Atch02CONF.zip” for 24 Priority B tags that were located in HFTD. As these tags were created during inspections, this attachment also contains their associated inspection reports. c. Please see “WMP-Discovery2023-2025_DR_SPD_014-Q003Atch03CONF.zip” for 26 additional Priority B tags to satisfy subpart (c) of this request. As these tags were created during inspections, this attachment also contains their associated inspection reports. | Henry Sweat | 2024-05-14 | 2024-05-31 | 2024-05-31 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_014.zip | 3 | N/A | 8 | 8.0 Wildfire Mitigations | 8.1.3 Asset Inspections | N/A
635 | CPUC - SPD (Safety Policy Division) | 014 | CPUC - SPD (Safety Policy Division)_014 | 4 | CPUC - SPD (Safety Policy Division)_014_Q4 | Provide all job bulletins related to ‘X’ tags. | PG&E does not have a job bulletin related to “X” tags, however, please see “WMP-Discovery2023-2025_DR_SPD_014-Q004Atch01CONF.pdf” for PG&E’s X tag Standard “Level 2 Priority X Electric Corrective (EC) Standard.” | Henry Sweat | 2024-05-14 | 2024-05-28 | 2024-05-28 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_014.zip | 1 | N/A | 8 | 8.0 Wildfire Mitigations | 8.1.3 Asset Inspections | N/A
636 | CPUC - SPD (Safety Policy Division) | 014 | CPUC - SPD (Safety Policy Division)_014 | 5 | CPUC - SPD (Safety Policy Division)_014_Q5 | Provide number of A, B, X, E, F for Aerial, Ground and Pole Test and Treat finds during inspecions in 2023, and 2024 broken down by HFTD and non‐HFTD. Include number of inspecions and find rate for each tag type. Submit the same informaion in the same format as Table RN‐PG&E‐23‐04‐7 (attached in email) for 2023 and 2024 from PG&E’s 2023‐2025 Wildfire Mitgation Plan Supplemental Response to Revision Notice, except provide the actual tag finds, rather than “Forecast Tag Finds.” Indicate if helicopters or planes were used for any of the aerial inspec􀆟ons. | 2023-2024 Actual Finds by Inspection Type Annual Inspections 2023 Annual Inspections 2024 (YTD) Inspection Type Tier Priority Find Rate Actual Inspections by Tier Actual Tag Find Find Rate Actual Inspections by Tier Actual Tag Find Aerial Non-HFTD /HFRA A #N/A* 700 #N/A* 0.32% 1,581 5 X #N/A* #N/A* 0.89% 14 B #N/A* #N/A* 1.14% 18 E #N/A* #N/A* 15.31% 242 F #N/A* #N/A* 0.38% 6 Tier 2 A #N/A* 30,000 #N/A* 0.25% 42,538 107 X #N/A* #N/A* 0.50% 214 B 2.58% 774 3.20% 1,361 E 1.57% 471 13.74% 5,844 F 0.49% 147 0.40% 170 Tier 3 A #N/A* 7,300 #N/A* 0.23% 25,762 58 X #N/A* #N/A* 0.47% 120 B 2.42% 177 3.53% 910 E 0.82% 60 12.67% 3,263 F 0.22% 16 0.42% 109 Ground Non-HFTD /HFRA A 0.73% 4,908 36 4.76% 84 4 X 0.00% 0 0.00% 0 B 2.38% 117 0.00% 0 E 27.87% 1,368 2.38% 2 Annual Inspections 2023 Annual Inspections 2024 (YTD) Inspection Type Tier Priority Find Rate Actual Inspections by Tier Actual Tag Find Find Rate Actual Inspections by Tier Actual Tag Find F 7.58% 372 1.19% 1 Tier 2 A 0.46% 221,021 1,006 1.30% 1,926 25 X 0.00% 0 0.52% 10 B 3.32% 7,327 3.01% 58 E 27.00% 59,670 9.29% 179 F 5.27% 11,654 2.80% 54 Tier 3 A 1.06% 9,803 104 1.54% 455 7 X 0.00% 0 0.22% 1 B 2.54% 249 3.08% 14 E 15.21% 1,491 13.19% 60 F 4.09% 401 4.62% 21 Zone 1 A 0.67% 1,486 10 0.00% 47 0 X 0.00% 0 0.00% 0 B 1.88% 28 2.13% 1 E 21.40% 318 6.38% 3 F 3.97% 59 6.38% 3 PTT Non-HFTD /HFRA A 0.00% 504 0 0.00% 83 0 X 0.00% 0 1.20% 1 B 0.99% 5 0.00% 0 E 2.98% 15 3.61% 3 F 0.00% 0 0.00% 0 Tier 2 A 0.00% 11,684 0 0.10% 2,041 2 X 0.00% 0 0.00% 0 B 0.39% 45 0.83% 17 E 4.73% 553 5.19% 106 F 0.00% 0 0.10% 2 Tier 3 A 0.00% 7,321 0 0.00% 956 0 X 0.00% 0 0.00% 0 B 0.18% 13 0.31% 3 E 4.66% 341 5.54% 53 F 0.00% 0 0.10% 1 Zone 1 E 5.26% 76 4 0.00% 8 0 * PG&E is using the same aerial data for 2023 that was previously provided in Table RN-PG&E-23-04-7 since it was based off 2023 actuals, per footnote (a). Note: No helicopters or planes were used for any of the aerial inspections. Only drones were used. | Henry Sweat | 2024-05-14 | 2024-05-28 | 2024-05-28 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_014.zip | 0 | N/A | 8 | 8.0 Wildfire Mitigations | 8.1.3 Asset Inspections | N/A
636 | CPUC - SPD (Safety Policy Division) | 014 | CPUC - SPD (Safety Policy Division)_014 | 5(a) | CPUC - SPD (Safety Policy Division)_014_Q5(a) | Provide number of A, B, X, E, F for Aerial, Ground and Pole Test and Treat finds during inspecions in 2023, and 2024 broken down by HFTD and non‐HFTD. Include number of inspecions and find rate for each tag type. Submit the same informaion in the same format as Table RN‐PG&E‐23‐04‐7 (attached in email) for 2023 and 2024 from PG&E’s 2023‐2025 Wildfire Mitgation Plan Supplemental Response to Revision Notice, except provide the actual tag finds, rather than “Forecast Tag Finds.” Indicate if helicopters or planes were used for any of the aerial inspec􀆟ons. | ANSWER 005 REVISED 01 Please see the table below, which has been updated to include the 2023-2024 actual find data for aerial inspections. This actual find data for aerial inspections is current as of May 22, 2024. We were still gathering and quality checking this data when we provided our initial May 28, 2024 response. 2023-2024 Actual Finds by Inspection Type 2023-2024 Actual Finds by Inspection Type Annual Inspections 2023 Annual Inspections 2024 (YTD) Inspection Type Tier Priority Find Rate Actual Inspections by Tier Actual Tag Find Find Rate Actual Inspections by Tier Actual Tag Find Aerial* Non-HFTD /HFRA A 0.56% 708 4 0.32% 1,581 5 X 0.00% 0 0.70% 11 B 3.11% 22 1.08% 17 E 31.36% 222 15.31% 242 F 4.38% 31 0.38% 6 Tier 2 A 0.20% 17,209 34 0.25% 42,538 107 X 0.00% 0 0.31% 131 B 2.31% 398 3.18% 1,353 E 8.59% 1,478 13.70% 5,826 F 1.59% 274 0.39% 168 Tier 3 A 0.30% 19,062 58 0.23% 25,762 58 X 0.00% 0 0.30% 78 B 2.34% 447 3.52% 906 Annual Inspections 2023 Annual Inspections 2024 (YTD) Inspection Type Tier Priority Find Rate Actual Inspections by Tier Actual Tag Find Find Rate Actual Inspections by Tier Actual Tag Find E 3.28% 626 12.65% 3,258 F 0.69% 132 0.42% 109 Zone 1 B 10.00% 10 1 0.00% 9 0 E 10.00% 1 0.00% 0 X 0.00% 0 0.00% 0 Ground Non-HFTD /HFRA A 0.73% 4,908 36 4.76% 84 4 X 0.00% 0 0.00% 0 B 2.22% 109 0.00% 0 E 27.65% 1,357 2.38% 2 F 7.50% 368 1.19% 1 Tier 2 A 0.43% 221,021 958 1.09% 1,926 21 X 0.00% 0 0.42% 8 B 3.19% 7,045 3.01% 58 E 26.73% 59,084 9.09% 175 F 5.22% 11,539 2.80% 54 Tier 3 A 1.05% 9,803 103 1.32% 455 6 X 0.00% 0 0.22% 1 B 2.41% 236 2.86% 13 E 14.63% 1,434 13.19% 60 F 4.02% 394 4.62% 21 Zone 1 A 0.67% 1,486 10 0.00% 47 0 X 0.00% 0 0.00% 0 B 1.82% 27 2.13% 1 E 21.27% 316 6.38% 3 F 3.90% 58 6.38% 3 PTT Non-HFTD /HFRA A 0.00% 504 0 0.00% 83 0 X 0.00% 0 1.20% 1 B 0.99% 5 0.00% 0 E 2.98% 15 3.61% 3 F 0.00% 0 0.00% 0 Tier 2 A 0.00% 11,684 0 0.10% 2,041 2 X 0.00% 0 0.00% 0 B 0.39% 45 0.83% 17 E 4.73% 553 5.19% 106 F 0.00% 0 0.10% 2 Tier 3 A 0.00% 7,321 0 0.00% 956 0 X 0.00% 0 0.00% 0 B 0.18% 13 0.31% 3 E 4.66% 341 5.54% 53 F 0.00% 0 0.10% 1 Zone 1 E 5.26% 76 4 0.00% 8 0 Note: No helicopters or planes were used for any of the aerial inspections. Only drones were used. *Note: 1. Aerial data solely reflects new finds and does not reflect tag reassessments 2. Aerial scope in 2023 prioritized the inspection focus on urgent A and B tags | Henry Sweat | 2024-05-14 | 2024-05-31 | 2024-06-05 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_014.zip | 0 | N/A | 8 | 8.0 Wildfire Mitigations | 8.1.3 Asset Inspections | N/A
636 | CPUC - SPD (Safety Policy Division) | 014 | CPUC - SPD (Safety Policy Division)_014 | 5(a2) | CPUC - SPD (Safety Policy Division)_014_Q5(a2) | Provide number of A, B, X, E, F for Aerial, Ground and Pole Test and Treat finds during inspecions in 2023, and 2024 broken down by HFTD and non‐HFTD. Include number of inspecions and find rate for each tag type. Submit the same informaion in the same format as Table RN‐PG&E‐23‐04‐7 (attached in email) for 2023 and 2024 from PG&E’s 2023‐2025 Wildfire Mitgation Plan Supplemental Response to Revision Notice, except provide the actual tag finds, rather than “Forecast Tag Finds.” Indicate if helicopters or planes were used for any of the aerial inspec􀆟ons. | PG&E responded to “WMP-Discovery2023-2025_DR_SPD_014-Q001.pdf” (Q001), “WMP-Discovery2023-2025_DR_SPD_014-Q002.pdf” (Q002) and “WMPDiscovery2023- 2025_DR_SPD_014-Q003.pdf” (Q003), of this request by reviewing the most recently created 100 tags in its Priority A, X and B categories. PG&E responded to “WMP-Discovery2023-2025_DR_SPD_014-Q005Rev01.pdf” (Q005), by providing a count of all tags created from inspections only in 2024. As more than 100 tags were created in 2024, the counts reported in Q005 should include more tags. PG&E also included the non-HFTD/non-HFRA tier in the data pull for Question 005, which was not originally included in Table RN‐PG&E‐23‐04‐7. In addition, PG&E initially used a slightly different methodology when applying filters to pull the tag count data for Question 005 compared to what was used for Q001-Q003 in PG&E’s system of record, since the data for those questions was pulled by different teams. PG&E has since aligned on the data pull methodology and is providing updated counts for Q005 as shown in the table below. 2023-2024 Actual Finds by Inspection Type Annual Inspections 2023 Annual Inspections 2024 (YTD) Inspection Type Tier Priority Find Rate Actual Inspections by Tier Actual Tag Find Find Rate Actual Inspections by Tier Actual Tag Find Aerial* Non-HFTD /HFRA A 0.56% 708 4 0.32% 1,580 5 X 0.00% 0 0.70% 11 B 3.11% 22 1.08% 17 E 31.64% 224 15.32% 242 Annual Inspections 2023 Annual Inspections 2024 (YTD) Inspection Type Tier Priority Find Rate Actual Inspections by Tier Actual Tag Find Find Rate Actual Inspections by Tier Actual Tag Find F 4.38% 31 0.38% 6 Non-HFTD /non-HFRA A 0.00% 744 0 0.00% 8 0 X 0.00% 0 0.00% 0 B 0.81% 6 0.00% 0 E 1.48% 11 25.00% 2 F 0.40% 3 0.00% 0 Tier 2 A 0.20% 17,208 34 0.23% 42,535 99 X 0.00% 0 0.32% 135 B 2.62% 450 3.27% 1,392 E 9.18% 1,580 14.00% 5,954 F 1.64% 282 0.40% 171 Tier 3 A 0.30% 19,061 58 0.21% 25,762 55 X 0.00% 0 0.32% 83 B 2.57% 489 3.61% 929 E 3.47% 662 12.97% 3,342 F 0.72% 137 0.43% 110 Zone 1 B 10.00% 10 1 0.00% 9 0 E 10.00% 1 0.00% 0 Ground Non-HFTD /HFRA A 0.18% 4,902 9 2.33% 86 2 X 0.00% 0 0.00% 0 B 2.43% 119 0.00% 0 E 27.76% 1,361 3.49% 3 F 7.59% 372 1.16% 1 Non-HFTD /non-HFRA A 0.33% 313,213 1049 0.43% 77,719 337 X 0.00% 0 0.36% 281 B 4.15% 13008 2.16% 1677 E 32.86% 102914 12.65% 9830 F 7.22% 22602 4.75% 3689 Tier 2 A 0.10% 220,872 228 1.24% 2,251 28 X 0.00% 0 0.49% 11 B 3.35% 7,396 2.62% 59 E 26.97% 59,575 9.55% 215 F 5.27% 11,649 2.93% 66 Tier 3 A 0.30% 9,786 29 2.15% 466 10 X 0.00% 0 0.21% 1 B 2.63% 257 2.79% 13 E 15.30% 1,497 13.95% 65 F 4.13% 404 4.94% 23 Zone 1 A 0.27% 1,484 4 0.00% 47 0 X 0.00% 0 0.00% 0 Annual Inspections 2023 Annual Inspections 2024 (YTD) Inspection Type Tier Priority Find Rate Actual Inspections by Tier Actual Tag Find Find Rate Actual Inspections by Tier Actual Tag Find B 1.82% 27 2.13% 1 E 21.50% 319 6.38% 3 F 3.98% 59 10.64% 5 PTT Non-HFTD /HFRA A 0.00% 503 0 1.20% 83 1 X 0.00% 0 1.20% 1 B 0.99% 5 0.00% 0 E 3.38% 17 3.61% 3 F 0.00% 0 0.00% 0 Non-HFTD /non-HFRA A 0.01% 71,256 4 0.07% 4,545 3 X 0.00% 0 0.07% 3 B 0.40% 284 0.35% 16 E 5.00% 3561 8.34% 379 F 0.00% 2 0.00% 0 Tier 2 A 0.00% 11,683 0 0.15% 2,041 3 X 0.00% 0 0.00% 0 B 0.43% 50 0.98% 20 E 4.95% 578 5.29% 108 F 0.00% 0 0.10% 2 Tier 3 A 0.00% 7,321 0 0.00% 956 0 X 0.00% 0 0.00% 0 B 0.20% 15 0.63% 6 E 5.03% 368 5.54% 53 F 0.00% 0 0.10% 1 Zone 1 E 5.33% 75 4 0.00% 8 0 *Notes: 1. No helicopters or planes were used for any of the aerial inspections. Only drones were used. 2. The aerial data solely reflects new finds and does not reflect tag reassessments. 3. The aerial scope in 2023 prioritized the inspection focus on urgent A and B tags. | Henry Sweat | 2024-05-14 | 2024-06-21 | 2024-06-20 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_014.zip | 0 | N/A | 8 | 8.0 Wildfire Mitigations | 8.1.3 Asset Inspections | N/A
636 | CPUC - SPD (Safety Policy Division) | 014 | CPUC - SPD (Safety Policy Division)_014 | 5(a2supp) | CPUC - SPD (Safety Policy Division)_014_Q5(a2supp) | Provide number of A, B, X, E, F for Aerial, Ground and Pole Test and Treat finds during inspecions in 2023, and 2024 broken down by HFTD and non‐HFTD. Include number of inspecions and find rate for each tag type. Submit the same informaion in the same format as Table RN‐PG&E‐23‐04‐7 (attached in email) for 2023 and 2024 from PG&E’s 2023‐2025 Wildfire Mitgation Plan Supplemental Response to Revision Notice, except provide the actual tag finds, rather than “Forecast Tag Finds.” Indicate if helicopters or planes were used for any of the aerial inspec􀆟ons. | Per the follow-up email request from the Original Requester on July 19, 2024: 1. Do you mind double checking this Response? In the attached spreadsheet, I highlighted a few of the items that changed a lot – but it might be worth doing a full review? 2. Also, would you mind explaining the methodology change between the two revisions? Was it just including Non HFTD/Non HFRA as well in the find rate? 3. For the data, if the inspector found an item which was already an existing tag in the backlog, was it included as a “find”? PG&E responds as follows: 1. As noted in “WMP-Discovery2023-2025_DR_SPD_014-Q005Rev02.pdf” (Rev02), PG&E initially used a slightly different methodology when applying filters to pull the tag count data for Question No. 005 compared to what was used for Q001-Q003 of the same request. PG&E met internally and aligned on the data pull methodology to provide tag counts included for Q005 of Rev02. The highlighted items in the spreadsheet that changed were a result of the updated methodology that is described in the response to question number two, below. 2. Besides including non-HFTD/non-HFRA, the updated methodology also included using the same start-to-end timeline and "tag status" to align with the methodology in Q001-003 of Rev02. 3. The Electric Distribution maintenance and inspection tag process assigns one Electric Corrective (EC) Notification to each structure. If the inspector identifies a find/condition that is already identified in an existing open tag, the inspector is required to review any open EC notifications to assess if any of the previously identified conditions have deteriorated or changed since the last inspection. The inspector will escalate the priority of the notification if any condition identified in the previous inspection has worsened and needs to be remediated as a higher priority. If new findings are identified during review of any open EC notification, the finding is added to the existing EC tag to ensure all identified findings are planned, executed, and prioritized together. For example, if a new finding with a higher priority condition is identified during an open EC notification review, it is added to the existing EC notification and the EC notification is escalated to the highest priority finding. | Henry Sweat | 2024-05-14 | 2024-07-26 | 2024-07-26 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_014.zip | 0 | N/A | 8 | 8.0 Wildfire Mitigations | 8.1.3 Asset Inspections | N/A
637 | CPUC - SPD (Safety Policy Division) | 014 | CPUC - SPD (Safety Policy Division)_014 | 6 | CPUC - SPD (Safety Policy Division)_014_Q6 | Explain tag re‐prioritization oversight process where an inspector’s initial prioritization is changed. a. Provide the number of tags in 2024 found during inspections where the inspector identified A, X, and B tags where the tag was re‐prioritized to a less urgent priority, and which priority it was re‐assigned. b. Provide inspection reports and work orders, including all photos, for the last 10 created tags found during inspections for each of A, X and B where the tag was re‐prioritized to a less urgent priority. c. Provide a list of all tags found in April during inspections where the inspector identified A, X, and B tags where the tag was re‐prioritized to a less urgent priority. The list should include (1) the notification number, (2) the date each tag was found, (3) the original priority, (4) the changed priority and (5) a description of the finding. | PG&E understands this to be requesting tags related to overhead (OH) inspections. Please see below for tags responsive to this request. If an A or X tag are determined not to be emergency tags during the oversight process, the tag is cancelled and a new tag is created with a lesser priority. If a Gatekeeper determines a B tag’s initial prioritization should be de-prioritized, logic in the gatekeeper screen will force the gatekeeper to provide reasons for de-prioritization. These reasons/responses are sent to the submitter via an SAP auto-email generation to finalize the changes made. a. Please see the table below for the requested information, which is current as of May 20, 2024: Tag Count Original Priority Less Urgent Priority 1 A X 1 A B 661 B E 18 B F 2 X B 1 X C 2 X Re-assessed and cancelled b. Please see attachment “WMP-Discovery2023-2025_DR_SPD_014-Q006Atch01CONF.zip” for the requested Priority B tags and associated inspection reports. Please see attachment “WMP-Discovery2023-2025_DR_SPD_014-Q006Atch02CONF.zip” for Priority A and X tags and associated inspection reports. Please note, PG&E only identified eight Priority A and X tags during inspections where the tag was re-prioritized to a less urgent priority. c. Please see attachment “WMP-Discovery2023-2025_DR_SPD_014-Q006Atch03.xlsx” for the requested information. | Henry Sweat | 2024-05-14 | 2024-05-31 | 2024-05-28 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_014.zip | 3 | N/A | 8 | 8.0 Wildfire Mitigations | 8.1.3 Asset Inspections | N/A
637 | CPUC - SPD (Safety Policy Division) | 014 | CPUC - SPD (Safety Policy Division)_014 | 6(a) | CPUC - SPD (Safety Policy Division)_014_Q6(a) | Explain tag re‐prioritization oversight process where an inspector’s initial prioritization is changed. a. Provide the number of tags in 2024 found during inspections where the inspector identified A, X, and B tags where the tag was re‐prioritized to a less urgent priority, and which priority it was re‐assigned. b. Provide inspection reports and work orders, including all photos, for the last 10 created tags found during inspections for each of A, X and B where the tag was re‐prioritized to a less urgent priority. c. Provide a list of all tags found in April during inspections where the inspector identified A, X, and B tags where the tag was re‐prioritized to a less urgent priority. The list should include (1) the notification number, (2) the date each tag was found, (3) the original priority, (4) the changed priority and (5) a description of the finding. | PG&E is amending its response to subpart b) of Question No. 006. Per email correspondence with the Safety Policy Division (SPD) on June 12, 2024, PG&E inadvertently omitted the inspection reports in “WMP-Discovery2023-2025_DR_SPD_014-Q006Atch01CONF.zip.” Please see “WMP-Discovery2023-2025_DR_SPD_014-Q006Rev01Atch01.zip” for the requested Priority B tags and associated inspection reports. In addition, PG&E inadvertently included two Electric Corrective (EC) tags which were not associated with inspections. Please remove EC tag 128772906 and 128773036 from SPD records and replace with EC tag 128776178 associated with SAP ID 102178986 Inspection Report and EC tag 128776206 associated with SAP ID 104045760 Inspection Report. PG&E understands this to be requesting tags related to overhead (OH) inspections. Please see below for tags responsive to this request. If an A or X tag are determined not to be emergency tags during the oversight process, the tag is cancelled and a new tag is created with a lesser priority. If a Gatekeeper determines a B tag’s initial prioritization should be de-prioritized, logic in the gatekeeper screen will force the gatekeeper to provide reasons for de-prioritization. These reasons/responses are sent to the submitter via an SAP auto-email generation to finalize the changes made. a. Please see the table below for the requested information, which is current as of May 20, 2024: Tag Count Original Priority Less Urgent Priority 1 A X 1 A B 661 B E 18 B F 2 X B 1 X C 2 X Re-assessed and cancelled b. Please see attachment “WMP-Discovery2023-2025_DR_SPD_014-Q006Rev01Atch01CONF.zip” for the requested Priority B tags and associated inspection reports. Please see attachment “WMP-Discovery2023-2025_DR_SPD_014-Q006Atch02CONF.zip” for Priority A and X tags and associated inspection reports. Please note, PG&E only identified eight Priority A and X tags during inspections where the tag was re-prioritized to a less urgent priority. c. Please see attachment “WMP-Discovery2023-2025_DR_SPD_014-Q006Atch03.xlsx” for the requested information. | Henry Sweat | 2024-05-14 | 2024-06-13 | 2024-06-13 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_014.zip | 1 | N/A | 8 | 8.0 Wildfire Mitigations | 8.1.3 Asset Inspections | N/A
638 | CPUC - SPD (Safety Policy Division) | 014 | CPUC - SPD (Safety Policy Division)_014 | 7 | CPUC - SPD (Safety Policy Division)_014_Q7 | Provide the count of tags for each tag type in 2024 where an existing tag was re‐prioritized to a more urgent priority and the priority to which it was re‐assigned due to an inspection. | PG&E interprets this as a request for tags that were re-prioritized to a more urgent priority during an inspection and not during the oversight process. This would occur when an asset with an existing tag was scheduled for an inspection due to General Order 165 requirements. Please see the table below for the requested information. Original Priority Tag Count Escalated Priority B 0 N/A E 216 B F 62 B Please note, A tags are the highest priority. Tags identified as X priority can get upgraded to an A priority, however, this occurs procedurally, and not during an inspection. | Henry Sweat | 2024-05-14 | 2024-05-28 | 2024-05-28 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_014.zip | 0 | N/A | 8 | 8.0 Wildfire Mitigations | 8.1.3 Asset Inspections | N/A
639 | CPUC - SPD (Safety Policy Division) | 014 | CPUC - SPD (Safety Policy Division)_014 | 8 | CPUC - SPD (Safety Policy Division)_014_Q8 | What would motivate an inspector to override the prioritization for a tag in the job aid and increase the priority or deadline? a. In this scenario, what prevents a de‐prioritization of the tag during the review by a supervisor or other PG&E employee? | An Inspector may override a tag priority if, in the Inspector’s opinion, the situation is more urgent than the minimum priority outlined in the job aid. This could be because of exposure or severity of condition. PG&E’s Centralized Inspection Review Team (CIRT) also reviews tags following an inspection and could increase the priority of a tag if they determine the equipment’s impact of failure or impact of exposure to the public is at risk. a. There is a system control within SAP’s Gatekeeper screen that prevents Electric Corrective (EC) tags from being created with a priority lower than the minimum allowed for the FDA selected. Currently, CIRT Gatekeeper (Qualified Electrical Worker who performs desktop review of tags after they are submitted) may de-prioritize a tag prior to creation, but not beyond its minimum priority assigned in per PG&E guidance (existing procedures such as the OH/UG job aid, etc). Once an EC tag has been created in the system, the required end date field is locked in the system and access is not granted to update this field. | Henry Sweat | 2024-05-14 | 2024-05-28 | 2024-05-28 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_014.zip | 0 | N/A | 8 | 8.0 Wildfire Mitigations | 8.1.3 Asset Inspections | N/A
640 | CPUC - SPD (Safety Policy Division) | 014 | CPUC - SPD (Safety Policy Division)_014 | 9 | CPUC - SPD (Safety Policy Division)_014_Q9 | When does the field engineer get involved with addressing a high (A, X, B) priority tag? Provide examples. a. Can the field engineer change the priority of a tag? Provide examples. b. Describe the role of field engineers in the process for working on high priority tags. | a. No, field engineers do not change the priority level of a tag. b. If the work is assigned to a General Construction crew or contractor, then a Field Engineer coordinates the work required for the tag. PG&E inspectors create and identify the tag’s priority. | Henry Sweat | 2024-05-14 | 2024-05-28 | 2024-05-28 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_014.zip | 0 | N/A | 8 | 8.0 Wildfire Mitigations | 8.1.3 Asset Inspections | N/A
641 | CPUC - SPD (Safety Policy Division) | 014 | CPUC - SPD (Safety Policy Division)_014 | 10 | CPUC - SPD (Safety Policy Division)_014_Q10 | Discuss the process for updating the Distribution Inspection Job Aid. a. What is the process? b. Who has final say? c. Which licensed civil (structural practitioner) or structural engineers reviewed the job aid? Provide their feedback and comments in full, including any email correspondence. Summarize any comments made in meetings discussing the Job Aid. d. Provide meeting notes from meetings discussing changes to Job Aid from the Wildfire Steering Governance Committee, or a similar type of committee governing distribution assets or inspections, provide them. | a. PG&E follows a management of change process which includes identifying stakeholders, documenting approvals through System Inspections and Asset Strategy Leadership, and communicating the updates with the target audience for the job aid. b. During the process outlined above, a defined standards council is identified who is responsible for reviewing and approving the final job aid. PG&E’s Director of System Inspections and Director of Asset Management finalized the referenced Distribution Inspection job aid. c. The stakeholders that participate in the update process include engineers from Engineering Standards, Work Methods, Asset Strategy, and Applied Technology Services (ATS). In addition, stakeholders included personnels from System Inspections and Field Operations. Feedback was received from the stakeholders over multiple meetings. Meeting notes are not available, however, several studies were conducted by PG&E’s ATS engineering team in collaboration with Asset Strategy and Standards engineers which provided an engineering basis for several of the changes made to the job aid. Please see the following attachments for copies of the studies and meeting presentations contributing to the referenced job aid. WMP-Discovery2023-2025_DR_SPD_014-Q010 Page 2 Attachment Description WMP-Discovery2023-2025_DR_SPD_014- Q010Atch01CONF.pdf Wildfire Risk Committee Presentation WMP-Discovery2023-2025_DR_SPD_014- Q010Atch02CONF.pdf Effects of Splice Location on Distribution Lines WMP-Discovery2023-2025_DR_SPD_014- Q010Atch03CONF.pdf FDA Tag Evaluation WMP-Discovery2023-2025_DR_SPD_014- Q010Atch04CONF.pdf Electric Distributions Engineering Criteria for Allowable Broken Strands for a Conductor WMP-Discovery2023-2025_DR_SPD_014- Q010Atch05CONF.pdf Electric Distributions Engineering Criteria for Remaining Circumference and Horizontal Cut Depth WMP-Discovery2023-2025_DR_SPD_014- Q010Atch06CONF.pdf Electric Distributions Engineering Criteria for Woodpecker Feeding Holes WMP-Discovery2023-2025_DR_SPD_014- Q010Atch07CONF.pdf Electric Distributions Engineering Criteria for Woodpecker Starter and Nesting Holes WMP-Discovery2023-2025_DR_SPD_014- Q010Atch08CONF.pdf Electric Distributions Engineering Criteria for Hole Proximity on Wood Poles d. Please see the response to subpart (c) above for the requested information. | Henry Sweat | 2024-05-14 | 2024-05-28 | 2024-05-28 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_014.zip | 8 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23-09 – Decrease in Detailed Distribution Inspections | ACI 23-09 – Decrease in Detailed Distribution Inspections
642 | OEIS | 021 | OEIS_021 | 1 | OEIS_021_Q1 | Regarding PG&E’s 2025 Distribution Hardening GH-01 Risk Impact: a. In table 8-3 of PG&E’s 2023-2025 WMP, PG&E targets a 4.7% risk impact in 2025 for initiative GH-01.1 PG&E also states that it is redeveloping its undergrounding workplan.2 Please explain how PG&E calculated the 4.7% risk impact for GH-01 given the 2025 workplan was not finalized at the time of WMP submission. Provide all supporting documentation necessary to justify the 4.7% risk impact for initiative GH-01 in 2025. | a. Please see attachment WMPWMP-Discovery2023-2025_DR_OEIS_021- Q001Atch01.xlsx for the requested information. The projected GH-01 risk reduction estimates leveraged the System Hardening workplan as of February 22, 2024, and was normalized to be proportionate to the mileage targets for 2025 (520 System Hardening miles). To normalize the risk reduction estimates based on the target miles, PG&E selected for projects that were marked to move forward post-GRC decision and their corresponding project status (SAP status). The steps taken are further described in the attachment (see worksheet “2025 Risk Reduction Estimate”) referencing summary information and formulas to calculate the reported 4.7% risk reduction. The 2025 workplan data, including project status, hardening miles, and risk reduction values, is provided in the attachment (see worksheet “2025 GH-01 Workplan”). When taking the snapshot of the workplan on February 22, 2024, PG&E provided the best data available at the time, recognizing that PG&E’s 2025 and 2026 workplan was still evolving to account for the risk reduction and funding requirements from GRC D.23-11-069. | Brad Hill | 2024-05-20 | 2024-05-23 | 2024-05-23 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/OEIS_021.zip | 1 | N/A | 8 | Section 8.1.2 - Grid Design and System Hardening | 8.1.2.2 Undergrounding of electric lines and/or equipment | 2.1.1.2 GH-04 Undergrounding
643 | CPUC - SPD (Safety Policy Division) | 015 | CPUC - SPD (Safety Policy Division)_015 | 1 | CPUC - SPD (Safety Policy Division)_015_Q1 | I’m requesting these files: Data Request: CalAdvocates_041-Q003 (CalAdvocates-PGE2025WMP-05) Data Request Date: April 8, 2024 PG&E Date of Response to Data Request: April 29, 2024 PG&E Document No. or Title: WMP-Discovery2023-2025_DR_CalAdvocates_041-Q003Atch01CONF.zip | Please see the following for PG&E’s complete response to WMP-Discovery2023-2025_DR_CalAdvocates_041-Q003: • WMP-Discovery2023-2025_DR_CalAdvocates_041-Q003.pdf • WMP-Discovery2023-2025_DR_CalAdvocates_041-Q003Atch01CONF.zip • WMP-Discovery2023-2025_DR_CalAdvocates_041-Q003Atch02.xlsx | Henry Sweat | 2024-05-24 | 2024-05-28 | 2024-05-28 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_015.zip | 3 | N/A | 6 | Section 6 - Risk Methodology and Assessment | 6.1.2 Summary of Risk Models | B.1.1. WDRM v4
644 | CPUC - SPD (Safety Policy Division) | 016 | CPUC - SPD (Safety Policy Division)_016 | 1 | CPUC - SPD (Safety Policy Division)_016_Q1 | In response to ACI PG&E-23-13 – Workforce Planning and Resource Allocation to Respond to EPSS Events, Customer Average Interruption Duration Index (CAIDI) metric PG&E indicated: customers on average experiencing EPSS outages of 176 minutes in 2022 and 193 minutes in 2023 (We note that the CAIDI score when excluding Major Event Days (MED) was 183 minutes for 2023). What was the key reason(s) or driver(s), if known, for the increase in CAIDI from 2022 to 2023? | Excluding Major Event Days (MEDs), the increase in CAIDI from 2022 to 2023 was approximately seven minutes. In 2023, the additional implementation of Down Conductor Detection (DCD) resulted in outages that accounted for an increase in EPSS CAIDI of approximately ten minutes. Excluding both MEDs and DCD outages, the EPSS CAIDI in 2023 was approximately 173 minutes. In 2024, the EPSS PMO plans to implement DCD technology firmware upgrades, developed in partnership with our vendor, across devices currently DCD capable in the field in an effort to reduce occurrence of DCD trips where no cause was found after patrol or the outage was related to planned system switching activities. | Henry Sweat | 2024-05-30 | 2024-06-04 | 2024-06-04 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_016.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--13 | ACI 23-13 Workforce Planning and Resource Allocation
645 | CPUC - SPD (Safety Policy Division) | 016 | CPUC - SPD (Safety Policy Division)_016 | 2 | CPUC - SPD (Safety Policy Division)_016_Q2 | Generally, what is PG&E’s corporate process and strategic procedure for switching to a new model to support decision-making regarding mitigation alternatives (e.g., migrating from WDRM v3 to WDRM v4)? What steps are involved? | PG&E utilizes Utility Standard: TD-7201S, Wildfire Risk Management Distribution Standard to help guide its decision-making in this area. Specifically, section 4 describes our management of change process. Section 4 of this procedure is copied below. 4. WDRM Management of Change 4.1 In support of PG&E’s stand that “Catastrophic Wildfires Shall Stop,” the nascent science of wildfire risk modeling necessitates updates and improvements on a frequent basis. 1. The risk models based on machine learning (ML) and artificial intelligence (AI) provide advanced technics to support this stand. While advanced and powerful, they are statistical forecasts. As such, the statistical or predictive performance of one model and then a subsequent improved model can be evaluated. 4.2 The prioritization of locations or assets provided by models is not necessarily similar. Models with similar statistical predictive performance can be achieved with different model results. 1. For example, if two models with similar predictive performances address 75% of future outage locations, the actual ranked prioritization in which 75% is identified can differ. a. IF one of the statistically close models incorporates data that improves identified required corrective work to mitigate the risk, THEN the work plan may need to rely more heavily on that model. 4.3 In accordance with the above facts, base the transition from one model to the next for work plan development on both the improvement in predictive performance and the nature of the work plan related to the model features. 4.4 Programs with a long lead time where work plans are developed a year or more in advance (such as system hardening/undergrounding) may decide to keep or “grandfather” all or a portion of the existing work plan commitment before switching to the new model version. Other programs with shorter work plan cycle times may switch to the new model sooner. 4.5 For each of the programs identified in the following Section 5, guidelines for transitioning to new models are provided. 1. The WRGSG must approve both the WDRM and the Wildfire Consequence Model before they are released for prioritizing and planning work. | Henry Sweat | 2024-05-30 | 2024-06-04 | 2024-06-04 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_016.zip | 0 | N/A | 6 | 6.0 Risk Methodology and Assessment | 6.2.1 Risk and Risk Component Identification | 1. Signfiicant Updates to Risk Models (WDRM v4 & WTRM v2)
646 | CPUC - SPD (Safety Policy Division) | 016 | CPUC - SPD (Safety Policy Division)_016 | 3 | CPUC - SPD (Safety Policy Division)_016_Q3 | Provide a list of all memorandum (memo) and balancing accounts where WMP costs are currently being recorded as of May 31, 2024. a. In each of the memorandum and balancing accounts where WMP costs are being recorded provide the current WMP cost balances as follows (if future years [e.g., 2025] are expected to use memo accounts, add columns and data for them as well): Year 2020 2021 2022 2023 2024 Recorded Account Capital Expenditure ($) Recorded Account O&M Expenditure ($) Authorized GRC Capital Expenditure ($) Authorized GRC O&M Expenditure ($) b. Regarding planning for work with budgeting for future years, how does PG&E use its memo and balancing accounts with regard to projecting expenditures, projects, and workplans? | a. Please see “WMP-Discovery2023-2025_DR_SPD_016-Q003Atch01.xlsx” which represents the total spend recorded to each identified wildfire balancing or memorandum account in SAP, at the time the respective costs were extracted and prepared for the Commission's reasonableness review process. Please note, these costs are not adjusted for the WF OII Disallowance amount ordered by the Commission. For 2024, PG&E is providing Year to Date through Quarter 1. PG&E does not have an approved 2025 Investment Plan at this time. b. Through PG&E’s planning process, PG&E forecasts the work for future years within known memo and balancing accounts. When future year plans have been approved, plans are broken out by memo and balancing account. | Henry Sweat | 2024-05-30 | 2024-06-10 | 2024-06-10 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_016.zip | 1 | N/A | 4.3 | 4.0 Overview of WMP | 4.3 Proposed Expenditures | 2.3 Expenditures
647 | CPUC - SPD (Safety Policy Division) | 016 | CPUC - SPD (Safety Policy Division)_016 | 4 | CPUC - SPD (Safety Policy Division)_016_Q4 | Provide GIS data that show progressive sectionalization of EPSS-enabled circuits: a. Data snapshot of circuits from January 1, 2022 b. Data snapshot of circuits from January 1, 2023 c. Data snapshot of circuits from January 1, 2024 | PG&E is still compiling data and will provide the requested information as soon as possible. | Henry Sweat | 2024-05-30 | 2024-06-04 | 2024-06-04 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_016.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--26 Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI 23-26 Evaluation and Reporting of Safety Impacts Related to EPSS
647 | CPUC - SPD (Safety Policy Division) | 016 | CPUC - SPD (Safety Policy Division)_016 | 4(s) | CPUC - SPD (Safety Policy Division)_016_Q4(s) | Provide GIS data that show progressive sectionalization of EPSS-enabled circuits: a. Data snapshot of circuits from January 1, 2022 b. Data snapshot of circuits from January 1, 2023 c. Data snapshot of circuits from January 1, 2024 | PG&E has prepared this response per clarification discussion with the Safety Policy Division on June 13, 2023. The response to Question No. 004 and Question No. 005 of this request includes active devices on PG&E’s system which isolate protective zones. Please note, numbers reported out regarding sectionalizing devices in Wildfire Mitigation Plans varies over the years due to business-driven decisions, such as replacing or removing some sectionalizing devices. The lists provided in these responses includes active devices in PG&E service territory as of June 26, 2024. Please see “WMP-Discovery2023-2025_DR_SPD_016-Q004Supp01Atch01.xlsx” for the requested information. PG&E is compiling a GIS data file inclusive of the data requested in both Question No. 004 and Question No. 005 and will provide as soon as its available. Please note, changes that have occurred on a circuit over time are not visually represented in GIS data. The file being provided will include a snapshot of devices that are presently active. The data will show the exact location of the sectionalizing device, however, will not delineate its downstream effect in the attached line work. The circuit alignment included represents the entire circuit, not just the protected portion, and should be used for reference only. | Henry Sweat | 2024-05-30 | 2024-06-27 | 2024-06-27 | https://preview.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_016.zip | 1 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--26 Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI 23-26 Evaluation and Reporting of Safety Impacts Related to EPSS
647 | CPUC - SPD (Safety Policy Division) | 016 | CPUC - SPD (Safety Policy Division)_016 | 4(s2) | CPUC - SPD (Safety Policy Division)_016_Q4(s2) | Provide GIS data that show progressive sectionalization of EPSS-enabled circuits: a. Data snapshot of circuits from January 1, 2022 b. Data snapshot of circuits from January 1, 2023 c. Data snapshot of circuits from January 1, 2024 | An attachment to this response contains CONFIDENTIAL information provided pursuant to the accompanying confidentiality declaration. Please see “WMP-Discovery2023-2025_DR_SPD_016-Q004Supp02Atch01CONF.zip” for GIS data requested for both Question No. 004 and Question No. 005 of “CONFSPD_WSPS_PG&E_2024_006 (SPD_016).pdf”. Please note, changes that have occurred on a circuit over time are not visually represented in GIS data. The file provided includes a snapshot of devices that are presently active. The data shows the exact location of the sectionalizing device, however, does not delineate its downstream effect in the attached line work. The circuit alignment included represents the entire circuit, not just the protected portion, and should be used for reference only. | Henry Sweat | 2024-05-30 | 2024-07-10 | 2024-07-10 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_016.zip | 1 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--26 Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI 23-26 Evaluation and Reporting of Safety Impacts Related to EPSS
648 | CPUC - SPD (Safety Policy Division) | 016 | CPUC - SPD (Safety Policy Division)_016 | 5 | CPUC - SPD (Safety Policy Division)_016_Q5 | Provide GIS Data that show progressive sectionalization of PSPS-enabled circuits: a. Data snapshot of circuits from January 1, 2020 b. Data snapshot of circuits from January 1, 2021 c. Data snapshot of circuits from January 1, 2022 d. Data snapshot of circuits from January 1, 2023 e. Data snapshot of circuits from January 1, 2024 | PG&E is still compiling data and will provide the requested information as soon as possible. | Henry Sweat | 2024-05-30 | 2024-06-04 | 2024-06-04 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_016.zip | 0 | N/A | 9 | Section 9 - Public Safety Power Shutoff | 9.1.5 Performance Metrics Identified by the Electrical Corporation | 2.1.1.3 PS-07: Reduce PSPS Impacts to Customers
648 | CPUC - SPD (Safety Policy Division) | 016 | CPUC - SPD (Safety Policy Division)_016 | 5(s) | CPUC - SPD (Safety Policy Division)_016_Q5(s) | Provide GIS Data that show progressive sectionalization of PSPS-enabled circuits: a. Data snapshot of circuits from January 1, 2020 b. Data snapshot of circuits from January 1, 2021 c. Data snapshot of circuits from January 1, 2022 d. Data snapshot of circuits from January 1, 2023 e. Data snapshot of circuits from January 1, 2024 | PG&E has prepared this response per clarification discussion with the Safety Policy Division on June 13, 2023. The response to Question No. 004 and Question No. 005 of this request includes active devices on PG&E’s system which isolate protective zones. Please note, numbers reported out regarding sectionalizing devices in Wildfire Mitigation Plans varies over the years due to business-driven decisions, such as replacing or removing some sectionalizing devices. The list provided for Question No. 005 includes active devices in PG&E service territory as of June 27, 2024.Please note, PSPS includes switches as sectionalizing devices, whereas EPSS does not. Please note, there are multiple instances where we removed SCADA and the motor from an MSO in the same location as a recloser. Both devices are considered sectionalizing devices on this list for PSPS, however, the MSO (now switch) is unlikely to be utilized. Please see “WMP-Discovery2023-2025_DR_SPD_016-Q005Supp01Atch01.xlsx” for the requested information. PG&E is compiling a GIS data file inclusive of the data requested in both Question No. 004 and Question No. 005 and will provide as soon as it is available. Please note, changes that have occurred on a circuit over time are not visually represented in GIS data. The file being provided will include a snapshot of devices that are presently active. The data will show the exact location of the sectionalizing device, however, it will not delineate its downstream effect in the attached line work. The circuit alignment included represents the entire circuit, not just the protected portion, and should be used for reference only. ATTACHMENT: WMP-Discovery2023-2025_DR_SPD_016-Q005Supp01Atch01.xlsx | Henry Sweat | 2024-05-30 | 2024-06-28 | 2024-06-28 | https://preview.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_016.zip | 1 | N/A | 9 | Section 9 - Public Safety Power Shutoff | 9.1.5 Performance Metrics Identified by the Electrical Corporation | 2.1.1.3 PS-07: Reduce PSPS Impacts to Customers
649 | CPUC - SPD (Safety Policy Division) | 016 | CPUC - SPD (Safety Policy Division)_016 | 6 | CPUC - SPD (Safety Policy Division)_016_Q6 | PG&E describes in “WMP-Discovery2023_DR_CalAdvocates_015-Q018Atch01.docx” a brief description of “Critical attributes” and “Conformance attributes” used to define pass rate. For the following questions, Vegetation Programs refer to the following programs: Distribution Routine, Distribution Second Patrol, Focus Tree inspections, Vegetation Management for Operational Mitigations, Tree Removal Inventory, Focused Tree Inspection (FTI), Transmission, Pole Clearing and Field Quality Control (FQC). a. Provide the criteria for “critical attributes” evaluated by QA/QC inspectors for each Vegetation Program. b. Provide three examples of “critical attributes” evaluated by QA/QC inspectors for each Vegetation Program. c. Provide the criteria for “conformance attributes” evaluated by QA/QC inspectors for each Vegetation Program. d. Provide three examples of “conformance attributes” evaluated by QA/QC inspectors for each Vegetation Program. e. Define the criteria assessed for the “critical pass rate” for each Vegetation Program. Comment on how it relates to “critical attributes” and “conformance attributes.” f. Provide PG&E’s standards for QA and QC for each Vegetation Program. g. Provide the survey used by QA and QC inspectors to record information for each Vegetation Program. h. Describe how an attribute is assessed as a pass/fail and then aggregated up to the pass rate for Vegetation Program. i. Define “Locations”, as used in Table 8-18-1 (Revised) and Table 8-18-2 (Revised). j. Explain when QC or QA would have different criteria for evaluation and discuss how this manifests in the pass rate for each type. For instance, when would work pass QA but not QC and vice versa. k. “WMP-Discovery2023_DR_CalAdvocates_015-Q018Atch01.docx” states the pass rate is: Total Passing responses for Critical and Conformance Attributes divided by (Total Responses for Critical and Conformance Attributes minus N/A responses) whereas footnote 224 on page 708 of “TN13804_20240402T112956_PGE's_20232025_Wildfire_Mitigation_Plan_Revision_5” indicates that the pass rate is based on: the number of assets reviewed by QC that do not have a Critical Attribute (as defined by Asset Strategy) failure or miss divided by the number of assets reviewed by QC. The definition of pass rate appears to be different in a few ways such as (1) the units are different (number of attributes versus number of assets) and (2) one includes conformance attribute, whereas the other does not. Explain the discrepancies between these two criteria and describe how they are used. l. Provide the last 5 completed QC reviews for Distribution Routine that include a finding. m. Provide the last 5 completed QA reviews for Distribution Routine that include a finding. n. Explain why “WMP-Discovery2023-2025_DR_CalAdvocates_039-Q001Atch04.docx” has multiple rows of data where there were 0 trees inspected and 0 trees failed? i. Define trees inspected. (Is this number of strike trees between two poles? Is this just five random trees near a pole?) o. Explain the process of an inspection for Routine Distribution Inspections and FTI for both QA and QC. Specifically discuss the required/other tasks an inspector performs when sent to a location. | PG&E’s Field Quality Control (FQC) is a distinct team within the Quality Management organization that performs active observations of vegetation management personnel to evaluate conformance with procedural requirements. The scope, results, and methodology are separate from VMQC/VMQA functions. a. Please see Section 1 of PG&E’s Active Observation Sampling, Data Collection, and Pass Rate Calculations provided as “WMP-Discovery2023-2025_DR_SPD_016-Q006Atch01CONF.pdf” for the requested information. b. Please see the table below for three examples of “critical attributes” evaluated by QA/QC inspectors for each Vegetation Program: Distribution Routine Distribution Second Patrol Transmission Vegetation Control 1. Does the VMI independently prescribe work to mitigate risk for green trees with significant defects that may impact the facilities in the event of failure and did not meet P1 or P2 criteria? 1. Did the VMI independently and appropriately prescribe work to address all instances of strain and abrasion encountered during the observation? 2. Does the VMI independently 1. Does VMI prescribe all necessary work to maintain PG&E’s Radial Clearance requirements prior to the next patrol cycle? 2. Does VMI prescribe all necessary work to prevent hazard tree fall-1. Were all qualifying poles where the VC tech was able to perform work appropriately and independently cleared to scope, including submission of observation report when necessary?Distribution Routine Distribution Second Patrol Transmission Vegetation Control 2. Does the VMI independently prescribe work to mitigate risk for all dead and dying trees that may impact the facilities in the event of failure, but did not meet P1 or P2 criteria? 3. Does the VMI independently prescribe work to maintain MDRs through the next routine cycle for all trees requiring pruning? prescribe work for all structurally unsound green limbs and dead palm fronds above the conductors with the potential to fail into the facilities before the next routine patrol but did not meet P1 or P2 criteria? 3. Does the VMI independently prescribe work to mitigate risk for all dead, dying, and declining trees, or dead portions of trees including dead overhangs that can contact the facilities in the event of failure, but did not meet P1 or P2 criteria? ins prior to the next patrol cycle? 3. If encountered in the field, were all HN-Immediate conditions properly handled? 2. Did the VC tech ensure that the partial/full 1255(c/d) designation was only applied to poles that qualified for an exemption? 3. Was VC Tech able to identify all non-exempt equipment types that were encountered over the course of the observation? c. Please see Section 1 of PG&E’s Active Observation Sampling, Data Collection, and Pass Rate Calculations provided as “WMP-Discovery2023-2025_DR_SPD_016-Q006Atch01CONF.pdf” for the requested information. d. Please see the table below for three examples of “conformance attributes” evaluated by QA/QC inspectors for each Vegetation Program. Distribution Routine Distribution Second Patrol Transmission Vegetation Control 1. Did the VMI independently prescribe using the appropriate priority codes? 2. Does the VMI independently utilize correct markings 1. Did the VMI independently prescribe work using the appropriate priority codes? 2. Did VMI attempt customer 1. Does the VMI independently utilize correct markings according to the vegetation management marking standard? 1. Did the VC tech complete all necessary pruning cuts to ANSI A300 standards? 2. Did VC tech attempt contact with all Distribution Routine Distribution Second Patrol Transmission Vegetation Control according to the vegetation management marking standard? 3. Does the VMI independently prescribe all necessary pruning to maintain EVM scope elements on the EVM transition to Routine segments? contact for all parcels where work was prescribed? 3. Did VMI issue “Missed Tree” tags for all trees or tree parts which were prescribed work for fall-in risk when the tree conditions requiring work were present and/or predictable during the most recent routine patrol (approximately 6 months prior)? 2. When prescribing tree work in HFTD, does VMI prescribe adequate clearance? 3. Does VMI prescribe all necessary work to maintain PG&E’s Overhang requirements prior to the next patrol cycle? customers prior to entering their property? 3. Does VC tech perform all work in accordance with applicable BMPs? e. The critical pass rate is the aggregate pass/fail rate of all critical attribute questions within a program checklist (survey). Conformance attributes are not considered in the critical pass rate. f. Please see the table below for the following QA/QC Standards related to vegetation management: Attachment Title Attachment Name Field Quality Control Business Document WMP-Discovery2023-2025_DR_SPD_016-Q006Atch02CONF.pdf Conducting Active Observations WMP-Discovery2023-2025_DR_SPD_016-Q006Atch03CONF.pdf QAVMP Focused Tree Inspection Standard Work Document WMP-Discovery2023-2025_DR_SPD_016-Q006Atch04.pdf Quality Assurance Vegetation Management Performance WMP-Discovery2023-2025_DR_SPD_016-Q006Atch05CONF.pdf Vegetation Management Quality Control (VMQC) for Routine VM Electric Distribution WMP-Discovery2023-2025_DR_SPD_016-Q006Atch06CONF.pdf g. Please see the table below for the following QA/QC surveys related to vegetation management: Attachment Title Attachment Name Focused Tree Inspection Questions WMP-Discovery2023-2025_DR_SPD_016-Q006Atch07.pdf QC Work Verification Guide WMP-Discovery2023-2025_DR_SPD_016-Q006Atch08.pdf Active Observation Surveys WMP-Discovery2023-2025_DR_SPD_016-Q006Atch09.xlsx Attachment Title Attachment Name QAP Quality Verification User Guide WMP-Discovery2023-2025_DR_SPD_016-Q006Atch10.pdf QAM VM FTI WMP-Discovery2023-2025_DR_SPD_016-Q006Atch11.pdf h. Not applicable for VMQA-P and VMQC. VMQA-P and VMQC doesn’t use ‘attributes’ to obtain Pass Rate. i. Location boundaries are pre-assigned to QA-P and are created initially By QC using the below criteria: Distribution: ‘The verifier must determine and define the sample location boundary to perform our QC WV survey by reading the data fields entered by the VMI in the sample location assigned from system of record.' See QC response for additional details on how Distribution locations are defined. Transmission: ‘The verifier must determine and define the sample location boundary to perform our WV survey by reading the data fields entered by the VMI in the sample location assigned from the VM Execution System of Record.' See QC response for additional details on how Transmission locations are defined QC VC defines ‘Location’ (VC Pole location) the area where the ‘subject pole’ is. VMQC: QC Distribution ‘Location’ is defined in “WMP-Discovery2023-2025_DR_SPD_016-Q006Atch06CONF.pdf” as follows: ‘The verifier must determine and define the sample location boundary to perform our QC WV survey by reading the data fields entered by the VMI in the sample location assigned from system of record. The verifier must enter comments to describe exactly what work area is considered the sample area to assess the surrounding vegetation. If inadequate comments are provided from the system of record sample location, the verifier can either establish the boundary they believe fits the situation or skip the review until further information can be obtained.’ QC Transmission ‘Location’ is defined in “WMP-Discovery2023-2025_DR_SPD_016-Q006Atch12CONF.pdf” as follows: ‘The verifier must determine and define the sample location boundary to perform our WV survey by reading the data fields entered by the VMI in the sample location assigned from the VM Execution System of Record. The verifier must enter comments to describe exactly what work area is considered the sample area to assess the surrounding vegetation. If inadequate comments are provided from the VM Execution System of Record sample location, the verifier can either establish the boundary they believe fits the situation or skip the review until further information can be obtained. ’QC VC defines ‘Location’ (VC Pole location) the area where the ‘subject pole’ is located. j. QA and QC would have different criteria as it applies VMQC and VMQA pass rates. QC & QA have aligned criteria for programs currently being reviewed by both QA-P & QC (Distribution, Transmission, Vegetation Control, and Focused Tree Inspection) k. The Pass Rate referenced in “WMP-Discovery2023_DR_CalAdvocates_015-Q018Atch01.docx” includes pass rate definitions and calculations for FQC. This pass rate definition does not apply to VMQC or VMQA. The pass rate denoted in footnote 224 is the pass rate for VMQC, which audits completed work locations with different attributes and pass rate criteria. Pass rate attributes are different for FQC and VMQC/VMQA, based on differences in the methodologies used to evaluate performance. Field Quality Control (FQC) is a distinct team within the Quality Management organization that performs active observations of vegetation management personnel to evaluate conformance with procedural requirements. The scope, results, and methodology are separate from VMQC/VMQA functions. l. Please see the following two attachments for the requested information “WMP-Discovery2023-2025_DR_SPD_016-Q006Atch13CONF.xlsx” for the most recent distribution routine findings and “WMP-Discovery2023-2025_DR_SPD_016-Q006Atch14CONF.xlsx” for the most recent VMQC findings. m. Please see the following attachment for the requested information: “WMP-Discovery2023-2025_DR_SPD_016-Q006Atch15CONF.xlsx” n. There are locations that have ‘No trees/brush listed by the VMI on the system of record’ and there are ‘No trees/brush failed by the QC WV’, this situation is reflected as ‘0 trees inspected, and 0 trees failed’ in the data. QC trees inspected are defined in the ‘Vegetation Management Quality Control (VMQC) for “WMP-Discovery2023-2025_DR_SPD_016-Q006Atch06CONF.pdf" as follows: Total trees inspected = the total number of trees AND brush listed by the VMI on the system of record sample location plus the number of trees AND brush that failed by QC WV but not listed by VMI. o. Please see the table below for documents outlining the process of an inspection for Routine Distribution Inspections and FTI for both QA and QC. Attachment Title Attachment Name Conducting Active Observations WMP-Discovery2023-2025_DR_SPD_016-Q006Atch03.pdf Vegetation Management Quality Control (VMQC) for Routine VM Electric Distribution WMP-Discovery2023-2025_DR_SPD_016-Q006Atch06.pdf Quality Control (QC) Vegetation Management Focused Tree Inspection (FTI) WMP-Discovery2023-2025_DR_SPD_016-Q006Atch16CONF.pdf | Henry Sweat | 2024-05-30 | 2024-06-04 | 2024-06-04 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_016.zip | 16 | N/A | 8.2.3.6 | Vegetation Management and Inspections | High-Risk Species | N/A
650 | CPUC - SPD (Safety Policy Division) | 016 | CPUC - SPD (Safety Policy Division)_016 | 7 | CPUC - SPD (Safety Policy Division)_016_Q7 | Mitigation Effectiveness a. Regarding use of the WBCA tool to incorporate cost effectiveness components, reliability considerations, and location-specific mitigation effectiveness calculations, as described in the 2025 WMP Update on page 51, list all mitigations which will employ location-specific mitigation effectiveness calculations when WBCA is adopted, with their WMP Initiative Activity name and Utility Initiative Tracking ID code. b. Provide the data used to create Table ACI-PG&E-23-05-3. i. SPD expects to see a CPZ-level breakdown of the risk and the expected mitigation effectiveness for each driver. ii. The data should include how the CPZ data is aggregated up to the level in the Table ACI-PG&E-23-05-3, and an explanation for how this occurs. iii. The data should also include how the risk for each driver is aggregated and an explanation for how this occurs. iv. Provide the data used to determine each mitigation effectiveness. c. PG&E stated the following: Another compounding factor is PG&E’s heavily forested service territory in the highest wildfire risk portions of High-Fire Threat District (HFTD). It is common for vegetation induced faults to bring down distribution wires in a way that they touch each other and create line-to-line or two-line-to-ground faults. These types of faults are not as likely in service territories that have more chapparal or low-lying brush vegetation because it is far less common for overhead strike potential to introduce multi-phase system fault conditions. Implementation of REFCL in areas with significant large tree habitats with high tree strike potential would not produce the same effectiveness as areas like California’s high desert. An accurate assessment of the effectiveness of REFCL systems requires consideration of the specific geographic risk factors for the circuits upon which this technology is installed. Provide data which substantiates this claim. Provide data which shows the prevalence of SLG, LL, LLG, LLL and LLLG faults on circuits in the HFTD. Provide data which shows the prevalence of SLG, LL, LLG, LLL LLLG faults for vegetation induced faults. Discuss how effective PG&E expects REFCL to be for each fault type and risk driver. | a. The WBCA will evaluate different mitigations and combinations of mitigations that will likely change as we introduce new mitigation technology onto our system and/or replace existing mitigation approaches with new ones. Additionally, mitigations may change as we receive additional guidance from Energy Safety. The current list of alternatives that PG&E can analyze with the WBCA are shown in Table 1 below. The WBCA analyzes location-specific information at the circuit segment level for alternatives 1 through 8. The WBCA does not analyze Alternative 9, REFCL, because it can only be analyzed at the substation level. The WBCA cannot conduct circuit segment level analysis of REFCL. The WMP Initiative Activity name and Tracking ID for the alternative mitigations are shown in Table 1 below. Table 1 – WBCA Mitigation Alternatives WMP Activity Name and Tracking IDs Alternative WMP Activity Name WMP Tracking ID Notes Alternative 1 - Baseline Represents the current state of the grid and is not a named WMP initiative. Alternative 2 - Underground Primary 10K Undergrounding GH-04 Alternative 3 - Underground All PG&E is evaluating its approach regarding the undergrounding of secondary and service lines. Underground All is not a named WMP initiative. Alternative 4 - Covered Conductor with EPSS and Downed Conductor Detection (DCD) System Hardening – Distribution Protective Equipment and Device Settings GH-01 GM-07 Alternative 5 - Bare Conductor Rebuild with EPSS and DCD Downed Conductor Detection Protective Equipment and Device Settings GM-06 GM-07 Alternative 6 – Line Removal with Remote Grid 10K Undergrounding GH-04 Line removal with remote grid is included in PG&E’s overall system hardening program. Alternative 7 - EPSS including DCD/Partial Voltage with Bare Conductor Protective Equipment and Device Settings GM-07 Bare conductor is not a named WMP initiative. Alternative 8 – EPSS, DCD and PSPS with Bare Conductor While we originally analyzed this alternative that was included in WMP ACI 23-05, it is not included in the Attachment 1 because inclusion of PSPS as part of long term mitigation planning it is not an alternative we are considering. Alternative 9 – REFCL REFCL is not a named WMP initiative. It was considered but not selected for this WMP period. (See PG&E 2023-2025 WMP R5, pp. 283-284). Additionally, because REFCL cannot be analyzed at the circuit segment level it is not included in Attachment 1. Alternative 10 – Covered Conductor System Hardening – Distribution GH-01 b. Please see “WMP-Discovery2023-2025_DR_SPD_016-Q007Atch01.xlsx.” i. The data used to create Table ACI-PG&E-23-05-3 does not use CPZ-level breakdown of the risk. Instead, Table ACI-PG&E-23-05-3 utilizes subject matter expertise review of the outage combinations, and subsequently, applies this against historical risk events in order to derive the effectiveness for the mitigation. See the following worksheets in the attachment with the associated data provided: • The worksheet titled ‘Outage_HFTD’ shows the risk event data. • The worksheet titled ‘Grid Hardening SME Input_v3’ shows the SME review of each outage combination and the mitigation solution’s potential effectiveness. • The worksheet titled ‘Mapping’ shows the conversion of SME defined effectiveness to percentage effectiveness (e.g. low = 20%). • The worksheet titled ‘Result’ shows the computed effectiveness across the historical outage dataset to arrive at the summarized values of Table ACI-PG&E-23-05-3. ii. Not applicable. As discussed in subpart b(i) above, the CPZ data is not aggregated up to the level in the Table ACI-PG&E-23-05-3. iii. Not applicable. The risk for each driver at the CPZ level was not aggregated to calculate the mitigation effectiveness for Table ACI-PG&E-23-05-3. iv. The data used to create Table ACI-PG&E-23-05-3 is shown in attachment “WMP-Discovery2023-2025_DR_SPD_016-Q007Atch01.xlsx.” c. The original response was not provided from a predefined dataset but rather based upon subject matter expertise. Please see “WMP-Discovery2023-2025_DR_SPD_016-Q007Atch02.xlsx,” which is a summary of EPSS outages from 2022 to present and which demonstrates that a high percentage of primary system faults for known vegetation causes involve multiple phases based upon captured relay target information. Table 2 below summarizes the information in this attachment. Events involving multiple phases would show a decreased effectiveness of REFCL on ignitions as REFCL is only effective for single line to ground faults. Various correlations can be observed showing an increased probability of multi-phase faults due to increasing HFTD tier as well as tree strike potential risk. Table 2. Vegetation Caused Faults on EPSS Circuits (2022 – Present) Fault Condition % of Events % Circuit primary overhead miles in Tier 2 % Circuit Primary Overhead Miles in Tier 3 % of Priority Tree Mitigation Multiphase Target 54.50% 52.39% 55.50% 57.26% Single Phase Target 43.67% 44.69% 42.47% 39.85% Fault Condition % of Events % Circuit primary overhead miles in Tier 2 % Circuit Primary Overhead Miles in Tier 3 % of Priority Tree Mitigation No Fault Target 1.83% 2.92% 2.03% 2.89% | Henry Sweat | 2024-05-30 | 2024-06-20 | 2024-06-20 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_016.zip | 2 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--05 – Updating Grid Hardening Decision Making | ACI 23-05 Updating Grid Hardening Decision Making
651 | CPUC - SPD (Safety Policy Division) | 016 | CPUC - SPD (Safety Policy Division)_016 | 8 | CPUC - SPD (Safety Policy Division)_016_Q8 | Provide additional information on the criteria for “Red Flag” Conditions – it appears that PG&E also refers to them as “dry wind” conditions [see page 10 of 2025 WMP Update and PG&E’s response to MGRA_Data Request No. 9_Q2]. a. Reconcile the terminology –are these synonyms? Explain why if not. b. Explain how this partition has impacted modeling in WDRM v4. c. Provide the percentage of WDRM v4 risk associated with these days. d. Provide the percentage of WDRM v3 risk associated with these days. e. Discuss how the risk Bow Tie differs in its use of these days compared to WDRM v4 and v3. f. Explain how this criteria compares to classification of weather in both FPI v4.0 and v5.0. Is it similar to R4 or R5 (or another level)? Why/why not? g. Explain how this criteria connects to weather that would result in PG&E’s use of a PSPS event. h. Explain how this criteria relates to PG&E’s enablement criteria for EPSS. i. Provide a list of all CPUC-reportable ignitions for each year from 2014 through April 30, 2024 that occurred during “Red Flag” conditions, Provide the data in the same format as the CPUC-Reportable Ignitions Template submitted yearly to the CPUC, with an additional column indicating if the ignition was in the (1) Tier 2, (2) Tier 3, (3) HFRA (exclusive of HFTD) and (4) non-HFTD/HFRA. j. Provide the number of circuit mile days on an annual basis that met the “Red Flag” conditions criteria starting in 1980 (or the first year PG&E’s 30-year meteorology data set) through April 30, 2024. k. Provide the predicted number of circuit mile days per year expected to meet the “Red Flag” conditions criteria based on PG&E’s modeling. l. In PG&E’s response to MGRA_Data Request No. 9_Q2, PG&E states that the additional explanatory power of dry wind is modest over the predictive destructive condition. Explain. i. Discuss if this is related to the predictive destructive condition already being predicated on an FPI threshold. | a. “Red Flag” conditions are not the same as “dry wind” conditions. Dry Wind Conditions (DWC) status was developed for the consequence modeling in response to both internal and external reviews of Wildfire Consequence (WFC) model v3.4 recommending the inclusion of Red Flag Warnings (RFW) issued by the National Weather Service (NWS). RFW warnings are issued by the NWS when there are weather conditions that would intensify fires. These RFW warnings are issued across a mixture of watershed areas, ridgelines, and jurisdictional boundaries such as county lines. The criteria for issuing a RFW warning is also not consistent across all these areas. The inconsistencies in RFW criteria causes problems when trying to fit it as a model covariate as the result may be a prediction based on RFW definition rather than the actual local conditions. To avoid the RFW inconsistency issue, the DWC was developed as an internal status covariate for use in the WFC model that could be used across the entire PG&E service territory. The DWC conditions criteria is listed in this table. Measurement Limit (daily average) Wind Speed >= 19 mph 10-hr Dry Fuel Moisture <= 6% Relative Humidity <= 30% b. Wildfires seem to occur in ‘regimes’ defined by the location, topography, near environment (natural and human), weather (short-term and cumulative), climate, et al. • The objective is to identify regimes, that are both discriminative of wildfire characteristics, and well enough populated to provide robust statistics. • With the addition of PGE-DryWind in v4, we have three factors whose combinations (of Boolean values) define 8 regimes: HFRA, Predicted-Destructive, and PGE-DryWind. The PGE-DryWind definition relies on wind-speed and relative humidity crossing thresholds which approximate Federal Red-flag conditions in PG&E service territory. While a very large component of this is already captured by the criteria defining 'Predicted Destructive' conditions via the FPI models, those models rely heavily on burnable fuel presence and characteristics in addition to weather. We find that there is merit in considering extreme conditions of wind and relative humidity in isolation, to identify areas and conditions conducive to wildfires even in sparse fuel conditions. c. In the WDRM v4 consequence, roughly 6.5% of the total wildfire consequence is associated with historical Dry Wind conditions. This approximation to consequence is obtained with the weighted sum over the 8 strata defined by the labels given in the table below. The weights are the fraction of days each pixel is in each of the 8 strata, and the summand is the mean MAVF of historical fires in each strata. WMP-Discovery2023-2025_DR_SPD_016-Q008 Page 3 The product of the MAVF and the Percent of Grid Pixel-Days approximates the relative importance of contributions of each stratum to the total consequence and hence risk. The percentage of strata with Dry Wind True is roughly 6.5%. Specifically, from the table below, (502x0.07 + 1.78x0.16 + 1.8x0.04 + 0.46x1.16) / (502x0.07 + 1.78x0.16 + 1.8x0.04 + 0.46x1.16 + 180x2.36 + 1.96x31.56 + 8.64x0.17 + 0.37x64.49) = 6.5%. HFRA Dry Wind Conditions Predicted Destructive MAVf Percent of Grid Pixel-Days True True True 502 0.07 True True False 1.78 0.16 True False True 180 2.36 True False False 1.96 31.56 False True True 1.80 0.04 False True False 0.46 1.16 False False True 8.64 0.17 False False False 0.37 64.49 d. For WDRM v3, we did not have the PGE Dry-Wind strata for historical fires. Therefore, the MAVF value takes only 4 values corresponding to the combination of HFRA X Predicted Destructive labels. e. The risk bow-tie uses red-flag warning days as they were historically called by weather forecasters using region specific criteria. As described in the response to subpart (a) above, the dry-wind condition is different but designed to retain the predictive power of RFW. f. The R1 to R5 conditions are an output of the FPI model which uses factors such as wind speed and fuel moisture as inputs. The “dry wind” conditions are a classification of wind speeds, fuel moisture, and humidity. While there is likely to be a significant overlap in areas with high R scores from the FPI model and areas that meet the “dry wind” conditions criteria, they are not directly correlated. g. PSPS decisions are driven by the R1-R5 conditions which are an output of the FPI model which uses factors such as wind speed and fuel moisture as inputs. The “dry wind” conditions are a classification of wind speeds, fuel moisture, and humidity. While there is likely to be a significant overlap in areas with high R scores from the FPI model and areas that meet the “dry wind” conditions criteria, “dry wind” conditions are not directly used as an input to PSPS decision making. h. Similar to PSPS, EPSS enablement criteria uses R scores from the FPI model which is similar to the DWC “dry winds” criteria as explained in subparts (f) and (g). i. Please see attachment “WMP-Discovery2023-2025_DR_SPD_016-Q008Atch01.csv” for the training fires used in fitting the Wildfire consequence model. They are VIIRS detected fires within the training season (June-November inclusive) with lightning fires removed from low-fire danger days (as non-representative). The predicted_destructive_flag, the pdw_flag (PG&E Dry wind) flags, and the rfw_flag (red flag warning) flags are present. j. Since the WFC model does not use RFW days as a direct input as described in response to subpart (a) for this question, an export showing “Red Flag” conditions over the requested period is not available. k. The WFC model is designed to quantify Wildfire Consequence. It is not designed to make predictions of future weather conditions which determine “Red Flag” conditions. l. Yes. The explanatory power of dry wind is modest. PGE-Dry Wind definition relies on wind-speed and relative humidity crossing thresholds which approximate Federal Red-flag conditions in PG&E service territory. While a very large component of this is already captured by the criteria defining 'Predicted Destructive' conditions via the FPI models, these models rely heavily on burnable fuel presence and characteristics in addition to weather. There is merit in considering extreme conditions of wind and relative humidity in isolation, to identify areas and conditions conducive to wildfires even in sparse fuel conditions even if the additional impact is small. | Henry Sweat | 2024-05-30 | 2024-06-12 | 2024-06-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_016.zip | 1 | N/A | 6 | 6.0 Risk Methodology and Assessment | 6.2.1 Risk and Risk Component Identification | 1. Signfiicant Updates to Risk Models (WDRM v4 & WTRM v2)
652 | CPUC - SPD (Safety Policy Division) | 016 | CPUC - SPD (Safety Policy Division)_016 | 9 | CPUC - SPD (Safety Policy Division)_016_Q9 | Answer the following with regards to QA/QC for system inspections. a. Provide the procedures for QA and QC for all System Inspections for transmission and distribution assets. b. Provide the procedures for detailed inspections (aerial and ground) of distribution and transmission assets. c. Describe what is in a Critical Pass Rate, and how that differs from other types of findings – for Distribution QA the “other” findings appear to be classified as “High,” “Medium,” and “Low” as seen in “WMP-Discovery2023-2025_DR_CalAdvocates_039-Q001Atch01.xlsx.” Provide examples. d. Explain when QC or QA would have different criteria for evaluation and discuss how this manifests in the pass rate. For instance, when would an inspection pass QA but not QC and vice versa. e. Explain why a CritAtt would not result in a new EC tag. Provide examples. See column P of “WMP-Discovery2023-2025_DR_CalAdvocates_039-Q001Atch01.xlsx” for reference. f. Define “STIP” in Column N of “WMP-Discovery2023-2025_DR_CalAdvocates_039-Q001Atch01.xlsx”. g. Explain why some findings identified during QA/QC inspections classified as “High” are considered “Critical Attributes” and others are not? i. Referencing ““WMP-Discovery2023-2025_DR_CalAdvocates_039-Q001Atch05.xlsx,” justify why the finding in Row 4 is not considered a Critical Attribute, whereas the finding in Row 148 is considered a Critical Attribute. Discuss why the finding in Row 4 is not a Critical Attribute considering (1) the two rows have the same identified description “Molding missing, broken, damaged, or loose,” (2) the risk rank and HFTD risk tier is the same (see Columns L through N), but (3) the finding in Row 4 is a Priority E whereas the finding in Row 148 is a Priority F, especially since (3) implies that Row 4 was more risky and thus a more critical miss. | a. Please see attachment “WMP-Discovery2023-2025_DR_SPD_016-Q009Atch01CONF.pdf” for PG&E’s Quality Assurance System Inspections Business Process Document and attachment “WMP-Discovery2023-2025_DR_SPD_016-Q009Atch02CONF.pdf” for PG&E’s procedure for System Inspections Quality Control. b. PG&E uses the guidance set forth in its Electric Distribution Preventative Maintenance (EDPM) Manual for detailed distribution inspections and the Electric Transmission Preventative Maintenance (ETPM) Manual for detailed transmission inspections. Please see attachment “WMP-Discovery2023-2025_DR_SPD_016-Q009Atch03CONF.pdf” for the EDPM and the following link for PG&E’s ETPM: https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/td-1001m-etpmm.pdf. Please see attachments “WMP-Discovery2023-2025_DR_SPD_016-Q009Atch04CONF.pdf” and “WMP-Discovery2023-2025_DR_SPD_016-Q009Atch05CONF.pdf” for aerial inspections. c. Critical Pass Rate is the number of unique SAP Equipment IDs with zero Critical Attribute Findings divided by total number of unique SAP Equipment IDs reviewed. Critical Attribute findings differ from “other” findings in that they are the highest priority condition, as defined by Asset Strategy. The “other” findings that are categorized as “High”, “Medium”, or “Low” risk are not used in calculating the Critical Pass Rate. See SAP Equipment ID 104088798 for an example of a Critical Attribute finding. See SAP Equipment ID 104138705 for an example of a “High” finding. See SAP Equipment ID 104060532 for an example of a “Low” finding. There were no “Medium” findings in document “WMP-Discovery2023-2025_DR_CalAdvocates_039-Q001Atch01.xlsx.” d. QC and QA utilize the same critical miss criteria that is set by Asset Strategy. Current QC and QA audits do not have a pass/fail acceptance criteria for completed inspections. QC and QA audits review inspection checklist attributes and pass/fail the attribute. e. All Critical Attribute findings as defined by Asset Strategy would result in either the creation of a new EC tag or the updating of an existing EC tag. Any Critical Attribute in column P that does not correspond to a Critical Attribute in column N (totalSTIP) is a data entry error that does not adversely affect the pass rate because the pass rate is calculated per column N. f. “STIP” in column N refers to the number of Critical Attribute findings for the corresponding SAP Equipment ID. g. The QA/QC discrepancy rankings include Critical, High, Medium, and Low. PG&E identified attributes/conditions in the system inspection checklist that posed the potential for wildfire risk if the condition existed in the field. Critical Attribute ranked findings are directly related to wildfire risk and represent the highest-level concerns. High, Medium, and Low findings represent non-wildfire risk concerns related to administrative errors, documentation issues, equipment reliability, public safety, etc. h. When referencing “WMP-Discovery2023-2025_DR_CalAdvocates_039- Q001Atch05.xlsx," it appears that Row 4 and Row 148 both identify the finding Description in column “H” as “Molding missing, broken, damaged, or loose,” additionally, both have the same assigned Risk Rank of “High” in column “L”. PG&E is unclear regarding the “Critical Attribute” Risk Rank that was cited in the original question and will require addition information to provide an appropriate response. | Henry Sweat | 2024-05-30 | 2024-06-04 | 2024-06-04 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_016.zip | 5 | N/A | 8 | Section 8.1.3 - Asset Inspection | 8.1.3 Asset Inspections | N/A
653 | CPUC - SPD (Safety Policy Division) | 016 | CPUC - SPD (Safety Policy Division)_016 | 10 | CPUC - SPD (Safety Policy Division)_016_Q10 | For each year from 2020 through 2023, and January 1, 2024, through April 30, 2024, and for each work order priority level: a. Provide a list and examples of all cause categories used when canceling work orders. b. Provide the number of cancelled work orders for each priority work under each cause category. c. Provide the number of cancelled work orders for each priority work order under each cause category that was cancelled after the due date. d. Provide the number of cancelled work orders for each priority work order under each cause category that was cancelled within ten days before the due date. e. Provide the number of cancelled work orders for each priority that were replaced by another work order under each cause category and the priority to which it was assigned. f. Provide the number of cancelled work orders for each priority which were cancelled because the work order was no longer considered necessary (for instance, PG&E has referenced the criteria for splices adjacent to insulators may have changed). ii. For this case, explain how PG&E is actively attempting to identify these work orders and streamline the process for assessing them. How many does PG&E anticipate remain in the backlog? | PG&E is responding to this request with respect to its overhead distribution tags. PG&E identified approximately 350 emergency tags that were cancelled over the requested time period. PG&E is still analyzing and gathering this information and tentatively plans to respond by Thursday, June 13, 2024. Please note that PG&E does not use cancellation codes in its System of Record when cancelling emergency tags, which are created and assigned with a Priority A or Priority X category. a) There are seven cancellation reason codes can be applied to cancelled Electric Corrective (EC) notifications that have been assigned with a Priority B, E, F, or H category. If a notification is cancelled and is missing a cancellation reason code, the notification review team reviews that notification and applies the correct cancellation code or reopens the notification if it was cancelled incorrectly. PG&E does not include cancellations without a cancellation reason code against WMP tag commitments. A list of the cancellation codes is below: 1. “Dummy” For Order Only: EC is a “dummy” notification created to generate an order ONLY. 2. All Found Completed/Resolved on Arrival: All work found completed/resolved upon arrival in the field. 3. Completed Under Another Program: Work belongs to/is being completed under another program (COE, Reliability, WRO, System Hardening etc.); 4. Converted to Another Notif-Type: EC is being converted to another notification-type; example: EC converted to IF (Idle Facility) notification). 5. Created in Error (Desk Cancelation): Notification was created in error (desk cancelation); example: EC was created for work that is not required in the GO 165 Program in error, such as to install bolt covers. 6. Duplicate EC for Same Location: Duplicate EC exists for the same location; the duplicate notification will be referenced in the notification’s long text when canceling for this reason. 7. No Compelling/Regulator Condition Exist: No compelling or regulatory condition exists, i.e. standards change. b) Please see the data table below. Count of notification Column Labels Row Labels B E F H Grand Total 2020 86 2553 82 2721 "Dummy" for order only 1 1 All Found Completed/Resolved on Arrival 38 308 6 352 Completed under another Program 1 43 1 45 Converted to another Notif-Type 1 29 30 Created in Error (Desk Cancelation) 13 13 Duplicate EC for Same Location 22 2055 74 2151 No Compelling/Regulator Condition Exist 24 101 1 126 (blank) 3 3 2021 1 679 1864 185 2729 All Found Completed/Resolved on Arrival 319 1047 117 1483 Completed under another Program 25 76 5 106 Converted to another Notif-Type 17 13 30 Created in Error (Desk Cancelation) 8 18 26 Duplicate EC for Same Location 1 66 440 33 540 No Compelling/Regulator Condition Exist 239 260 29 528 WMP-Discovery2023-2025_DR_SPD_016-Q010 Page 3 Count of notification Column Labels Row Labels B E F H Grand Total (blank) 5 10 1 16 2022 2395 10223 5147 258 18023 "Dummy" for order only 1 10 1 12 All Found Completed/Resolved on Arrival 458 4012 2506 95 7071 Completed under another Program 281 877 310 59 1527 Converted to another Notif-Type 53 178 80 1 312 Created in Error (Desk Cancelation) 392 171 69 3 635 Duplicate EC for Same Location 412 3154 1475 68 5109 No Compelling/Regulator Condition Exist 214 1550 673 32 2469 (blank) 584 271 33 888 2023 1681 17147 7522 997 27347 "Dummy" for order only 19 2 21 All Found Completed/Resolved on Arrival 608 7194 4508 360 12670 Completed under another Program 306 2257 721 100 3384 Converted to another Notif-Type 47 91 26 1 165 Created in Error (Desk Cancelation) 104 295 64 463 Duplicate EC for Same Location 343 3796 1163 505 5807 No Compelling/Regulator Condition Exist 238 2617 964 30 3849 (blank) 35 878 74 1 988 2024 500 4343 1075 103 6021 "Dummy" for order only 1 1 1 3 All Found Completed/Resolved on Arrival 141 517 278 3 939 Completed under another Program 120 797 211 34 1162 Converted to another Notif-Type 13 46 17 76 Created in Error (Desk Cancelation) 29 58 23 110 Duplicate EC for Same Location 111 819 301 10 1241 No Compelling/Regulator Condition Exist 76 2088 240 56 2460 (blank) 9 17 4 30 Grand Total 4577 32478 18161 1625 56841 c) Please see the data table below. Please note, there is no data available for the years 2020-2022. Count of notification Column Labels Row Labels B E F H Grand Total 2022 505 7087 2610 223 10425 "Dummy" for order only 2 2 All Found Completed/Resolved on Arrival 185 3300 1580 76 5141 Completed under another Program 102 671 100 54 927 Converted to another Notif-Type 7 118 39 1 165 Created in Error (Desk Cancelation) 38 72 15 2 127 Count of notification Column Labels Row Labels B E F H Grand Total Duplicate EC for Same Location 87 1658 585 61 2391 No Compelling/Regulator Condition Exist 65 1244 283 29 1621 (blank) 21 22 8 51 2023 608 13449 2967 824 17848 "Dummy" for order only 5 5 All Found Completed/Resolved on Arrival 252 6569 2062 299 9182 Completed under another Program 120 1661 219 90 2090 Converted to another Notif-Type 13 66 13 1 93 Created in Error (Desk Cancelation) 28 98 8 134 Duplicate EC for Same Location 114 2793 378 412 3697 No Compelling/Regulator Condition Exist 61 2235 282 21 2599 (blank) 20 22 5 1 48 2024 317 3531 260 79 4187 All Found Completed/Resolved on Arrival 102 425 66 3 596 Completed under another Program 82 608 78 14 782 Converted to another Notif-Type 10 38 1 49 Created in Error (Desk Cancelation) 14 38 7 59 Duplicate EC for Same Location 55 652 70 6 783 No Compelling/Regulator Condition Exist 49 1763 36 56 1904 (blank) 5 7 2 14 Grand Total 1430 24067 5837 1126 32460 d) Please see the data table below. Please note, there is no data available for the years 2020-2022. Count of notification Column Labels Row Labels B E F H Grand Total 2022 181 105 40 3 329 All Found Completed/Resolved on Arrival 39 40 10 89 Completed under another Program 14 7 3 1 25 Converted to another Notif-Type 7 3 10 Created in Error (Desk Cancelation) 59 1 60 Duplicate EC for Same Location 30 45 25 2 102 No Compelling/Regulator Condition Exist 27 9 2 38 (blank) 5 5 2023 134 124 23 281 All Found Completed/Resolved on Arrival 56 39 11 106 Completed under another Program 17 20 2 39 Converted to another Notif-Type 4 4 Created in Error (Desk Cancelation) 9 2 11 Duplicate EC for Same Location 24 36 7 67 Count of notification Column Labels Row Labels B E F H Grand Total No Compelling/Regulator Condition Exist 20 20 1 41 (blank) 4 7 2 13 2024 15 21 3 39 All Found Completed/Resolved on Arrival 5 3 1 9 Completed under another Program 3 4 1 8 Converted to another Notif-Type 1 1 Created in Error (Desk Cancelation) 1 1 Duplicate EC for Same Location 2 4 6 No Compelling/Regulator Condition Exist 5 8 1 14 Grand Total 330 250 66 3 649 e) Please see the data table below. Count of notification Column Labels Row Labels B E F H Grand Total 2020 1 43 1 45 Completed under another Program 1 43 1 45 2021 25 76 5 106 Completed under another Program 25 76 5 106 2022 281 877 310 59 1527 Completed under another Program 281 877 310 59 1527 2023 306 2257 721 100 3384 Completed under another Program 306 2257 721 100 3384 2024 120 797 211 34 1162 Completed under another Program 120 797 211 34 1162 Grand Total 707 3957 1361 199 6224 f) Please see the data table below. Count of notification Column Labels Row Labels B E F H Grand Total 2020 24 101 1 126 No Compelling/Regulator Condition Exist 24 101 1 126 2021 239 260 29 528 No Compelling/Regulator Condition Exist 239 260 29 528 2022 214 1550 673 32 2469 No Compelling/Regulator Condition Exist 214 1550 673 32 2469 2023 238 2617 964 30 3849 No Compelling/Regulator Condition Exist 238 2617 964 30 3849 2024 76 2088 240 56 2460 No Compelling/Regulator Condition Exist 76 2088 240 56 2460 Count of notification Column Labels Row Labels B E F H Grand Total Grand Total 528 6518 2238 148 9432 iIt is difficult to determine how many work orders in the backlog are no longer necessary until the EC tags are validated. To identify and address these work orders, PG&E utilizes the Procedure, “Open Electric Corrective (EC) Tag Validation Procedure, TD-8123P-200” which provides a process for validating an open EC tag and assess whether the condition on the tag has worsened. Please see “WMP-Discovery2023-2025_DR_SPD_016-Q010Atch01CONF.pdf” for a copy of this procedure. Open tag validations occur during ground and aerial inspections cycles in both HFTD and Non-HFTD, as well as Field Safety Re-Assessments (FSR) and Comprehensive Pole Inspections (CPI) for the risk prioritized work plan locations which ensure that PG&E is working on necessary EC notifications. | Henry Sweat | 2024-05-30 | 2024-06-10 | 2024-06-10 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_016.zip | 1 | N/A | 8 | Section 8.1.7 - Open Work Orders | 8.1.7.2 Open Work Orders - Distribution Tags | N/A
653 | CPUC - SPD (Safety Policy Division) | 016 | CPUC - SPD (Safety Policy Division)_016 | 10(s) | CPUC - SPD (Safety Policy Division)_016_Q10(s) | bs652ehg3yewiquAGSEW36Tqg`2 | As a supplement to our initial response of June 10, 2024, please see the response below which provides the requested information for Priority A and X overhead distribution tags. This information was not included in the initial response as we needed additional time to gather and quality control the data. a. Please see the table below. WMP-Discovery2023-2025_DR_SPD_016-Q010Supp01 Page 2 Cancellation Code Example Conv The EC notification is being converted to another notification type. The replacement notification will be referenced in the notification’s long text when cancelling for this reason. For example: an EC notification is converted to an IF notification. No photo is required. DUMM The EC notification is a “dummy” notification created to generate an order ONLY. No work is required in the field. No photo is required. DUPL A duplicate EC notification exists for the same location. The duplicate notification will be referenced in the notification’s long text when cancelling for this reason. No photo is required. EROR The notification was created in error (desk cancellation). For example: an EC notification was not intended to be created or multiple EC notifications generated due to communication errors. No photo is required. NOCR No compelling or regulatory condition exists. A minimum of two photos are required for this cancelation reason. PG&E will return to field if photos are not provided. PROG This work belongs to/is being completed under another program (COE, Reliability, WRO, etc.). No photo is required. b. Please see the table below for the requested information for Priority A tags. Count of Notification No Column Labels CONV DUPL EROR NCOA NOCR PROG Grand Total 2020 14 54 17 4 2 11 102 2021 20 55 59 9 12 19 174 2022 13 67 123 11 16 13 243 2023 25 48 80 30 17 11 211 2024 3 3 8 1 15 Grand Total 75 227 287 54 47 55 745 Please see the table below for the requested information for Priority X tags. Please note, PG&E only started implementing Priority X tags in 2024. Count of Notification No Column Labels CONV EROR PROG Grand Total 2024 4 6 1 11 Grand Total 4 6 1 11 c. PG&E s unable to provide this information. For Priority A notifications, the “Required End Date” is system generated, which uses a default entry of 1-30 days after the notification is created. Priority A notifications are created for emergency work or an unsafe condition requiring immediate response and standby to protect the public. We meet the requirements of GO 95, Rule 18, for Level 1 Safety Hazards by acting immediately to address the condition. The results of the immediate action are captured in the creation of an emergency notification (nature of the work, the date the work was performed, and the identity of the persons performing the work). As such, the ‘Required End Date’ field in SAP for these Emergency notifications does not reflect an accurate deadline and is not applicable for Priority-A EC notifications. For Priority X notifications, the required end date is used as due date. X Tags PROG Grand Total Canceled after required end date 1 1 d. For Priority A notifications, please see the response to subpart (c) above which explains how we handle Priority A notifications. For Priority X notifications, please see the table below. X Tags CONV EROR Grand Total Canceled before required end date 4 6 10 e. Please see the tables below for the requested information. Please note, if a notification is changed to a new priority, the replacement notification will be referenced in the long text, however, the new priority for that notification is not required to be included. Original Priority Count replaced New Priority A 39 B A 9 E A 1 F A 1 X A 25 Unknown – new priority was not identified in long text. Original Priority Count replaced New Priority X 2 B X 1 Cancelled X 1 Unknown – new priority was not identified in long text. f. Please see code "NOCR" in the tables provided in subpart (b) above for work that was cancelled because the work was no longer deemed. i. Please see PG&E’s initial response to subpart (i) of this data request, provided to the requesting party on June 10, 2024. | Henry Sweat | 2024-05-30 | 2024-06-13 | 2024-06-13 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_016.zip | 0 | N/A | 8 | Section 8.1.7 - Open Work Orders | 8.1.7.2 Open Work Orders - Distribution Tags | N/A
654 | CPUC - SPD (Safety Policy Division) | 016 | CPUC - SPD (Safety Policy Division)_016 | 11 | CPUC - SPD (Safety Policy Division)_016_Q11 | Discuss how work orders are bundled. a. When an area is selected for bundling, explain whether all or only a partial list of work orders is addressed in a bundling project. iii. How would the remaining work orders not addressed by the bundled project be addressed? b. Are there different types of bundling projects? a. How does the project type affect the bundling? c. How are work orders near their correction deadline handled when bundled? a. Are these work orders (especially Priority A, B and X work orders) allowed to exceed their due date if they are part of a bundling project in process which has a later overall due date? b. Would such individual work orders be recorded as being completed on time? d. Are new work orders created for bundling projects, or are the existing work orders used? e. How would a situation be addressed where a contractor hired to do a bundling project finds multiple work orders already completed due to past work, such as emergency storm work, but were erroneously included in the bid? iv. Would PG&E still pay for the work, or would the contractor refund payment, or be would the contractor not charge for the work orders erroneously included in the bid? | a. PG&E is prioritizing bundling pole and non-pole priority E and F overhead HFTD/HFRA EC notifications when bundling an area, as well as when possible with other notification types. If an area consists of both HFTD and non-HFTD notifications, the non-HFTD notifications may not be addressed within the bundling project. In addition, a bundled notification may not be executed with the bundle if there are external constraints, for instance customer access or permitting requirements that are unique to only a small portion of the bundle some of the notifications maybe removed from the bundle to allow execution of the rest of the notifications. i. The remaining notifications will be addressed during the annual work planning cycle. b. There are two main types of planned bundling projects when it comes to bundling pole and non-pole priority E and F overhead HFTD/HFRA EC notifications. The first type consists of single isolation zone bundles and the second type consists of multiple isolation zones bundled by circuit. i. The main differences between these two types of bundling projects consist of the following: 1. Circuit level bundles are usually much larger consisting of over 100 notifications and take multiple weeks to execute while isolation zone bundles are smaller and are executed in one to a few days typically. 2. Circuit-level bundles are project managed while single isolation zone bundles are managed within the divisions and individual work centers. 3. The majority of the circuit-level bundles are resourced by contract partners while single isolation zone bundles are resourced through the normal work and resource planning process. 4. Circuit level bundles are forecasted to be more efficient to execute as PG&E can bundle more activities increasing throughput with the same amount of resources. c. Bundles are developed through PG&E’s annual planning process and are prioritized based on risk reduction and executability with an emphasis on bundling pole and non-pole priority E and F overhead HFTD/HFRA EC notifications. With the current HFTD maintenance tag backlog, bundling and working tags by isolation zone instead of working newly created tags to meet current GO95 time requirements, described as Steady State previously, will allow us to accelerate our program to be in compliance in HFTD by 2029. Bundling by isolation zone provides us the flexibility to address the most risk first through a risk spend efficiency (RSE) approach. i. Priority A and X EC notifications are strictly out of scope for these types of bundling projects due to the risk they pose on the public and our system. Priority B EC notifications are typically excluded from bundling projects as they are emergent, however, if work is able to be bundled at the operational level by crews executing a priority B EC notification, then they are encouraged to do so. ii. We do not change the required end date (compliance to GO95 Rule 18 timeline) when bundling EC notifications and bundles are not given a separate compliance date. If an EC notification is completed past its due date it will continue to be recorded as being completed late no matter if it is in a bundle or not. d. Currently, the existing work orders are used for bundling projects. e. The contractor would notify the contract manager to modify the work authorization in the bid to remove the work already completed and adjust the overall value of those projects. i. Each vendor has agreed on pricing in their contractors for COA (Completed on Arrival) projects. ii. PG&E is also looking for ways to minimize this scenario, for instance on circuit bundles we performed aerial inspections on all assets months before construction to verify the current status of the assets to increase the quality of our work plan and contractor bids. | Henry Sweat | 2024-05-30 | 2024-06-04 | 2024-06-04 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_016.zip | 0 | N/A | 8 | Section 8.1.7 - Open Work Orders | 8.1.7.2 Open Work Orders - Distribution Tags | N/A
655 | CPUC - SPD (Safety Policy Division) | 016 | CPUC - SPD (Safety Policy Division)_016 | 12 | CPUC - SPD (Safety Policy Division)_016_Q12 | What is PG&E’s False Start rate for addressing work orders? a. What factors are the most common for a false start? | PG&E is completing this response per clarification from the Safety Policy Division that “false start” are situations when job crews arrive at a job site and are unable to complete the job as scheduled. For Planned Electric Distribution Maintenance work, Major Work Categories 07, 2A, and KA, PG&E’s schedule adherence rate for January 2024 to June 04, 2024, is 68%. 22,997 units were completed, and 10,875 units were not completed. Of the 10,875 units not completed, 1,075 units (10%) is the rate of the units that would be considered not completed due to false start. a. From this year’s data, the most common factors for a false start are: i. Additional time required (unforeseen field conditions) (2.5%) ii. Clearance not set (1.1%) iii. Field conditions changed (4.8%) iv. Miscalculated hours of effort (0.2%) v. No USA (0.1%) vi. Field decision not to work (0.9%) vii. Contractor field decision not to work (0.5%) Overall, the three highest factors for not meeting schedule adherence are Emergency, Inclement Weather, and Rest Period. These factors for not completing against schedule are typically determined prior to a crew arriving at a job site and not being able to complete the work as scheduled. | Henry Sweat | 2024-05-30 | 2024-06-10 | 2024-06-10 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_016.zip | 0 | N/A | 8 | Section 8.1.7 - Open Work Orders | 8.1.7.2 Open Work Orders - Distribution Tags | N/A
656 | CPUC - SPD (Safety Policy Division) | 016 | CPUC - SPD (Safety Policy Division)_016 | 13 | CPUC - SPD (Safety Policy Division)_016_Q13 | The following questions reference information from the provided in response the previous Data Request CPUC – SPD (Safety Policy Division)_004. a. Provide an updated version of “WMP-Discovery2023_DR_SPD_004-Q001Atch01.xlsx” that includes the data from 2023 and any adjustments since the previous submission made to ignition data in previous years by PG&E. b. “WMP-Discovery2023_DR_SPD_004-Q001Atch01.xlsx” indicates 49 CPUC-reportable ignitions occurred during R3, R4, or R5 (R3+) conditions in 2022. The spreadsheet also states in 2022 that there were 3,479,209 Overhead Circuit Mile Days (CMDs) in R3, R4 or R5 conditions. Dividing 49 ignitions by 3,479,209 CMDs * 100,000 returns an ignition rate of 1.41 ignitions per 100k CMD in R3+ conditions. The ISM submitted a separate graph which indicates the ignition rate was 1.03 which SPD understands was produced by PG&E (see Figure 3 on page 6 of the Q1 2024 ISM report, available at: PG&E Independent Safety Monitor Report (ca.gov)). The two ignition rates differ (the rate also appears to differ from other ignition rates computed in the following table) but appear to have similar units and presumably the same methodology and same data. i. Explain the discrepancy, and if there was a different methodology or data source. ii. Discuss the differences and the advantages of one methodology or data source over the other. Data supplied to SPD in CPUC-SPD (Safety Policy Division)_004 FPI Ignition Rate R3 R4 R5 R5+ Total (R3+) 2022 Ignitions Total 26 21 2 0 49 1.41 Ignitions in HFTD/HFRA 21 17 2 0 40 1.15 Ignitions in HFTD/HFRA Distribution 20 15 2 37 1.06 CMDs 2015280 1351493 112436 0 3479209 | a. Please see “WMP-Discovery2023-2025_DR_SPD_016-Q013Atch01CONF.xlsx” which includes the requested data from 2023 and any adjustments since the previous submission made to ignition data in previous years by PG&E. b. i. Per the Independent Safety Monitor’s Status Update Report, published on March 29, 2024, the graph in figure 3 represents the count of R3+ CPUC reportable ignitions in HFTD and/or HFRA normalized by the cumulative R3+ circuit mile days for that same period. There are ignitions included on WMP-Discovery2023_DR_SPD_004-Q001Atch01.xlsx that had an FPI rating of R3 or above but are not in HFTD nor HFRA and would have been excluded from the analysis conducted by the ISM. PG&E’s internal methodology for calculating the results of this metric from 2022 yield 0.95 R3+ ignitions per circuit mile day. This differs slightly from the ISM’s analysis where the cumulative circuit mile day total used as the denominator represented the total number of circuit miles in R3+ conditions calculated at the Fire Index Area (FIA) level; PG&E’s internal methodology uses the cumulative circuit mileage associated with an FPI value calculated for each unique circuit, a more granular approach. The circuit-specific circuit mileage data was unavailable at the time of the ISM’s analysis. ii. PG&E’s internal approach of calculating the ignitions and cumulative circuit miles associated with the FPI calculated for each independent circuit is more granular and a better representation of the risk actualized (in terms of high FPI ignitions in risky places) versus the exposure for that risk in that period. In addition, the circuit level values better align with our operational mitigations (for example: when we would enable EPSS protection). | Henry Sweat | 2024-05-30 | 2024-06-04 | 2024-06-04 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_016.zip | 0 | N/A | Appendix D | Appendix D - Areas for Continued Improvement | ACI PG&E-22-06 – Addressing Increase in Risk Events | N/A
657 | CPUC - SPD (Safety Policy Division) | 016 | CPUC - SPD (Safety Policy Division)_016 | 14 | CPUC - SPD (Safety Policy Division)_016_Q14 | SPD understands PG&E recently attended the 2024 Annual Conference ¦ International Wildfire Risk Mitigation Consortium (umsgroup.com). Provide all presentations from that conference and provide the Conference program/schedule. | The International Wildfire Risk Mitigation Consortium 2024 Annual Conference agenda is provided here: https://iwrmcannualconference.umsgroup.com/iwrmc-2024-annual-conference-agenda/ . Please see table below for presentations made by PG&E employees and which are attached to this response. Agenda Item Title Attachment Name Leveraging LiDAR to Identify & Mitigate Risk Associated with Low Hanging Communication Lines WMP-Discovery2023-2025_DR_SPD_016-Q014Atch01CONF.pdf Panel Discussion & Roundtable Q&A: PSPS Execution WMP-Discovery2023-2025_DR_SPD_016-Q014Atch02CONF.pdf PG&E Wildfire Risk Models - Overview & Incorporation of Egress, Suppression, and Internal Resources WMP-Discovery2023-2025_DR_SPD_016-Q014Atch03CONF.pdf Reducing Customer Vulnerability WMP-Discovery2023-2025_DR_SPD_016-Q014Atch04CONF.pdf Measuring Risk & Mitigation Effectiveness WMP-Discovery2023-2025_DR_SPD_016-Q014Atch05CONF.pdf PG&E's 2024 Vegetation Management WMP-Discovery2023-2025_DR_SPD_016-Q014Atch06CONF.pdf | Henry Sweat | 2024-05-30 | 2024-06-04 | 2024-06-04 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_016.zip | 6 | N/A | Appendix D | Appendix D - Areas for Continued Improvement | ACI PG&E-22-06 – Addressing Increase in Risk Events | N/A
657 | CPUC - SPD (Safety Policy Division) | 016 | CPUC - SPD (Safety Policy Division)_016 | 14(s) | CPUC - SPD (Safety Policy Division)_016_Q14(s) | SPD understands PG&E recently attended the 2024 Annual Conference ¦ International Wildfire Risk Mitigation Consortium (umsgroup.com). Provide all presentations from that conference and provide the Conference program/schedule. | In addition to the presentations provided to the Safety Policy Division on June 4, 2022, please also see “WMP-Discovery2023-2025_DR_SPD_016-Q014Supp01Atch01.pdf” for the conference schedule. PG&E also reached out to the International Wildfire Risk Mitigation Consortium (IWRMC) to obtain copies of additional presentations to satisfy this request. The IRWMC offered the opportunity to meet to discuss its mission and the presentations shared during the Consortium. Please contact us at electricdatarequests@pge.com, if you wish for PG&E to facilitate scheduling this discussion. Please see below for a copy of the communication from IWRMC: Dear SPD, Here is a copy of the IWRMC Adelaide Conference agenda that we can share with you. Unfortunately, the presentations made during the conference are all proprietary to the individual companies that presented them. We are precluded by NDA from releasing them to any non-member entity. E Source and our partner firms are deeply committed and proud to be associated with the International Wildfire Risk Mitigation Consortium (IWRMC). Over the past 4 years, we have been bringing the best utility companies, consultancies, engineering firms and technology vendors, as well as key external stakeholders such as Universities, Emergency response, Land Management, Forestry and other agencies, together to address the existential threat of wildfire and broader climate change. The mission of the program is to accelerate learning and sharing of best practices among industry participants, to gather and share research, ideas, strategies and experiences from around the world, and to focus the efforts and initiatives of program members on those areas and challenges that offer the greatest leverage in effectively and economically reducing wildfire risk. We believe that Regulators and sound regulation are critically important to enabling the industry to successfully navigate this complex set of challenges. We would be pleased to share more information about the program with SPD if and when that would be of interest to you. Please let us know and we can set up a call to discuss your interests and how we might be most helpful. | Henry Sweat | 2024-05-30 | 2024-06-07 | 2024-06-07 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_016.zip | 1 | N/A | Appendix D | Appendix D - Areas for Continued Improvement | ACI PG&E-22-06 – Addressing Increase in Risk Events | N/A
658 | CPUC - SPD (Safety Policy Division) | 016 | CPUC - SPD (Safety Policy Division)_016 | 15 | CPUC - SPD (Safety Policy Division)_016_Q15 | These questions are based off the Pole Loading Assessment work described in Section 8.1.3.2.4 of “TN13804_20240402T112956_PGE's_20232025_Wildfire_Mitigation_Plan_Revision_5.pdf” a. Provide summary statistics for the pole calculations already performed including: i. Number of pole calculations performed in the HFTD ii. Number of pole calculations remaining in the HFTD iii. Number of poles where the calculated safety factor was less than the safety factor specified by GO-95, Rule 44.1, Table 4 in the HFTD iv. Number of poles where the calculated safety factor was less than the safety factor specified by GO-95, Rule 44.3 in the HFTD v. Number of poles where the calculated safety factor was less than the safety factor specified by GO-95, Rule 44.1, Table 4 in the HFTD despite no strength deterioration being incorporated into the calculation. vi. Number of poles where the calculated safety factor was less than the safety factor specified by GO-95, Rule 44.3 in the HFTD despite no strength deterioration being incorporated into the calculation. vii. Provide the same information for poles not located in the HFTD. b. Provide an updated completion date for the program for both HFTD and non-HFTD areas. c. When the calculated safety factor is less than the safety factor specified by GO-95, Rule 44.1, Table 4 or GO-95, Rule 44.3, discuss typical root causes. d. Describe how this information related to the pole loading assessment is profiled to inspectors performing inspections. e. Provide the loading criteria used for the pole loading assessments. f. Describe how the pole loading assessments incorporate the intrusive inspection data from the Pole Test and Treat program, and how the Pole Test and Treat program will incorporate the pole loading data when performing inspections. g. Describe how the pole loading assessments incorporate observations from system inspections, such as leaning or damaged poles. h. Describe PG&E’s actions when the calculated safety factor for a pole is less than the safety factor specified by GO-95, Rule 44.1, Table 4 and separately when the calculated safety factor for a pole is less than the safety factor specified by GO-95, Rule 44.3. i. Discuss calculations performed on crossarms and conductors, and provide similar data as requested in part (a). j. Provide “WMP-Discovery2023_DR_CalAdvocates_032-Q008Atch01CONF.zip.” If one of these poles calculations does not include a pole calculation with a down guy, provide a randomly chosen pole calculation with a down guy. k. Explain how the tensions from both vertical and horizontal loads in the conductors are calculated, especially when adjacent spans are not the same length, do not have the same sag, or are not at the same elevation. l. Discuss which measurements used in the pole loading assessments are provided by LIDAR, and what other sources of measurements are used in the assessments. i. What is the accuracy of the LIDAR being used? ii. What is the max range of the LIDAR? iii. What does PG&E use for measurements for assessments where LIDAR cannot obtain suitable measurements? m. Describe any calculations performed related to deflections, pole foundations, clearances between conductors, and aeolian vibrations. | a. The Pole Loading Assessment (PLA) Program began in 2020 and conducted a desktop-based assessment of the pole loading by utilizing the pole attributes from EDGIS and LiDAR data. The PLA Program is above and beyond the requirements in GO 95, Rule 44, because no work is occurring at the poles as part of the PLA Program, so no new installation or reconstruction requires Pole Loading Calculations (PLCs). PG&E is performing proactive pole loading assessments to risk-prioritize maintenance and remediation of in-service poles. The PLA desktop-based assessments are performed by a team of data analysts. These assessments highlighted higher risk poles that need further engineering analysis. The higher risk poles are currently being prioritized for a comprehensive engineering analysis (which includes field validation, where needed). Once this analysis is completed, we will have the Safety Factor (SF) for the poles. i. The PLA Program completed desktop-based assessments on approximately 530,000 poles in HFTD areas. The pole loading for the remaining poles in HFTD areas has been assessed through other programs, such as system hardening. ii. No poles are remaining in HFTD areas for the PLA Program. iii. PG&E is currently prioritizing the higher risk poles for a comprehensive engineering analysis (which includes field validation, where needed). thus, the requested SFs are not yet available but will be available after this analysis is complete. iv. Please see the response to subpart a(iii) above which explains our process and why the requested information is not yet available. v. Please see the response to subpart a(iii) above which explains our process and why the requested information is not yet available. vi. Please see the response to subpart a(iii) above which explains our process and why the requested information is not yet available. vii. PG&E has not started assessing poles in non-HFTD areas. b. Please see the response to subpart (a) above for the status of poles in HFTD areas. As stated in subpart a(vii), PG&E has not yet started assessing poles in non-HFTD areas. c. Please see the response to subpart (a) above for an explanation of the status of this work. PG&E is in the beginning stages of understanding the causes and influences of overload conditions through the comprehensive engineering analysis of higher risk poles. d. Once the comprehensive engineering analysis is complete, the pole will either be determined to be overloaded or not overloaded. If the pole is determined to be overloaded and in need of remediation, an Electric Corrective (EC) notification will be created to perform the remediation activities through the maintenance program. Inspectors have visibility of the open EC notifications for the inspection locations. e. Please see the response to subpart a(iii) above. PG&E is in the beginning stages of performing comprehensive engineering analysis of the higher risk poles. f. The pole loading assessments incorporate the remaining strength captured during the most recent intrusive inspection. g. Minor physical damage on the pole does not significantly impact the pole loading. In addition, pole leaning is typically indicative of a pole foundation issue or improper guying. As such, these types of conditions are entered directly into the maintenance program for remediation via an EC notification. h. Please see the response to subpart a(iii) above. PG&E is in the beginning stages of performing comprehensive engineering analysis of the higher risk poles. i. PG&E does not perform such calculations as part of the PLA Program. j. Please see attachment “WMP-Discovery2023_DR_CalAdvocates_032-Q008Atch01CONF.zip” for the requested information. Multiple poles included in this zip file have down guys. k. O-Calc Pro considers both vertical and horizontal loading of all components modeled on the pole, which includes conductors, framing equipment, OH equipment, etc. In addition, the span lengths, angles, height of attachments and elevations are calculated leveraging EDGIS positions, which are derived from the LiDAR data. Further, O-Calc Pro’s conductor tensions are configured based on PG&E’s Standards, which are based on new installations and do not account for relaxation while in-service. l. The position of the pole is derived from EDGIS, which is based on LiDAR data. As discussed in subpart k, the span lengths, angles, heights of attachments and elevations are calculated leveraging EDGIS position, which are derived from the LiDAR data as well. Additional data, such as framing and OH equipment are observed from recently collected field inspection photographs. i. PG&E uses multiple types of LiDAR (aerial: rotary (helicopter) and fixed wing, and ground: vehicle). The accuracy of the LiDAR is dependent on the vintage (year collected), as well as the method of collection. The expectation is that the position of the pole is +/- 3 feet in EDGIS, as derived from the LiDAR data. ii. Please see the response to subpart l(i) above for the requested information. iii. The PLA Program leverages pole positions from EDGIS, which is based on LiDAR data. Additional data, such as framing and OH equipment are observed from recently collected field inspection photographs. If there is crucial data missing, the team can send someone to the field to gather the required information for performing the PLC. m. PG&E does not perform these calculations as part of the PLA Program. | Henry Sweat | 2024-05-30 | 2024-06-19 | 2024-06-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_016.zip | 1 | N/A | 8 | Section 8.1.3 - Asset Inspection | 8.1.3.2.4 LiDAR based Pole Loading Assessments | N/A
659 | CPUC - SPD (Safety Policy Division) | 016 | CPUC - SPD (Safety Policy Division)_016 | 16 | CPUC - SPD (Safety Policy Division)_016_Q16 | CONFIDENTIAL - Provide the data in excel format used to create the chart on slide 2, 5, 6, 8 of the presentation to the Wildfire Risk Governance Committee presented on October 12th, 2023 (sent to SPD as “WMP-Discovery2023-2025_DR_SPD_014-Q010Atch01CONF"). | Please see attachment “WMP-Discovery2023-2025_DR_SPD_016-Q016Atch01.xlsx” for the requested information. | Henry Sweat | 2024-05-30 | 2024-06-10 | 2024-06-10 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_016.zip | 1 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23-09 – Decrease in Detailed Distribution Inspections | ACI 23-09 – Decrease in Detailed Distribution Inspections
660 | CPUC - SPD (Safety Policy Division) | 016 | CPUC - SPD (Safety Policy Division)_016 | 17 | CPUC - SPD (Safety Policy Division)_016_Q17 | CONFIDENTIAL – This question refers to the table labeled “AG Population, B Find Rates” on slide 29 of the presentation to the Wildfire Risk Governance Committee presented on October 12th, 2023 (sent to SPD as “WMP-Discovery2023-2025_DR_SPD_014-Q010Atch01CONF"). Provide an explanation of the table. Specifically discuss the difference between a CIRT aligned B tag versus those found by an Aerial Inspection/Ground Inspection. a. Provide an explanation of the table. b. Define a “CIRT-aligned B tag” and discuss the difference between a CIRT-aligned B tag versus those found by an Aerial Inspection/Ground Inspection. c. Provide the actual numbers of tags identified by Ground and Aerial inspections in the table. d. Provide the unique number of tags identified by Aerial (i.e. those tags not identified by Aerial and not identified by Ground inspections) in the table. e. For “Crossarm Decayed/Rotten”, does the table imply that of the 53 B-tags found in the sample, that Aerial Inspections identified 50-75% of the B-tags and that Ground Inspections identified 25-50% of the B-tags? i. Does this mean a minimum of 13, and a maximum of 26 of the B-Tags were identified by Ground and not identified by Aerial? a. What was the sample size for this table? | a. The table is a view of the number of B tags for the FDAs listed (Crossarm and Pole). It is an analysis of the finds by each method, where they overlap, and where they did not. “AG” refers to Aerial Inspection/Ground Inspection. b. A CIRT review was the process step after Ground or Aerial performed their inspection. CIRT then reviewed the prioritization assignment. This phrase reflects those instances in which CIRT agreed with the priority assigned. c. For the Ground and Aerial inspections reflected in the Harvey balls, 325 were Aerial inspections and 196 were Ground inspections. The total number of unique tags is 463. d. PG&E interprets this to mean tags identified by Aerial inspection and not identified by Ground inspection. 267 tags were identified by Aerial inspection and not by Ground inspection. e. Yes. For “Crossarm Decayed/Rotten”, the table does imply that of the 53 B-tags found in the sample, that Aerial Inspections identified 50-75% of the B-tags and that Ground Inspections identified 25-50% of the B-tags. i. Yes. A minimum of 13, and a maximum of 26 of the B-Tags were identified by Ground inspection and not identified by Aerial inspection. f. The sample size for this table for the entire Aerial and Ground population study was 12,126 inspections. | Henry Sweat | 2024-05-30 | 2024-06-10 | 2024-06-10 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_016.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23-09 – Decrease in Detailed Distribution Inspections | ACI 23-09 – Decrease in Detailed Distribution Inspections
661 | CPUC - SPD (Safety Policy Division) | 017 | CPUC - SPD (Safety Policy Division)_017 | 1 | CPUC - SPD (Safety Policy Division)_017_Q1 | SPD understands PG&E has updated its EPSS enablement criteria since publishing FIGURE PG&E-8.1.8-2 in PG&E’s 2023-2025 Wildfire Mitigation Plan per page 133 of PG&E’s 2025 WMP Update. Provide an updated figure similar to FIGURE PG&E-8.1.8-2 and discuss the changes. | PG&E continues to observe two enablement criteria approved by our Wildfire Risk Governance Steering Committee in 2022, one during peak wildfire risk conditions and one during non-peak risk conditions. Included below are the EPSS peak and non-peak wildfire risk condition enablement criteria. Separately, we are in the process of evaluating wildfire risk and reliability tradeoffs when EPSS settings are enabled and anticipate finalizing the analysis by the end of Q2 2024. | Henry Sweat | 2024-06-10 | 2024-06-13 | 2024-06-13 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_017.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--26 Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI 23-26 Evaluation and Reporting of Safety Impacts Related to EPSS
662 | CPUC - SPD (Safety Policy Division) | 017 | CPUC - SPD (Safety Policy Division)_017 | 2 | CPUC - SPD (Safety Policy Division)_017_Q2 | When did this change take effect? | See response to SPD_017-Q001. The non-peak wildfire risk enablement criteria was approved by the PG&E Wildfire Risk Governance Steering Committee on February 2, 2022, and the peak season wildfire risk enablement criteria was approved on June 6, 2022. | Henry Sweat | 2024-06-10 | 2024-06-13 | 2024-06-13 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_017.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--26 Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI 23-26 Evaluation and Reporting of Safety Impacts Related to EPSS
663 | CPUC - SPD (Safety Policy Division) | 017 | CPUC - SPD (Safety Policy Division)_017 | 3 | CPUC - SPD (Safety Policy Division)_017_Q3 | Prepare a table which shows the number of Circuit Mile Days where EPSS is enabled for 2022 and 2023 for the criteria in FIGURE PG&E-8.1.8-2 as compared to the new criteria. Additionally, provide the expected number of Circuit Mile Days where EPSS will be enabled for both criteria for a typical year. | Please see response to SPD_017-Q001. PG&E continues to leverage the same enablement criteria first approved by PG&E’s Wildfire Risk Governance Steering Committee in 2022 and provided in response to Question No. 001. EPSS settings were enabled for approximately 5,960,000 Circuit Mile Days in 2022 and approximately 5,520,000 Circuit Mile Days in 2023. Given EPSS enablement is dependent on the forecasted daily wildfire risk conditions in PG&E’s service area and may vary any given year in accordance with extremity of peak season conditions, an expected number of Circuit Mile Days where EPSS will be enabled is not available. However, based on the prior two years of program utilization, PG&E has averaged approximately 5,740,000 Circuit Mile Days of EPSS settings enablement a year. | Henry Sweat | 2024-06-10 | 2024-06-13 | 2024-06-13 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_017.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--26 Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI 23-26 Evaluation and Reporting of Safety Impacts Related to EPSS
664 | CPUC - SPD (Safety Policy Division) | 017 | CPUC - SPD (Safety Policy Division)_017 | 4 | CPUC - SPD (Safety Policy Division)_017_Q4 | Discuss the reason for the changes. | Please see response to SPD_017-Q001. PG&E continues to observe its EPSS peak season and non-peak season wildfire risk enablement criteria according to risk conditions observed across its service area. Biannually, recommendations are presented by leaders across PG&E to an officer-in-charge for approval to transition to peak season wildfire risk enablement criteria or to non-peak wildfire risk enablement criteria depending on observed field conditions. | Henry Sweat | 2024-06-10 | 2024-06-13 | 2024-06-13 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_017.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--26 Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI 23-26 Evaluation and Reporting of Safety Impacts Related to EPSS
665 | CPUC - SPD (Safety Policy Division) | 017 | CPUC - SPD (Safety Policy Division)_017 | 5 | CPUC - SPD (Safety Policy Division)_017_Q5 | Compute the additional risk reduced (or increased) due to the changes in criteria. The computation should account for lower probabilities of fires at lower FPI levels. Compute the additional risk induced due to increased (or reduced due to decreased) outages, due to the change in criteria. | PG&E is still completing the requested analysis and will provide the requested change in risk by Monday, July 1, 2024. | Henry Sweat | 2024-06-10 | 2024-06-13 | 2024-06-13 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_017.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--26 Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI 23-26 Evaluation and Reporting of Safety Impacts Related to EPSS
666 | CPUC - SPD (Safety Policy Division) | 017 | CPUC - SPD (Safety Policy Division)_017 | 6 | CPUC - SPD (Safety Policy Division)_017_Q6 | Provide the analysis referenced in ACI PG&E-23-26 which computes the risk associated with EPSS-enablement thresholds. SPD understands the analysis shows a demonstration of trade-offs between reliability and wildfire risk mitigation effectiveness for each FPI level, as well as inclusion of areas outside the HFTD. SPD already has access to the analysis provided with the RAMP filing, and would like to see the more detailed FPI based analysis. | Please see response to SPD_017-Q005. | Henry Sweat | 2024-06-10 | 2024-06-13 | 2024-06-13 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_017.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--26 Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI 23-26 Evaluation and Reporting of Safety Impacts Related to EPSS
667 | OEIS | 022 | OEIS_022 | 1 | OEIS_022_Q1 | Regarding Monitoring Potential Hazard Trees a. For Focused Tree Inspections, does One VM have the capability to document potential defects or issues found with “inventory only trees”1 so that PG&E may monitor the condition of those trees? b. For all other VM inspection types, are inspectors able to document potential defects or issues found with trees not prescribed for work so that PG&E may monitor the condition of those trees? | a. For the FTI program, the One VM application is not set up to document potential defects or issues with 'inventory only trees." Inspectors prescribe work based off potential defects or issues that would cause the tree to fail within 15 months. Vegetation is inspected twice a year in HFTD areas which allows PG&E to continually monitor the health of the vegetation along its lines. b. For other VM programs housed within One VM, the application is not set up to document potential defects or issues when a tree is not prescribed for work. | Brad Hill | 2024-06-11 | 2024-06-14 | 2024-06-14 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/OEIS_022.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23-19 – Continued Progression of Vegetation Management Maturity | ACI 23-19 Continued Progresion of Vegatation Management Maturity
668 | CalPA | Set WMP-49 | CalPA_Set WMP-49 | 1 | CalPA_Set WMP-49_Q1 | How did PG&E come up with the 25 random numbers when it decided on the 25 out of 50 fast-trip outages to provide responses to? | PG&E selected the first 25 outages listed in the referenced file “Random Fast-Trip August 2023 Outages.xlsx” to provide the information requested in CalAdvocates_048-Q010. | Tyler Holzschuh | 2024-06-13 | 2024-06-27 | 2024-06-14 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_049.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--26 Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI 23-26 Evaluation and Reporting of Safety Impacts Related to EPSS
669 | OEIS | 023 | OEIS_023 | 1 | OEIS_023_Q1 | Regarding PG&E’s distribution asset inspection initiatives and pilots: a. Provide the number of inspections performed and find rate of level 1 and 2 conditions from January 1, 2020, to December 31, 2023, for the following inspection initiative or pilot programs. If the inspection initiative or pilot program began after January 1, 2020, please specify the start date of the initiative in the response. i. Infrared inspections ii. LiDAR based pole loading assessments iii. Aerial inspections iv. Detailed ground inspections v. Intrusive pole inspections vi. Patrol inspections b. For each inspection initiative or pilot below, please provide the estimated percentage of conditions that PG&E would likely not have identified through detailed ground, patrol, or intrusive pole inspections. Describe how PG&E calculated the estimated percentage. i. Infrared inspections ii. LiDAR based pole loading assessments iii. Aerial inspections | Please see the tables below for the requested information. | Nathan Poon | 2024-06-20 | 2024-07-10 | 2024-07-10 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/OEIS_023.zip | 0 | N/A | 8 | Section 8.1.3 - Asset Inspection | Section 8.1.3 - Asset Inspection | N/A
670 | OEIS | 023 | OEIS_023 | 2 | OEIS_023_Q2 | Regarding PG&E’s transmission asset inspection programs and pilots: a. Provide the find rate of level 1 and 2 conditions and number of inspections performed from January 1, 2020, to December 31, 2023, for the following inspection initiatives and pilot programs. If the inspection initiative or pilot began after January 1, 2020, please specify the start date of the initiative in the response. i. Aerial detailed inspections ii. Infrared inspections iii. Conductor measurement iv. Below grade foundation assessment v. Corona inspections vi. Ultrasonic pole inspections vii. Corrosion climbing assessment viii. Proactive sampling and testing ix. LiDAR assessment x. Climbing detailed inspections xi. Intrusive Pole inspections xii. Patrol inspections | a. The three tables below provide the number of completed inspection units, Level 1 and Level 2 finds (count of notifications) and the Level 1 and Level 2 find rates (notifications per inspection unit). The counts of notifications for aerial and climbing detailed inspections, LiDAR assessment, intrusive pole inspections, and patrols are derived from the dataset used to generate Table 2 in the 2024 Q1 WMP QDR. The counts of aerial inspections from 2021-2023 also are taken from Table 2 of the QDR. The counts of climbing detailed inspections and patrols are derived from data in SAP. The inspection units and counts of notifications for the remaining programs are based on data collected by the program managers. Table 1: Completed inspection units. 2020 2021 2022 2023 Inspection units # Inspections # Inspections # Inspections # Inspections i. Aerial detailed inspections Structures 52,834 66,645 59,022 50,491 ii. Infrared inspections Miles 5,355 7,500 9,474 8,011 iii. Conductor measurement Spans 3 13 13 0 iv. Below grade foundation assessment Structures (started in 2021) N/A 99 545 352 v. Corona inspections Miles 5,355 7,500 9,474 8,011 vi. Ultrasonic pole inspections Structures (started in 2022) N/A N/A 157 8 vii. Corrosion climbing assessment Structures (started in 2023) N/A N/A N/A 172 viii. Proactive sampling and testing Samples 3 17 25 17 ix. LiDAR assessment Spans (started in 2023) N/A N/A N/A 27,147 2020 2021 2022 2023 Inspection units # Inspections # Inspections # Inspections # Inspections x. Climbing detailed inspections Structures 2,911 3,317 3,607 4,180 xi. Intrusive Pole inspections Structures 14,841 17,512 12,645 10,376 xii. Patrol inspections Structures 142,660 130,677 111,206 105,480 Table 2: Level 1 and Level 2 finds (count of notifications) 2020 2021 2022 2023 2020 2021 2022 2023 Level 1 Finds Level 1 Finds Level 1 Finds Level 1 Finds Level 2 Finds Level 2 Finds Level 2 Finds Level 2 Finds i. Aerial detailed inspections 178 103 88 234 17,159 22,666 21,508 15,289 ii. Infrared inspections 0 1 2 2 3 15 12 16 iii. Conductor measurement 0 0 0 0 0 0 0 0 iv. Below grade foundation assessment N/A – started in 2021 0 0 0 N/A – started in 2021 9 3 0 v. Corona inspections 0 0 0 0 0 0 1 0 vi. Ultrasonic pole inspections N/A – started in 2022 N/A 0 0 N/A – started in 2022 N/A 0 0 vii. Corrosion climbing assessment N/A – started in 2023 N/A N/A 0 N/A – started in 2023 N/A N/A 62 viii. Proactive sampling and testing N/A - sampling drives proactive repair/replace decisions ix. LiDAR assessment N/A N/A N/A 1 N/A N/A N/A 727 x. Climbing detailed inspections 1 0 0 0 335 251 616 512 xi. Intrusive Pole inspections 0 0 1 4 221 191 1,637 1,242 xii. Patrol inspections 456 420 226 497 1,047 1,267 715 508 Table 3: Level 1 and Level 2 find rates (count of notifications per inspection unit) 2020 2021 2022 2023 2020 2021 2022 2023 Level 1 Find Rate Level 1 Find Rate Level 1 Find Rate Level 1 Find Rate Level 2 Find Rate Level 2 Find Rate Level 2 Find Rate Leve l 2 Find Rate i. Aerial detailed inspections 0.00337 0.00155 0.00149 0.00463 0.32477 0.34010 0.36441 0.302 81 ii. Infrared inspections 0.00000 0.00013 0.00021 0.00025 0.00056 0.00200 0.00127 0.002 00 iii. Conductor measurement 0.00000 0.00000 0.00000 0.00000 0.00000 0.00000 0.00000 0.000 00 iv. Below grade foundation assessment N/A – started in 2021 0.00000 0.00000 0.00000 N/A – started in 2021 0.09091 0.0550 0.000 00 v. Corona inspections 0.00000 0.00000 0.00000 0.00000 0.00000 0.00000 0.00011 0.000 00 vi. Ultrasonic pole inspections N/A – started in 2022 N/A 0.0000 0 0.00000 N/A – started in 2022 N/A 0.0000 0 0.00000 vii. Corrosion climbing assessment N/A – started in 2023 N/A N/A 0.00000 N/A – started in 2023 N/A N/A 0.36047 viii. Proactive sampling and testing N/A - sampling drives proactive repair/replace decisions ix. LiDAR assessment N/A N/A N/A 0.00004 N/A N/A N/A 0.02678 x. Climbing detailed inspections 0.00034 0.00000 0.00000 0.00000 0.11508 0.07567 0.17078 0.12249 xi. Intrusive Pole inspections 0.00000 0.00000 0.00008 0.00039 0.01489 0.01091 0.12946 0.11970 xii. Patrol inspections 0.00320 0.00321 0.00203 0.00471 0.00734 0.00970 0.00643 0.00482 b. i. Aerial detailed inspections PG&E estimates roughly >2/3 of Aerial finds would not have been identified through Ground inspections based on an analysis of tags found on structures receiving Ground and Aerial inspections in the same year. Note this is due to the difference in vantage point and the aerial review process allowing for additional data sources during desktop review. ii. Infrared inspections PG&E estimates the majority of infrared findings would not be identified through other inspection methods due to the failure mode being internal electrical connection degradation not visible externally. iii. Conductor measurement PG&E estimates the majority of LineVue findings would not be identified through other inspection methods due to the failure mode being internal steel core conductor corrosion not visible externally. iv. Below grade foundation assessment PG&E estimates the majority of below grade foundation findings would not be identified through other inspection methods due to the failure mode being foundation integrity degradation not visible to the above ground inspection methods. v. Corona inspections PG&E does not have an estimate at this time due to the small number of finds. vi. Ultrasonic pole inspections PG&E does not have an estimate at this time due to the lack of findings. vii. Corrosion climbing assessment PG&E estimates that the majority of findings could be identified through a detailed Climbing, Aerial, or Ground inspection due to the visual assessment tower members during the pilot. This pilot includes quantitative measurement of material loss due to corrosion which provides input into calibration of our asset degradation model and informs asset repair vs replace decisions. viii. Proactive sampling and testing PG&E does not have an estimate at this time. The findings of this pilot mainly inform proactive repair/replace decisions. ix. LiDAR assessment PG&E estimates the majority of LiDAR findings would not be identified through other inspection methods due to the quantitative spatial nature which is difficult for other inspection methods to provide. | Nathan Poon | 2024-06-20 | 2024-07-01 | 2024-07-01 | https://preview.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/OEIS_023.zip | 0 | N/A | 8 | Section 8.1.3 - Asset Inspection | Section 8.1.3 - Asset Inspection | N/A
671 | CalPA | Set WMP-50 | CalPA_Set WMP-50 | 1 | CalPA_Set WMP-50_Q1 | The Filsinger Energy Partners’ PG&E Independent Safety Monitor Status Update Report, October 6, 2023 (ISM Report 3) stated that there were 1,400 action items in the Multiple Outage Review and Evaluation (MORE) for 2022. However, in 2023 WMP data request CalAdvocates-PGE- 2023WMP-34, Question 1, there are apparently 900 action items listed. Please explain the discrepancy. | The ISM Report 3 included items that were not actual action items to be performed on the circuit, but rather captured the action item of the review by the MORE team. The referenced CalAdvocate data set did not include the review as an action item. The discrepancy is due in large part to the removal of the review action item called “MORE Assessment.” A MORE Assessment was completed for each circuit that reached trigger level criteria at the time, which resulted in action items such as a settings review, planned work opportunities, etc. As such, these action items were removed in order to provide a cleaner data set as a part of the CalAdvocates data request response. Additionally in 2024, the MORE process has fully migrated from a manual spreadsheet tracking system to a digital platform to better keep records and provide transparency across the organization for action item tracking. | Amanda Asadi | 2024-06-24 | 2024-07-09 | 2024-07-09 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_050.zip | 0 | N/A | 8.1.8.1.1 | Grid Operations and Procedures | Protective Equipment and Device Settings | N/A
672 | CalPA | Set WMP-50 | CalPA_Set WMP-50 | 2 | CalPA_Set WMP-50_Q2 | In response to Data request CalAdvocates-PGE-2023WMP-34, Question 1, PG&E states, “no additional action required” for 36 circuits in 2022. Please explain why no additional action was required. | PG&E used the term “no additional action required” in the referenced data request to account for when a review was complete and the previously identified action items were either appropriate or additional actions items were not required due to one of the following reasons upon reviewing the outages and causes: • Outage Frequency (i.e., outages occurred across a long period of time on the circuit) • Cause Type (for example, a 3rd Party - Car Pole outage triggering a MORE review) PG&E would then continue to monitor the circuit for additional outages that may result in new action items as needed. | Amanda Asadi | 2024-06-24 | 2024-07-09 | 2024-07-09 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_050.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--26 Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI 23-26 Evaluation and Reporting of Safety Impacts Related to EPSS
673 | CalPA | Set WMP-50 | CalPA_Set WMP-50 | 3 | CalPA_Set WMP-50_Q3 | Data request CalAdvocates-PGE-2023WMP-34, Question 3, Attachments 1 and 2 show claims and complaints received from 5/19/2023 to 12/12/2023. Please provide an Excel sheet of claims and complaints filed by customers related to outages on circuits with EPSS settings enabled at the time of outage that were received in 2021, 2022, 1/1/2023 to 5/18/2023, 12/13/2023 to 12/31/2023. For each claim or complaint, provide the following information in separate columns: a) The Circuit name and ID associated with the complaint; b) The date each complaint or claim was received; c) Description of each complaint or claim; d) Resolution of each complaint or claim; e) Due date of each resolution; f) Actual completion date of each resolution. | Please be advised an attachment to this response contains CONFIDENTIAL information and is being provided pursuant to the accompanying confidentiality declaration. Please see “WMP-Discovery2023-2025_DR_CalAdvocates_050-Q003Atch01.xlsm” and “WMP-Discovery2023-2025_DR_CalAdvocates_050-Q003Atch02CONF.xlsm” for CPUC complaint information and claims information related to EPSS outages. Please note, EPSS related complaints are only tracked through complaints provided to PG&E by the CPUC, which is the data provided in the spreadsheet. Details of the complaint and resolution are in the individual cells in the excel file. Please note, there are no due dates for claims and the date given is the date the claim was closed. Please note that a population of EPSS complaints was inadvertently coded as “service interruption/outage” complaints. As such, PG&E is reviewing all “service interruption/outage” complaints and will provide any additional EPSS complaint data at a later date. | Amanda Asadi | 2024-06-24 | 2024-07-26 | 2024-07-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_050.zip | 2 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--26 Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI 23-26 Evaluation and Reporting of Safety Impacts Related to EPSS
673 | CalPA | Set WMP-50 | CalPA_Set WMP-50 | 3(s) | CalPA_Set WMP-50_Q3(s) | Data request CalAdvocates-PGE-2023WMP-34, Question 3, Attachments 1 and 2 show claims and complaints received from 5/19/2023 to 12/12/2023. Please provide an Excel sheet of claims and complaints filed by customers related to outages on circuits with EPSS settings enabled at the time of outage that were received in 2021, 2022, 1/1/2023 to 5/18/2023, 12/13/2023 to 12/31/2023. For each claim or complaint, provide the following information in separate columns: a) The Circuit name and ID associated with the complaint; b) The date each complaint or claim was received; c) Description of each complaint or claim; d) Resolution of each complaint or claim; e) Due date of each resolution; f) Actual completion date of each resolution. | PG&E completed the analysis of the population of EPSS complaints which were inadvertently coded as “service interruption/outage” complaints. Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_050-Q003Supp01Atch01CONF.xlsm” for “service interruption/outage” complaints which were still being reviewed when the original response was submitted on July 12, 2024. Details of the complaint and resolution are identified in the Excel file. Please note that the Circuit Name and Circuit ID were not mapped when the complaint was originally received in 2021. The attachment reflects the current Circuit Name and Circuit ID for the address in which the complaint was received. | Amanda Asadi | 2024-06-24 | 2024-07-26 | 2024-07-26 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_050.zip | 1 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--26 Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI 23-26 Evaluation and Reporting of Safety Impacts Related to EPSS
674 | CalPA | Set WMP-50 | CalPA_Set WMP-50 | 4 | CalPA_Set WMP-50_Q4 | Provide an Excel spreadsheet of all distribution circuits in HFTD or High Fire Risk Areas (HFRAs), or crossing HFTD and HFRA boundaries, existing as of January 1, 2024 (as rows) that includes the following information in separate columns: a) Circuit Name b) Circuit ID c) Date PG&E first activated EPSS settings on any part of the circuit3 | Please see “WMP-Discovery2023-2025_DR_CalAdvocates_050-Q004Atch01.xlsx” for the requested information. Please note, circuits scoped for the EPSS program in 2024 are based on primary overhead in HFRA and HFRA Tier 1 Buffer Areas and are not relative to HFTD areas. | Amanda Asadi | 2024-06-24 | 2024-07-09 | 2024-07-09 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_050.zip | 1 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--26 Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI 23-26 Evaluation and Reporting of Safety Impacts Related to EPSS
675 | CALPA | Set WMP-50 | CALPA_Set WMP-50 | 5 | CALPA_Set WMP-50_Q5 | Data request CalAdvocates-PGE-2023WMP-34, Questions 9 and 10, PG&E states that Garberville 1101 and Otter 1102 had Fuse Save Installations “identified as a proactive strategy to both minimize wildfire risk while also providing reliability improvement benefits under EPSS enablement conditions.” a) Please provide an excel sheet of circuits that PG&E identified that might need proactive strategies ahead of EPSS enablement. b) Please provide the criteria PG&E used to determine which circuits might need proactive strategies for reliability improvement under EPSS enablement. | a) Please see “WMP-Discovery2023-2025_DR_CalAdvocates_050-Q005Atch01.xlsx” for a list of EPSS circuits identified for proactive reliability improvement work in 2024. b) Reliability improvement work identified as “proactive” relative to the EPSS program includes vegetation management, animal mitigation work, and sectionalizing work on EPSS capable zones experiencing multiple outages. Circuits and zones are identified for proactive work based on a combination of factors including historic EPSS outage activity, which includes causes of outages, customer impact, in some cases history of animal interaction in the geographic area, and all historical outage activity for sectionalizing work. | Amanda Asadi | 2024-06-24 | 2024-07-19 | 2024-07-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_050.zip | 1 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--26 Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI 23-26 Evaluation and Reporting of Safety Impacts Related to EPSS
676 | CalPA | Set WMP-50 | CalPA_Set WMP-50 | 6 | CalPA_Set WMP-50_Q6 | Provide an Excel table that lists (as rows) each sustained outage that occurred from January 1, 2023 through December 31, 2023 on any of the circuits identified in your response to Question 5 of data request CalAdvocates-PGE-2023WMP-34. For each outage, the Excel table should include the following information in separate columns: a) Outage ID b) Circuit Name c) Circuit ID d) Division e) Was EPSS enabled on this circuit at the time of the outage? f) FNL (First No Light) g) Outage End Day & Time h) CESO (Count of Customers Experiencing Sustained Outages) i) Customer Minutes j) Cause k) Restoration Time (Minutes) | Please see “WMP-Discovery2023-2025_DR_CalAdvocates_050-Q006Atch01.xlsx” for the requested information. Please note, column M indicates if the outage was sustained or momentary. | Amanda Asadi | 2024-06-24 | 2024-07-09 | 2024-07-09 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_050.zip | 1 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--26 Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI 23-26 Evaluation and Reporting of Safety Impacts Related to EPSS
677 | CalPA | Set WMP-50 | CalPA_Set WMP-50 | 7 | CalPA_Set WMP-50_Q7 | Provide an Excel table that lists (as rows) each momentary outage that occurred from January 1, 2023 through December 31, 2023 on any of the circuits identified in your response to Question 5 of data request CalAdvocates-PGE-2023WMP-34. For each outage, the Excel table should include the following information in separate columns: a) Outage ID b) Circuit Name c) Circuit ID d) Division e) Was EPSS enabled on this circuit at the time of the outage? f) FNL (First No Light) g) Outage End Day & Time h) CESO (Count of Customers Experiencing Sustained Outages) i) Customer Minutes j) Cause k) Restoration Time (Minutes) | Please see “WMP-Discovery2023-2025_DR_CalAdvocates_050-Q006Atch01.xlsx” for the requested information. Please note, column M indicates if the outage was sustained or momentary. | Amanda Asadi | 2024-06-24 | 2024-07-09 | 2024-07-09 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_050.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--26 Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI 23-26 Evaluation and Reporting of Safety Impacts Related to EPSS
678 | CalPA | Set WMP-50 | CalPA_Set WMP-50 | 8 | CalPA_Set WMP-50_Q8 | Provide an Excel table that lists (as rows) each sustained outage that occurred from January 1, 2017 through December 31, 2023 on the following circuits: SCE REFUGIO 1701, SCE VEGAS 1701, SCE TEJON TIE 1101, SCE TEHACHAPI 1101, SCE MCFARLAND 1101, VALLEY SPRINGS 1101, LAKEWOOD 1103, VASONA 1102, NAPA 1110, PUEBLO 2104, BIG TREES 0402, LOS OSITOS 2101, LAS POSITAS 2103, LAS AROMAS 0401, ORINDA 0401, SPENCE 1101. For each outage, the Excel table should include the following information in separate columns: a) Outage ID b) Circuit Name c) Circuit ID d) Division e) Was EPSS enabled on this circuit at the time of the outage? f) When was this circuit made EPSS-capable? g) FNL (First No Light) h) Outage End Day & Time i) CESO (Count of Customers Experiencing Sustained Outages) j) Customer Minutes k) Cause l) Restoration Time (Minutes) | Please see “WMP-Discovery2023-2025_DR_CalAdvocates_050-Q008Atch01.xlsx” for the requested information. Column N indicates if the outage was sustained or momentary. Please note, as the following circuits did not have any outages, they have not been included in the attachment: SCE VEGAS 1701, SCE TEJON TIE 1101, SCE MCFARLAND 1101, PUEBLO 2104. As of July 2, 2024, these circuits have not been made EPSS-capable. | Amanda Asadi | 2024-06-24 | 2024-07-09 | 2024-07-09 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_050.zip | 1 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--26 Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI 23-26 Evaluation and Reporting of Safety Impacts Related to EPSS
679 | CalPA | Set WMP-50 | CalPA_Set WMP-50 | 9 | CalPA_Set WMP-50_Q9 | Provide an Excel table that lists (as rows) each momentary outage that occurred from January 1, 2017 through December 31, 2023 on the following circuits: SCE REFUGIO 1701, SCE VEGAS 1701, SCE TEJON TIE 1101, SCE TEHACHAPI 1101, SCE MCFARLAND 1101 VALLEY SPRINGS 1101, LAKEWOOD 1103, VASONA 1102, NAPA 1110, PUEBLO 2104, BIG TREES 0402, LOS OSITOS 2101, LAS POSITAS 2103, LAS AROMAS 0401, ORINDA 0401, SPENCE 1101. For each outage, the Excel table should include the following information in separate columns: a) Outage ID b) Circuit Name c) Circuit ID d) Division e) Was EPSS enabled on this circuit at the time of the outage? f) When was this circuit made EPSS-capable? g) FNL (First No Light) h) Outage End Day & Time i) CESO (Count of Customers Experiencing Sustained Outages) j) Customer Minutes k) Cause l) Restoration Time (Minutes) | Please see “WMP-Discovery2023-2025_DR_CalAdvocates_050-Q008Atch01.xlsx” for the requested information. Please note, column N indicates if the outage was sustained or momentary. | Amanda Asadi | 2024-06-24 | 2024-07-09 | 2024-07-09 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_050.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--26 Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI 23-26 Evaluation and Reporting of Safety Impacts Related to EPSS
680 | CalPA | Set WMP-50 | CalPA_Set WMP-50 | 10 | CalPA_Set WMP-50_Q10 | Provide an Excel spreadsheet of the following distribution circuits (as rows): SCE REFUGIO 1701, SCE VEGAS 1701, SCE TEJON TIE 1101, SCE TEHACHAPI 1101, SCE MCFARLAND 1101, VALLEY SPRINGS 1101, LAKEWOOD 1103, VASONA 1102, NAPA 1110, PUEBLO 2104, BIG TREES 0402, LOS OSITOS 2101, LAS POSITAS 2103, LAS AROMAS 0401, ORINDA 0401, SPENCE 1101. Include the following information in separate columns: a) Circuit Name b) Circuit ID e) Division (e.g., Los Padres Division)4 f) Date PG&E first activated EPSS settings on any part of the circuit5 g) Total Customers h) Number of CPZs contained on the circuit i) Circuit SAIDI for 2017 j) Circuit SAIDI for 2018 k) Circuit SAIDI for 2019 l) Circuit SAIFI for 2017 m) Circuit SAIFI for 2018 n) Circuit SAIFI for 2019 o) Circuit MAIFI for 2017 p) Circuit MAIFI for 2018 q) Circuit MAIFI for 2019 | Please see “WMP-Discovery2023-2025_DR_CalAdvocates_050-Q008Atch01.xlsx” for the requested information. In addition to the circuits included in the attachment, please see the table below for Circuit ID’s for the Circuits which did not have outages and were not provided in the attachment. Circuit Name Circuit ID SCE Vegas 1701 188881701 SCE Tejon Tie 1101 258191101 SCE McFarland 1101 258111101 Pueblo 2104 043292104 | Amanda Asadi | 2024-06-24 | 2024-07-09 | 2024-07-09 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_050.zip | 0 | N/A | 11.4 | Appendix D - Areas for Continued Improvement | 11.4 ACI PG&E-23--26 Evaluation and Reporting of Safety Impacts Relating to EPSS | ACI 23-26 Evaluation and Reporting of Safety Impacts Related to EPSS
681 | CalPA | Set WMP-51 | CalPA_Set WMP-51 | 1 | CalPA_Set WMP-51_Q1 | On page 410 of PG&E’s 2023-2025 WMP R6, Table PG&E-8.1.2-3 is presented as the following (referred to herein as the July 5 table): IMAGE On April 5, 2024, in response to data request CalAdvocates-PGE-2025WMP-03, question 11 (CalAdvocates_039-Q011), PG&E provided the following version of Table PG&E-8.1.2-3 (referred to herein as the April 5 table): IMAGE State the basis for why PG&E made each of the following changes to Table PG&E-8.1.2-3 in the three months from April 5, 2024 to July 5, 2024: a) In 2023, the total number of miles in the “Fire Rebuild” category is 109 miles in the April 5 table, but 111 miles in the July 5 table. b) In 2024, the total number of miles in the “Top 20% Risk-Ranked Circuit Segments” category is 204 miles in the April 5 table, but 180 miles in the July 5 table. c) In 2024, the total number of miles in the “Fire Rebuild” category is 49 miles in the April 5 table, but 55 miles in the July 5 table. d) In 2024, the total number of miles in the “PSPS” category is 33 miles in the April 5 table, but 29 miles in the July 5 table. e) In 2024, the total number of miles in the “Other UG Programs” category is 2 miles in the April 5 table, but 0 miles in the July 5 table. f) In the two-year period from 2025 to 2026, the total number of miles in the “Top 20% Risk-Ranked Circuit Segments” category is 795 miles in the April 5 table, but 711 miles in the July 5 table. g) In the two-year period from 2025 to 2026, the total number of miles in the “Fire Rebuild” category is 44 miles in the April 5 table, but 41 miles in the July 5 table. h) In the two-year period from 2025 to 2026, the total number of miles in the “PSPS” category is 2 miles in the April 5 table, but 7 miles in the July 5 table. i) In the two-year period from 2025 to 2026, the total number of miles in the “UG System Hardening” category is 4 miles in the April 5 table, but 12 miles in the July 5 table. j) In the two-year period from 2025 to 2026, the total number of miles in the “Other UG Programs” category is 2 miles in the April 5 table, but 5 miles in the July 5 table. | As described in our WMP Section 8.1.2.2, PG&E’s undergrounding workplan evolves overtime. Project schedules can change because of project dependencies, such as permitting and easement delays. Further, the workplan evolved to account for the 2023 GRC Decision. Below describes the changes specifically made between when the two workplans were submitted between April 5 and July 5. a) The July 5 table incorporates miles from Greenville Community Rebuild projects. These projects were inadvertently missing from all versions of the summary table prior to the July 5 version. b) This change was driven by seven projects shifting schedules from 2024 to 2025 and one from 2024 to 2026. c) As with subpart (a), the July 5 table incorporates miles from Greenville Community Rebuild projects. These projects were inadvertently missing from all versions of the summary table prior to the July 5 version. d) This change was driven by two projects shifting schedules from 2024 to 2025. e) This change was driven by one project shifting schedule from 2024 to 2025. f) The primary driver in the reduction of miles for 2025-2026 is the need to align the workplan to the 2023-2026 GRC mileage targets. These changes include removing existing projects and adding/scoping to drive to the GRC risk reduction targets. g) This change was driven by Butte Rebuild project schedule changes between 2024 and 2025 (one project moved from 2024 to 2025, another from 2025 to 2024), resulting in a net impact of increased miles in 2024 and reduced miles in 2025-2026. h) This change was driven by the same two projects described in subpart (d), plus one project being removed from the workplan. i) One four-mile project from the April 5 table has been removed from the July 5 table, and 12 miles from eight projects were added. Of the 12 miles added, 11 miles are in the Top 20% Risk category and will be moved accordingly once risk reduction calculations have been updated in our system of record for the associated projects. j) This change was driven by the same project described in subpart (e), as well as a single new project that was missing risk rank data at the time of the July 5 report creation. This will be updated in our system of record and will be included in future iterations of this table. | Holly Wehrman | 2024-07-09 | 2024-07-12 | 2024-07-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_051.zip | 0 | N/A | 8 | Section 8.1.2 - Grid Design and System Hardening | 8.1.2.11.2 Other grid topology improvements to mitigate or reduce PSPS events - Distribution | N/A
682 | CPUC - SPD (Safety Policy Division) | 018 | CPUC - SPD (Safety Policy Division)_018 | 1 | CPUC - SPD (Safety Policy Division)_018_Q1 | Submit the 2024 Q2 QDR Confidential and non-Confidential versions (including both spatial and non-spatial) via Kiteworks to SPD’s Wildfire and Safety Performance Section. | Please find the requested 2024 Q2 QDR Spatial and Non-Spatial files attached to this response: • OEIS Cover letter Q2 2024 Submission.pdf • PG&E_2024_Q2_Tables1-15_R0.xlsx • PG&E_2024_Q2_SpatialDataStatusReport.xlsx • PG&E_2024_Q2_CONF.zip • PG&E_2024_Q2_Risk Event Photos - Ignitions_CONF.zip • PG&E_2024_Q2_Initiative Photo Log - Asset Inspections_CONF_1.zip • PG&E_2024_Q2_Initiative Photo Log - Asset Inspections_CONF_2.zip • PG&E_2024_Q2_Initiative Photo Log - Asset Inspections_CONF_3.zip • PG&E_2024_Q2_Initiative Photo Log - Asset Inspections_CONF_4.zip | Henry Sweat | 2024-08-02 | 2024-08-06 | 2024-08-02 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_018.zip | 9 | N/A | QDR | N/A | N/A | N/A
683 | CalPA | Set WMP-52 | CalPA_Set WMP-52 | 1 | CalPA_Set WMP-52_Q1 | The following questions relate to your WMP Quarterly Data Report for Q2 of 2024, Table 13, received on August 2, 2024, which reports asset-related corrective notifications on electric circuits that were open at the end of the quarter. This follow-up data request seeks information for ALL open work orders in your territory, not only open work orders in High Fire Threat Districts. Please add the following information to each row of Table 13 in separate columns: i. Name of the associated circuit ii. ID number of the associated circuit iii. Geographic latitude in decimal degrees, truncated to seven decimal places iv. Geographic longitude in decimal degrees, truncated to seven decimal places v. Priority of the original notification, using PG&E’s internal priority level codes vi. Object/damage code or other internal description of defect vii. Poses ignition risk (Y/N) viii. General Order 95 Exception Granted (Y/N) ix. Circuit Segment Identification Number x. Past Due as of July 31, 2024 (Y/N) | Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_052- Q001Atch01.xlsx” for the requested information. The following explanatory notes provide context for the data: • Column K in Table 13 (Column h. in the attachment) in the QDR provides the original priority using PG&E’s internal priority level. Column Q (responsive to subpart v) in the attached dataset provides the current priority using PG&E’s internal priority level. Conditions that pose an ignition risk (responsive to subpart vii) within HFTD or PG&E High Fire Risk Areas (HFRA) are evaluated using a combination of object/damage codes and individual review during gatekeeping by the Centralized Inspection Review Team (CIRT). Since the same object/damage codes can contain both ignition and non-ignition risk conditions and non-HFTD non-HFRA notifications are not individually reviewed for ignition risk, ignition risk is only labeled for notifications within HFTD or HFRA. • PG&E has not requested from the Commission, or been granted, formal exceptions for maintenance tags under General Order (GO) 95, Rule 18. However, PG&E has internally identified maintenance tags that have been extended under reasonable circumstances including those identified under GO 95, Rule 18, which have been noted in Column U (responsive to subpart viii). • Notifications are not associated with circuit segments. The Functional Location has been provided for the Circuit Segment Identification Number, located in Column V of the attachment. | Benjamin Katzenberg | 2024-08-19 | 2024-09-06 | 2024-09-06 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_052.zip | 1 | N/A | QDR | N/A | N/A | N/A
684 | CalPA | Set WMP-52 | CalPA_Set WMP-52 | 2 | CalPA_Set WMP-52_Q2 | The following questions relate to your WMP Quarterly Data Report for Q2 of 2024, Table 13, received on August 2, 2024, which reports asset-related corrective notifications on electric circuits that were open at the end of the quarter. This follow-up data request seeks information for ALL open work orders in your territory, not only open work orders in High Fire Threat Districts. Please provide a list of structures, assets, and facilities that may qualify as “other” in column b (“Equipment type”) of Table 13. | Transmission equipment included under “other” in Table 13, Column B includes the “object” types (see the response to Question No. 001, subpart vi) associated with the assets/components below: • Markers/signs • Tower foundations (including bay water towers) • Hardware • Shield wire/optical ground wire • Animal/raptor guards • Dampers • Spacers • Jumpers • FAA lighting and batteries • Anti-climbing guards • Tie wire • Cathodic protection • Clearance infractions • Emergency. Distribution equipment included under “other” in Table 13, Column B includes the “object” types (see the response to Question No. 001, subpart vi) associated with the assets/components below: • High Sign • Tree/Vine • Marking • Hardware/Framing • Molding • Ground • OH Facility • Pole Step • Bird Protection • Guy Marker. | Benjamin Katzenberg | 2024-08-19 | 2024-09-06 | 2024-09-06 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_052.zip | 0 | N/A | QDR | N/A | N/A | N/A
685 | CalPA | Set WMP-52 | CalPA_Set WMP-52 | 3 | CalPA_Set WMP-52_Q3 | The following questions relate to your WMP Quarterly Data Report for Q2 of 2024, Table 13, received on August 2, 2024, which reports asset-related corrective notifications on electric circuits that were open at the end of the quarter. This follow-up data request seeks information for ALL open work orders in your territory, not only open work orders in High Fire Threat Districts. Please provide any internal categories or codes you use to prioritize asset-related corrective notifications and work orders. For each internal category, please provide: i. your working definition; and ii. the General Order 95, Rule 18 priority level to which it corresponds. | The table below shows PG&E’s internal priority levels and timelines, the corresponding General Order (GO) 95, Rule 18 levels and required timelines, and a description of the priority levels. | Benjamin Katzenberg | 2024-08-19 | 2024-09-06 | 2024-09-06 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_052.zip | 0 | N/A | QDR | N/A | N/A | N/A
686 | CalPA | Set WMP-52 | CalPA_Set WMP-52 | 4 | CalPA_Set WMP-52_Q4 | The following questions relate to your WMP Quarterly Data Report for Q2 of 2024, Table 13, received on August 2, 2024, which reports asset-related corrective notifications on electric circuits that were open at the end of the quarter. This follow-up data request seeks information for ALL open work orders in your territory, not only open work orders in High Fire Threat Districts. Please provide an excel spreadsheet listing open work orders as of July 31, 2024, that were first created: i. Between May 9, 2016 and May 31, 2018. ii. Prior to May 9, 2016. | Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_052- Q004Atch01.xlsx” for the requested information. The following notes provide additional context for data related to Transmission assets: • Notifications 126761436 and 128202924 were created in 2023 and 2024, respectively, from distribution Electric Corrective (EC) notifications and were assigned a notification date (date when the condition was found in the field) from the original distribution EC. • Notification 114337373 was created for broken glass insulators and originally was closed in 2018 after repairs to the insulators. It was reopened in 2023 due to chipped/cracked insulators with a note stating that “insulators are considered as the switch components and cannot be change[d] out without the switch replacement." | Benjamin Katzenberg | 2024-08-19 | 2024-09-06 | 2024-09-06 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_052.zip | 1 | N/A | QDR | N/A | N/A | N/A
687 | CalPA | Set WMP-52 | CalPA_Set WMP-52 | 5 | CalPA_Set WMP-52_Q5 | The following questions relate to your WMP Quarterly Data Report for Q2 of 2024, Table 13, received on August 2, 2024, which reports asset-related corrective notifications on electric circuits that were open at the end of the quarter. This follow-up data request seeks information for ALL open work orders in your territory, not only open work orders in High Fire Threat Districts. Please provide an excel spreadsheet listing work orders that were open as of May 31, 2018. If possible, provide this list in a format and including details consistent with Table 13 of your 2024 Q2 QDR. If some of the information included in Table 13 is not available, please include: i. Work Order Identifier ii. Priority of the original notification, using internal priority level codes in use at the time iii. Date on which the work order was created iv. Date on which the work order was closed. | Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_052- Q005Atch01.xlsx” for the requested information. | Benjamin Katzenberg | 2024-08-19 | 2024-09-06 | 2024-09-06 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_052.zip | 1 | N/A | QDR | N/A | N/A | N/A
688 | CalPA | Set WMP-52 | CalPA_Set WMP-52 | 6 | CalPA_Set WMP-52_Q6 | The following questions relate to your WMP Quarterly Data Report for Q2 of 2024, Table 13, received on August 2, 2024, which reports asset-related corrective notifications on electric circuits that were open at the end of the quarter. This follow-up data request seeks information for ALL open work orders in your territory, not only open work orders in High Fire Threat Districts. Please provide a list of work orders closed in Q1 and Q2 of 2024 using the format and including details consistent with Table 13 of your 2024 Q2 QDR. | Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_052- Q006Atch01.xlsx” for the requested information. The following notes provide additional context on data for Transmission assets: • Some notifications, including the three closed notifications that were created before 2019, were reopened temporarily for administrative reasons, such as delinking from order numbers or making other minor corrections to notification information, and then closed again in 2024. These notifications received an SAP completion date based on the date in 2024 when they were closed following the administrative changes, and not the original closure date. | Benjamin Katzenberg | 2024-08-19 | 2024-09-06 | 2024-09-06 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_052.zip | 1 | N/A | QDR | N/A | N/A | N/A
689 | CalPA | Set WMP-52 | CalPA_Set WMP-52 | 7 | CalPA_Set WMP-52_Q7 | The following questions relate to your WMP Quarterly Data Report for Q2 of 2024, Table 13, received on August 2, 2024, which reports asset-related corrective notifications on electric circuits that were open at the end of the quarter. This follow-up data request seeks information for ALL open work orders in your territory, not only open work orders in High Fire Threat Districts. Please provide the most recent version of your distribution infrastructure inspection checklist. | PG&E does not have a PDF or Excel version of the distribution checklist to provide as the checklist is embedded in an electronic application. As such, a physical copy of the checklist is unavailable, however, please see “WMP-Discovery2023- 2025_DR_CalAdvocates_052-Q007Atch01CONF.pdf” for a copy of the presentation provided to inspectors which outlines the questions and conditions of the current checklist as well as guidance in completing accurately. The specific steps included in the checklist start on page seven of the attachment. | Benjamin Katzenberg | 2024-08-19 | 2024-09-06 | 2024-09-06 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_052.zip | 1 | N/A | QDR | N/A | N/A | N/A
690 | CalPA | Set WMP-52 | CalPA_Set WMP-52 | 8 | CalPA_Set WMP-52_Q8 | The following questions relate to your WMP Quarterly Data Report for Q2 of 2024, Table 13, received on August 2, 2024, which reports asset-related corrective notifications on electric circuits that were open at the end of the quarter. This follow-up data request seeks information for ALL open work orders in your territory, not only open work orders in High Fire Threat Districts. Do you use performance metrics to determine the effectiveness of the changes applied to your distribution infrastructure inspection procedure? i. If yes, please provide a list of the performance metrics including a brief description and how each metric is calculated/determined. ii. If no, please explain how you validate the effectiveness of changes to your inspection process. | PG&E is developing performance metrics to measure the effectiveness of the changes applied to the distribution infrastructure inspection procedure. PG&E is evaluating multiple strategies, which include reviewing the volume of locations that have been escalated, in addition to reviewing the volume of locations that failed in the field, prior to notification execution. As the inspection procedure was recently updated in 2024, PG&E does not plan to finalize performance metrics until at least 2025, to allow for a minimum of one full year of data to be collected and analyzed. | Benjamin Katzenberg | 2024-08-19 | 2024-09-06 | 2024-09-06 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_052.zip | 0 | N/A | QDR | N/A | N/A | N/A
691 | CalPA | Set WMP-52 | CalPA_Set WMP-52 | 9 | CalPA_Set WMP-52_Q9 | The following questions relate to your WMP Quarterly Data Report for Q2 of 2024, Table 13, received on August 2, 2024, which reports asset-related corrective notifications on electric circuits that were open at the end of the quarter. This follow-up data request seeks information for ALL open work orders in your territory, not only open work orders in High Fire Threat Districts. Do you use performance metrics to determine the effectiveness of your bundling approach to remediating open work orders (as described in Advice Letter 7167-E-A)? i. If yes, please provide a list of the performance metrics including a brief description and how each metric is calculated/determined. ii. If no, please explain how you validate the effectiveness of your bundling approach to remediation of open work orders. | i. Yes, PG&E uses performance metrics to determine the effectiveness of the bundling approach to remediate open work orders as described in the referenced Advice Letter. Please see below for the requested description for each metric. Bundling Percentage - The percent of completed tags that were bundled through Operational Bundling. Metric Calculation/Description: The percent of completed tag jobs that were bundled with other work. A notification is considered bundled if it was completed on the same day as another job in the same isolation zone OR was completed on the same isolation zone during the duration of another longer term job. Bundled Unit Cost Reduction – The percent reduction in unit cost of the bundled work compared to the 2023 Unit Cost. Metric Calculation/Description: The percent difference between an operationally bundled tag's or Mega Bundle tag’s unit cost and the 2023 unit cost. For operational bundling, this is measured for internally resourced jobs. For Mega Bundle's frozen scope of work, this is measured through a mix of internally resourced work and work contracted through a competitive lowest cost bidding process. Mega Bundle Completion - The percent completion of 2024 Mega Bundle Scope. Metric Calculation/Definition: The number of completed tags in the Mega Bundle scope divided by the number of total tags within the Mega Bundle scope. Please note, The Mega Bundle Scope includes Circuit Projects which combine approximately 10,000 individual scopes of work to be executed collectively as projects by circuit and isolation zone. Through these bundled scopes, it allows for effective planning to increase productivity, reduce truck rolls, minimize planned customer outages, and achieve cost-effective negotiated contract pricing. ii. Not applicable. Please see response to subpart (i). | Benjamin Katzenberg | 2024-08-19 | 2024-09-06 | 2024-09-06 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_052.zip | 0 | N/A | QDR | N/A | N/A | N/A
692 | CalPA | Set WMP-52 | CalPA_Set WMP-52 | 10 | CalPA_Set WMP-52_Q10 | The following questions relate to your WMP Quarterly Data Report for Q2 of 2024, Table 13, received on August 2, 2024, which reports asset-related corrective notifications on electric circuits that were open at the end of the quarter. This follow-up data request seeks information for ALL open work orders in your territory, not only open work orders in High Fire Threat Districts. In Table 13 of your 2024 Q2 QDR, there are 139 X tags (which require completion within 7 days) with an average of 29 days past due. i. Please explain what delay factors PG&E has encountered in remediation of X tags. ii. How does PG&E intend to address delays in completing X tags? iii. What has been PG&E’s average completion time for X tags in the first half of 2024? In other words, for all X tags closed in the first half of 2024, what was the average number of days open? | PG&E disagrees with the statement that there are 139 X tags with an average of 29 days past due in Table 13 of the 2024 Quarter 2 Quarterly Data Report (QDR). Please see Columns E-F of attachment “WMP-Discovery2023-2025_DR_CalAdvocates_052- Q010Atch01.xlsx” which shows that of the 139 X Tags referenced, PG&E completed work on an average of three days. i. Factors that can contribute to potential delays in completing tag work can include work that starts on day seven and is not able to be completed until day eight, a lack of resources when critical emergencies need to be prioritized, and a syncing issue that was identified in June 2024 between iPads (used to create tags) and SAP (PG&E’s system of record). This issue occurred when users were in low network mode, no network, or airplane mode, and created a delay in seeing tags needing to be completed. ii. PG&E underwent a syncing enhancement update in August 2024 which now requires users to resolve syncing issue before proceeding with other work. iii. In the first half of 2024, PG&E has been able to average completing work on X tags in approximately 2.4 days. | Benjamin Katzenberg | 2024-08-19 | 2024-09-06 | 2024-09-06 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_052.zip | 1 | N/A | QDR | N/A | N/A | N/A
693 | CPUC - SPD (Safety Policy Division) | 019 | CPUC - SPD (Safety Policy Division)_019 | 1 | CPUC - SPD (Safety Policy Division)_019_Q1 | Explain why the median corrective action time for a level 1 finding exceeded 1 day in table 2 of the 2024 Q2 QDR. [See metric “Time between level 1 asset inspection finding and resulting maintenance activity” which includes – metric numbers 3.d.2.a through 3.t.4.a). | There are several reasons why a median corrective action time for a Level 1 finding could exceed one day. Some examples of delays are discussed below. PG&E will immediately respond to all Level 1 (A priority) notifications and immediately repair the condition (fully or temporarily), not to exceed the next day. In situations where immediate resolution is not possible, PG&E will continuously monitor the nonconformance until it is mitigated. The associated notification will be closed as soon as possible following infield mitigation. Closure of a notification will take place after the work has been verified with applicable documentation and photo evidence uploaded into SAP. Additionally, night emergency work will occasionally stay open until the next day when higher quality pictures that verify mitigation can be taken to document the work completion. Also, if the Level 1 condition was temporarily mitigated but more repairs were needed, this could exceed one day for ongoing work still needing to be addressed. Finally, some notifications reported in the Quarterly Data Report (QDR) originated as Level 2 or 3 and later were escalated to Level 1, for example, through a field safety reassessment. Since the timelines for the original priority levels were longer, the time between the finding and closure of these notifications will exceed one day. | Henry Sweat | 2024-08-29 | 2024-09-12 | 2024-09-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_019.zip | 0 | N/A | QDR | N/A | N/A | N/A
694 | CPUC - SPD (Safety Policy Division) | 019 | CPUC - SPD (Safety Policy Division)_019 | 2 | CPUC - SPD (Safety Policy Division)_019_Q2 | Provide a breakdown of all of the level 1 asset findings or corrective actions (per GO 95 Priority Level) that made up the results of table 2. SPD requests a table containing the following columns with each level 1 asset inspection for years 2020 Q1 through present listed on the Y axis. Follow the attached excel formatting: 1. Work Order Number 2. Asset Type (overhead, underground) 3. Line Type (Transmission, Distribution-Primary, Distribution-Secondary) 4. PG&E Tag Priority 5. Longitude 6. Latitude 7. Location (Division) 8. Date created / found 9. Completion date (If applicable) 10. Method found (inspection, normal order of work, storm work) 11. GO 95 Required Compliance Date, 12. Location (HFTD Tier 2, HFTD Tier 3, HFTD Zone 1, HFRA (Non-HFTD), Non HFTD/Non HFRA)), 13. Segment ID 14. Circuit ID 15. Wire down Event ID (If Applicable) 16. Outage event ID (If Applicable) 17. Facility Damage Action (FDA) 18. Cause / Notes 19. Explanation for a non-immediate repair. If repair took longer than 1 day to complete, explain reason why. | Please see attachment “WMP-Discovery2023-2025_DR_SPD_019- Q002Ath01CONF.xlsx” for the requested information. Please note, the last maintenance date for each asset was included in the provided template (Column R), however, it was not included in the narrative of the data request. Since providing the last maintenance date requires a substantial amount of manual data gathering, please let us know if this information is being requested. If so, we would greatly appreciate some additional time to provide this information. We would be happy to meet and confer on this issue if it would be helpful. Notes: • “Location (Division)” (#7): Transmission maintenance work is organized by work center and not division. Work center is provided in response to this question. • “Method found” (#10): Method is tracked through manually added statuses for different inspection and patrol types. These are the same statuses used to derive the QDR Table 2 inspection type and method. • “Wire down event ID” (#15): Wire down event IDs are outage event IDs for which a wire down was noted. • “Outage event ID” (#16): Outage events are not directly associated with tags and were matched to tags using the circuit and date. If the same circuit experienced multiple outages on the same date, all outage IDs from that date are listed. • “Cause/notes” (#18) and “explanation for non-immediate repair” (#19): The long text comments are provided and are the only readily queried source of information related to the cause and available explanations for non-immediate repair. | Henry Sweat | 2024-08-29 | 2024-09-12 | 2024-09-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_019.zip | 1 | N/A | QDR | N/A | N/A | N/A
694 | CPUC - SPD (Safety Policy Division) | 019 | CPUC - SPD (Safety Policy Division)_019 | 2(sf) | CPUC - SPD (Safety Policy Division)_019_Q2(sf) | SPD is trying to look at the P1 data sent to us. PG&E has always described P1s as being addressed immediately, but if you look at the closed date – a large number of the tags are closed multiple days after they were created. When we looked closer at the data, we found that for some of them, the field work was completed or other make safe work was performed on the day the tag was created, but the tag was not closed until later. The DR states we should read the comments to understand why the tags were closed later, but this is difficult when roughly 60,000 distribution tags were completed more than one day after the creation date. Advise on the best way to determine the field work/make safe completed by date. Should we meet to discuss, or should we issue a supplemental data request where PG&E determines the date? | Please note, the supplemental response to Question 002 responds to the clarification SPD was seeking on September 20, 2024, regarding the closure dates included for Priority 1 A tags. PG&E initially fulfilled this request by providing the date the notification was closed in SAP, the system of record. PG&E has updated this attachment to include the date the work was completed, which is reflected in Column J. Note, Canceled notifications will not have a completed-on date. As explained in “WMP-Discovery2023-2025_DR_SPD_019-Q001,” submitted to the SPD on September 12, 2024, PG&E will respond to a level 1 notification immediately, however, the notification will not be closed until all supporting information has been documented in SAP. Please see “WMP-Discovery2023-2025_DR_SPD_019-Q002Supp01Atch01CONF.xlsx” for the updated attachment. | Henry Sweat | 2024-09-20 | 2024-10-07 | 2024-10-03 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_019.zip | 1 | N/A | QDR | N/A | N/A | N/A
695 | CPUC - SPD (Safety Policy Division) | 019 | CPUC - SPD (Safety Policy Division)_019 | 3 | CPUC - SPD (Safety Policy Division)_019_Q3 | Explain if a same day repair would be designated as 0 or 1 day in table 2. | PG&E designates same day repairs as “0” in table 2. | Henry Sweat | 2024-08-29 | 2024-09-12 | 2024-09-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_019.zip | 0 | N/A | QDR | N/A | N/A | N/A
696 | CPUC - SPD (Safety Policy Division) | 019 | CPUC - SPD (Safety Policy Division)_019 | 4 | CPUC - SPD (Safety Policy Division)_019_Q4 | Table 13 in the Q2 2024 QDR lists Work Order number 121706053 as an open level 1 work order originating on July 9th 2021. Provide the work order and background information regarding this asset including why this work order remained open as of 6/30/2024. | Please see attachment “WMP-Discovery2023-2025_DR_SPD_019- Q004Atch01CONF.pdf” for the requested work order. Tag 121706053 was reopened on August 1, 2024, for correction of closure. Originally the tag was closed out as COMP (completed) but when it was reopened, it was corrected to CNCL (canceled) due to being a duplicate location to a lower priority tag, where the work was completed. Please see the comments included on the work order for additional information. | Henry Sweat | 2024-08-29 | 2024-09-12 | 2024-09-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_019.zip | 1 | N/A | QDR | N/A | N/A | N/A
697 | CPUC - SPD (Safety Policy Division) | 019 | CPUC - SPD (Safety Policy Division)_019 | 5 | CPUC - SPD (Safety Policy Division)_019_Q5 | Table 13 in the Q2 2024 QDR lists Work Order numbers 128769192 and 129125787 as open as of 6/30/2024. Provide the work orders and discuss why these work orders remained open as of 6/30/2024. | Please see attachment “WMP-Discovery2023-2025_DR_SPD_019- Q005Atch01CONF.pdf” for Electric Corrective (EC) tag 128769192 and attachment “WMP-Discovery2023-2025_DR_SPD_019-Q005Atch02CONF.pdf” for Line Corrective (LC) tag 129125787. PG&E is still researching Notification 128769192 and will follow up with additional details as to why the work order stayed open as of June 30, 2024, as soon as possible. July 3, 2024. Once created, PG&E needed to wait until the customer could repair their weather head to coordinate the service installation. The notification was also pending clerical processing to close out the completed paperwork, however, is now closed in SAP. Notification 129125787 was not closed in SAP until July 1, 2024; however, the work was completed in the field on June 26, 2024, per the long text comment generated by the Construct application. | Henry Sweat | 2024-08-29 | 2024-09-12 | 2024-09-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_019.zip | 2 | N/A | QDR | N/A | N/A | N/A
697 | CPUC - SPD (Safety Policy Division) | 019 | CPUC - SPD (Safety Policy Division)_019 | 5(s) | CPUC - SPD (Safety Policy Division)_019_Q5(s) | Table 13 in the Q2 2024 QDR lists Work Order numbers 128769192 and 129125787 as open as of 6/30/2024. Provide the work orders and discuss why these work orders remained open as of 6/30/2024. | Work on notification 128769192 was completed on May 13, 2024. The tag remained open, as it was pending closure. | Henry Sweat | 2024-08-29 | 2024-09-20 | 2024-09-20 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_019.zip | 0 | N/A | QDR | N/A | N/A | N/A
698 | CPUC - SPD (Safety Policy Division) | 019 | CPUC - SPD (Safety Policy Division)_019 | 6 | CPUC - SPD (Safety Policy Division)_019_Q6 | SPD observed discrepancies in table 2 regarding the reporting unit used for the category 3 - Time between level 1 asset inspection finding and resulting maintenance activity. The 2023 QDRs designate this time in days, while the first two quarters of the 2024 QDR list hours as their unit of measure. There is also a note on the 2024 QDRs listing the following: “Please note that PGE is reporting this metric in Days as the duration of correcting these infractions are typically in months.” Please confirm if this metric has been reported in days and why the 2024 QDRs is listing the measurement in hours. | The fields in PG&E’s System of Record, SAP, are recorded in days. As such, PG&E is reporting the referenced metric in days in the QDR. In 2023, PG&E modified the QDR template to change the metric from days to hours. PG&E was asked by Energy Safety not to modify the QDR template metrics going forward. In 2024, PG&E added a note to the referenced table in the QDR reports to note that even though the metric column reflects hours, the units of measurement are still reflective of days due to system limitations. | Henry Sweat | 2024-08-29 | 2024-09-12 | 2024-09-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_019.zip | 0 | N/A | QDR | N/A | N/A | N/A
699 | CPUC - SPD (Safety Policy Division) | 019 | CPUC - SPD (Safety Policy Division)_019 | 7 | CPUC - SPD (Safety Policy Division)_019_Q7 | Submit the following documents for a pole which (1) has a pole loading calculation and (2) was identified by the pole test and treat inspection program to have 40% or less remaining strength: • Pole test and treat inspection report • The procedures used to perform and pole test and treat • Work order for the pole • The calculation (in spreadsheet form) for the remaining strength. The spreadsheet submitted should be able to modifiable so that SPD can recalculate parameters depending on different properties. • Papers or testing data which justifies the methodology used to calculate the remaining strength. • The pole loading calculation. • A description of actions taken by PG&E after the inspection. | PG&E has identified Pole 100884900 (subject pole), which has both a Pole Loading Calculation (PLC) and was identified by the Pole Test and Treat (PTT) program to have less than 40% Remaining Strength (RS). Please see explanations below and referenced attachments for each of the bullets from the original question. • PTT inspected the subject pole on December 5, 2023. Please see attachment “WMP-Discovery2023-2025_DR_SPD_019-Q007Atch01CONF.pdf” for the PTT inspection report. • PTT utilized Utility Procedure, TD-2325P-01, Revision 3 to inspect the subject pole. Please see attachment “WMP-Discovery2023-2025_DR_SPD_019- Q007Atch02CONF.pdf” for the Utility Procedure. • PTT rejected the subject pole on December 5, 2023, recommending replacement. PTT generated Electric Corrective (EC) Notification 127543038 to replace the subject pole. Please see attachment “WMP-Discovery2023-2025_DR_SPD_019- Q007Atch03CONF.pdf” for the EC notification. • PG&E intrusive inspectors utilize our Inspect Application to document their inspections. The Inspect Application has a strength calculator (D-Calc) built into the intrusive inspection checklist, which is used to document the decay observed and results in a remaining strength. PG&E welcomes the opportunity to demonstrate the Inspect Application and embedded strength calculator to SPD. • PG&E purchased D-Calc from EDM and integrated the strength calculator into the Inspect Application. Please see attachment “WMP-Discovery2023- 2025_DR_SPD_019-Q007Atch04.pdf” for EDM’s D-Calc software manual from July 2015. • PG&E Estimating team performed a PLC for Pole 100884900. Please see attachment “WMP-Discovery2023-2025_DR_SPD_019-Q007Atch05CONF.pdf” for the PLC. • PTT inspected this pole on December 5, 2023. PG&E’s Estimating team performed a PLC for this pole in February 2024, which indicated a Bending Safety Factor (SF) of 1.33. Due to the low SF, the Asset Strategy team upgraded the EC Notification to a Priority-B replacement, due within 6-Months. The EC Notification was estimated, permitted and provided to construction for execution. Pole 100884900 was replaced on June 19, 2024. | Henry Sweat | 2024-08-29 | 2024-09-12 | 2024-09-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_019.zip | 3 | N/A | 8 | Section 8.1.3 - Asset Inspection | 8.1.3.2.4 LiDAR based Pole Loading Assessments | N/A
700 | CPUC - SPD (Safety Policy Division) | 019 | CPUC - SPD (Safety Policy Division)_019 | 8 | CPUC - SPD (Safety Policy Division)_019_Q8 | In response to SPD_016-Q15, PG&E stated it completed pole loading desktopbased assessments for 530,000 poles in the HFTD area. SPD understands a subset of these poles are undergoing further engineering analysis. Submit the following for each of the 530,000 poles in the HFTD area that was assessed as part of the desktop-based assessment (see the attached spreadsheet for the template): • SAP ID, • Horizontal Loading Criteria (for cylindrical shapes), • Loading Type (Heavy or Light), • Safety Factor Calculated by Desktop-based assessment, • Yes/No for Undergoing Further Engineering Assessment. | Please see “WMP-Discovery2023-2025_DR_SPD_019-Q002Ath01CONF.xlsx” for the requested data for the approximately 530,000 poles in HFTD areas that have completed pole loading desktop-based assessments, plus an additional approximately 16,000 poles that are in the buffer areas surrounding the HFTD areas. These poles have also received a desktop-based pole loading assessment. In addition to Pole SAP Equipment ID, Horizontal Loading Criteria, Loading Type, Safety Factor (SF), and Yes/No for Undergoing Further Engineering Assessment, we have included Grade of Construction (GOC) and Maximum Capacity Utilization (MCU). PG&E has included GOC because it is a critical data element when assessing the poles loading capability. In addition, MCU is included because it is an easier to compare data point, as it is essentially a SF percentage that incorporates the GOC. Therefore, with MCU, it is possible to understand the loading capacity of the pole with just the one data point. Please understand that for all poles that are undergoing further engineering assessment, PG&E has not reported SF or MCU, as these are currently in-progress. We would be happy to meet to review this data with you to discuss the program more in-depth if it would be helpful. | Henry Sweat | 2024-08-29 | 2024-09-12 | 2024-09-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_019.zip | 0 | N/A | 8 | Section 8.1.3 - Asset Inspection | 8.1.3.2.4 LiDAR based Pole Loading Assessments | N/A
701 | CPUC - SPD (Safety Policy Division) | 019 | CPUC - SPD (Safety Policy Division)_019 | 9 | CPUC - SPD (Safety Policy Division)_019_Q9 | Submit one example of a one desktop-based assessment pole loading calculation for an unguyed tangent pole and highlight where the criteria submitted in the spreadsheet as part of question 8 may be obtained from the calculation. | Please reference attachments “WMP-Discovery2023-2025_DR_SPD_019- Q009Atch01.pdf” and “WMP-Discovery2023-2025_DR_SPD_019-Q009Atch02.pdf” for one desktop-based assessment Pole Loading Calculation (PLC) for an un-guyed tangent pole with the criteria submitted as part of Question 008, also listed below, highlighted for reference. • Pole SAP ID • Horizontal Loading Criteria • Loading Type • Safety Factor • Grade of Construction • Maximum Capacity Utilization Attachment “WMP-Discovery2023-2025_DR_SPD_019-Q009Atch01.pdf” is the PLC that resulted from the Desktop-Based Assessment. This PLC utilized the conductors from our EDGIS system of record, which indicated that the pole had #4CU conductor on one side and 2ACSR on the other side. Please see Figure 1 on “WMP-Discovery2023- 2025_DR_SPD_019-Q009Atch03CONF.pdf”. These conductors resulted in the pole being imbalanced, and presumed to be overloaded, as both sets of conductors are at full tension and double dead-ended at the subject pole. “WMP-Discovery2023-2025_DR_SPD_019-Q009Atch02CONF.pdf” is the PLC that resulted from the Further Engineering Assessment. This PLC utilized enhanced imagery and work management records from SAP to recognize that the #4CU conductor is actually 2ACSR conductor in the field. Please see Figure 2 on “WMP-Discovery2023- 2025_DR_SPD_019-Q009Atch03CONF.pdf”. The correction that the pole is not double dead ended and has 2ACSR on both sides balanced the subject pole and validated that it is not in an overloaded condition. | Henry Sweat | 2024-08-29 | 2024-09-12 | 2024-09-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_019.zip | 3 | N/A | 8 | Section 8.1.3 - Asset Inspection | 8.1.3.2.4 LiDAR based Pole Loading Assessments | N/A
702 | CPUC - SPD (Safety Policy Division) | 019 | CPUC - SPD (Safety Policy Division)_019 | 10 | CPUC - SPD (Safety Policy Division)_019_Q10 | When will the further engineering assessment be completed? | G&E currently plans to risk prioritize the locations that require engineering assessment and complete all the subject engineering analysis by end of Quarter 2 of 2026. | Henry Sweat | 2024-08-29 | 2024-09-12 | 2024-09-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_019.zip | 0 | N/A | 8 | Section 8.1.3 - Asset Inspection | 8.1.3.2.4 LiDAR based Pole Loading Assessments | N/A
703 | CPUC - SPD (Safety Policy Division) | 019 | CPUC - SPD (Safety Policy Division)_019 | 11 | CPUC - SPD (Safety Policy Division)_019_Q11 | For inspectors for PG&E’s distribution overhead inspection programs, (1) how are future weather conditions profiled to inspectors, (2) when would and how would an inspector consider weather conditions when prioritizing a work order as Priority A, X, B, E or F (such as an inspector seeing a vulnerable asset and also having knowledge of high winds incoming)? | 1) PG&E Inspector Training advises inspectors to check the weather reports each morning before they report to the field. This can be done in multiple ways, including checking the weather application on their cell phone and/or reviewing daily emails from PG&E’s meteorology department. 2) Inspectors take into consideration the weather conditions in recommending a priority level when creating Electric Corrective (EC) notifications for compelling abnormal conditions. Per the formal inspector training, inspectors learn they can assign default priorities for many scenarios, including weather conditions. | Henry Sweat | 2024-08-29 | 2024-09-12 | 2024-09-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_019.zip | 0 | N/A | 8 | Section 8.1.3 - Asset Inspection | 8.1.3 Asset Inspections | N/A
704 | CPUC - SPD (Safety Policy Division) | 019 | CPUC - SPD (Safety Policy Division)_019 | 12 | CPUC - SPD (Safety Policy Division)_019_Q12 | Describe Focus Tree Inspection progress thus far in 2024 (provide the date at which the data is current through in the response). Include the following: • Number of total trees prescribed to be worked • Number of total trees worked thus far • Number of total trees prescribed for removal • Number of total trees removed thus far • Number of miles inspected • Number of strike trees inspected • Number of strike trees per mile of lines inspected before removals • Number of strike trees per mile after removals • Number of trees inspected • Confirm the number of strike trees inspected, number of miles inspected and number of trees removed in the pilot program in 2023. • The Q2 2023 QDR seems to state $0 dollars were spent, please explain (see row 49 and Table 11). Provide an update comparing costs estimated as part of the Revision Notice compared to forecasted costs for the rest of the year and the costs currently incurred. Explain any variance. | Please see the following data for the requested information through September 6, 2024: • Number of trees prescribed to be worked: 51,374 • Number of total trees worked thus far: 2,116 • Number of total trees prescribed for removal: 42,101 • Number of total trees removed thus far: 1,750 • Number of miles inspected: 1,122.6 • Number of strike trees per mile of lines inspected before removals: 45.76 • Number of strike trees per mile after removals: 8.26 • Number of trees inspected: 760,893 • Number of strike trees inspected in 2023: 7,393 • Number of miles inspected in 2023: 273.93 • Number of trees removed in 2023: 5,030 • PG&E believes this question is referring to the Quarter 2 2024 QDR where in row 49 in Table 11 there is $0 for Vegetation Management Activity ‘Clearance’. PG&E is capturing VM-03 under Fall-In Mitigation Activity in row 51. The costs for VM-03 specifically are as follows: o 2023 Recorded: $27.3M which was a portion of the total of $75.5M for Fall-In Mitigation. o 2024 Forecast: $216.4M which was a portion of the total of $309M for FallIn Mitigation. o 2025 Forecast: PG&E will provide an update for this year in the next QDR. | Henry Sweat | 2024-08-29 | 2024-09-12 | 2024-09-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_019.zip | 0 | N/A | 8.2.2.2.5 | Vegetation Management and Inspections | Focused Tree Inspections | N/A
704 | CPUC - SPD (Safety Policy Division) | 019 | CPUC - SPD (Safety Policy Division)_019 | 12(a) | CPUC - SPD (Safety Policy Division)_019_Q12(a) | SPD understands FTI program was performed on areas with 45.76 strike trees per mile. Separately, SPD understands PG&E has roughly 200 strike trees per mile across its HFTD. SPD understands that number of trees is not equal to risk – but is surprised that this program is being performed in areas with less strike trees per mile. Can you double check that the number is correct given this context? | PG&E amends its response to “WMP-Discovery2023-2025_DR-SPD_019-Q012.pdf,” submitted to SPD on September 12, 2024. PG&E originally calculated the number of strike trees per mile inspected before and after removal using the number of trees prescribed to be worked. This calculation has been revised to instead factor the number of trees inspected. As of September 27, 2024, PG&E confirms the average number of strike trees per mile of lines inspected on Focused Tree Inspection (FTI) prior to removal is 677.80. Please see the calculation below for how this number was determined: Average number of strike trees per mile of lines inspected on FTI prior to removal Number of trees inspected: 760,893 Number of miles inspected:1,122.6 760,893 / 1,122.6 = 677.80 As of September 27, 2024, PG&E confirms the average number of strike trees per mile of lines inspected after removals is 640.30. Please see the calculation below for how this number was determined: Average number of strike trees per mile of lines inspected after removal Number of trees inspected: 760,893 Number of total trees prescribed for removal: 42,101 Number of miles inspected:1,122.6 (760,893 – 42,101) / 1,122.6 = 640.29 Please see the following data for the requested information through September 6, 2024: • Number of trees prescribed to be worked: 51,374 • Number of total trees worked thus far: 2,116 • Number of total trees prescribed for removal: 42,101 • Number of total trees removed thus far: 1,750 • Number of miles inspected: 1,122.6 • Number of strike trees per mile of lines inspected before removals: 45.76 677.80 • Number of strike trees per mile after removals: 8.26 640.29 • Number of trees inspected: 760,893 • Number of strike trees inspected in 2023: 7,393 • Number of miles inspected in 2023: 273.93 • Number of trees removed in 2023: 5,030 • PG&E believes this question is referring to the Quarter 2 2024 QDR where in row 49 in Table 11 there is $0 for Vegetation Management Activity ‘Clearance’. PG&E is capturing VM-03 under Fall-In Mitigation Activity in row 51. The costs for VM-03 specifically are as follows: o 2023 Recorded: $27.3M which was a portion of the total of $75.5M for Fall-In Mitigation. o 2024 Forecast: $216.4M which was a portion of the total of $309M for Fall-In Mitigation. o 2025 Forecast: PG&E will provide an update for this year in the next QDR. | Henry Sweat | 2024-09-20 | 2024-10-02 | 2024-10-01 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_019.zip | 0 | N/A | 8.2.2.2.5 | Vegetation Management and Inspections | Focused Tree Inspections | N/A
705 | CPUC - SPD (Safety Policy Division) | 019 | CPUC - SPD (Safety Policy Division)_019 | 13 | CPUC - SPD (Safety Policy Division)_019_Q13 | Provide Ignition reports (also known as PIIRs) for CPUC reportable ignitions that occurred on R3+ days in 2024. | PG&E is still preforming investigations for some ignitions that occurred on R3+ days in 2024. PG&E has provided reports for ignitions where its investigations have concluded. Please see the table below for the Preliminary Ignition Investigation Report (PIIR) for CPUC reportable ignitions that occurred on R3+ days in 2024. CPUC Reportable Ignition Date of Ignition Attachment Name 20240455 May 21, 2024 WMP-Discovery2023-2025_DR_SPD_019- Q013Atch01CONF.pdf 20240610 June 8, 2024 WMP-Discovery2023-2025_DR_SPD_019- Q013Atch02CONF.pdf 20240655 June 15, 2024 WMP-Discovery2023-2025_DR_SPD_019- Q013Atch03CONF.pdf 20240753 June 25, 2024 WMP-Discovery2023-2025_DR_SPD_019- Q013Atch04CONF.pdf 20240770N June 27, 2024 WMP-Discovery2023-2025_DR_SPD_019- Q013Atch05CONF.pdf 20240909N July 9, 2024 WMP-Discovery2023-2025_DR_SPD_019- Q013Atch06CONF.pdf 20240949 July 14, 2024 WMP-Discovery2023-2025_DR_SPD_019- Q013Atch07CONF.pdf Please note, these reports are preliminary and are based on available information at the time they were drafted. Event data is subject to change based upon subsequently discovered information. | Henry Sweat | 2024-08-29 | 2024-09-12 | 2024-09-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_019.zip | 7 | N/A | Appendix D | Appendix D - Areas for Continued Improvement | ACI PG&E-22-06 – Addressing Increase in Risk Events | N/A
706 | CPUC - SPD (Safety Policy Division) | 019 | CPUC - SPD (Safety Policy Division)_019 | 14 | CPUC - SPD (Safety Policy Division)_019_Q14 | Provide Ignition reports (also known as PIIRs) for CPUC reportable ignitions that occurred on days when EPSS was enabled in 2024. Reports already provided in response to Question 13 need not be resubmitted in response to Question 14. | PG&E interprets this request as asking for ignition reports for CPUC reportable ignitions which occurred on primary lines on EPSS enabled circuits in 2024. PG&E is still undergoing investigations for some ignitions that occurred on days when EPSS was enabled in 2024. PG&E has provided reports for ignitions where the investigations have concluded. Please see the table below for PIIRs for CPUC reportable ignitions which occurred on primary lines on EPSS enabled circuits in 2024 that were not provided in Question 13. CPUC Reportable Ignition Date of Ignition Attachment Name 20240434 May 18, 2024 WMP-Discovery2023-2025_DR_SPD_019- Q014Atch01CONF.pdf 20240605 June 7, 2024 WMP-Discovery2023-2025_DR_SPD_019- Q014Atch02CONF.pdf Please note, these reports are preliminary and are based on available information at the time they were drafted. Event data is subject to change based upon subsequently discovered information. | Henry Sweat | 2024-08-29 | 2024-09-12 | 2024-09-12 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_019.zip | 2 | N/A | Appendix D | Appendix D - Areas for Continued Improvement | ACI PG&E-22-06 – Addressing Increase in Risk Events | N/A
707 | CPUC - SPD (Safety Policy Division) | 020 | CPUC - SPD (Safety Policy Division)_020 | 1 | CPUC - SPD (Safety Policy Division)_020_Q1 | Please provide a copy of the example spreadsheet with data discussed and presented in the meeting of 8/26/2025 at 9am-10am between PG&E and CPUC/SPD with the agenda as follows: a. Provide and discuss additional example(s) in the WMP Cost Reporting Template with a goal of providing all mitigation initiatives by end of September (when Final Decision on WMP is expected). | PG&E includes the following attachment of the WMP Cost Reporting Template in draft version that we reviewed with SPD on August 26: Attachment “WMP-Discovery2023- 2025_DR_SPD_020-Q001Atch01.xlsx.” This file contains the sample initiatives discussed with SPD on August 5 (System Hardening Distribution and 10k Undergrounding) and the initiatives discussed on August 26 (HFTD/HFRA Open Tag Reduction – Transmission; HFTD/HFRA Open Tag Reduction – Distribution Backlog; and Eliminate HFTD HFRA Distribution Backlog). The information provided is a sample of the level of detail PG&E proposes to provide in response to the template provided by SPD. We have referenced prior filings to populate this sample draft version; however, open questions remain as indicated in the template. “WMP-Discovery2023-2025_DR_SPD_020-Q001Atch01.xlsx” is the original template sent out by SPD and does not reflect any template changes discussed on August 26. | Edwin Schmitt | 2024-08-27 | 2024-09-04 | 2024-09-04 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_020.zip | 1 | N/A | 4.3 | 4.0 Overview of WMP | 4.3 Proposed Expenditures | 2.3 Expenditures
708 | CPUC - SPD (Safety Policy Division) | 021 | CPUC - SPD (Safety Policy Division)_021 | 1 | CPUC - SPD (Safety Policy Division)_021_Q1 | 1. Complete tabs 2 through 6 of the attached spreadsheet. For tabs 2 through 5, complete a corresponding data row for each of the 114 mitigation initiatives in the most recent QDR, Table 11 according to the directions in the spreadsheet and the two attached guidance documents listed below: • Guidance for WMP Cost Reporting (applicable to tab 2 through 5) • Guidance for Account Tracking (applicable to tab 6) | PG&E and SPD met on September 27, 2024, to discuss clarifications within this request as well as a tranche schedule for production. Per this meeting, and follow up correspondence from SPD received October 1, 2024, PG&E will submit data on a weekly basis in tranches to SPD, with all data being submitted by November 1, 2024. PG&E would like to clarify that there are 109 activities with costs related to the Wildfire Mitigation Plan (WMP). PG&E is providing Columns A-G of the “General Info (1 of 5)” worksheet in Tranche 1, as well as information regarding SB 884. Please see attachment “WMP-Discovery2023-2025_DR_SPD_021-Q001Atch01.zip” for Tranche 1 of this request. Please see the following explanations per the instructions to report on the Utility Tracking ID included in Table 11 from the most recent Quarterly Data Report (QDR). Table 11 of the QDR includes: • WMP Initiative Categories (Column B); • WMP Initiative Activities (Column C), which are a subset of initiative categories; and • Utility Initiative Tracking IDs (UITID) (Column D) for WMP commitments. Table 11 shows some costs at the level of a specific commitment, such as CO-05 or GH-07, while it shows others at the level of an Initiative Activity. Within the latter group, Table 11 shows that some Initiative Activities have associated commitments, while others do not. In this data request response, PG&E listed each commitment in its own row, and, for those Initiative Activities with no associated commitments, listed each remaining Initiative Activity (‘Emergency Preparedness Plan’, ‘Fire Potential Index’) as its own row. PG&E used naming and unique keys consistent with both the QDR and the WMP to identify each row. For commitments, PG&E used the UITIDs, which can be found in Table 1 of the QDR, and for Initiative Activities with no commitments, PG&E used Table PG&E-A-2: Definitions of Initiatives – By Category in the WMP (version R6 pp. 990-996), located at the following link: https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/pge-wmp-r6-07052024.pdf. Please see the following clarifications regarding “Section E” of the attachment included in this request: Regarding “Section E: SB 884 Activity,” PG&E anticipates submitting its SB 884 Electric Undergrounding Plan in 2025. Work forecast in the SB 884 Electric Undergrounding Plan will begin in 2027. Therefore, there are no forecast units and no forecast costs for SB 884 in 2023, 2024, or 2025. | Kevin Miller | 2024-09-10 | 2024-10-04 | 2024-10-04 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_021.zip | 1 | N/A | 4.3 | 4.0 Overview of WMP | 4.3 Proposed Expenditures | 2.3 Expenditures
708 | CPUC - SPD (Safety Policy Division) | 021 | CPUC - SPD (Safety Policy Division)_021 | 1(s) | CPUC - SPD (Safety Policy Division)_021_Q1(s) | 1. Complete tabs 2 through 6 of the attached spreadsheet. For tabs 2 through 5, complete a corresponding data row for each of the 114 mitigation initiatives in the most recent QDR, Table 11 according to the directions in the spreadsheet and the two attached guidance documents listed below: • Guidance for WMP Cost Reporting (applicable to tab 2 through 5) • Guidance for Account Tracking (applicable to tab 6) | Please see attachment “Please see attachment “WMP-Discovery2023-2025_DR_SPD_021-Q001Atch01.zip” for Tranche 2/Supp01 of this request. Regarding the “General Info (1 of 5)” worksheet, PG&E is providing the Risk Spend Efficiency (RSE) from the 2023 GRC application as available, as Cost-Benefit Ratios (CBR)s were not calculated when the 2023 GRC was filed. The Column labeled “Cost requested in original GRC Application ($000s)” has been completed based on PG&E’s 2023 GRC Reply Brief (December 9, 2022) with the non-labor escalation update. The Column labeled “GRC Activity Section and Page Number” refers to the sections as filed in the 2023 GRC February 25, 2022, update and the page number is as reported in the table of contents for the Exhibit and Chapter for the referenced section. Please see the following clarifications for Sections of the attachment included in this request. Note, data is not included in worksheets “non-HFTD, CapEx (4 of 5)” or “non-HFTD, OpxEx (5 of 5)” as costs reported in this Tranche only reflect High Fire Threat District (HFTD) work. Regarding “Section A: “WMP Cost and Unit Data”, PG&E will provide recorded costs for 2023 and forecast costs for 2024 and 2025. Units have been provided for unitized WMP initiatives in the “HFTD, CapEx (2 of 5)” worksheet. Please see “General Info (1 of 5)” worksheet, Column "Type of Units (e.g., miles, # of inspections, # of poles repaired/replaced, etc.)" for initiatives with corresponding units. Note, these units have not been replicated in the “HFTD, OpEx (3 of 5)” worksheet as PG&E did not want to appear to be duplicating these units. Regarding “Section B: Costs and Units Authorized in Last GRC,” the column requesting “Costs authorized in last GRC (2023 ($) for WMP 2023”, represents PG&E’s final escalated General Rate Case (GRC) forecasts. Regarding “Section C: Costs and Units Forecast to be Requested in the Next GRC,” PG&E is unable to provide forecasted data for the next GRC submission at this time as it is still under development. This information will be provided in the next update to this data request after PG&E’s next GRC filing in May 2025. Regarding “Section D: Costs Recovered via Application (Memo or Balancing Account),” per PG&E’s discussion with SPD on September 27, 2024, costs reflected are recorded and not recovered. Regarding “Section E: SB 884 Activity,” PG&E anticipates submitting its SB 884 Electric Undergrounding Plan in 2025. Work forecast in the SB 884 Electric Undergrounding Plan will begin in 2027. Therefore, there are no forecast units and no forecast costs for SB 884 in 2023, 2024, or 2025. Regarding “Section F: FERC or Other,” PG&E is unable to provide forecasted data for this category. Transmission project costs are not tracked at the level of granularity required to identify if Wildfire Mitigation Plan (WMP) Initiative tracking codes are applicable. In addition, mitigations listed in the WMP are not included at the project level but rather program level. PG&E will provide data only for WMP related Transmission activities in this section. Per PG&E’s discussion with SPD on September 27, 2024, these costs will only be available for a small sub-set of transmission programs as they pertain to the WMP. For the three initiatives (Situational Awareness (SA)-02; SA-10; SA-11) being provided in this response, they are only applicable to the following tab: CapEx HFTD. The other three tabs will be blank for these initiatives. Please advise if SPD prefers PG&E to remove rows or include non-applicable, when relevant, instead of leaving these cells blank. | Kevin Miller | 2024-09-10 | 2024-10-11 | 2024-10-11 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_021.zip | 1 | N/A | 4.3 | 4.0 Overview of WMP | 4.3 Proposed Expenditures | 2.3 Expenditures
708 | CPUC - SPD (Safety Policy Division) | 021 | CPUC - SPD (Safety Policy Division)_021 | 1(s2) | CPUC - SPD (Safety Policy Division)_021_Q1(s2) | 1. Complete tabs 2 through 6 of the attached spreadsheet. For tabs 2 through 5, complete a corresponding data row for each of the 114 mitigation initiatives in the most recent QDR, Table 11 according to the directions in the spreadsheet and the two attached guidance documents listed below: • Guidance for WMP Cost Reporting (applicable to tab 2 through 5) • Guidance for Account Tracking (applicable to tab 6) | Please see attachment “WMP-Discovery2023-2025_DR_SPD_021-Q001Supp02Atch01.zip” for Tranche 3/Supp02 of this request. Note, the clarifications provided in previous Tranches also apply to this request. Tranche 3 includes Situational Awareness (SA) 03, 07, 08, 09 and 12 Wildfire Mitigation Plan (WMP) initiatives SA which only include work in High Fire Threat District (HFTD) areas. Some of the initiatives being provided include blank cells for costs in the worksheets. These initiatives have costs; however, the costs are in a Provider Cost Center (PCC) for the WMP objective, and line-item costs are not able to be extracted. Some initiatives being provided reflect (0) for costs in the worksheets. These initiatives have costs related to the WMP, however, their recorded or forecasted costs are currently $0. PG&E has provided WMP units for unitized initiatives in their applicable tab. Note, if units are capital than they are reflected only in the “CapEx” tabs; likewise, if units are expense, they are only reflected in the “OpEx” tabs. PG&E did not repeat unit data on other tabs, even if costs are present. Blank cells in the unit columns indicate that the work is either not unitized, or that PG&E executed 0 units of the work. | Kevin Miller | 2024-09-10 | 2024-10-18 | 2024-10-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_021.zip | 1 | N/A | 4.3 | 4.0 Overview of WMP | 4.3 Proposed Expenditures | 2.3 Expenditures
708 | CPUC - SPD (Safety Policy Division) | 021 | CPUC - SPD (Safety Policy Division)_021 | 1(s3) | CPUC - SPD (Safety Policy Division)_021_Q1(s3) | 1. Complete tabs 2 through 6 of the attached spreadsheet. For tabs 2 through 5, complete a corresponding data row for each of the 114 mitigation initiatives in the most recent QDR, Table 11 according to the directions in the spreadsheet and the two attached guidance documents listed below: • Guidance for WMP Cost Reporting (applicable to tab 2 through 5) • Guidance for Account Tracking (applicable to tab 6) | Please see attachment “WMP-Discovery2023-2025_DR_SPD_021-Q001Supp03Atch01.zip” for Tranche 4/Supp03 of this request. Please note that the data and calculations throughout the file are interconnected and updates, edits, and corrections to data in future deliveries will affect previously produced values. As a result, due to the nature of rolling deliveries of the requested data, future submissions can be expected to amend previously produced values. In the interest of timely submission of the requested data, we lock our file each week for production. Any updates to the data discovered after the file is locked will be represented in future deliveries. At this time, for example, we have identified six initiatives—AI-08, GH-04, GH-08, GH-Other Grid Topology Improvements to Minimize Risk of Ignitions, GD-Other Technologies and Systems Not Listed Above, and SA-Weather Forecasting—that will have updated data for memorandum or balancing accounts and will be updated in a future delivery. The data that will be updated includes values provided for those initiatives in “Section D: Costs Recorded via Application (Memo or Balancing Account)” in the “HFTD, Cap Ex (2 of 5),” “HFTD, OpEx (3 of 5),” “Non-HFTD, Cap Ex (4 of 5),” and “Non-HFTD, OpEx (5 of 5)” worksheets, as well as across the Accounts Tracking tab. Other updates may be made as we continue our review. Tranche 4 includes the requested Grid Design, Operations, and Maintenance and Situational Awareness and Forecasting WMP initiatives for tabs 1-5, as well as the Accounts Tracking tab. Please note that, upon review, certain costs have been re-categorized among Wildfire Mitigation Plan (WMP) Initiatives relative to our Quarterly Data Report (QDR). We are reviewing prior QDR submissions to determine whether errata or amendments should be submitted as a result. Regarding “Section A: WMP Cost and Unit Data” in the “HFTD, Cap Ex (2 of 5),” “HFTD, OpEx (3 of 5),” “Non-HFTD, Cap Ex (4 of 5),” and “Non-HFTD, OpEx (5 of 5)” worksheets, please note that we do not provide unit data for unnamed initiatives (e.g. “GD-Distribution pole replacements and reinforcements,” WMP Section 8.1.2.3) because these categories include variously unitized activities or non-unitized activities. Regarding “Section B: Costs and Units Authorized in Last GRC,” please note that the 2023 GRC did not provide HFTD and non-HFTD forecasts for many programs, so we are reporting all authorized dollars and units for those programs in Section B in the “HFTD, Cap Ex (2 of 5)” and “HFTD, OpEx (3 of 5)” worksheets. Regarding “Section C: Costs and Units Forecast to be Requested in the Next GRC” in the “HFTD, Cap Ex (2 of 5),” “HFTD, OpEx (3 of 5),” “Non-HFTD, Cap Ex (4 of 5),” and “Non-HFTD, OpEx (5 of 5)” worksheets, we understand that this section will be filled in after PG&E submits our 2027 GRC. Regarding “Section D: Costs Recorded via Application (Memo or Balancing Account)” in the “HFTD, Cap Ex (2 of 5),” “HFTD, OpEx (3 of 5),” “Non-HFTD, Cap Ex (4 of 5),” and “Non-HFTD, OpEx (5 of 5)” worksheets, we understand “Application (Memo or Balancing Account” to include the following memo or balancing accounts where costs are recorded, including those authorized and funded in the GRC. This population consists of the Wildfire Mitigation Balancing Account (WMBA); MicroGrids Memorandum Account (MGMA); Wildfire Mitigation Plan Memorandum Account (WMPMA)/Fire Risk Mitigation Memorandum Account (FRMMA); Vegetation Management Balancing Account (VMBA); Catastrophic Emergency Memorandum Account (CEMA); Overhead Underground Maintenance Balancing Account (OUMBA). Regarding “Section E: SB884 Activity” in the “HFTD, Cap Ex (2 of 5),” “HFTD, OpEx (3 of 5),” “Non-HFTD, Cap Ex (4 of 5),” and “Non-HFTD, OpEx (5 of 5)” worksheets, we anticipate submitting its SB 884 Electric Undergrounding Plan in 2025. Work forecast in the SB 884 Electric Undergrounding Plan will begin in 2027. Therefore, there are no forecast units and no forecast costs for SB 884 in 2023, 2024, or 2025. Regarding “Section F: FERC or Other” in the “HFTD, Cap Ex (2 of 5),” “HFTD, OpEx (3 of 5),” “Non-HFTD, Cap Ex (4 of 5),” and “Non-HFTD, OpEx (5 of 5)” worksheets, we understand this to mean costs related to the Transmission Owner case. Regarding the Accounts Tracking tab, please note that we are continuing to review the “FERC USOA” column and will provide further information in future deliveries. Regarding the Accounts Tracking tab, please note that blank entries in “Unit” columns indicate non-unitized initiatives. Regarding the Accounts Tracking tab, we understand “GRC Authorized Expenditures” to refer to expenditures authorized in the 2023 GRC, which includes years 2023 through 2026. Regarding the Accounts Tracking tab, we understand “GRC Authorized Revenue Requirement (Entered Rates)” to refer to the revenue requirement of expenditures authorized in our 2023 GRC for years 2023 and 2024. Regarding the Accounts Tracking tab, we understand “Recorded Cost Expenditures” to refer to 2023 Recorded costs regardless of memorandum or balancing account. Regarding the Accounts Tracking tab, we understand “Recorded Cost Revenue Requirement (Entered Rates)” to refer to 2023 Recorded costs regardless of memorandum or balancing account. Operational expenditures for 2023 have entered rates, with the exception of Transmission Base, WMPMA, and FRMMA, and capital expenditures for 2023 and 2024, with the exception of Transmission Base, WMPMA, and FRMMA, have entered rates. Regarding the Accounts Tracking tab, we understand “Recorded Cost Revenue Requirement (Yet to Enter Rates)” to refer to 2023 Recorded costs regardless of memorandum or balancing account. Operational expenditures for 2023 for Transmission Base, WMPMA, and FRMMA, and capital expenditures for 2023 through 2026 for Transmission Base, WMPMA, and FRMMA, have yet to enter rates. Regarding the Accounts Tracking tab, we understand “Non-GRC Authorized Expenditures” to refer to non-GRC balancing and memorandum accounts. We include CEMA, EPIC, MGMA, Transmission Base, WMPMA, and FRMMA. We have no non-GRC Authorized Expenditures for 2023. Regarding the Accounts Tracking tab, we understand “Non-GRC Authorized Revenue Requirements (Entered Rates)” to refer to non-GRC balancing and memorandum accounts. We include CEMA, EPIC, MGMA, Transmission Base, WMPMA, and FRMMA. No operational or capital expenditures for 2023 have entered rates. Regarding the Accounts Tracking tab, we understand “Non-GRC Recorded Cost Expenditures” to refer to non-GRC balancing and memorandum accounts. We include CEMA, EPIC, MGMA, Transmission Base, WMPMA, and FRMMA. Regarding the Accounts Tracking tab, we understand “Non-GRC Recorded Costs Revenue Requirements (Entered Rates)” to refer to non-GRC balancing and memorandum accounts. We include CEMA, EPIC, MGMA, Transmission Base, WMPMA, and FRMMA. Operational expenditures for 2023 have entered rates, with the exception of Transmission Base, WMPMA, and FRMMA, and no capital expenditures have entered rates. Regarding the Accounts Tracking tab, we understand “Non-GRC Recorded Costs Revenue Requirement (Yet to Enter Rates)” to refer to non-GRC balancing and memorandum accounts. We include CEMA, EPIC, MGMA, Transmission Base, WMPMA, and FRMMA. Operational expenditures for 2023 for Transmission Base, WMPMA, and FRMMA, and capital expenditures for 2023 through 2026 for Transmission Base, WMPMA, and FRMMA, have yet to enter rates. Regarding the Accounts Tracking tab, we understand the “Pending” columns to refer to all costs regardless of memorandum or balancing account, and “Pending Non-GRC Expenditures” to refer to non-GRC balancing and memorandum accounts. We include CEMA, EPIC, MGMA, WMPMA, and FRMMA in “Pending Non-GRC Expenditures.” At this time, we do not have a pending GRC; “Pending GRC Expenditures” and “Pending GRC Revenue Requirements” are therefore blank. Some of the initiatives being provided include blank cells for costs in the worksheets. These initiatives have costs; however, the costs are in a Provider Cost Center (PCC) for the WMP objective, and line-item costs are not able to be extracted. Some initiatives being provided reflect (0) for costs in the worksheets. These initiatives have costs related to the WMP, however, their recorded or forecasted costs are currently $0. We leave the Account Total and Wildfire Mitigation Program Total columns blank for SPD to conduct their calculations. | Kevin Miller | 2024-09-10 | 2024-12-20 | 2024-12-20 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_021.zip | 1 | N/A | 4.3 | 4.0 Overview of WMP | 4.3 Proposed Expenditures | 2.3 Expenditures
708 | CPUC - SPD (Safety Policy Division) | 021 | CPUC - SPD (Safety Policy Division)_021 | 1(s6) | CPUC - SPD (Safety Policy Division)_021_Q1(s6) | 1. Complete tabs 2 through 6 of the attached spreadsheet. For tabs 2 through 5, complete a corresponding data row for each of the 114 mitigation initiatives in the most recent QDR, Table 11 according to the directions in the spreadsheet and the two attached guidance documents listed below: • Guidance for WMP Cost Reporting (applicable to tab 2 through 5) • Guidance for Account Tracking (applicable to tab 6) | Please see attachment “WMP-Discovery2023-2025_DR_SPD_021-Q001Supp06Atch01.zip” for Tranche 7/Supp06 of this request. Tranche 7 includes data for all Wildfire Mitigation Plan (WMP) initiatives for worksheets 1-5, as well as the Account Tracking worksheet. This delivery reflects our recorded data as of Thursday, January 9, 2025. In order to populate the Account Tracking tab, our data is locked each week and further updates and edits cannot be made thereafter. At this time, we have not identified further edits or updates to the data presented here. As we have previously noted, certain costs have been re-categorized among WMP Initiatives relative to our Quarterly Data Report (QDR). We are reviewing prior QDR submissions to determine whether errata or amendments should be submitted as a result. If, in the course of generating that errata, further updates to this submission are discovered, we will inform SPD. We have reviewed our prior deliveries and determined that duplicate values across tabs 2-5 were the result of an error in the formulas used to derive the values. This formula has been fixed in this delivery and the values are corrected. Please note that certain initiatives are not tracked at an HFTD and non-HFTD level. We provide HFTD and non-HFTD allocations of recorded costs for such initiatives by allocating values based on the percentage of our distribution line-miles in HFTD and non-HFTD, respectively. Please note that we provide actual cost and unit data for 2023, and forecasted cost and unit data consistent with our QDR for 2024 and 2025 in the Sections A, D, and F in the “HFTD, Cap Ex (2 of 5),” “HFTD, OpEx (3 of 5),” “Non-HFTD, Cap Ex (4 of 5),” and “Non-HFTD, OpEx (5 of 5)” worksheets. Regarding “Section A: WMP Cost and Unit Data” in the “HFTD, Cap Ex (2 of 5),” “HFTD, OpEx (3 of 5),” “Non-HFTD, Cap Ex (4 of 5),” and “Non-HFTD, OpEx (5 of 5)” worksheets, please note that we do not provide unit data for unnamed initiatives (e.g. “VM-Emergency response vegetation management,” WMP Section 8.2.3.8) because these categories include variously unitized activities or non-unitized activities. Regarding “Section B: Costs and Units Authorized in Last GRC,” please note that the 2023 GRC did not provide HFTD and non-HFTD forecasts for many programs, so we are reporting all authorized dollars and units for those programs in Section B in the “HFTD, Cap Ex (2 of 5)” and “HFTD, OpEx (3 of 5)” worksheets. Regarding “Section C: Costs and Units Forecast to be Requested in the Next GRC” in the “HFTD, Cap Ex (2 of 5),” “HFTD, OpEx (3 of 5),” “Non-HFTD, Cap Ex (4 of 5),” and “Non-HFTD, OpEx (5 of 5)” worksheets, we understand that this section will be filled in after PG&E submits our 2027 GRC. Regarding “Section D: Costs Recorded via Application (Memo or Balancing Account)” in the “HFTD, Cap Ex (2 of 5),” “HFTD, OpEx (3 of 5),” “Non-HFTD, Cap Ex (4 of 5),” and “Non-HFTD, OpEx (5 of 5)” worksheets, we understand “Application (Memo or Balancing Account” to include the following memo or balancing accounts where costs are recorded, including those authorized and funded in the GRC. This population consists of the Wildfire Mitigation Balancing Account (WMBA); MicroGrids Memorandum Account (MGMA); MicroGrids Balancing Account (MGBA); Elect Program Invest Charge BA (EPIC); Wildfire Mitigation Plan Memorandum Account (WMPMA)/Fire Risk Mitigation Memorandum Account (FRMMA); Vegetation Management Balancing Account (VMBA); Catastrophic Emergency Memorandum Account (CEMA); Overhead Underground Maintenance Balancing Account (OUMBA). Regarding “Section E: SB884 Activity” in the “HFTD, Cap Ex (2 of 5),” “HFTD, OpEx (3 of 5),” “Non-HFTD, Cap Ex (4 of 5),” and “Non-HFTD, OpEx (5 of 5)” worksheets, we anticipate submitting its SB 884 Electric Undergrounding Plan in 2025. Work forecast in the SB 884 Electric Undergrounding Plan will begin in 2027. Therefore, there are no forecast units and no forecast costs for SB 884 in 2023, 2024, or 2025. Regarding “Section F: FERC or Other” in the “HFTD, Cap Ex (2 of 5),” “HFTD, OpEx (3 of 5),” “Non-HFTD, Cap Ex (4 of 5),” and “Non-HFTD, OpEx (5 of 5)” worksheets, we understand this to mean costs related to the Transmission Owner case. Please note that certain initiatives (e.g. RM - Risk Methodology and Assessment) include the full 2024 and 2025 WMP forecast amount in this section. Those values do not represent the expected actual allocation of cost to the Transmission Owner case. Regarding the Account Tracking tab, please note that the CPUC Proceeding Number, CPUC Decision Number, and Any Other ID Number columns have been updated to reflect the proceedings and decisions related to the most recent authorization of revenue associated with the relevant memorandum or balancing account. Regarding the Account Tracking tab, please note that blank entries in “Unit” columns indicate non-unitized initiatives. WMP-Discovery2023-2025_DR_SPD_021-Q001Supp06 Page 3 Regarding the Account Tracking tab, we understand “GRC Authorized Expenditures” to refer to expenditures authorized in the 2023 GRC, which includes years 2023 through 2026. Regarding the Account Tracking tab, we understand “GRC Authorized Revenue Requirement (Entered Rates)” to refer to the revenue requirement of expenditures authorized in our 2023 GRC for years 2023 and 2024. Regarding the Account Tracking tab, we understand “Recorded Cost Expenditures” to refer to 2023 Recorded costs regardless of memorandum or balancing account. Regarding the Account Tracking tab, please note that we determined that expenditures under the CEMA and MGMA accounts have yet to enter rates. This update is reflected in our data and in the explanations of the sections including “Entered Rates” and “Yet to Enter Rates,” below. Regarding the Account Tracking tab, we understand “Recorded Cost Revenue Requirement (Entered Rates)” to refer to 2023 Recorded costs regardless of memorandum or balancing account. Operational expenditures for 2023 have entered rates, with the exception of Transmission Base, CEMA, MGMA, WMPMA, and FRMMA, and capital expenditures for 2023 and 2024, with the exception of Transmission Base, CEMA, MGMA, EPIC, WMPMA, and FRMMA, have entered rates. Regarding the Account Tracking tab, we understand “Recorded Cost Revenue Requirement (Yet to Enter Rates)” to refer to 2023 Recorded costs regardless of memorandum or balancing account. Operational expenditures for 2023 for Transmission Base, CEMA, MGMA, WMPMA, and FRMMA, and capital expenditures for 2023 through 2026 for Transmission Base, CEMA, MGMA, WMPMA, and FRMMA, have yet to enter rates. Regarding the Account Tracking tab, we understand “Non-GRC Authorized Expenditures” to refer to non-GRC balancing and memorandum accounts. We include CEMA, Electric Program Investment Charge (EPIC), MGMA, Transmission Base, WMPMA, and FRMMA. We have no non-GRC Authorized Expenditures for 2023. Regarding the Account Tracking tab, we understand “Non-GRC Authorized Revenue Requirements (Entered Rates)” to refer to non-GRC balancing and memorandum accounts. We include CEMA, EPIC, MGMA, Transmission Base, WMPMA, and FRMMA. No operational or capital expenditures for 2023 have entered rates. Regarding the Account Tracking tab, we understand “Non-GRC Recorded Cost Expenditures” to refer to non-GRC balancing and memorandum accounts. We include CEMA, EPIC, MGMA, Transmission Base, WMPMA, and FRMMA. Regarding the Account Tracking tab, we understand “Non-GRC Recorded Costs Revenue Requirements (Entered Rates)” to refer to non-GRC balancing and memorandum accounts. We include CEMA, EPIC, MGMA, MGBA, Transmission Base, WMPMA, and FRMMA. Operational expenditures for 2023 have entered rates, with the exception of Transmission Base, CEMA, WMPMA, and FRMMA, and no capital expenditures have entered rates. Regarding the Account Tracking tab, we understand “Non-GRC Recorded Costs Revenue Requirement (Yet to Enter Rates)” to refer to non-GRC balancing and memorandum accounts. We include CEMA, EPIC, MGMA, Transmission Base, WMPMA, and FRMMA. Operational expenditures for 2023 for Transmission Base, CEMA, MGMA, WMPMA, and FRMMA, and capital expenditures for 2023 through 2026 for Transmission Base, CEMA, MGMA, WMPMA, and FRMMA, have yet to enter rates. Regarding the Account Tracking tab, we understand the “Pending” columns to refer to all costs regardless of memorandum or balancing account, and “Pending Non-GRC Expenditures” to refer to non-GRC balancing and memorandum accounts. We include CEMA, EPIC, MGMA, MGBA WMPMA, and FRMMA in “Pending Non-GRC Expenditures.” At this time, we do not have a pending GRC; “Pending GRC Expenditures” and “Pending GRC Revenue Requirements” are therefore blank. Some of the initiatives being provided include blank cells for costs in the worksheets. These initiatives have costs; however, the costs are in a Provider Cost Center (PCC) for the WMP objective, and line-item costs are not able to be extracted. Some initiatives being provided reflect (0) for costs in the worksheets. These initiatives have costs related to the WMP, however, their recorded or forecasted costs are currently $0. We leave the Account Total and Wildfire Mitigation Program Total columns blank for SPD to conduct their calculations. | Kevin Miller | 2024-09-10 | 2025-01-10 | 2025-01-10 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_021.zip | 1 | N/A | QDR | N/A | N/A | N/A
708 | CPUC - SPD (Safety Policy Division) | 021 | CPUC - SPD (Safety Policy Division)_021 | 1(s7) | CPUC - SPD (Safety Policy Division)_021_Q1(s7) | 1. Complete tabs 2 through 6 of the attached spreadsheet. For tabs 2 through 5, complete a corresponding data row for each of the 114 mitigation initiatives in the most recent QDR, Table 11 according to the directions in the spreadsheet and the two attached guidance documents listed below: • Guidance for WMP Cost Reporting (applicable to tab 2 through 5) • Guidance for Account Tracking (applicable to tab 6) | Please see attachment “WMP-Discovery2023-2025_DR_SPD_021-Q001Supp07Atch01.zip” for Tranche 8/Supp07 of this request. This amendment includes data for all Wildfire Mitigation Plan (WMP) initiatives for worksheets 1-5, as well as the Account Tracking worksheet. Upon the completion of our delivery of Tranche 7 of this Data Request on January 10, 2025, we determined that our 2023 Quarterly Data Report (QDR) submission required correction. In the course of generating that correction, submitted on February 2, 2025, we discovered several items in our January 10, 2025 submission that require amendment. Please see below for a list of changes made to our 2023 recorded costs in this amendment: • Approximately $6.1 million in operational expenses attributed to “CO- Public outreach and education awareness program” moved to “GD-Equipment Settings to Reduce Wildfire Risk (Grid Ops)”; • Approximately $3.6 million in operational expenses attributed to GM-09 moved from HFTD to non-HFTD; • Approximately $497,000 in operational expenses newly attributed to GM-01 in the Distribution Base Account; • Approximately $3.9 million in operational expenses newly attributed to GM-01 in the Transmission Base Account; WMP-Discovery2023-2025_DR_SPD_021-Q001Supp07 Page 2 • Approximately $8.9 million in operational expenses newly attributed to GM-09 in the Transmission Base Account; • Approximately $9.2 million in operational expenses removed from “GD-Equipment maintenance and repair” in the OUMBA Balancing Account; • Approximately $2.7 million in operational expenses removed from “GD-Equipment maintenance and repair” in the Distribution Base Account; • Approximately $1.9 million in operational expenses attributed to VM-03 moved from non-HFTD to HFTD; • Approximately $2.6 million in operational expenses attributed to M-08 moved from the VMBA Balancing Account to the Transmission base Account; • Approximately $10.6 million in operational expenses attributed to VM-08 moved from the Transmission Base to the VMBA Balancing Account; • Approximately $53 million in capital expenses removed from “GD-Equipment maintenance and repair” in the OUMBA Balancing Account. | Kevin Miller | 2024-09-10 | 2025-02-14 | 2025-02-14 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_021.zip | 1 | N/A | QDR | N/A | N/A | N/A
708 | CPUC - SPD (Safety Policy Division) | 021 | CPUC - SPD (Safety Policy Division)_021 | 1(s4) | CPUC - SPD (Safety Policy Division)_021_Q1(s4) | 1. Complete tabs 2 through 6 of the attached spreadsheet. For tabs 2 through 5, complete a corresponding data row for each of the 114 mitigation initiatives in the most recent QDR, Table 11 according to the directions in the spreadsheet and the two attached guidance documents listed below: • Guidance for WMP Cost Reporting (applicable to tab 2 through 5) • Guidance for Account Tracking (applicable to tab 6) | Please see attachment “WMP-Discovery2023-2025_DR_SPD_021-Q001Supp04Atch01.zip” for Tranche 5/Supp04 of this request. Tranche 5 includes the requested Vegetation Management and Inspections and Community Outreach and Engagement Wildfire Mitigation Plan (WMP) initiatives for worksheets 1-5, as well as the Accounts Tracking worksheet. Tranche 5 also includes the Grid Design, Operations, and Maintenance and Situational Awareness and Forecasting WMP initiatives for worksheets 1-5, as well as the Accounts Tracking worksheet. Please note that the data and calculations throughout the file are interconnected and updates, edits, and corrections to data in future deliveries will affect previously produced values. As a result, due to the nature of rolling deliveries of the requested data, future submissions can be expected to amend previously produced values. In the interest of timely submission of the requested data, we lock our file each week for production. Any updates to the data discovered after the file is locked will be represented in future deliveries. At this time, for example, we have identified several initiatives—CO-01, CO-02, CO-04, CO-05, VM-08, VM-13, VM-19, VM-22, and VM-Wood and slash management—that will be updated in a future delivery. The data that will be updated includes values provided for those initiatives in “Section D: Costs Recorded via Application (Memo or Balancing Account)” in the “HFTD, Cap Ex (2 of 5),” “HFTD, OpEx (3 of 5),” “Non-HFTD, Cap Ex (4 of 5),” and “Non-HFTD, OpEx (5 of 5)” worksheets, as well as across the Accounts Tracking tab. Additionally, GRC forecast data related to the initiative titled “VM-Fall-in-mitigation” will be identified in future deliveries. Other updates may be identified as we continue our review. Please note that this delivery includes updated data for previously produced Grid Design, Operations, and Maintenance and Situational Awareness and Forecasting initiatives, including updated values for AI-08, GH-04, GH-08, GH-Other Grid Topology Improvements to Minimize Risk of Ignitions, GD-Other Technologies and Systems Not Listed Above, and SA-Weather Forecasting, among others. Other updates may be identified as we continue our review. Please note that, upon review, certain costs have been re-categorized among WMP Initiatives relative to our Quarterly Data Report (QDR). We are reviewing prior QDR submissions to determine whether errata or amendments should be submitted as a result. Please note that we did not forecast our work under the Community Outreach and Engagement category by WMP Initiative ID in our 2023 GRC. As such, we report all GRC forecasts under this category in the section titled “CO-Public outreach and education awareness program.” Regarding “Section A: WMP Cost and Unit Data” in the “HFTD, Cap Ex (2 of 5),” “HFTD, OpEx (3 of 5),” “Non-HFTD, Cap Ex (4 of 5),” and “Non-HFTD, OpEx (5 of 5)” worksheets, please note that we do not provide unit data for unnamed initiatives (e.g. “VM-Emergency response vegetation management,” WMP Section 8.2.3.8) because these categories include variously unitized activities or non-unitized activities. Regarding “Section B: Costs and Units Authorized in Last GRC,” please note that the 2023 GRC did not provide HFTD and non-HFTD forecasts for many programs, so we are reporting all authorized dollars and units for those programs in Section B in the “HFTD, Cap Ex (2 of 5)” and “HFTD, OpEx (3 of 5)” worksheets. Regarding “Section C: Costs and Units Forecast to be Requested in the Next GRC” in the “HFTD, Cap Ex (2 of 5),” “HFTD, OpEx (3 of 5),” “Non-HFTD, Cap Ex (4 of 5),” and “Non-HFTD, OpEx (5 of 5)” worksheets, we understand that this section will be filled in after PG&E submits our 2027 GRC. Regarding “Section D: Costs Recorded via Application (Memo or Balancing Account)” in the “HFTD, Cap Ex (2 of 5),” “HFTD, OpEx (3 of 5),” “Non-HFTD, Cap Ex (4 of 5),” and “Non-HFTD, OpEx (5 of 5)” worksheets, we understand “Application (Memo or Balancing Account” to include the following memo or balancing accounts where costs are recorded, including those authorized and funded in the GRC. This population consists of the Wildfire Mitigation Balancing Account (WMBA); MicroGrids Memorandum Account (MGMA); Wildfire Mitigation Plan Memorandum Account (WMPMA)/Fire Risk Mitigation Memorandum Account (FRMMA); Vegetation Management Balancing Account (VMBA); Catastrophic Emergency Memorandum Account (CEMA); Overhead Underground Maintenance Balancing Account (OUMBA). Regarding “Section E: SB884 Activity” in the “HFTD, Cap Ex (2 of 5),” “HFTD, OpEx (3 of 5),” “Non-HFTD, Cap Ex (4 of 5),” and “Non-HFTD, OpEx (5 of 5)” worksheets, we anticipate submitting its SB 884 Electric Undergrounding Plan in 2025. Work forecast in the SB 884 Electric Undergrounding Plan will begin in 2027. Therefore, there are no forecast units and no forecast costs for SB 884 in 2023, 2024, or 2025. Regarding “Section F: FERC or Other” in the “HFTD, Cap Ex (2 of 5),” “HFTD, OpEx (3 of 5),” “Non-HFTD, Cap Ex (4 of 5),” and “Non-HFTD, OpEx (5 of 5)” worksheets, we understand this to mean costs related to the Transmission Owner case. Regarding the Accounts Tracking tab, please note that we are continuing to review the “FERC USOA” column and will provide further information in future deliveries. Regarding the Accounts Tracking tab, please note that blank entries in “Unit” columns indicate non-unitized initiatives. Regarding the Accounts Tracking tab, we understand “GRC Authorized Expenditures” to refer to expenditures authorized in the 2023 GRC, which includes years 2023 through 2026. Regarding the Accounts Tracking tab, we understand “GRC Authorized Revenue Requirement (Entered Rates)” to refer to the revenue requirement of expenditures authorized in our 2023 GRC for years 2023 and 2024. Regarding the Accounts Tracking tab, we understand “Recorded Cost Expenditures” to refer to 2023 Recorded costs regardless of memorandum or balancing account. Regarding the Accounts Tracking tab, please note that we determined that expenditures under the CEMA and MGMA accounts have yet to enter rates. This update is reflected in our data and in the explanations of the sections including “Entered Rates” and “Yet to Enter Rates,” below. Regarding the Accounts Tracking tab, we understand “Recorded Cost Revenue Requirement (Entered Rates)” to refer to 2023 Recorded costs regardless of memorandum or balancing account. Operational expenditures for 2023 have entered rates, with the exception of Transmission Base, CEMA, MGMA, WMPMA, and FRMMA, and capital expenditures for 2023 and 2024, with the exception of Transmission Base, CEMA, MGMA, WMPMA, and FRMMA, have entered rates. Regarding the Accounts Tracking tab, we understand “Recorded Cost Revenue Requirement (Yet to Enter Rates)” to refer to 2023 Recorded costs regardless of memorandum or balancing account. Operational expenditures for 2023 for Transmission Base, CEMA, MGMA, WMPMA, and FRMMA, and capital expenditures for 2023 through 2026 for Transmission Base, CEMA, MGMA, WMPMA, and FRMMA, have yet to enter rates. Regarding the Accounts Tracking tab, we understand “Non-GRC Authorized Expenditures” to refer to non-GRC balancing and memorandum accounts. We include CEMA, EPIC, MGMA, Transmission Base, WMPMA, and FRMMA. We have no non-GRC Authorized Expenditures for 2023. Regarding the Accounts Tracking tab, we understand “Non-GRC Authorized Revenue Requirements (Entered Rates)” to refer to non-GRC balancing and memorandum accounts. We include CEMA, EPIC, MGMA, Transmission Base, WMPMA, and FRMMA. No operational or capital expenditures for 2023 have entered rates. Regarding the Accounts Tracking tab, we understand “Non-GRC Recorded Cost Expenditures” to refer to non-GRC balancing and memorandum accounts. We include CEMA, EPIC, MGMA, Transmission Base, WMPMA, and FRMMA. Regarding the Accounts Tracking tab, we understand “Non-GRC Recorded Costs Revenue Requirements (Entered Rates)” to refer to non-GRC balancing and memorandum accounts. We include CEMA, EPIC, MGMA, Transmission Base, WMPMA, and FRMMA. Operational expenditures for 2023 have entered rates, with the exception of Transmission Base, CEMA, MGMA, WMPMA, and FRMMA, and no capital expenditures have entered rates. Regarding the Accounts Tracking tab, we understand “Non-GRC Recorded Costs Revenue Requirement (Yet to Enter Rates)” to refer to non-GRC balancing and memorandum accounts. We include CEMA, EPIC, MGMA, Transmission Base, WMPMA, and FRMMA. Operational expenditures for 2023 for Transmission Base, CEMA, MGMA, WMPMA, and FRMMA, and capital expenditures for 2023 through 2026 for Transmission Base, CEMA, MGMA, WMPMA, and FRMMA, have yet to enter rates. Regarding the Accounts Tracking tab, we understand the “Pending” columns to refer to all costs regardless of memorandum or balancing account, and “Pending Non-GRC Expenditures” to refer to non-GRC balancing and memorandum accounts. We include CEMA, EPIC, MGMA, WMPMA, and FRMMA in “Pending Non-GRC Expenditures.” At this time, we do not have a pending GRC; “Pending GRC Expenditures” and “Pending GRC Revenue Requirements” are therefore blank. Some of the initiatives being provided include blank cells for costs in the worksheets. These initiatives have costs; however, the costs are in a Provider Cost Center (PCC) for the WMP objective, and line-item costs are not able to be extracted. Some initiatives being provided reflect (0) for costs in the worksheets. These initiatives have costs related to the WMP, however, their recorded or forecasted costs are currently $0. We leave the Account Total and Wildfire Mitigation Program Total columns blank for SPD to conduct their calculations. | Kevin Miller | 2024-09-10 | 2024-12-27 | 2024-12-27 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_021.zip | 1 | N/A | 4.3 | 4.0 Overview of WMP | 4.3 Proposed Expenditures | 2.3 Expenditures
708 | CPUC - SPD (Safety Policy Division) | 021 | CPUC - SPD (Safety Policy Division)_021 | 1(s5) | CPUC - SPD (Safety Policy Division)_021_Q1(s5) | 1. Complete tabs 2 through 6 of the attached spreadsheet. For tabs 2 through 5, complete a corresponding data row for each of the 114 mitigation initiatives in the most recent QDR, Table 11 according to the directions in the spreadsheet and the two attached guidance documents listed below: • Guidance for WMP Cost Reporting (applicable to tab 2 through 5) • Guidance for Account Tracking (applicable to tab 6) | Please see attachment “WMP-Discovery2023-2025_DR_SPD_021-Q001Supp05Atch01.zip” for Tranche 6/Supp05 of this request. Tranche 6 includes the requested Emergency Preparedness and Risk Methodology and Assessment Mitigation Plan (WMP) initiatives for worksheets 1-5, as well as the Account Tracking worksheet. Tranche 6 also includes the Grid Design, Operations, and Maintenance, Situational Awareness and Forecasting, Vegetation Management and Inspections, and Community Outreach and Engagement Wildfire WMP initiatives for worksheets 1-5, as well as the Account Tracking worksheet. Please note that the data and calculations throughout the file are interconnected and updates, edits, and corrections to data in future deliveries will affect previously produced values. As a result, due to the nature of rolling deliveries of the requested data, future submissions can be expected to amend previously produced values. In the interest of timely submission of the requested data, we lock our file each week for production. Any updates to the data discovered after the file is locked will be represented in future deliveries. At this time, for example, we have identified several initiatives— EP-Customer support in wildfire and PSPS emergencies; EP-Emergency preparedness plan; EP-External collaboration and coordination, and; EP-Public emergency communication strategy —that will be updated in a future delivery. The data that will be updated includes values provided for those initiatives in “Section D: Costs Recorded via Application (Memo or Balancing Account)” in the “HFTD, Cap Ex (2 of 5),” “HFTD, OpEx (3 of 5),” “Non-HFTD, Cap Ex (4 of 5),” and “Non-HFTD, OpEx (5 of 5)” worksheets, as WMP-Discovery2023-2025_DR_SPD_021-Q001Supp05 Page 2 well as across the Account Tracking tab. Other updates may be identified as we continue our review. Please note that this delivery includes updated data for previously produced Vegetation Management and Inspections and Community Outreach and Engagement Wildfire initiatives, including updated values for CO-01, CO-02, CO-04, CO-05, VM-08, VM-13, VM-19, VM-22, and VM-Wood and slash management, among others. Other updates may be identified as we continue our review. Please also note that GRC forecasts related to "VM-Fall-in-mitigation" are reported across VM-03, VM-04, VM-17, and VM-18. Please further note that, upon review, certain costs have been re-categorized among WMP Initiatives relative to our Quarterly Data Report (QDR). We are reviewing prior QDR submissions to determine whether errata or amendments should be submitted as a result. Additionally, please note that we did not forecast our work under the Community Outreach and Engagement category by WMP Initiative ID in our 2023 GRC. As such, we report all GRC forecasts under this category in the section titled “CO-Public outreach and education awareness program.” Further, please note that we have updated our data to re-categorize 2023 recorded costs related to the Community Outreach and Engagement from initiatives, CO-01, CO-02, CO-04 and CO-05 into: CO-Public outreach and education awareness program; CO-Best practice sharing with other utilities; CO-Engagement with access and functional needs populations, and CO-Collaboration on local wildfire mitigation planning. Upon review, we determined that recorded costs for 2023 could not be allocated on an initiative level and were more properly allocated as presented here. Please note that our 2024 and 2025 forecasts remain allocated by numbered initiative, but that these forecasts are inclusive of activities beyond those described in the initiatives. Further, please note that we did not forecast our work in our 2023 GRC under the Emergency Preparedness category by WMP Initiative ID. As such, we report our GRC forecasts under this category in the sections titled “EP-External Collaboration and Coordination,” and “EP-Emergency Preparedness Plan.” Further, please note that we have updated our data to re-categorize 2023 recorded costs related to Emergency Preparedness into: EP-Customer support in wildfire and PSPS emergencies; EP-Emergency preparedness plan; EP-External collaboration and coordination, and; EP-Public emergency communication strategy. Upon review, we determined that recorded costs for 2023 could not be allocated on an initiative level and were more properly allocated as presented here. Please note that portions of our 2024 and 2025 forecasts remain allocated by numbered initiative, but that these forecasts are inclusive of activities beyond those described in the initiatives. Please note that certain initiatives are not tracked at an HFTD and non-HFTD level. We provide HFTD and non-HFTD allocations of such initiatives by allocating values based on the percentage of our distribution line-miles in HFTD and non-HFTD, respectively. Regarding “Section A: WMP Cost and Unit Data” in the “HFTD, Cap Ex (2 of 5),” “HFTD, OpEx (3 of 5),” “Non-HFTD, Cap Ex (4 of 5),” and “Non-HFTD, OpEx (5 of 5)” worksheets, please note that we do not provide unit data for unnamed initiatives (e.g. “VM-Emergency response vegetation management,” WMP Section 8.2.3.8) because these categories include variously unitized activities or non-unitized activities. WMP-Discovery2023-2025_DR_SPD_021-Q001Supp05 Page 3 Regarding “Section B: Costs and Units Authorized in Last GRC,” please note that the 2023 GRC did not provide HFTD and non-HFTD forecasts for many programs, so we are reporting all authorized dollars and units for those programs in Section B in the “HFTD, Cap Ex (2 of 5)” and “HFTD, OpEx (3 of 5)” worksheets. Regarding “Section C: Costs and Units Forecast to be Requested in the Next GRC” in the “HFTD, Cap Ex (2 of 5),” “HFTD, OpEx (3 of 5),” “Non-HFTD, Cap Ex (4 of 5),” and “Non-HFTD, OpEx (5 of 5)” worksheets, we understand that this section will be filled in after PG&E submits our 2027 GRC. Regarding “Section D: Costs Recorded via Application (Memo or Balancing Account)” in the “HFTD, Cap Ex (2 of 5),” “HFTD, OpEx (3 of 5),” “Non-HFTD, Cap Ex (4 of 5),” and “Non-HFTD, OpEx (5 of 5)” worksheets, we understand “Application (Memo or Balancing Account” to include the following memo or balancing accounts where costs are recorded, including those authorized and funded in the GRC. This population consists of the Wildfire Mitigation Balancing Account (WMBA); MicroGrids Memorandum Account (MGMA); Wildfire Mitigation Plan Memorandum Account (WMPMA)/Fire Risk Mitigation Memorandum Account (FRMMA); Vegetation Management Balancing Account (VMBA); Catastrophic Emergency Memorandum Account (CEMA); Overhead Underground Maintenance Balancing Account (OUMBA). Regarding “Section E: SB884 Activity” in the “HFTD, Cap Ex (2 of 5),” “HFTD, OpEx (3 of 5),” “Non-HFTD, Cap Ex (4 of 5),” and “Non-HFTD, OpEx (5 of 5)” worksheets, we anticipate submitting its SB 884 Electric Undergrounding Plan in 2025. Work forecast in the SB 884 Electric Undergrounding Plan will begin in 2027. Therefore, there are no forecast units and no forecast costs for SB 884 in 2023, 2024, or 2025. Regarding “Section F: FERC or Other” in the “HFTD, Cap Ex (2 of 5),” “HFTD, OpEx (3 of 5),” “Non-HFTD, Cap Ex (4 of 5),” and “Non-HFTD, OpEx (5 of 5)” worksheets, we understand this to mean costs related to the Transmission Owner case. Please note that certain initiatives (e.g. RM - Risk Methodology and Assessment) include the full 2024 and 2025 WMP forecast amount in this section. Those values do not represent the expected actual allocation of cost to the Transmission Owner case. Regarding the Account Tracking tab, please note that we are continuing to review the “FERC USOA” column and will provide further information in future deliveries. Regarding the Account Tracking tab, please note that blank entries in “Unit” columns indicate non-unitized initiatives. Regarding the Account Tracking tab, we understand “GRC Authorized Expenditures” to refer to expenditures authorized in the 2023 GRC, which includes years 2023 through 2026. Regarding the Account Tracking tab, we understand “GRC Authorized Revenue Requirement (Entered Rates)” to refer to the revenue requirement of expenditures authorized in our 2023 GRC for years 2023 and 2024. Regarding the Account Tracking tab, we understand “Recorded Cost Expenditures” to refer to 2023 Recorded costs regardless of memorandum or balancing account. Regarding the Account Tracking tab, please note that we determined that expenditures under the CEMA and MGMA accounts have yet to enter rates. This update is reflected in our data and in the explanations of the sections including “Entered Rates” and “Yet to Enter Rates,” below. WMP-Discovery2023-2025_DR_SPD_021-Q001Supp05 Page 4 Regarding the Account Tracking tab, we understand “Recorded Cost Revenue Requirement (Entered Rates)” to refer to 2023 Recorded costs regardless of memorandum or balancing account. Operational expenditures for 2023 have entered rates, with the exception of Transmission Base, CEMA, MGMA, WMPMA, and FRMMA, and capital expenditures for 2023 and 2024, with the exception of Transmission Base, CEMA, MGMA, WMPMA, and FRMMA, have entered rates. Regarding the Account Tracking tab, we understand “Recorded Cost Revenue Requirement (Yet to Enter Rates)” to refer to 2023 Recorded costs regardless of memorandum or balancing account. Operational expenditures for 2023 for Transmission Base, CEMA, MGMA, WMPMA, and FRMMA, and capital expenditures for 2023 through 2026 for Transmission Base, CEMA, MGMA, WMPMA, and FRMMA, have yet to enter rates. Regarding the Account Tracking tab, we understand “Non-GRC Authorized Expenditures” to refer to non-GRC balancing and memorandum accounts. We include CEMA, Electric Program Investment Charge (EPIC), MGMA, Transmission Base, WMPMA, and FRMMA. We have no non-GRC Authorized Expenditures for 2023. Regarding the Account Tracking tab, we understand “Non-GRC Authorized Revenue Requirements (Entered Rates)” to refer to non-GRC balancing and memorandum accounts. We include CEMA, EPIC, MGMA, Transmission Base, WMPMA, and FRMMA. No operational or capital expenditures for 2023 have entered rates. Regarding the Account Tracking tab, we understand “Non-GRC Recorded Cost Expenditures” to refer to non-GRC balancing and memorandum accounts. We include CEMA, EPIC, MGMA, Transmission Base, WMPMA, and FRMMA. Regarding the Account Tracking tab, we understand “Non-GRC Recorded Costs Revenue Requirements (Entered Rates)” to refer to non-GRC balancing and memorandum accounts. We include CEMA, EPIC, MGMA, Transmission Base, WMPMA, and FRMMA. Operational expenditures for 2023 have entered rates, with the exception of Transmission Base, CEMA, MGMA, WMPMA, and FRMMA, and no capital expenditures have entered rates. Regarding the Account Tracking tab, we understand “Non-GRC Recorded Costs Revenue Requirement (Yet to Enter Rates)” to refer to non-GRC balancing and memorandum accounts. We include CEMA, EPIC, MGMA, Transmission Base, WMPMA, and FRMMA. Operational expenditures for 2023 for Transmission Base, CEMA, MGMA, WMPMA, and FRMMA, and capital expenditures for 2023 through 2026 for Transmission Base, CEMA, MGMA, WMPMA, and FRMMA, have yet to enter rates. Regarding the Account Tracking tab, we understand the “Pending” columns to refer to all costs regardless of memorandum or balancing account, and “Pending Non-GRC Expenditures” to refer to non-GRC balancing and memorandum accounts. We include CEMA, EPIC, MGMA, WMPMA, and FRMMA in “Pending Non-GRC Expenditures.” At this time, we do not have a pending GRC; “Pending GRC Expenditures” and “Pending GRC Revenue Requirements” are therefore blank. Some of the initiatives being provided include blank cells for costs in the worksheets. These initiatives have costs; however, the costs are in a Provider Cost Center (PCC) for the WMP objective, and line-item costs are not able to be extracted. WMP-Discovery2023-2025_DR_SPD_021-Q001Supp05 Page 5 Some initiatives being provided reflect (0) for costs in the worksheets. These initiatives have costs related to the WMP, however, their recorded or forecasted costs are currently $0. We leave the Account Total and Wildfire Mitigation Program Total columns blank for SPD to conduct their calculations. | Kevin Miller | 2024-09-10 | 2025-01-03 | 2025-01-03 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_021.zip | 1 | N/A | 4.3 | 4.0 Overview of WMP | 4.3 Proposed Expenditures | 2.3 Expenditures
709 | CalPA | Set WMP-53 | CalPA_Set WMP-53 | 1 | CalPA_Set WMP-53_Q1 | Does PG&E agree with the mapping of similar risk sub-models between WDRM versions v3 and v4 as shown Table 1? If not, please arrange the table so that sub-models found in WDRM v3 are aligned with the similar sub-model found in WDRM v4. In the event that multiple sub-models in one version have been incorporated into a single sub-model in another version, please clarify. | PG&E does not agree with the mapping shown in Table 1 and has re-arranged the table to show the mapping between sub-models. There is no Support Structure Leaking model. To clarify some of the mappings: • The v3 voltage control equipment model was split into the v4 voltage regulator and v4 capacitor bank models. • The v4 DPD, v4 Fuse, and v4 Switch models were previously included in one of the v3 conductor models based on their voltage level (i.e. primary vs. secondary). The other models maintained a one-to-one mapping. WDRM v3 WDRM v4 1 Animal Bird 1 Animal – Bird 2 Animal Squirrel 2 Animal – Squirrel 3 Animal Other 3 Animal – Other 4 Primary Conductor 5 DPD (primary) 6 Fuse (primary) 13 Switch (primary) 7 Primary Conductor – Line Slap 8 Primary Conductor – Wire Down 9 Primary Conductor – Other 5 Secondary Conductor 10 Secondary Conductor 5 DPD (secondary) 6 Fuse (secondary) 13 Switch (secondary) 6 Support Structure Equipment cause 12 Support Structure – Equipment 7 Support Structure Electrical 11 Support Structure – Electrical 8 Third-party Balloon 14 Third Party – Balloon 9 Third-party Vehicle 15 Third Party – Vehicle 10 Third-party Other 16 Third Party – Other 11 Transformer Equipment Cause 17 Transformer – Equipment 12 Transformer Equipment Leaking 18 Transformer – Leaking 13 Vegetation Branch 19 Vegetation – Branch 14 Vegetation Trunk 20 Vegetation – Trunk 15 Vegetation Other 21 Vegetation – Other 16 Voltage Control Equipment 22 Voltage Regulator 4 Capacitor Bank 17 Other Equipment 23 Other Equipment | Matthew Taul | 2024-09-18 | 2024-10-02 | 2024-09-27 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_053.zip | 0 | N/A | 6.1.2 | Section 6 - Risk Methodology and Assessment | 6.1.2 Summary of Risk Models | B.1.1. WDRM v4
710 | CalPA | Set WMP-53 | CalPA_Set WMP-53 | 2 | CalPA_Set WMP-53_Q2 | For each probability sub-model that was present in WDRM v3 and has a corresponding nearly-identically-named sub-model in WDRM v4, please list and describe the ways in which the sub-model in WDRM v4 differs from the sub-model in WDRM v3. | The evolution of the Distribution Event Probability Models (sub-models) is described in the WDRM v4 Documentation suite that has been provided as attachment “WMP-Discovery2023-2025_DR_CalAdvocates_053-Q006Atch01CONF.zip.” Relevant sections included in the “Distribution Event Probability Models v4 Documentation.pdf” include: • Section 2.1, Version Evolution, provides an overview of event probability model evolution from v3 to v4. In particular, it showcases the transition from spatial pixel-based models to asset-based models for most equipment asset models for v4. • Section 2.2, Probability of Failure/Outage Improvements, details general improvements that were made for v4 event probability models. • Section 3.5, Probability of Failure/Outage Improvements, individually documents the development of each of the v4 event probability models. Each model section includes a Key Developments sub-section that describes important changes for v4. | Matthew Taul | 2024-09-18 | 2024-10-02 | 2024-09-27 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_053.zip | 0 | N/A | 6.1.2 | Section 6 - Risk Methodology and Assessment | 6.1.2 Summary of Risk Models | B.1.1. WDRM v4
711 | CalPA | Set WMP-53 | CalPA_Set WMP-53 | 3 | CalPA_Set WMP-53_Q3 | For the newly introduced probability models for ignition risk introduced in WDRM v4 that were not present in WDRM v3, please provide a data dictionary to describe these new risk models and what additional risk they represent. | There were no new probability models introduced in WDRM v4 that captured additional risk which were not present in WDRM v3. Please reference PG&E’s response to Question No. 001, which provides the correct mapping between models and accounts for the referenced highlighted sub-models. Each WDRM v4 model is described in detail in the Event Probability Model documentation. | Matthew Taul | 2024-09-18 | 2024-10-02 | 2024-09-27 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_053.zip | 0 | N/A | 6.1.2 | Section 6 - Risk Methodology and Assessment | 6.1.2 Summary of Risk Models | B.1.1. WDRM v4
712 | CalPA | Set WMP-53 | CalPA_Set WMP-53 | 4 | CalPA_Set WMP-53_Q4 | For those probability models for ignition risk left out of WDRM v4 that were present in WDRM v3, please explain the reasons this model was excluded in the most recent version. In the event this risk model was incorporated into a different model in WDRM v4, please clarify. | There were no probability models left out of WDRM v4 that were present in WDRM v3. Please reference PG&E’s response to Question No. 001, which provides the correct mapping between models. | Matthew Taul | 2024-09-18 | 2024-10-02 | 2024-09-27 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_053.zip | 0 | N/A | 6.1.2 | Section 6 - Risk Methodology and Assessment | 6.1.2 Summary of Risk Models | B.1.1. WDRM v4
713 | CalPA | Set WMP-53 | CalPA_Set WMP-53 | 5 | CalPA_Set WMP-53_Q5 | In response to CalAdvocates-PGE-2025WMP-05 Question 8 on whether an entity was performing an independent review of WDRM V4, PG&E answered that “The E3 review is scheduled to be available by the end of Q2 2024.” a) If the E3 independent review of the WDRM v4 has completed, please provide a copy of any reports and outputs. b) If instead the E3 independent review has not concluded, when does PG&E expect the review to be completed? | a) Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_053-Q005Atch01CONF.pdf” for the requested E3 Review of PG&E WDRM v4 and Transmission Composite Model (TCM). b) Not applicable, please see the response to subpart (a) above. | Matthew Taul | 2024-09-18 | 2024-10-02 | 2024-09-27 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_053.zip | 1 | N/A | 6.1.2 | Section 6 - Risk Methodology and Assessment | 6.1.2 Summary of Risk Models | B.1.1. WDRM v4
714 | CalPA | Set WMP-53 | CalPA_Set WMP-53 | 6 | CalPA_Set WMP-53_Q6 | In response to CalAdvocates-PGE-2025WMP-05 Question 9 on whether PG&E has created a detailed overview document that details WDRM v4, PG&E answered that “PG&E is currently creating the detailed overview documentation for the WDRM v4. It is scheduled to be available by the end of Q2 2024.” a) If the detailed overview document has been completed, please provide a copy, including any supporting workpapers. b) If instead the detailed overview document has not been completed, when does PG&E expect the document to be completed? | a) Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_053-Q006Atch01CONF.zip” for the requested WDRM v4 documentation suite. b) Not applicable, please see the response to subpart (a) above. | Matthew Taul | 2024-09-18 | 2024-10-02 | 2024-09-27 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_053.zip | 1 | N/A | 6.1.2 | Section 6 - Risk Methodology and Assessment | 6.1.2 Summary of Risk Models | B.1.1. WDRM v4
715 | CPUC - SPD (Safety Policy Division) | 022 | CPUC - SPD (Safety Policy Division)_022 | 1 | CPUC - SPD (Safety Policy Division)_022_Q1 | 2. We looked at QDR metric 15.b from Q1 and Q2 (metric name – Level 2 Findings Fixed) to try to see if we could correlate the number of Level 2 findings fixed with the number of findings fixed reported by PG&E in the last meeting. We got ~55k compared to 69k reported in the last meeting. We wanted to double check why the numbers are not the same. I attached my spreadsheet so your team can see exactly what I did. | PG&E believes there may have been a misunderstanding regarding the Level 2 Findings discussed during the meeting on September 12, 2024. During the September 12 meeting with SPD, PG&E reported the year-to-date Safety and Operational Metrics (SOM) as of June 2024 for Level 2 findings were 69% on time. PG&E did not report on the number of tags completed. It is difficult to compare the SOM with the Quarterly Data Report (QDR). SOMs measure the timeliness of Tier 2 and Tier 3 HFTD Level 2 tags by their maximum allowable timeframes per GO 95 compared to QDR which reports on the total number of tags completed each quarter regardless of their compliance due dates. Furthermore, SOMs includes vegetation management tags whereas the QDR does not and the QDR also includes non-HFTD tags. PG&E would be happy to further discuss or clarify this item at future meetings, if it would be helpful. | Henry Sweat | 2024-09-18 | 2024-10-11 | 2024-10-07 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_022.zip | 0 | N/A | QDR | N/A | N/A | N/A
716 | OEIS | 025 | OEIS_025 | 1 | OEIS_025_Q1 | Specific to VMP ID VP_BC125-D06_1674177_2020, please confirm the following: a. Confirm if the GPS point 37.56086076985676, -120.00231237377247 is the location of the log and slash for the associated VMP ID b. Confirm the wood destination for the tree in question. c. Confirm if the log and slash in the attached photographs matches the tree in question (Pinus sabiniana, sixty feet height with 24-inch dbh off Sherlock Road, Mariposa, CA) d. If this is not the same tree, please supply photographs of the tree or tree stump and slash. | PG&E completed a clean-up and disposal of wood and slash at the Sherlock Road location as of September 25, 2024. Please see the following before and after photos: • Pre-disposal: “WMP-Discovery2023-2025_DR_OEIS_025-Q001Atch01.pdf;” and • Post-disposal: “WMP-Discovery2023-2025_DR_OEIS_025-Q001Atch02.pdf.” a. PG&E performed a field visit to the coordinates listed above on September 23, 2024, and confirms that the log and slash for VMP ID VP_BC125-D06_1674177_2020 are located these GPS coordinates. b. PG&E confirms the original destination for the wood in question was located at the following coordinates: 37.56086076985676, -120.00231237377247. Please note, a clean-up was facilitated at this location and the wood and slash have been removed. c. Yes, the log and slash photographs provided by Energy Safety in this request match the tree in question. d. Not applicable, please see the response to subpart (c) above. | Ramzi Ibrahim | 2024-09-17 | 2024-09-27 | 2024-09-27 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/OEIS_025.zip | 2 | N/A | QDR | N/A | N/A | N/A
717 | OEIS | 025 | OEIS_025 | 2 | OEIS_025_Q2 | Specific to VMP ID: VP_BC125-H01_1633087_2020, VP_BC125-H01_1632351_2020, VP_BC125-H01_1633192_2020, VP_BC125-H01_1632349_2020 a. Confirm if the GPS point 37.52410, -120.00378 is the location of the log, chips, and slash for the associated VMP ID VP_BC125-H01_1633087_2020 b. Confirm if the GPS point 37.52359, -120.00448 is the general location of the various log, chips, and slash for the associated VMP IDs: VP_BC125- H01_1632351_2020, VP_BC125-H01_1633192_2020, VP_BC125- H01_1632349_2020 c. Confirm the wood, chips, and slash destination for the trees in question. d. Confirm if the logs, chips, and slash in the attached photographs match the trees in question on Gold Creek Lane, Mariposa, CA e. If these are not the same trees, please supply photographs of the tree or tree stump, chips, and slash. | PG&E completed clean up and disposal of wood and slash at the Gold Creek Lane location as of September 25, 2024. Please see the table below for before and after photos. Gold Creek Lane Pre-Clean-Up WMP-Discovery2023-2025_DR_OEIS_025-Q002Atch01.pdf Pre-Clean-Up WMP-Discovery2023-2025_DR_OEIS_025-Q002Atch02.pdf Pre-Clean-Up WMP-Discovery2023-2025_DR_OEIS_025-Q002Atch03.pdf Pre-Clean-Up WMP-Discovery2023-2025_DR_OEIS_025-Q002Atch04.pdf Pre-Clean-Up WMP-Discovery2023-2025_DR_OEIS_025-Q002Atch05.pdf Gold Creek Lane Pre-Clean-Up WMP-Discovery2023-2025_DR_OEIS_025-Q002Atch06.pdf Pre-Clean-Up WMP-Discovery2023-2025_DR_OEIS_025-Q002Atch07.pdf Post-Clean-Up WMP-Discovery2023-2025_DR_OEIS_025-Q002Atch08.pdf Post-Clean-Up WMP-Discovery2023-2025_DR_OEIS_025-Q002Atch09.pdf Post-Clean-Up WMP-Discovery2023-2025_DR_OEIS_025-Q002Atch10.pdf Post-Clean-Up WMP-Discovery2023-2025_DR_OEIS_025-Q002Atch11.pdf Post-Clean-Up WMP-Discovery2023-2025_DR_OEIS_025-Q002Atch12.pdf Post-Clean-Up WMP-Discovery2023-2025_DR_OEIS_025-Q002Atch13.pdf Post-Clean-Up WMP-Discovery2023-2025_DR_OEIS_025-Q002Atch14.pdf a. PG&E performed a field visit to the coordinates listed above on September 23, 2024, and confirms that the log and slash for VMP ID VP_BC125- H01_1633087_2020 are located at these GPS coordinates. b. PG&E performed a field visit to the coordinates listed above on September 23, 2024, and confirms that the log and slash for the following VPs are located at these GPS coordinates: o VP_BC125- H01_1632351_2020 o VP_BC125-H01_1633192_2020 o VP_BC125- H01_1632349_2020. c. PG&E confirms the original destination for the wood in question for the following was located at the following coordinates: 37.52359, -120.00448: o VP_BC125- H01_1632351_2020 o VP_BC125-H01_1633192_2020 o VP_BC125- H01_1632349_2020. Please note, a clean-up was facilitated at this location and the wood and slash have been removed. d. Yes, the log and slash photographs provided by Energy Safety in the DR-268 data request matches the tree in question. e. Not applicable, please see the response to subpart (d) above. | Ramzi Ibrahim | 2024-09-17 | 2024-09-27 | 2024-09-27 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/OEIS_025.zip | 14 | N/A | QDR | N/A | N/A | N/A
718 | CalPA | Set WMP-54 | CalPA_Set WMP-54 | 1 | CalPA_Set WMP-54_Q1 | a) Has PG&E done any research into Is limiters4 for wildfire mitigation?5 b) If yes, please provide a brief description of the research PG&E has done, including at least the minimum following information: Research Study Name Description of Research Objectives Results Start Date End Date c) Has PG&E evaluated the potential use of Is limiters in PG&E’s system for wildfire mitigation purposes? d) If the answer to part (c) is yes, please provide a brief description of all potential use case(s) PG&E has evaluated for Is limiters. e) If the answer to part (c) is yes, state the time frame during which this evaluation took place. f) If the answer to part (c) is yes, list all benefits that PG&E has identified regarding the use of Is limiters in PG&E’s system. g) If the answer to part (c) is yes, list all downsides that PG&E has identified regarding the use of Is limiters in PG&E’s system. h) If the answer to part (c) is yes, state the estimated cost (may be a range) regarding the use of Is limiters in PG&E’s system. i) Please provide all research documents and reports that PG&E has written, commissioned, or funded on this topic. j) Does PG&E plan to perform evaluation in the future regarding the use of Is limiters in PG&E’s system for wildfire mitigation purposes? State approximately when, if yes. | a) No, we have not done research into Is limiters for wildfire mitigation. b) Not applicable, please see the response to subpart (a) above. c) No, we have not evaluated the potential use of Is limiters in our system for wildfire mitigation purposes. d) Not applicable, please see the response to subpart (c) above. e) Not applicable, please see the response to subpart (c) above. f) Not applicable, please see the response to subpart (c) above. g) Not applicable, please see the response to subpart (c) above. h) Not applicable, please see the response to subpart (c) above. i) Not applicable, please see the response to subpart (c) above. j) No, we do not plan to perform evaluation in the future regarding the use of Is limiters in our system for wildfire mitigation purposes. | Tyler Holzschuh | 2024-10-29 | 2024-11-13 | 2024-11-13 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_054.zip | 0 | N/A | N/A | N/A | N/A | N/A
719 | CalPA | Set WMP-54 | CalPA_Set WMP-54 | 2 | CalPA_Set WMP-54_Q2 | a) Has PG&E done any research into semiconductor assisted circuit breakers6 for wildfire mitigation?7 b) If yes, please provide a brief description of the research PG&E has done, including at least the minimum following information: Research Study Name Description of Research Objectives Results Start Date End Date c) Has PG&E evaluated the potential use of semiconductor assisted circuit breakers in PG&E’s system for wildfire mitigation purposes? d) If the answer to part (c) is yes, please provide a brief description of all potential use case(s) PG&E has evaluated for semiconductor assisted circuit breakers. e) If the answer to part (c) is yes, state the time frame during which this evaluation took place. f) If the answer to part (c) is yes, list all benefits that PG&E has identified regarding the use of semiconductor assisted circuit breakers in PG&E’s system. g) If the answer to part (c) is yes, list all downsides that PG&E has identified regarding the use of semiconductor assisted circuit breakers in PG&E’s system. h) If the answer to part (c) is yes, state the estimated cost (may be a range) regarding the use of semiconductor assisted circuit breakers in PG&E’s system. i) Please provide all research documents and reports that PG&E has written, commissioned, or funded on this topic. j) Does PG&E plan to perform evaluation in the future regarding the use of semiconductor assisted circuit breakers in PG&E’s system for wildfire mitigation purposes? State approximately when, if yes. | a) No, we have not done research into semiconductor assisted circuit breakers for wildfire mitigation. b) Not applicable, please see the response to subpart (a) above. c) Yes, we have evaluated the potential use of semiconductor assisted circuit breakers limiters in our system for wildfire mitigation purposes. d) In approximately 2019-2020, we evaluated a proposal from SciBreak to develop a distribution class circuit breaker that could interrupt fault current in about three milliseconds using power electronics. e) This evaluation took place in approximately 2019-2020. f) The primary benefit identified was the potential to reduce fault energy by reducing fault clearing times. g) We determined that the proposed technology was novel and largely unproven. SciBreak did not offer a finished product and was not proposing circuit breakers that would meet many of the ANSI/IEEE standards for medium voltage circuit breakers that are industry standard. h) We do not have an estimated cost regarding the use of semiconductor assisted circuit breakers in our system. i) We are not aware of any research documents or reports that we have written, commissioned, or funded on this topic. j) No, we do not plan to perform evaluation in the future regarding the use of semiconductor assisted circuit breakers limiters in our system for wildfire mitigation purposes. | Tyler Holzschuh | 2024-10-29 | 2024-11-13 | 2024-11-13 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_054.zip | 0 | N/A | N/A | N/A | N/A | N/A
720 | CalPA | Set WMP-54 | CalPA_Set WMP-54 | 3 | CalPA_Set WMP-54_Q3 | a) Has PG&E done any research into thyristor crowbars8 for wildfire mitigation?9 b) If yes, please provide a brief description of the research PG&E has done, including at least the minimum following information: Research Study Name Description of Research Objectives Results Start Date End Date c) Has PG&E evaluated the potential use of thyristor crowbars in PG&E’s system for wildfire mitigation purposes? d) If the answer to part (c) is yes, please provide a brief description of all potential use case(s) PG&E has evaluated for thyristor crowbars. e) If the answer to part (c) is yes, state the time frame during which this evaluation took place. f) If the answer to part (c) is yes, list all benefits that PG&E has identified regarding the use of thyristor crowbars in PG&E’s system. g) If the answer to part (c) is yes, list all downsides that PG&E has identified regarding the use of thyristor crowbars in PG&E’s system. h) If the answer to part (c) is yes, state the estimated cost (may be a range) regarding the use of thyristor crowbars in PG&E’s system. i) Please provide all research documents and reports that PG&E has written, commissioned, or funded on this topic. j) Does PG&E plan to perform evaluation in the future regarding the use of thyristor crowbars in PG&E’s system for wildfire mitigation purposes? State approximately when, if yes. | a) No, we have not done research into thyristor crowbars for wildfire mitigation. b) Not applicable, please see the response to subpart (a) above. c) No, we have not evaluated the potential use of thyristor crowbars in our system for wildfire mitigation purposes. d) Not applicable, please see the response to subpart (c) above. e) Not applicable, please see the response to subpart (c) above. f) Not applicable, please see the response to subpart (c) above. g) Not applicable, please see the response to subpart (c) above. h) Not applicable, please see the response to subpart (c) above. i) Not applicable, please see the response to subpart (c) above. j) No, we do not plan to perform evaluation in the future regarding the use of thyristor crowbars in our system for wildfire mitigation purposes. | Tyler Holzschuh | 2024-10-29 | 2024-11-13 | 2024-11-13 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_054.zip | 0 | N/A | N/A | N/A | N/A | N/A
721 | CalPA | Set WMP-54 | CalPA_Set WMP-54 | 4 | CalPA_Set WMP-54_Q4 | a) Has PG&E done any research into other devices (aside from the types referenced in questions 1-3) that can de-energize powerlines in less than 10 milliseconds for wildfire mitigation? b) If yes, please provide a brief description of the research PG&E has done, including at least the minimum following information: Research Study Name Description of Research Objectives Results Start Date End Date c) Has PG&E evaluated the potential use of these other fast-trip devices in PG&E’s system for wildfire mitigation purposes? d) If the answer to part (c) is yes, please provide a brief description of all potential use case(s) PG&E has evaluated for these other fast-trip devices. e) If the answer to part (c) is yes, state the time frame during which this evaluation took place. f) If the answer to part (c) is yes, list all benefits that PG&E has identified regarding the use of these other fast-trip devices in PG&E’s system. g) If the answer to part (c) is yes, list all downsides that PG&E has identified regarding the use of these other fast-trip devices in PG&E’s system. h) If the answer to part (c) is yes, state the estimated cost (may be a range) regarding the use of these other fast-trip devices in PG&E’s system. i) Please provide all research documents and reports that PG&E has written, commissioned, or funded on this topic. j) Does PG&E plan to perform evaluation in the future regarding the use of these other fasttrip devices in PG&E’s system for wildfire mitigation purposes? State approximately when, if yes. | a) No, we have not done research into other devices (aside from the types referenced in questions 1-3) that can de-energize powerlines in less than 10 milliseconds for wildfire mitigation. b) N/A c) No, we have not evaluated the potential use of other devices (aside from the types referenced in questions 1-3) that can de-energize powerlines in less than 10 milliseconds in our system for wildfire mitigation purposes. d) N/A e) N/A f) N/A g) N/A h) N/A i) N/A j) No, we do not plan to perform evaluation in the future regarding the use of other devices (aside from the types referenced in questions 1-3) that can de-energize powerlines in less than 10 milliseconds in our system for wildfire mitigation purposes. | Tyler Holzschuh | 2024-10-29 | 2024-11-13 | 2024-11-13 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_054.zip | 0 | N/A | N/A | N/A | N/A | N/A
722 | OEIS | 026 | OEIS_026 | 1 | OEIS_026_Q1 | Q01. Regarding the cost of mitigations: a. PG&E discusses the following mitigation activities in its 2023-2025 Base WMP: i. Covered Conductor Installation ii. Undergrounding iii. Distribution Pole Replacements and Reinforcements iv. Distribution Traditional Hardening v. Transmission Pole/Tower Protections and Reinforcements vi. Transmission Traditional Hardening vii. Transmission Shunt Splices viii. Distribution Protective Devices ix. Breakaway Connector x. Surge Arrestor Removal/Replacement xi. Distribution Motorized Switch Operator (MSO) Replacements xii. Non-Exempt Expulsion Fuse Removal/Replacement xiii. Microgrids, including remote grids xiv. Avian/animal protection plan xv. Enhanced Powerline Safety Settings (EPSS) xvi. Distribution, Transmission, and Substation: Fire Action Schemes and Technology (DTS-FAST) xvii. Downed Conductor Detection (DCD) xviii. Rapid Earth Fault Current Limiter (REFCL) xix. Pole Mounted Sensors xx. Early Fault Detection (EFD) xxi. Distribution Fault Anticipation (DFA) xxii. Smart Tape For each of the above activities, provide: (1) The projected average capital cost per circuit mile1 of projects2 expected to be completed3 in 2025. (2) The average capital cost per circuit mile of projects completed from Jan 1, 2021, to Jun 30, 2024. (3) The average operation and maintenance cost per circuit mile per year4 of projects completed from Jan 1, 2021, to Jun 30, 2024. (4) A discussion of factors that have resulted in projects completed from Jan 1, 2021, to Jun 30, 2024, with a capital cost per circuit mile 20 percent more than the average cost per circuit mile from Jan 1, 2021, to Jun 30, 2024, for that given activity. List the factors and discuss how each impacts the cost. (5) A discussion of factors that have resulted in projects completed from Jan 1, 2021, to Jun 30, 2024, with a capital cost per circuit mile 20 percent less than the average cost per circuit mile from Jan 1, 2021, to Jun 30, 2024, for that given activity. List the factors and discuss how each impacts the cost. (6) Complete the following table for the 10 projects with the highest capital cost per circuit mile and 10 projects with the lowest capital cost per circuit mile completed in 2023. If less than 20 projects were completed in 2023, complete the table for all projects completed in 2023. Mitigation Activity Project ID Location Project length (circuit miles) Project Capital Cost Project Duration5 (days) Capital Cost per circuit mile | Please see “WMP-Discovery2023-2025_DR_OEIS_026-Q001Atch01.xlsx” for data responsive to subparts 1 through 6 of this request. Please note that, of the 22 mitigations listed here, only the following are unitized by circuit mile: Covered Conductor, Undergrounding, Transmission Traditional Hardening,5 and Remote Grids.6 We are unable to provide the information requested with respect to the other mitigations on a circuit mile basis. Please note that operation and maintenance costs after mitigation work is complete are not traceable to a specific mitigation. With regard to our response to subpart 6 for Covered Conductor and Undergrounding, please note that projects with very low milage may result in unrepresentatively high cost per circuit mile metrics. With regard to our response to subpart 6 for Remote Grid, please note that some projects do not currently have the necessary data in our system of record to calculate the project duration and are represented as "N/A.” With regard to our response to subpart 5 for Covered Conductor, Undergrounding, and Remote Grids, please note that work under our Base System Hardening (Base SH) program and work under our Fire Rebuild (FRRB) program are separated to provide visibility to the differences between the two programs. | Will Dundon | 2024-11-07 | 2024-12-20 | 2024-12-20 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/OEIS_026.zip | 1 | N/A | N/A | N/A | N/A | N/A
723 | OEIS | 026 | OEIS_026 | 2 | OEIS_026_Q2 | Q02. Regarding the deployment time of mitigation initiatives: a. For each mitigation activity listed in Q01. a. i-xxii, provide: i. The projected project duration (days/circuit mile)6 for projects expected to be completed in 2025. ii. The average project duration (days/circuit mile) of projects completed from Jan 1, 2021, to Jun 30, 2024. iii. A discussion of factors that have resulted in projects completed from Jan 1, 2021, to Jun 30, 2024, with a project duration (days/circuit mile) 20 percent more than the average project duration from Jan 1, 2021, to Jun 30, 2024, for that given activity. List the factors and discuss how each impacted the project duration. iv. A discussion of factors that have resulted in projects completed from Jan 1, 2021, to Jun 30, 2024, with a project duration (days/circuit mile) 20 percent less than the average project duration from Jan 1, 2021, to Jun 30, 2024, for that given activity. List the factors and discuss how each impacted the project duration. v. Complete the following table for the 10 projects with the longest duration per circuit mile and 10 projects with the lowest duration per circuit mile completed in 2023. If less than 20 projects were completed in 2023, complete the table for all projects completed in 2023. Mitigation Activity Project ID Location Project length (circuit miles) Project Capital Cost Project Duration (days) Duration per circuit mile | Please see “WMP-Discovery2023-2025_DR_OEIS_026-Q002Atch01.xlsx” for data responsive to subparts 1 through 5 of this request. Please note that, of the 22 mitigations listed here, only the following are unitized by circuit mile: Covered Conductor, Undergrounding, Transmission Traditional Hardening,2 and Remote Grids.3 We are unable to provide the information requested with respect to the other mitigations on a circuit mile basis. With regard to our response to subpart 5 for Covered Conductor, Undergrounding, and Remote Grids, please note that work under our Base System Hardening (Base SH) program and work under our Fire Rebuild (FRRB) program are separated to provide visibility to the differences between the two programs. Please also note that there are fewer projects listed in our response to subpart 5 for System Hardening Remote Grid compared to the System Hardening Remote Grid table in response to Q1 subpart 6, because orders that do not currently have the necessary data in our system of record to calculate the project duration are omitted in this response. With regard to our response to subpart 5 for Covered Conductor and Undergrounding, please note that projects with very low milage may result in unrepresentatively high duration per circuit mile metrics. | Will Dundon | 2024-11-07 | 2024-12-20 | 2024-12-20 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/OEIS_026.zip | 1 | N/A | N/A | N/A | N/A | N/A
724 | OEIS | 026 | OEIS_026 | 3 | OEIS_026_Q3 | Regarding mitigation compatibility a. For each mitigation activity listed in Q01. a. i-xxii: i. List the constraints associated with each activity (e.g., cannot be deployed on 3 wire systems, in areas with frequent freeze/thaw cycles, requires communication network to function). ii. Provide a completed compatibility table. Each cell must identify one of the following: (1) Mitigations are compatible and the combination will further reduce wildfire risk. (2) Mitigations are compatible, but combination will not further reduce wildfire risk. (3) Mitigations are compatible, but it is unknown if combination will further reduce wildfire risk. (4) Mitigations are not compatible/combination is impractical. The utility must submit two separate tables, one for transmission specific initiatives and one for distribution specific initiatives, if the transmission and distribution tables are not identical. Example Mitigation Initiative Compatibility Table: Mitigation Activity Covered Conductor Installation Undergrounding Distribution Pole Replacements and Reinforcements (Mitigation Activities continued…) Covered Conductor Installation Mitigations are not compatible/ combination is impractical Mitigations are compatible and combination will reduce additional wildfire risk Undergrounding Mitigations are not compatible/ combination is impractical Mitigations are not compatible/ combination is impractical Distribution Pole Replacements and Reinforcements Mitigations are compatible and combination will reduce additional wildfire risk Mitigations are not compatible/ combination is impractical (Mitigation Activities continued…) END OF | Please see “WMP-Discovery2023-2025_DR_OEIS_026-Q003Atch01.xlsx” for our response to this request. Please note that we have answered “N/A” for mitigations we are not executing. Please refer to the worksheet titled “Compatibility Table Notes” for further details regarding certain entries in the table. With regard to subpart (i), please note that we have provided general constraints associated with each mitigation and that this list is non-exhaustive of all possible constraints. | Will Dundon | 2024-11-07 | 2024-12-20 | 2024-12-20 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/OEIS_026.zip | 1 | N/A | N/A | N/A | N/A | N/A
725 | CALPA | Set WMP-55 | CALPA_Set WMP-55 | 1 | CALPA_Set WMP-55_Q1 | In PG&E’s 2023-2025 Wildfire Mitigation Plan R5 at 487-490, 8.1.3.2.1 Detailed Ground Inspection, the section described PG&E’s adoption of plat maps for detailed ground inspection. For purposes of this question, “lag time to VM remediation” is defined above. a) During the 2023-2025 WMP cycle, did the plat map tiers3 implemented in 2023 affect PG&E’s policy and procedures regarding the lag time to VM remediation? b) If yes, describe how. | (a) With regard to Vegetation Management (VM), the adoption of plat maps described in section 8.1.3.2.1 of the 2023-2025 WMP, titled “Asset Inspections – Detailed Ground Inspections,” did not affect policy and procedure regarding lag time to VM remediation because VM does not utilize plat maps. (b) Not applicable, please see the response to subpart (a) above. | Holly Wehrman | 2024-12-16 | 2025-01-13 | 2025-01-13 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_055.zip | 0 | N/A | 8.1.3.2.1 | Asset Inspections | Detailed Ground Inspection | N/A
726 | CALPA | Set WMP-55 | CALPA_Set WMP-55 | 2 | CALPA_Set WMP-55_Q2 | Populate the tab “Question 2” in the attached excel sheet, with data regarding lag time to VM remediation (Hours).4 Provide rows for each combination of HFTD tier and circuit type, for each quarter from Q1 of 2021 through Q3 of 2024. | Please see our response in the worksheet titled “Question 2” in attachment “WMPDiscovery2023-2025_DR_CalAdvocates_055-Q002Atch01.xlsx.” | Holly Wehrman | 2024-12-16 | 2025-01-13 | 2025-01-13 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_055.zip | 1 | N/A | 8.1.3.2.1 | Asset Inspections | Detailed Ground Inspection | N/A
727 | CALPA | Set WMP-55 | CALPA_Set WMP-55 | 3 | CALPA_Set WMP-55_Q3 | In PG&E’s 2023-2025 Wildfire Mitigation Plan R5 at 487-490, 8.1.3.2.1 Detailed Ground Inspection, the section described PG&E’s adoption of plat maps for detailed ground inspection. For purposes of this question, “lag time to asset remediation” is defined above. a. Did plat map tiers affect policy and procedures for lag time to asset remediation for level 1 findings from 2023-2025? If so, explain how. b. Did plat map tiers affect policy and procedures for lag time to asset remediation for level 2 findings from 2023-2025? If so, explain how. c. Did plat map tiers affect policy and procedures for lag time to asset remediation for level 3 findings from 2023-2025? If so, explain how. | a) No, plat map tiers did not affect policy and procedures for lag time to asset remediation for Level 1 findings from 2023-2025 because Level 1 findings are worked according to their priority, not according to their plat map tier. b) No, plat map tiers did not affect policy and procedures for lag time to asset remediation for Level 2 findings from 2023-2025 because Level 2 findings are worked according to their ignition risk, their HFTD tier, and whether they compromise worker safety. They are not prioritized according to their plat map tier. c) No, plat map tiers did not affect policy and procedures for lag time to asset remediation for Level 3 findings from 2023-2025 because Level 3 findings are worked according to the priority of their isolation zone, not their plat map tier. Isolation zones are bundled and prioritized by their Risk-Spend Efficiency to reduce customer outages and remediation costs | Holly Wehrman | 2024-12-16 | 2025-01-13 | 2025-01-13 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_055.zip | 0 | N/A | 8.1.3.2.1 | Asset Inspections | Detailed Ground Inspection | N/A
728 | CALPA | Set WMP-55 | CALPA_Set WMP-55 | 4 | CALPA_Set WMP-55_Q4 | Populate the tab “Question 4” in the attached excel sheet for lag time to asset remediation (Days).5 Provide rows for each combination of HFTD tier and circuit type, for each quarter from Q1 of 2021 through Q3 of 2024. | Please see our response in the worksheet titled “Question 4” in attachment “WMPDiscovery2023-2025_DR_CalAdvocates_055-Q002Atch01.xlsx.” Please note that we will supplement this response to include transmission data on Friday, January 17, 2025. | Holly Wehrman | 2024-12-16 | 2025-01-13 | 2025-01-13 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_055.zip | 0 | N/A | 8.1.3.2.1 | Asset Inspections | Detailed Ground Inspection | N/A
728 | CALPA | Set WMP-55 | CALPA_Set WMP-55 | 4(s) | CALPA_Set WMP-55_Q4(s) | Populate the tab “Question 4” in the attached excel sheet for lag time to asset remediation (Days).5 Provide rows for each combination of HFTD tier and circuit type, for each quarter from Q1 of 2021 through Q3 of 2024. | Please see our supplemental response in the worksheet titled “Question 4” in attachment “WMP-Discovery2023-2025_DR_CalAdvocates_055-Q004 Supp01Atch01.xlsx”. This supplement includes the requested data regarding the transmission circuit type. Please note, regarding transmission “Level 1” tags, we attempt to report data based on the tag’s original priority level, regardless of later escalation, and that reported averages may be affected by outliers due to challenges identifying all tags escalated from Level 2 or 3 to Level 1. This supplement also includes data regarding Level 1 tags for distribution circuits. | Holly Wehrman | 2024-12-16 | 2025-01-17 | 2025-01-17 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_055.zip | 1 | N/A | 8.1.3.2.1 | Asset Inspections | Detailed Ground Inspection | N/A
729 | CALPA | Set WMP-55 | CALPA_Set WMP-55 | 5 | CALPA_Set WMP-55_Q5 | Per Table 2 of PG&E’s WMP QDRs for 2024 Q1-Q3, there were a total of 23 utility-related ignitions in non-HFTD. This number of ignitions is greater than the full-year totals for 2022 and 2023 (7 in 2022 and 12 in 2023). Please explain this upward trend. | The increase in reported utility related ignitions is attributable to enhancements in our investigation processes and strengthened collaboration with field employees through our roadshow efforts. These improvements have allowed us to more accurately identify and document ignition events both at the initial reporting stage and throughout the investigation process | Holly Wehrman | 2024-12-16 | 2025-01-13 | 2025-01-13 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_055.zip | 0 | N/A | QDR | N/A | N/A | N/A
730 | CALPA | Set WMP-55 | CALPA_Set WMP-55 | 6 | CALPA_Set WMP-55_Q6 | Please provide a list of fires that (1) ignited in non-HFTD areas, (2) ignited in the period from 2017 through 2023, (3) where either PG&E or a fire agency determined that PG&E’s equipment was likely responsible for igniting the fire, and (4) where one or more of the following criteria applies: • The fire burned at least 100 acres, • The fire damaged or destroyed five or more structures, • The fire caused any serious injuries or fatalities, or • PG&E incurred liabilities exceeding $5 million. Populate the tab “Question 6” in the attached excel sheet. Each incident that meets the criteria described above should be a row. Provide the data columns shown in the spreadsheet. If exact data on certain variables (e.g., acres burned or financial liabilities incurred), provide the best available estimate. | Please see the worksheet titled “Question 6” in attachment “WMP-Discovery2023- 2025_DR_CalAdvocates_055-Q002Atch01.xlsx” for our response. With regard to the column titled “Financial liabilities that PG&E incurred,” please note that, any litigation settlements or claim payments related to the Redwood Valley, Sulphur, and 37 Fires would have been issued through the Wildfire Victims Trust. | Holly Wehrman | 2024-12-16 | 2025-01-13 | 2025-01-13 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_055.zip | 1 | N/A | QDR | N/A | N/A | N/A
731 | CALPA | Set WMP-55 | CALPA_Set WMP-55 | 7 | CALPA_Set WMP-55_Q7 | Table 1 of PG&E’s 2024 Q3 QDR states, with regard to the initiative “Eliminate HFTD-HFRA Distribution Backlog,” that PG&E has exceeded its interim target of work order closures. Table A below shows the number of open and overdue asset inspection work orders in the past four quarters. Table A: PG&E’s open or overdue asset inspection work orders at end of each quarter Systemwide 2023 Q4 2024 Q1 2024 Q2 2024 Q3 Number of asset management open work orders (total) 921,114 917,349 933,509 958,903 Number of asset management past due work orders (total) 508,233 497,657 533,537 594,361 Data source: Table 2 of WMP QDRs a) Please explain the reduction in the number of open and overdue work orders in 2024 Q1 compared to 2023 Q4. b) Please explain the increase in the number of open and overdue work orders in 2024 Q2 compared to 2024 Q1. c) Please explain the increase in the number of open and overdue work orders in 2024 Q3 compared to 2024 Q2. d) State PG&E’s number of overdue, ignition-risk, asset work orders in HFTD/HFRA as of the end of 2024 Q3. | a) There are fewer open and overdue work orders in 2024 Q1 compared to 2023 Q4 because: (1) inspectors are trained on the latest inspection job aid early in the year as full scale inspection ramps up towards the end of Q1; and (2) open work orders are completed more efficiently in Q1 because there are fewer emergent work orders to complete. b) In Q2, more work orders are generally created as inspections increase and emergent level 1 and level 2 work take priority over level 3 work. c) In Q3, more work orders are generally created as inspections increase and emergent level 1 and level 2 work take priority over level 3 work. d) For distribution, there are 163,610 overdue, ignition-risk, asset work orders in HFTD/HFRA as of the end of 2024 Q3. For transmission, there are 1,980 overdue, ignition-risk, asset work orders in HFTD/HFRA as of the end of 2024 Q3 | Holly Wehrman | 2024-12-16 | 2025-01-13 | 2025-01-13 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_055.zip | 0 | N/A | QDR | N/A | N/A | N/A
732 | CALPA | Set WMP-55 | CALPA_Set WMP-55 | 8 | CALPA_Set WMP-55_Q8 | Table 13 of PG&E’s 2024 Q2 QDR reports 175,426 asset work orders that related to distribution, were located in the HFTD, and had a due date prior to August 1, 2024.6 Table 13 of PG&E’s 2024 Q3 QDR reports 194,181 work orders that relate to distribution, are located in the HFTD, and have a due date prior to November 1, 2024.7 a) Please list all factors that contributed to the increase of approximately 19,000 overdue work orders. b) State how many of the 175,426 overdue work orders from 2024 Q2 were considered “ignition-risk.” c) State how many of the 194,181 overdue work orders from 2024 Q3 are considered “ignition-risk.” | a) The primary factors are: 1. Work orders were prioritized by risk-spend efficiency, not by due date. 2. Level three work orders from inspections in Q4 of previous years came due in this timeframe. b) 147,295 work orders were considered “ignition-risk.” c) 163,610 work orders were considered “ignition-risk.” | Holly Wehrman | 2024-12-16 | 2025-01-13 | 2025-01-13 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_055.zip | 0 | N/A | QDR | N/A | N/A | N/A
733 | CPUC - SPD (Safety Policy Division) | 024 | CPUC - SPD (Safety Policy Division)_024 | 1 | CPUC - SPD (Safety Policy Division)_024_Q1 | When reviewing PG&E’s QDR submission, SPD identified that Ignition 20231165M was associated with three wires down records including Wire Down ID: 1882569, 1882568 and 1882578. SPD noted it appears the wires down was associated with three outages including Outage ID: 1882569, 1882578, 1882568. SPD noted a similar issue with Wires Down 507 which has two Object IDs 20018 and 20109. SPD is concerned that multiple wires down events are being reported for a single wire down event. a. Explain why it appears multiple wires down events are being reported for a single wire down event. b. If there is a discrepancy, send a corrected data set. Explain how the data was corrected. i. If PG&E does not view this as a discrepancy –send an adjusted data set which only includes data for the wires down event closest to the actual wires event. Explain how the data was adjusted. c. Discuss if the apparent discrepancy will change the wires down data submitted as part of the Safety Operational Metrics (SOM) and Safety Performance Metrics (SPMs). Re-submit the data if it changes the data. d. SPD previously met with PG&E regarding apparent discrepancies between the reported wires down values in the QDR, SOM and SPM. SPD recalls some of the discrepancies may have been related to the date the data was pulled, but SPD recalls PG&E was planning to update the data sets. i. Ensure the data sent in 1.b is updated based on PG&E’s work updating the data sets. ii. Submit the updated data sets to SPD. e. When PG&E records a wire down event, if all three phases are down, would PG&E record this as one event, or three events? Is the number of wires down tracked? | a. We utilize our Integrated Logging Information System ("ILIS") to identify and calculate our wires down metrics. ILIS and Outage Events have been built to record outage information and customer details on the restoration process. The reporting structure for ILIS does not give single outage details for specific events. In most cases, wire downs will be over-reported due to this nature. The example above is a scenario where the initial outages were found to be due to unknown causes. Upon restoring power, another outage event occurred which resulted in the finding of a wire down event. The previous outages were changed from an unknown cause to a wire down event. We identify and calculate our wires down metrics according to our procedure, TD-2200P-01 Atch. 2. Please see “WMP-Discovery2023-2025_DR_SPD_024-Q001Atch01.pdf.” We currently believe we may be over-reporting this metric, and we are evaluating our practice and procedure to determine if changes to our calculation of this metric can be made to make this metric more accurate while also not under-reporting the number of wires down events. Please let us know if you would like to meet to discuss this request and our processes for calculating wires down metrics. We would be happy to explain our processes and limitations with you, as well as how we developed our current approach to this metric. b. The discrepancy cannot be resolved via our current process for calculating this metric for all the outages due to limitations in our current technology. Each wire down event would need to be evaluated and investigated individually due to the method we use to calculate this metric, described in our response to subpart a, above. Given the many years of data that would need to be manually reviewed to make the QDR data align, PG&E objects to this request on the grounds that it is overbroad and unduly burdensome. c. We calculate the wire down metric in our Safety Operational Metrics (SOM) and Safety Performance Metrics (SPM) in the same way that we do our QDR, and that data is subject to the same limitations described in our response to subparts a and b, above. Given the many years of data that would need to be manually reviewed, PG&E objects to this request on the grounds that it is overbroad and unduly burdensome. d. The discrepancy that SPD previously discussed with PG&E in regards to differences in the QDR and SOMs is unrelated to this issue. The referenced discrepancy was related to differences in numbers between multiple reports and this was due to the timing of the data pull for the report. That discrepancy has been resolved. Please refer to our most recent QDR, SOM, and SPM submissions for updated data that addresses this discrepancy. e. We do not record each phase as individual wire down events. We do not track the number of phases that fall at a particular location. | Henry Sweat | 2025-01-08 | 2025-01-23 | 2025-01-31 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_024.zip | 1 | N/A | QDR | N/A | N/A | N/A
734 | CPUC - SPD (Safety Policy Division) | 024 | CPUC - SPD (Safety Policy Division)_024 | 2 | CPUC - SPD (Safety Policy Division)_024_Q2 | SPD met with PG&E to discuss the tag creation criteria PG&E uses for slack guys, and PG&E’s study on slack guys (ATS Report: 006.4.2-23.9), which developed slack guy criteria based off PG&E’s permitted lean. SPD discussed PG&E’s response to SPD_019-Q001 which implied wind forces (or other horizontal forces) could cause a pole with no lean to develop significant stresses before the slack guy became taut under the current criteria. What actions (if any) is PG&E taking to adjust its tag creation criteria for slack guys? | To adjust for slack guys, PG&E updated ATS Report 006.4.2-23.9, Revision 1, which is included as attachment “WMP_Discovery2023-2025_DR_SPD_024-Q002Atch01CONF.pdf.” As a result of this updated ATS Report, PG&E will also update the Overhead Inspection Job Aid (TD-2305M-JA02). | Henry Sweat | 2025-01-08 | 2025-01-23 | 2025-01-23 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_024.zip | 1 | N/A | 2022 WMP 7.3 | Pole Loading | 7.3.3.13 Pole loading infrastructure hardening and replacement program based on pole loading assessment program | N/A
735 | CPUC - SPD (Safety Policy Division) | 024 | CPUC - SPD (Safety Policy Division)_024 | 3 | CPUC - SPD (Safety Policy Division)_024_Q3 | PG&E stated in the response to SPD_019_002 that PG&E planned to update calculations regarding deteriorated poles, and update TD-23095M-JA02 if necessary. Submit the updated calculations, updated ATS study and any changes in the job aid. Provide a narrative of what changes were made. | PG&E has updated ATS Report 006.4.2-23.11, Revision 1, which is attached as “WMP_Discovery2023-2025_DR_SPD_024-Q003Atch01CONF.pdf.” In addition, PG&E updated the Overhead Inspection Job Aid (TD-2305M-JA02), Revision 14, which is attached as “WMP_Discovery2023-2025_DR_SPD_024-Q003Atch02.pdf.” Please see page 30 for the updated decision tree. Previously, PG&E created replacement Priority E notifications for poles with cross grain cracks/cuts larger than 40% of the pole’s circumference. PG&E updated the criteria to create replacement Priority E notifications for poles with cross grain cracks/cuts larger than 30%, but less than 40% of the pole’s circumference. For poles with cross grain cracks/cuts larger than 40%, PG&E elected to utilize the Priority X notification. | Henry Sweat | 2025-01-08 | 2025-01-23 | 2025-01-23 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_024.zip | 2 | N/A | 2022 WMP 7.3 | Pole Loading Calculations | 7.3.4.13 Pole loading assessment program to determine safety factor | N/A
736 | CPUC - SPD (Safety Policy Division) | 024 | CPUC - SPD (Safety Policy Division)_024 | 4 | CPUC - SPD (Safety Policy Division)_024_Q4 | SPD met with PG&E to discuss PG&E’s remaining strength calculations. The ISM previously reported to SPD that PG&E plans to transition from using the current remaining strength calculation as criteria for replacement of poles to using the Safety Factor as the primary criteria. SPD also understands that there will also be a remaining strength criterion where poles with less than 25 percent remaining strength will be replaced automatically regardless of the Safety Factor. SPD reviewed the tool used to calculate the remaining strength and found it may not consider failures modes which could become critical for poles that are severely deteriorated. Since these failure modes are not considered, the tool may overestimate the strength of poles (and thus overestimate the Safety Factor) with estimated remaining strengths near, but slightly above 25 percent. SPD understands that under the new criteria for pole replacement, poles at this deterioration level, would have historically been replaced, but will no longer be replaced if the Safety Factor is above a certain threshold. What actions (if any) is PG&E taking to review (1) the accuracy of the remaining strength calculation at low remaining strengths and (2) the initially proposed criteria of 25 percent remaining strength? | 1) In order to assess the accuracy of the remaining strength calculation at low remaining strengths, and in accordance with GO 165, PG&E performs intrusive inspections on our poles, which includes assessing the internal condition of the pole. In order to adequately assess the decay pockets, our inspectors model the observed decay in D-Calc, an industry standard software, which provides a remaining strength of the pole. In accordance with our internal procedures, all poles with 35% or less calculated remaining strength are replaced expeditiously via our Priority-X notification. This threshold allows us to eliminate risk on our system by replacing these severely degraded poles urgently. As a result of our established process, we are preventatively addressing the risk of localized bucking in poles with severe decay. 2) PG&E is currently working through the process mapping and data exchanges for transitioning from remaining strength to safety factor. As part of that process, we are evaluating the appropriate thresholds. Additionally, as a further part of this process, WMP-Discovery2023-2025_DR_SPD_024-Q004 Page 2 PG&E has not yet committed to the 25% remaining strength as we are still analyzing what should be the appropriate threshold. | Henry Sweat | 2025-01-08 | 2025-01-23 | 2025-01-23 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_024.zip | 0 | N/A | 2022 WMP 7.3 | Pole Loading Calculations | 7.3.4.13 Pole loading assessment program to determine safety factor | N/A
737 | CPUC - SPD (Safety Policy Division) | 024 | CPUC - SPD (Safety Policy Division)_024 | 5 | CPUC - SPD (Safety Policy Division)_024_Q5 | In PG&E’s response to WMP-Discovery2023-2025_DR_SPD_019-Q002Supp01, PG&E stated that Priority A tags require immediate response. SPD’s review of PG&E’s response found numerous Priority A tags which took longer than two days to complete field work. a. Discuss when or why a Priority A tag would take longer than two days to complete field work. b. Discuss how PG&E mitigates risk of a Priority A tag in this situation. c. Work Order 128285084 was opened on 3/13/2024. The notes report the hazard was mitigated on 3/15. Why was the hazard not mitigated sooner? Should this hazard have been mitigated on 3/13? i. Submit the photos referenced in the work notes. d. Provide an overview and examples of “Other Inspections” (see column M of the excel response to WMP-Discovery2023-2025_DR_SPD_019-Q002Supp01). e. SPD did not see a classification in Column M for tags found by a troubleman during an outage. Provide and update submission which includes all Priority A tags. | a. When there is a situation where permanent repairs or replacements of an asset cannot be performed under reasonable circumstances such as third party refusal, customer issue, no access, permit required, or system emergencies (e.g. fires, sever weather conditions), correction times may be extended. b. In this situation, mitigating risks related to a Priority A tag involves executing work per the current PG&E Standard TD-2060S, provided here as attachment “WMP-Disocery2023-2025_DR_SPD_024-Q005Atch01CONF.pdf.” c. Priority A tags can multiple days to complete due to a variety of reasons. In the case of Work Order #128285084, all hazards were mitigated by removing the old pole and floating the conductors. This pole was located on the backside of Pinecrest Lake National Recreation Trail, north of the inlet, and set in solid rock, WMP-Discovery2023-2025_DR_SPD_024-Q005 Page 2 making this a challenging job to complete. Additionally, due to snow there were access issues to complete the work, hence a brief extension was issued to properly install a new pole. i. Please see the pictures in attachment “WMP-Disocery2023-2025_DR_SPD_024-Q005Atch02CONF.pdf.” d. Examples of types of “Other Inspections” include but are not limited to: pole test and treat, infrared, supervisor work verifications, and troubleshooter. This category generally includes all methods of inspection that were not GO 165 patrols or detailed inspections. e. Attachment “WMP-Discovery2023-2025_DR_SPD_024-Q005Atch03CONF.xlsx.” includes column “W” which provides the source of who submitted the A-tag. | Henry Sweat | 2025-01-08 | 2025-01-23 | 2025-01-23 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_024.zip | 3 | N/A | 8 | 8.0 Wildfire Mitigations | 8.1.3 Asset Inspections | N/A
738 | CPUC - SPD (Safety Policy Division) | 024 | CPUC - SPD (Safety Policy Division)_024 | 6 | CPUC - SPD (Safety Policy Division)_024_Q6 | Provide an update to the chart in the attached presentation which describes the percentage of circuit miles at each FPI level for each month which includes data from years 2021-2024 (see slide 38). SPD is primarily interested in the data – so it is not necessary to reproduce the exact chart if this data is easier for PG&E to provide in another way. | Please see attachment “WMP-Discovery2023-2025_DR_SPD_024-Q006Atch01.pdf” for an updated chart. Please note that our data for this chart is only final for the time period of 2021-2023, and we therefore cannot provide data for 2024. We will provide the 2024 data once finalized. | Henry Sweat | 2025-01-08 | 2025-01-23 | 2025-01-23 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_024.zip | 1 | N/A | Appendix D | Appendix D - Areas for Continued Improvement | ACI PG&E-22-06 – Addressing Increase in Risk Events | N/A
739 | CPUC - SPD (Safety Policy Division) | 024 | CPUC - SPD (Safety Policy Division)_024 | 7 | CPUC - SPD (Safety Policy Division)_024_Q7 | Provide GIS maps of the Overhead lines which are Covered Conductor which include the installation date of the covered conductor. | PG&E interprets the request for “GIS maps” as geospatial data. Please see the following attachments for data on PG&E’s primary overhead covered conductor lines as of January 16, 2024. The lines were selected by querying our Electric Distribution GIS (EDGIS) system of record where the primary overhead line’s Conductor Code attribute matches covered conductor. • “WMP-Discovery2023-2025_DR_SPD_024-Q007Attch01CONF.gdb.zip” – a geodatabase containing line features representing distribution primary overhead covered conductor lines. • “WMP-Discovery2023-2025_DR_SPD_024-Q007Attch02CONF.xlsx” – a tabular list of the lines contained in the accompanying geodatabase. Both files contain the following fields/attributes: • Circuit ID; • Circuit Name; • Status – indicates if the line is ‘In Service’ or ‘Idle’; • Install Year – where available, the year that the line was installed; • Customer Owned – where available, indicates the ownership of the line; and • Global ID – the record’s unique identifier that correlates to the line feature in the accompanying geodatabase. | Henry Sweat | 2025-01-08 | 2025-01-23 | 2025-01-23 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_024.zip | 2 | N/A | 8.1.2 | Grid Design and System Hardening | Various | ACI 23-08 Covered Conductor Inspection and Maintenance
740 | CPUC - SPD (Safety Policy Division) | 024 | CPUC - SPD (Safety Policy Division)_024 | 8(s) | CPUC - SPD (Safety Policy Division)_024_Q8(s) | Provide GIS maps that show the underground lines which include the installation date of the underground lines. a. Provide a list of segments of underground lines which have been de-energized during PSPS events since 2017, with the date each segment was de-energized. Include underground circuit segments which were de-energized by an outage on an upstream circuit segment, which lead to an outage of the underground circuit segment. b. Provide a list of segments of underground lines since 2021 which were de-energized during an outage when EPSS was enabled with the relevant outage id. Include underground circuit segments which were de-energized by an outage on an upstream circuit segment, which lead to an outage of the underground circuit segment. | PG&E is providing results from additional analysis to support the response to questions 8a and 8b.1 As described below, the original analysis was based on outage data paired with undergrounding conducted as part of the system hardening program, while the supplemental analysis is based on geospatial data of all undergrounding paired with outage data: • Original analysis – starting with a list of all PSPS and EPSS outages, the affected circuit segments were compared to the System Hardening project log to correlate with circuit segments that were undergrounded before the outage took place. This yielded a list of circuit segments with underground lines that were installed through the System Hardening program only, not all other undergrounding infrastructure. • Supplemental analysis – starting with a list of all underground distribution primary lines identified in EDGIS (Electric Distribution GIS, as of 1/28/25, the circuit segments of those lines were compared to the PSPS and EPSS outages to correlate the circuit segments that experienced an outage. This yields a list of all circuit segments with underground lines from our GIS system of record. The approach of the supplemental analysis results in a more comprehensive list of PG&E distribution underground primary lines that have been affected by outages. The original approach only considered undergrounded lines installed through the System Hardening program. Please see attachment “WMP-Discovery2023-2025_DR_SPD_024- Q008Supp01Atch01.xlsx” for a list of circuit segments that have experienced either a PSPS or EPSS outage between 2017 and 2024. Note the following regarding the data: • Circuit segments are included in this response if they contain a non-zero amount of distribution underground infrastructure and experienced PSPS and/or EPSS impacts. • The analysis is based on a list of transformers that are fed by underground primary conductor. 1 Please note that our response on January 23, 2025, stated that we were providing “data on PG&E’s primary underground lines as of January 16, 2024.” This was a typo; the data provided was as of January 16, 2025. • Although a circuit segment may be listed as experiencing an outage, the specific span on that circuit segment where the outage originated may not be underground. • There may be undergrounding work completed in the field that is not yet recorded in our GIS. In these cases, the applicable underground circuit segment may not be included in the list. • To determine if a circuit segment contained underground infrastructure, the installation date of the underground infrastructure was compared to the outage date. There are circuit segments that do not have an installation date in our GIS; these circuit segments were not included in this analysis. • The EPSS program was implemented by PG&E in late 2021. • Circuit configurations and naming conventions change over time. The provided Circuit ID and Circuit Name reflect data as of 1/31, while the provided WDRM V4 circuit segment names are static. Thus, the provided circuit name may not match the circuit name implied by the circuit segment name. • Please note that outage reduction due to undergrounding may be contingent on the configuration of the grid at the time of the PSPS event or EPSS outage. a. See column D (Count of PSPS Outages) of the attachment to identify the circuit segments that have experienced a PSPS outage. • Circuit segments that were de-energized because an upstream circuit segment was de-energized (as part of a PSPS outage) are included in this list but cannot be differentiated from circuit segments that were targeted for PSPS. • Please note that whether an area is subject to PSPS events after lines in that area have been undergrounded depends on whether, and how much of, the upstream and downstream line sections have been undergrounded. For example, an underground circuit segment may experience a PSPS outage if the undergrounded section remains connected to an overhead line (either upstream or downstream) that is subject to PSPS. As PG&E completes additional undergrounding, and underground sections are connected, more PSPS risk will be mitigated. • See worksheet ‘Q8a – PSPS Outages’ for a list of each aforementioned circuit segments’ outage dates and event identifier. b. Please see attachment “WMP-Discovery2023-2025_DR_SPD_024-Q008Supp01Atch0.xlsx,” (‘8b-EPSS’ worksheet). See column E (Count of EPSS Outages) of the attachment to identify the circuit segments that have experienced a EPSS outage. Note the following regarding the data: • Circuit segments that were de-energized because an upstream circuit segment was de-energized (due to an EPSS outage) is not available in our records and are not included in this list. • See worksheet ‘Q8b – EPSS Outages’ for a list of each aforementioned circuit segments’ outage dates and report identifier. PG&E would be pleased to meet with SPD to discuss the information provided in this response, if it would be helpful. | Henry Sweat | 2025-01-08 | 2025-02-07 | 2025-02-07 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_024.zip | 1 | N/A | 8 | Section 8.1.2 - Grid Design and System Hardening | 8.1.2.2 Undergrounding of electric lines and/or equipment | 2.1.1.2 GH-04 Undergrounding
740 | CPUC - SPD (Safety Policy Division) | 024 | CPUC - SPD (Safety Policy Division)_024 | 8 | CPUC - SPD (Safety Policy Division)_024_Q8 | Provide GIS maps that show the underground lines which include the installation date of the underground lines. a. Provide a list of segments of underground lines which have been de-energized during PSPS events since 2017, with the date each segment was de-energized. Include underground circuit segments which were de-energized by an outage on an upstream circuit segment, which lead to an outage of the underground circuit segment. b. Provide a list of segments of underground lines since 2021 which were de-energized during an outage when EPSS was enabled with the relevant outage id. Include underground circuit segments which were de-energized by an outage on an upstream circuit segment, which lead to an outage of the underground circuit segment. | PG&E interprets the request for “GIS maps” as seeking geospatial data. Please see the following attachments for data on PG&E’s primary underground lines as of January 16, 2024. The lines were selected by querying our Electric Distribution GIS (EDGIS) system of record where the primary line’s Install Code attribute is underground. • “WMP-Discovery2023-2025_DR_SPD_024-Q008Atch01CONF.gdb.zip” – a geodatabase containing line features representing distribution primary underground lines. • “WMP-Discovery2023-2025_DR_SPD_024-Q008Atch02CONF.xlsx” – a tabular list of the lines contained in the accompanying geodatabase. Both files contain the following fields/attributes: • Circuit ID; • Circuit Name; • Status – indicates if the line is ‘In Service’ or ‘Idle’; WMP-Discovery2023-2025_DR_SPD_024-Q008 Page 2 • Install Year – where available, the year that the line was installed; • Customer Owned – where available, indicates the ownership of the line; • Global ID – the record’s unique identifier that correlates to the line feature in the accompanying geodatabase. a. Please see attachment “WMP-Discovery2023-2025_DR_SPD_024-Q008Atch03.xlsx”, (‘8a-PSPS’ worksheet), for a list of PSPS outages that involved circuit segments that contain undergrounded lines. Circuit segments with undergrounded lines may only limit PSPS impacts if the entire circuit is undergrounded upstream to the substation. Note the following regarding the data: • Circuit segments are reported in this response because they contain at least a portion of distribution underground infrastructure. • The PSPS system of record captures outages at the service point and transformer level, which is then mapped to a circuit segment. • The PSPS system of record does not capture the type of line (overhead vs underground) of the circuit segment at the time of the outage. Therefore, the PSPS system of record has been compared to System Hardening and Undergrounding records to determine if a circuit segment contained distribution underground infrastructure at the time of the outage. o This approach does not account for undergrounding work under Rule 20A, 20B, or 20C, and does not account for pre-existing underground lines prior to the inception of the System Hardening and Undergrounding programs. o PG&E is currently conducting a more comprehensive analysis that will include results for all underground lines. This updated list will be submitted to SPD as a supplemental response to this data request. • Some PSPS outages do not have an attributed circuit segment. These records were not included in the comparison described above. • The data includes circuit segments that were de-energized because an upstream circuit segment was de-energized. b. Please see attachment “WMP-Discovery2023-2025_DR_SPD_024-Q008Atch03.xlsx” (‘8b-EPSS’ worksheet) for a list of EPSS outages that involved circuit segments that contain undergrounded lines. Note the following regarding the data: • Circuit segments are reported in this response because they contain at least a portion of distribution underground infrastructure. • The EPSS system of record does not capture the type of line (overhead vs underground) of the circuit segment at the time of the outage. Therefore, the EPSS system of record has been compared to System Hardening and Undergrounding records to determine if a circuit segment contained distribution underground infrastructure at the time of the outage. o This approach does not account for undergrounding work under Rule 20A, 20B, or 20C, and does not account for pre-existing underground lines prior to the inception of the System Hardening and Undergrounding programs. o PG&E is currently conducting a more comprehensive analysis that will include results for all underground lines. This updated list will be submitted to SPD as a supplemental response to this data request. • The data does not include circuit segments that were de-energized because an upstream circuit segment was de-energized. | Henry Sweat | 2025-01-08 | 2025-01-23 | 2025-01-23 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_024.zip | 3 | N/A | 8 | Section 8.1.2 - Grid Design and System Hardening | 8.1.2.2 Undergrounding of electric lines and/or equipment | 2.1.1.2 GH-04 Undergrounding
741 | CALPA | Set WMP-56 | CALPA_Set WMP-56 | 1 | CALPA_Set WMP-56_Q1 | In PG&E’s 2022 Wildfire Mitigation Plan, PG&E describes a “Distribution Arcing Fault Signature Library.”3 a) State the years when the Distribution Arcing Fault Signature Library program is or was active; b) Please provide all final reports from this program; and c) Please provide the names and brief summaries of all libraries created through this program, including when the research took place. | a) After completing this specific partnership research & development project with Lawrence Livermore and Oakridge National Laboratories at the end of 2021, PG&E performed a strategic assessment of the results. It was determined that the outcome of the pilot was not sufficient to develop a comprehensive fault signature library applicable to the larger incipient fault analytics tools that would be used to proactively detect and mitigate conditions that might result in a wildfire. No further action was taken since project completion at the end of 2021. b) Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_056-Q001Atch01.pdf” for the requested information. c) Please see the attachment identified in response to subpart (b) above for the requested information. | Tyler Holzschuh | 2025-01-13 | 2025-01-28 | 2025-01-28 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_056.zip | 1 | N/A | 8.1.2 | Grid Design and System Hardening | Grid Design and System Hardening | N/A
742 | CALPA | Set WMP-56 | CALPA_Set WMP-56 | 2 | CALPA_Set WMP-56_Q2 | a) Has PG&E performed or commissioned any analyses or reports on the cost-benefit tradeoffs of different protective4 schemes for wildfire mitigation between January 2017 and the present? b) If the answer to subpart a) is yes, please provide all relevant reports, including stating who performed the research and when the research took place. | a) Our understanding is that this question seeks analyses or reports comparing the cost-benefit tradeoffs of different protective schemes, defined as schemes and devices responsible for automatically de-energizing powerlines on errant conditions. At this time, we have not identified any analyses or reports on the cost-benefit tradeoffs of different protective schemes for wildfire mitigation between January 2017 and the present except for various cost-benefit analyses and risk-spend efficiency analyses contained in our public filings, including our 2017 RAMP, 2020 GRC, 2020 RAMP, 2020 GRC, 2023 GRC, 2023-2025 WMP, and 2024 RAMP. b) Please refer to the filings identified in our response to subpart (a) above. | Tyler Holzschuh | 2025-01-13 | 2025-01-28 | 2025-01-28 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_056.zip | 0 | N/A | 8.1.2 | Grid Design and System Hardening | Grid Design and System Hardening | ACI 23-07 – Deployment of New Technologies
743 | CALPA | Set WMP-56 | CALPA_Set WMP-56 | 3 | CALPA_Set WMP-56_Q3 | a) Has PG&E researched using technology from high voltage direct current (HVDC) circuit breakers5 (between January 2017 and the present) to make its enhanced powerline safety settings faster? b) If the answer to subpart a) is yes, please provide a detailed description of all research on this topic, including when the research took place. | a) No, we have not researched using technology from high voltage direct current (HVDC) circuit breakers to make the overall fault clearing time when our enhanced powerline safety settings are enabled faster. Please note that overall fault clearing time is made up of protective relay response time and the circuit interruption device interruption time. The response time of these two components is independent of one another. The type of circuit interruption device (e.g. HVDC circuit breaker) may affect overall fault clearing time, but is independent of the enhanced powerline safety settings themselves. b) Not applicable, please see the response to subpart (a) above. | Tyler Holzschuh | 2025-01-13 | 2025-01-28 | 2025-01-28 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_056.zip | 0 | N/A | 8.1.2 | Grid Design and System Hardening | Grid Design and System Hardening | ACI 23-07 – Deployment of New Technologies
744 | CPUC - SPD (Safety Policy Division) | 023 | CPUC - SPD (Safety Policy Division)_023 | 1 | CPUC - SPD (Safety Policy Division)_023_Q1 | Please provide an update to the WMP Cost Totals reported in the 2023-2025 WMP (Table 1) by populating the empty cells in Column 2 of Table 2, below. | Please see the table below for an update to the WMP Cost Totals. Please note that we obtained the “Actual 2023 costs” from our Q4, 2023 Quarterly Data Report. Column 1 Column 2 Actual 2023 costs $5,205,234,000 Proposed 2024 costs $4,985,814,560 Proposed 2025 costs $6,556,767,636 Actual 2020-2022 WMP 3-year Total costs $14,271,037,000 Difference between 2020-2022 actual and 2023-2025 proposed costs (+/-) +$2,476,779,196 Proposed 2023-2025 WMP 3-year Total costs $16,747,816,196 | Kevin Miller | 2024-10-15 | 2024-11-22 | 2024-11-22 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_023.zip | 0 | N/A | 4 | Section 4 - Overview of WMP | 4.3 Proposed Expenditures | 2.3 Expenditures
745 | CALPA | Set WMP-57 | CALPA_Set WMP-57 | 1 | CALPA_Set WMP-57_Q1 | Please fill out the following table with information on each of PG&E’s initiatives pertaining to mitigation of wildfire risk on its transmission system as detailed in its 2023-25 Base Wildfire Mitigation Plan (WMP).1 END OF REQUEST 1 Pacific Gas &Electric Company, 2023-25 Mitigation Plan R4 , January 4, 2024, accessed at https://efiling.energysafety.ca.gov/eFiling/Getfile.aspx?fileid=56145&shareable=true WMP Initiative Number WMP Initiative Name Cost Recovery Venue (i.e. CPUC or FERC) and Docket Number Spending Category or Program (e.g. Major Work Category/Major Activity Type codes) and short description of the program as authorized for cost recovery Capital or Expense Program Working hyperlink to the most recent testimony in support of cost recovery request Working hyperlink to the most recent regulatory decision authorizing cost recovery for this program | Please see “WMP-Discovery2023-2025_DR_CalAdvocates_057-Q001Atch01.xlsx”.2,3,4 Regarding columns C, G, and H, PG&E provides links below and noteworthy information on the TO Formula rate case. PG&E uses a Federal Energy Regulatory Commission (FERC)-approved formula rate model to recover costs from transmission customers through its Transmission Owner (TO) Tariff. With respect to this data request, the rates for calendar year 2023 were set using the TO20 Rate Year 2023 (RY2023) formula update (Docket No. ER19-13-000) and 2024 and 2025 rates were set using the TO21 RY2024 and RY2025 formula updates (Docket Nos. ER24-96-000 and ER25-624-000, respectively). It is important to note that the following features of the FERC formula rate as it applies to PG&E: • Testimony is only filed when the current formula is expiring and when PG&E is requesting a new/updated formula model. • The TO formula rate has a true up mechanism; this mechanism means that rates are trued up to actuals and customers pay the actual costs of the work. • Capital is initially set on a forecast basis, the year prior to the rate year. Capital is only forecasted out a single year for projects forecasted to be in service the following year (the rate year). The capital forecast is subsequently trued up to actuals. The TO capital expenditures forecast can be found in Schedule 9- PlantAdditions of the formula rate. • O&M is submitted on a recorded basis. The O&M recorded costs can be found in Schedule 18-OandM of the formula rate. • PG&E’s latest transmission rates went into effect on January 1, 2025, through the TO21 RY2025 formula update. TO21 is currently in settlement negotiations, and rates will be adjusted for any difference between current rates and the final TO21 formula rate in a subsequent rate year update. • There is no “decision” on the annual rate updates. The formula update rate goes into effect on January 1 annually. Intervenors can protest elements of the rate and PG&E will respond to any FERC directives regarding protests when issued. • TO20 was settled in FERC Docket No. ER19-13-000, et al. through a partial settlement and a global settlement. FERC approved both settlements. 2 We understand “WMP Initiative Number” to mean the “Initiative Tracking ID” as used in our 2023-2025 WMP (e.g. “AI-02,” “GH-05,” etc.). Please note that certain wildfire mitigation work is not tracked by a "WMP Initiative Number." In these cases we include only the WMP Initiative Name. 3 Please note that the Major Work Category and Major Activity Type data provided in the attachment are current as of February 27, 2025 but may be subject to change. 4 With regard to the request for a “short description of the program as authorized for cost recovery,” please note that we do not include itemized program descriptions in our Transmission Owner submissions. Our Transmission Owner submissions include Major Work Category (MWC) codes and descriptions thereof, but not of the associated WMP mitigations. We have included program descriptions from our 2023-2025 Wildfire Mitigation Plan. WMP-Discovery2023-2025_DR_CalAdvocates_057-Q001 Page 3 Below are links to the applicable TO filings for years 2023-2025. 1. TO20 (ER19-13-000): Transmission Owner Rate Case TO20 Formula 2. TO20 RY2023 (ER19-13-000): Annual Formula Transmission Rate Update Filing for Rate Year 2023 (TO20) 3. TO21 (ER24-96-000): Transmission Owner Rate Case TO21 Formula (ER24-96-000) 4. TO21 RY2024 (ER24-96-000): Included in the TO21 submission in item 3 above. 5. TO21 RY2025 (ER25-624-000): Annual Formula Transmission Rate Update Filing for Rate Year 2025 (TO21) | Gordon Miles | 2025-02-12 | 2025-02-27 | 2025-02-27 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_057.zip | 1 | N/A | 8 | 8.1 | 8.1.2/8.1.2.1-8.1.2.12/8.1.3/6.2 | N/A
746 | CPUC - SPD (Safety Policy Division) | 025 | CPUC - SPD (Safety Policy Division)_025 | 1 | CPUC - SPD (Safety Policy Division)_025_Q1 | Provide the confidential version of the pre-submission version of the WMP on 3/10/2025. | Please see “WMP-Discovery2023-2025_DR_SPD_025-Q001Atch01CONF.zip” for our WMP pre-submission to Energy Safety. Please note that this is not our final WMP submission and may be subject to revision before the final WMP is submitted in April. Please note that we have designated this entire submission as confidential to align with Energy Safety’s pre-submission process and guidelines which stipulate that the presubmission documents are only for Energy Safety’s use in performing a pre-submission check and are not to be used for a substantive review of WMP content. | Henry Sweat | 2025-03-05 | 2025-03-10 | 2025-03-10 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_025.zip | 1 | N/A | N/A | N/A | N/A | N/A
747 | CPUC - SPD (Safety Policy Division) | 025 | CPUC - SPD (Safety Policy Division)_025 | 2 | CPUC - SPD (Safety Policy Division)_025_Q2 | Provide the confidential version of TN14365_20240705T205735_20240705_PGE_2023_WMP_R6_Appendix_D_ACI_PGE_2216_Atch01.xlsx. a. If there is a more recent version than that submitted with R6 of the WMP, submit the more recent version. | Please see “WMP-Discovery2023-2025_DR_SPD_025-Q002Atch01CONF.xlsx” for an updated GH-04 (10K Undergrounding) 2023-2026 workplan as of March 14, 2025. Please note the attachment contains confidential information. | Henry Sweat | 2025-03-05 | 2025-03-19 | 2025-03-19 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_025.zip | 1 | N/A | Appendix D | Appendix D - Areas for Continued Improvement | Appendix D | N/A
747 | CPUC - SPD (Safety Policy Division) | 025 | CPUC - SPD (Safety Policy Division)_025 | 2(a) | CPUC - SPD (Safety Policy Division)_025_Q2(a) | Provide the confidential version of TN14365_20240705T205735_20240705_PGE_2023_WMP_R6_Appendix_D_ACI_PGE_2216_Atch01.xlsx. a. If there is a more recent version than that submitted with R6 of the WMP, submit the more recent version. | Please see “WMP-Discovery2023-2025_DR_SPD_025-Q002Rev01Atch01CONF.xlsx” for an updated GH-04 (10K Undergrounding) 2023-2026 workplan as of March 14, 2025. During our meeting with SPD on March 25, 2025, SPD noted that the response provided on March 19, 2025 appeared to include circuit names instead of circuit protection zones in Column M, “Circuit Protection Zone.” This revision provides corrected values for Column M, “Circuit Protection Zone.” Please note the attachment contains confidential information. | Henry Sweat | 2025-03-05 | 2025-03-26 | 2025-03-26 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_025.zip | 1 | N/A | Appendix D | Appendix D - Areas for Continued Improvement | Appendix D | N/A
748 | CPUC - SPD (Safety Policy Division) | 025 | CPUC - SPD (Safety Policy Division)_025 | 3 | CPUC - SPD (Safety Policy Division)_025_Q3 | Provide the confidential version of TN14365_20240705T205735_20240705_PGE_2023_WMP_R6_Appendix_D_ACI_PGE_2216_Atch01.xlsx. a. If there is a more recent version than that submitted with R6 of the WMP, submit the more recent version. | Reference for team: https://www.pge.com/assets/pge/docs/outages-and-safety/outagepreparedness-and-support/pge-wmp-r0-update-040224.pdf#page=23 Please see “WMP-Discovery2023-2025_DR_SPD_025-Q003Atch01.xlsx.” Please note that FIGURE PG&E-B.1.1-3 in our 2025 WMP Update was created as a risk buydown curve for HFTD Circuit Segments (CS) only, and that the graphic required a custom CS ranking that differs from the WDRM v4 System Hardening CS risk rankings. Specifically, generation of Figure PG&E-B.1.1-3 required the removal of several HFRAonly CS that have high enough risk values to be interspersed among the top-ranked System Hardening CS. Therefore, only HFTD CS are included in “WMP-Discovery2023- 2025_DR_SPD_025-Q003Atch01.xlsx” so that columns K and L would provide the correct data to recreate FIGURE PG&E-B.1.1-3. a. Please see “WMP-Discovery2023-2025_DR_SPD_025-Q003Atch01.xlsx.” Please note that “PSPS Risk per PriOH Mile” is not a metric we use in the ordinary course of business. PSPS risk is not assessed on a per-mile basis, but is influenced by the type and quantity of downstream customers impacted by a PSPS outage, regardless of the length of conductor supplying those customers. Please note that the “Wildfire Risk” and “PSPS Risk” metrics (columns F, G, I, and J) are not additive as the results are produced to different scales. The WDRM v4 produces relative CS risk values, but not absolute risk values. The PSPS risk model, WMP-Discovery2023-2025_DR_SPD_025-Q003 Page 2 however, is calibrated to produce absolute risk values that match the PG&E Enterprise Risk Model. b. Primary Overhead Miles represents CS primary overhead conductor miles for the complete CS, including both HFTD and non-HFTD miles. HFTD Overhead Miles represents the total primary and secondary overhead conductor miles within HFTD for a CS. c. The FIGURE PG&E-B.1.1-3 data have been provided in Columns K and L as requested. Column K, for the x-axis, is the CS HFTD (only) risk rank based on the CS Wildfire Risk per Primary Overhead Mile. Column L, for the y-axis is the remaining percentage of HFTD Wildfire Risk for all HFTD CS after removing the CS Wildfire Risk Total (Column F). The sum of HFTD Wildfire Risk used as the basis for calculating percentages is 963.539. The graphic notes 2 intersection points, which can be verified within the table of data provided. Row 943, GRAYS FLAT 0401904916, is the point at which 10,000 miles of HFTD have been accounted for in the buydown curve. Row 1,434, ELK CREEK 11012004, is the point at which 80% of the summed HFTD risk has been accounted for in the buydown curve. | Henry Sweat | 2025-03-05 | 2025-03-19 | 2025-03-19 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_025.zip | 1 | N/A | 6.1.2 | Section 6 - Risk Methodology and Assessment | 6.1.2 Summary of Risk Models | B.1.1. WDRM v4
748 | CPUC - SPD (Safety Policy Division) | 025 | CPUC - SPD (Safety Policy Division)_025 | 3(s) | CPUC - SPD (Safety Policy Division)_025_Q3(s) | Provide the confidential version of TN14365_20240705T205735_20240705_PGE_2023_WMP_R6_Appendix_D_ACI_PGE_2216_Atch01.xlsx. a. If there is a more recent version than that submitted with R6 of the WMP, submit the more recent version. | We have determined that the graphic shown as B.1.1-3 in our 2025 WMP Update was inadvertently generated with a non-final version of WDRM v4. The data we provided in our response on March 19, 2025 was drawn from our official, final WDRM v4, and the buydown curve generated from that data is correct. Please see the corrected graphic below. | Henry Sweat | 2025-03-05 | 2025-03-27 | 2025-03-27 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_025.zip | 0 | N/A | 6.1.2 | Section 6 - Risk Methodology and Assessment | 6.1.2 Summary of Risk Models | B.1.1. WDRM v4
749 | CPUC - SPD (Safety Policy Division) | 025 | CPUC - SPD (Safety Policy Division)_025 | 4 | CPUC - SPD (Safety Policy Division)_025_Q4 | Provide the latest GIS shapefiles which show PG&E’s WDRM and WTRM models. a. Provide the GIS shapefiles for PG&E’s WDRM and WTRM risk models discussed in the 2025 WMP Update. | Please note that the GIS shapefiles we produced as “WMP-Discovery2023- 2025_DR_CalAdvocates_041- Q003Atch01CONF.zip” in our response to WMPDiscovery2023-2025_DR_CalAdvocates_041-Q003, are the latest GIS shapefiles showing our WDRM model. Please see “WMP-Discovery2023-2025_DR_SPD_025-Q004Atch01CONF.zip” for GIS shapefiles showing our WTRM model. As GIS restricts layer names to 10 characters, the original WTRM v2 model output names had to be truncated. Please see “WMPDiscovery2023-2025_DR_SPD_025-Q004Atch02.xlsx” for GIS layer name descriptions. Please note that, in contrast to our WDRM, our WTRM models risk at support structures, not at a transmission circuit level. | Henry Sweat | 2025-03-05 | 2025-03-19 | 2025-03-19 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_025.zip | 2 | N/A | 6.1.2 | Section 6 - Risk Methodology and Assessment | 6.1.2 Summary of Risk Models | B.1.1. WDRM v4
750 | CPUC - SPD (Safety Policy Division) | 025 | CPUC - SPD (Safety Policy Division)_025 | 5 | CPUC - SPD (Safety Policy Division)_025_Q5 | Provide a list of each ignition related to primary lines which are covered conductor from 2014 through 2024. b. Provide the list in the same format as the ignitions data submitted yearly which are available on this website: Wildfire and Wildfire Safety. c. Indicate which ignitions were related to covered conductor installed after 2017 versus before 2017. d. Include ignitions associated with the secondary voltage lines which are connected to the covered conductor primary lines. For instance, the list should include ignitions associated with a service drop, or secondary line which branch off the covered conductor primary line. Indicate if the secondary voltage line was covered. e. Include ignitions associated with devices and other components that are connected to the covered conductor primary overhead line. For instance, the list should include ignitions associated with a transformer which is connected to the covered conductor. | . We are providing a list of ignitions associated with all primary distribution components where the conductor type is insulated primary conductor in the format of our annual submissions. Please see “WMP-Discovery2023-2025_DR_SPD_025- Q005Atch01.xlsx.” We added the insulated conductor attribute to the ignitions tracker in 2022 and this does not represent a complete list of ignitions associated with insulated primary conductor and components. Both ignitions are associated with covered conductor installed after 2017 and this is a complete list of ignitions associated with covered conductor installed since 2017. There may be additional older ignitions not attributed in the tracker associated with older insulation types and materials. b. Please see the response to subpart (a) of this request. WMP-Discovery2023-2025_DR_SPD_025-Q005 Page 2 c. We do not track the upstream primary conductor types and materials for secondary ignitions. d. Please see the response to subpart (a) of this request. | Henry Sweat | 2025-03-05 | 2025-03-19 | 2025-03-19 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_025.zip | 1 | N/A | 8.1.2 | Grid Design and System Hardening | Various | ACI 23-08 Covered Conductor Inspection and Maintenance
750 | CPUC - SPD (Safety Policy Division) | 025 | CPUC - SPD (Safety Policy Division)_025 | 5(s) | CPUC - SPD (Safety Policy Division)_025_Q5(s) | Provide a list of each ignition related to primary lines which are covered conductor from 2014 through 2024. b. Provide the list in the same format as the ignitions data submitted yearly which are available on this website: Wildfire and Wildfire Safety. c. Indicate which ignitions were related to covered conductor installed after 2017 versus before 2017. d. Include ignitions associated with the secondary voltage lines which are connected to the covered conductor primary lines. For instance, the list should include ignitions associated with a service drop, or secondary line which branch off the covered conductor primary line. Indicate if the secondary voltage line was covered. e. Include ignitions associated with devices and other components that are connected to the covered conductor primary overhead line. For instance, the list should include ignitions associated with a transformer which is connected to the covered conductor. | a. Per SPD’s follow-up request, received on March 21, 2025, we are providing a list of ignitions associated with all primary distribution components where the conductor type is insulated primary conductor in the format of our annual submissions. Please see “WMP-Discovery2023-2025_DR_SPD_025Q005Supp01Atch01.xlsx.” We added the insulated conductor attribute to the ignitions tracker in 2022 and this does not represent a complete list of ignitions associated with insulated primary conductor and components. Upon review, we identified one additional ignition that is responsive to this request. All ignitions are associated with covered conductor installed after 2017 and this is a complete list of ignitions associated with covered conductor installed since 2017. There may be additional older ignitions not attributed in the tracker associated with older insulation types and materials. WMP-Discovery2023-2025_DR_SPD_025-Q005Supp01 Page 2 With regard to ignition index no. 20220531, our records indicate that covered conductor was installed at the incident location prior to May 2, 2022, and was replaced like-for-like on May 3, 2022, after and due to the incident. b. Please see the response to subpart (a) of this request. c. We reviewed every secondary and service ignitions within the vicinity of where we installed covered conductor since 2017 did not identify any ignitions where the upstream primary system was covered conductor. d. Please see the response to subpart (a) of this request. | Henry Sweat | 2025-03-05 | 2025-03-26 | 2025-03-26 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_025.zip | 1 | N/A | 8.1.2 | Grid Design and System Hardening | Various | ACI 23-08 Covered Conductor Inspection and Maintenance
751 | CPUC - SPD (Safety Policy Division) | 025 | CPUC - SPD (Safety Policy Division)_025 | 6 | CPUC - SPD (Safety Policy Division)_025_Q6 | Provide E3’s latest audit of PG&E’s risk model. | Please see “WMP-Discovery2023-2025_DR_SPD_025-Q006Atch01.pdf” for E3’s review of the WDRM v4 and WTRM v2. | Henry Sweat | 2025-03-05 | 2025-03-19 | 2025-03-19 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_025.zip | 1 | N/A | 6.1.2 | Section 6 - Risk Methodology and Assessment | 6.1.2 Summary of Risk Models | B.1.1. WDRM v4
752 | CPUC - SPD (Safety Policy Division) | 025 | CPUC - SPD (Safety Policy Division)_025 | 7 | CPUC - SPD (Safety Policy Division)_025_Q7 | Describe the meaning of the risk values presented in “WMP-Discovery2023-2025_DR_CalAdvocates_041-Q005Atch01.xlsx.” Specifically address if the columns of the spreadsheet are showing the subset of the wildfire risk (probability of ignition multiplied by consequence) associated with that particular model. | Column “f”, “Pixel Event Models Average Risk,” represents the average risk [p(i) * Consequence] per pixel risk for a Circuit Segment from the set of subset event models that produce pixel risk results (Animal, Third Party, Vegetation, Secondary Conductor, Other Equipment). Column “h”, “Asset Event Model Risk per PriOH Mile,” represents the risk [p(i) * Consequence] divided by the primary overhead conductor miles for a Circuit Segment from the set of subset event models that directly model equipment asset risks (DPDs, Fuses, Support Structures, etc.). Column “i”, “SH Wildfire Risk per PriOH Mile,” represents the risk [p(i) * Consequence] divided by the primary overhead conductor miles for a Circuit Segment from the System Hardening (SH) composite set of pixel and asset subset event models. Note that because columns “f” and “h” are on different bases, that cannot be summed to produce the result found in column “i” All columns under the header “Event Model Wildfire Risk per PriOH Mile,” that display individual event subset model results are reporting the risk [p(i) * Consequence] divided by the primary overhead conductor miles for a Circuit Segment. All columns under the header “Composite Risk per PriOH Mile,” that display composite model results are reporting the risk [p(i) * Consequence] divided by the primary overhead conductor miles for a Circuit Segment. | Henry Sweat | 2025-03-05 | 2025-03-19 | 2025-03-19 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_025.zip | 0 | N/A | 6.1.2 | Section 6 - Risk Methodology and Assessment | 6.1.2 Summary of Risk Models | B.1.1. WDRM v4
753 | CPUC - SPD (Safety Policy Division) | 025 | CPUC - SPD (Safety Policy Division)_025 | 8 | CPUC - SPD (Safety Policy Division)_025_Q8 | Do the GIS shapefiles provided in “WMP-Discovery2023-2025_DR_CalAdvocates_041-Q003Atch01CONF” include a file which includes the total wildfire risk (probability of ignition multiplied by consequence)? a. Provide a brief narrative of each which specify if the file is focused on consequence, probability of ignition or consequence multiplied by probability of ignition. i. As an example: “WDRM v4 Asset – Switch calculates the probability of ignition due to switches” | The files provided in “WMP-Discovery2023-2025_DR_CalAdvocates_041- Q003Atch01CONF.zip” correspond with the GIS description keys provided in “WMPDiscovery2023-2025_DR_CalAdvocates_041-Q003Atch02.xlsx”. All values listed as risk values are the result of probability of ignition multiplied by consequence. Please see below for a table providing a cross reference between file names provided in “WMPDiscovery2023-2025_DR_CalAdvocates_041- Q003Atch01CONF.zip” and tabs and associated descriptions provided in “WMP-Discovery2023- 2025_DR_CalAdvocates_041-Q003Atch02.xlsx.” File Name Tab Name Description Risk Type WDRM v4 Composite - All Composite - All Composite of all 23 event models Risk per PriOH Mile WDRM v4 Composite - SH Composite – System Hardening Composite of 21 event models for System Hardening Risk per PriOH Mile WDRM v4 Composite - VM Composite – Vegetation Composite of 3 vegetation event probability models Risk per PriOH Mile WFC v4 Consequence Pixel WFC v4 – Consequence WFC v4 Consequence pixel values Consequence WFC v3_4 Consequence Pixel WFC v3.4 - Consequence WFC v3.4 Consequence pixel values used by WDRM v3 Consequence WDRM v4 EPM Pixel Asset – Pixel Models Pixel risk values for the 11 pixel event models Risk Value WDRM v4 Asset – CapBank Asset – CapBank Individual capacitor bank equipment risk values Risk Value WMP-Discovery2023-2025_DR_SPD_025-Q008 Page 2 File Name Tab Name Description Risk Type WDRM v4 Asset – DPD Asset – DPD Individual dynamic protection device equipment risk values Risk Value WDRM v4 Asset – Fuse Asset – Fuse Individual fuse equipment risk values Risk Value WDRM v4 Asset – Primary Conductor Asset – Primary Conductor Individual primary conductor equipment risk values for the primary conductor composite and the supporting 3 event sub-models Risk Value WDRM v4 Asset – Support Structure Asset – Support Structure Individual support structure equipment risk values for the support structure composite and the supporting 2 event sub-models Risk Value WDRM v4 Asset – Switch Asset – Switch Individual switch equipment risk values Risk Value WDRM v4 Asset – Transformer Asset – Transformer Individual transformer equipment risk values for the transformer composite and the supporting 2 event submodels Risk Value WDRM v4 Asset – Voltage Regulator Asset – Voltage Regulator Individual voltage regulator equipment risk values Risk Value | Henry Sweat | 2025-03-05 | 2025-03-19 | 2025-03-19 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_025.zip | 0 | N/A | 6.1.2 | Section 6 - Risk Methodology and Assessment | 6.1.2 Summary of Risk Models | B.1.1. WDRM v4
2023 Change Order 01 | CalPA | Set WMP-Change Order CalPA 01 | CalPA_Set WMP-Change Order CalPA 01 | 1 | CalPA_Set WMP-Change Order CalPA 01_Q1 | In PG&E’s 2023-2025 WMP Change Order submitted January 8 th, 2024, PG&E indicates changes to GH-01: System Hardening. These changes include an increase in the number of overhead hardened miles from 360 miles to 778 miles, and a reduction in the number of undergrounded miles from 2,000 miles to 1,230 miles between 2023 and 2026. a) Please provide an updated breakdown (similar to Table 8.1.2-1 in PG&E’s 2023-2025 WMP) of the yearly targets for overhead hardened miles and undergrounded miles between 2023 and 2026. b) Please provide a list of the overhead hardening projects PG&E plan to incorporate in its 2023-2025 WMP to reflect the increased target, as defined in the change order. c) Please provide a list of the undergrounding projects PG&E plan to remove or postpone from its 2023-2025 WMP to reflect the reduced target, as defined in the change order | a. Please see the updated table 8.1.2-1 below, which mirrors the table in PG&E’s 2023 -2025 WMP, for yearly estimates of overhead hardened, underground and line removal miles that contribute to the System Hardening Target miles between 2023 and 2026. Note, this updated table is anticipated to be included in the 2025 WMP update, which has not yet been finalized and filed. Note, the cited 778 overhead target miles includes both Estimated Overhead Covered Conductor Miles (738) and Estimated Line Removal Miles (40). UPDATED TABLE PG&E-8.1.2-1: OVERALL SYSTEM HARDENING MILEAGE FORECAST 1 Year Estimated Overhead Covered Conductor Miles Estimated System Hardening Undergrounding Miles Estimated Line Removal Miles Overall System Hardening Target Estimated Butte County Rebuild Undergrounding Miles 2023(a) 130 280 10 420 70 2024(b) 60 210 10 280 40 2025(c) 200 310 10 520 20 2026 348 430 10 788(d) 10 Total 738 1,230 40 2,008 140 (a) Miles provided for 2023 represent the original target miles, and do not reflect the actual miles completed for that year. (b) The numbers provided for 2024 assume that the target changes requested in our 2024 Change Order will be approved by Energy Safety. (c) Please note that the 2025 numbers are what we currently anticipate filing in our 2025 WMP Update, but it is possible that these numbers could change by the time of the final filing on April 2, 2024. (d) The 2023 WMP requires annual targets for 2023-2025. The 2026 miles are provided as a forecast only. b. Please see worksheet Q1b in attachment 2024WMPChangeOrderDiscovery_DR_CalAdvocates_001-Q001_Atch01 for a list of all currently scoped overhead hardening projects in the 2023 to 2026 workplan, as of February 22, 2024. The following list describes some of the reported fields included in the attachment: c. Please see worksheet Q1b in attachment “2024WMPChangeOrderDiscovery_DR_CalAdvocates_001-Q001Atch01.xlsx” for a list of all currently scoped overhead hardening projects in the 2023 to 2026 workplan, as of February 22, 2024. The following list describes some of the reported fields included in the attachment: • Actual or Planned Start Date (column K) – For the purpose of this data response, included in the file is the start date based on construction start date where available; however, there are early phases to the project, including project scoping and permitting, which take place in advance to construction. • Expected End Year (column L) – the expected end year for forecasted projects or the actual end year for completed projects. • Expected End Year (column L) – the expected end year for forecasted projects or the actual end year for completed projects. • GH-01 Change (column M) – a description of the project’s change from the original at the time of the 2023 WMP to the update workplan if applicable. The values used are: o In Original – Retained: the project was on the original workplan and has been retained on the updated workplan. o In Original – Changed from UG to OH: the project was on the original workplan as UG work, but has been replaced with OH work on the updated workplan. o Added: the project was not on the original workplan, but has been added to the updated workplan. • Total Planned OH Miles (column N) – sum of all planned overhead hardening miles between 2023 and 2026. • OH – 2023 Complete (column O) – the overhead hardening miles completed in 2023. • OH – 2024 Planned (column P) – the sum of overhead hardening miles completed and remaining in 2024. • OH – 2025 Forecast (column Q) – the overhead hardening miles currently forecasted for 2025. • OH – 2026 Forecast (column R) – the overhead hardening miles currently forecasted for 2026. Note, the forecasted miles included in the attachment exceed the Estimated Overhead Conductor Miles as shown in the updated Table PG&E 8.1.2.1 above in Question 001, subpart (a) because we must intentionally build-in additional miles, as compared to the annual targets, to account for unforeseen delays related to factors such as access, weather, permitting, land rights acquisition, materials or other constraints that may be experienced during the project lifecycle. Thus, some of the projects included in this workplan may not be completed in the 2023 to 2026 timeframe. Generally, PG&E will continue working on these projects until they can be completed in a future year. d. Please see worksheet Q1c in attachment “2024WMPChangeOrderDiscovery_DR_CalAdvocates_001-Q001Atch01.xlsx” for a list of undergrounding projects that were originally included in PG&E’s 2023 to 2026 workplan submitted with the 2023-2025 WMP, but have since been removed from the revised workplan. Per the request, we have not included the undergrounding projects that were in the original plan and are being retained in the portfolio or projects that have been added to the portfolio. Additionally, this GH-01 System Hardening workplan excludes Butte County rebuild projects, which have not changed. The following list describes some of the reported fields: • Actual or Planned Start Date (column K) – For the purpose of this data response, included in the file is the start date based on construction start date where available in the original workplan; however, there are early phases to the project, including project scoping and permitting, which take place in advance to construction. • Expected End Date (column L) – the expected end year for forecasted projects on the original workplan. • GH-01 Change (column M) – a description of the project’s change from the original to the update workplan if applicable. The values used are: o In Original – Removed: the project was on the original workplan and has been removed from the updated workplan. o In Original – Changed from UG to OH: the project was on the original workplan as UG work, but has been replaced with OH work on the updated workplan. o In Original – Changed from UG to Line Removal: the project was on the original workplan as UG work, but has been replaced with Line Removal work on the updated workplan. o In Original – Fully Completed in 2022: the project was on the original workplan and has since been validated to be fully completed in 2022, therefore it is no longer part of the workplan for 2023 and beyond. • Total Planned UG Miles (column N) – the sum of all planned undergrounding miles between 2023 and 2026 from the original workplan. • UG – 2023 Forecast (column O) – undergrounding miles originally forecasted for 2023. • UG – 2024 Forecast (column P) – undergrounding miles originally forecasted for 2024. • UG – 2025 Forecast (column Q) – undergrounding miles originally forecasted for 2025. • UG – 2026 Forecast (column R) – undergrounding miles originally forecasted for 2026. For transparency, we also included worksheet “GH-01 Workplan” in attachment 2024WMPChangeOrderDiscovery_DR_CalAdvocates_001-Q001_Atch01, which is the most recent System Hardening (GH-01) workplan as of February 22, 2024. This workplan includes planned system hardening work for overhead hardening, line removal and system hardening undergrounding through 2026. This workplan will be updated in PG&E’s annual System Hardening Accountability Report that will be filed on July 1, 2024 per reporting requirements of GRC Ordering Paragraphs (OP) 20-23. For transparency, we also included worksheet “GH-01 Workplan” in attachment “2024WMPChangeOrderDiscovery_DR_CalAdvocates_001-Q001Atch01.xlsx”, which is the most recent System Hardening (GH-01) workplan as of February 22, 2024. This workplan includes planned system hardening work for overhead hardening, line removal and system hardening undergrounding through 2026. This workplan will be updated in PG&E’s annual System Hardening Accountability Report that will be filed on July 1, 2024 per reporting requirements of GRC Ordering Paragraphs (OP) 20-23. | Franky Lao | 2024-02-07 | 2024-02-27 | 2024-02-27 | N/A | 1 | N/A | 1.2 | 1.2.1 Align System Hardening and Undergrounding Programs to GRC Decision | GH-01: System Hardening – Distribution | N/A
2023 Change Order 02 | CalPA | Set WMP-Change Order CalPA 01 | CalPA_Set WMP-Change Order CalPA 01 | 2 | CalPA_Set WMP-Change Order CalPA 01_Q2 | In PG&E’s 2023-2025 WMP Change Order submitted January 8 th, 2024, PG&E indicates changes to GH-04: 10k Undergrounding. These changes include a reduction in the number of undergrounded miles from 450 miles to 250 miles for 2024. Using the provided spreadsheet attachment, titled PG&E UG Workplan_2024, please provide a list of all undergrounding projects that PG&E originally planned to complete in 2024, as well as any newly added projects. | Please see worksheet Q2 in attachment “2024WMPChangeOrderDiscovery_DR_CalAdvocates_001-Q002Atch01.xlsx”. This includes a list of all undergrounding projects originally planned for completion in 2024, including Butte Community Rebuild work, that were included in the 2023 to 2026 workplan. Additionally, we have included all new projects added to the portfolio with estimated completion dates between 2023 to 2026. This list of projects is based on the workplan as of February 22, 2024. The following are clarifications on some of the reported fields: • Actual or Planned Start Date (column K) – For the purposes of this data response, included in the file is the start date based on construction start date; however, there are early phases to the project, including project scoping and permitting, which take place in advance to construction. • Expected End Date (column L) - The expected end year for forecasted projects or the actual end year for completed projects. For projects that are on the updated workplan, this value represents the requested ‘Revised Expected End Date (if applicable)’. For projects that are not on the updated workplan, this value represents the originally planned expected end date. • GH-04 Change (column M) – PG&E interprets the requested column ‘Original or Revised WMP’ as an indication of the project’s change between the original and updated workplans. Therefore, that column has been renamed to ‘GH-04 Change’. The values used are: o Added: the project was not on the original workplan, but has been added to the updated workplan. o In Original – Retained: the project was on the original workplan and has been retained on the updated workplan. o In Original – Removed: the project was on the original workplan and has been removed from the updated workplan. o In Original – Changed from UG to OH: the project was on the original workplan as UG work, but has been replaced with OH work on the updated workplan. o In Original – Changed from UG to Line Removal: the project was on the original workplan as UG work, but has been replaced with Line Removal work on the updated workplan. • Total Planned UG Miles (column N): o For projects on the current workplan, the sum of all currently planned undergrounding miles between 2023 and 2026. o For projects that have been removed from the updated workplan, the sum of all planned undergrounding miles between 2023 and 2026 from the original workplan. • UG – 2023 Complete (column O) – undergrounding miles completed in 2023. • UG – 2024 Planned (column P): o For projects on the current workplan, sum of the undergrounding miles completed and remaining in 2024. o For projects that have been removed from the updated workplan, undergrounding miles originally forecasted for 2024. • UG – 2025 Forecast (column Q) – undergrounding miles originally forecasted for 2025 o For projects on the current workplan, the undergrounding miles forecasted for 2025. o For projects that have been removed from the updated workplan, undergrounding miles originally forecasted for 2025. • UG – 2026 Forecast (column R) – undergrounding miles originally forecasted for 2026: o For projects on the current workplan, the undergrounding miles forecasted for 2026. o For projects that have been removed from the updated workplan, undergrounding miles originally forecasted for 2026. • Total Planned Circuit Miles (column S) – Total of all completed and forecasted system hardening miles since the inception of the program, including overhead hardening, undergrounding, and line removal. Note, the forecasted miles exceed the Estimated System Hardening Undergrounding Miles as shown in the updated Table PG&E 8.1.2.1 in Question 001, subpart (a) because we must intentionally build-in additional miles, as compared to the annual targets, to account for unforeseen delays related to factors such as access, weather, permitting, land rights acquisition, materials or other constraints that may be experienced during the project lifecycle. Thus, some of the projects included in this workplan may not be completed in the 2023 to 2026 timeframe. Generally, PG&E will continue working on these projects until they can be completed in a future year. Based on the note included on the column header in the attached template, PG&E interprets the requested column ‘Total Planned Removal Miles’ as miles of existing overhead conductor that has been replaced with underground conductor. The collection of this data for completed and planned projects is an ongoing effort and it will be reported in subsequent reports as more information becomes available. • This workplan will be updated in PG&E’s annual System Hardening Accountability Report that will be filed on July 1, 2024, per reporting requirements of GRC Ordering Paragraphs (OP) 20-23. | Franky Lao | 2024-02-07 | 2024-02-27 | 2024-02-27 | N/A | 1 | N/A | 1.2 | 1.2.1 Align System Hardening and Undergrounding Programs to GRC Decision | GH-04: 10K Undergrounding | N/A
2023 Change Order 03 | CalPA | Set WMP-Change Order CalPA 01 | CalPA_Set WMP-Change Order CalPA 01 | 3 | CalPA_Set WMP-Change Order CalPA 01_Q3 | In PG&E’s 2023-2025 WMP Change Order submitted January 8 th, 2024, PG&E indicates changes to PS-07: Reduce PSPS Impacts to Customers. These changes include a reduction in the number of customers being mitigated from PSPS events from 18,000 to 9,980 for 2024. Per PG&E at page 15, “The targeted number of customers being mitigated from PSPS events is directly tied to the number of miles of undergrounding completed.” a) Does overhead hardening have an impact on the reduction of PSPS impacts to customers? b) If yes, how was this influence considered when PG&E calculated the number of customers being mitigated from PSPS events in 2024. c) If no, please explain. | a. In the analysis, we applied the 2022 guidance in the weather lookback period of 2018-2022. Other mitigation methods such as overhead hardening, sectionalizing devices, and PSPS protocols are already factored into the lookback. This allows us to calculate the number of customers we are able to mitigate with the two planned mitigations (undergrounding and motor switch operator (MSO)) we expect to complete in 2023-2025. b. Please see our response to subpart a. c. Please see our response to subpart a. | Franky Lao | 2024-02-07 | 2024-02-27 | 2024-02-27 | N/A | 0 | N/A | 1.2 | 1.2.1 Align System Hardening and Undergrounding Programs to GRC Decision | PS-07: Reduce PSPS Impacts to Customers | N/A
2023 Change Order 04 | OEIS | Set WMP-Change Order OEIS 01 | OEIS_Set WMP-Change Order OEIS 01 | 1 | OEIS_Set WMP-Change Order OEIS 01_Q1 | Regarding underground and system hardening target reduction in 2024 a. PG&E states that it is unable to meet its underground and system hardening targets in 2024 due to GRC decision D.23-11-069.1 Energy Safety approved PG&E’s plan to complete 1,175 underground and 235 covered conductor system hardening miles from 2023-2025.2 The GRC decision approved funding for 1,230 miles of underground and 778 miles of covered conductor system hardening from 2023-2026.3 Please provide: i. The reasoning, including any supporting documentation and data, behind PG&E’s decision to reduce both underground and covered conductor hardening miles in 2024, given that the GRC approved enough funding to cover the approved work provided in PG&E’s 2023-2025 WMP. ii. PG&E’s interpretation of the “definition of high-risk miles that the CPUC ordered in the final GRC decision.”4 iii. The number of originally planned underground system hardening miles in 2024 that do not meet this definition of high-risk miles and the basis for originally planning said miles in 2024. iv. The number of originally planned covered conductor system hardening miles in 2024 that do not meet this definition of high-risk miles and the basis for originally planning said miles in 2024. v. The average PSPS risk reduction and wildfire risk reduction per mile of the underground hardening miles originally scoped for 2024 in PG&E’s 2023-2025 WMP that PG&E intends to remove via its 2023-2025 WMP Change Order. Provide the risk reduction numbers using WDRM v2 and WDRM v3. vi. The average PSPS risk reduction and wildfire risk reduction per mile of the underground hardening miles originally scoped for 2024 in PG&E’s 2023-2025 WMP that PG&E does not intend to remove via its 2023-2025 WMP Change Order. Provide the risk reduction numbers using WDRM v2 and WDRM v3. vii. The average PSPS risk reduction and wildfire risk reduction per mile of the covered conductor hardening miles originally scoped for 2024 in PG&E’s 2023-2025 WMP that PG&E intends to remove via its 2023-2025 WMP Change Order. Provide the risk reduction numbers using WDRM v2 and WDRM v3. viii. The average PSPS risk reduction and wildfire risk reduction per mile of the covered conductor hardening miles originally scoped for 2024 in PG&E’s 2023-2025 WMP that PG&E does not intend to remove via its 2023-2025 WMP Change Order. Provide the risk reduction numbers using WDRM v2 and WDRM v3. | The 2023-2025 system hardening plan included in PG&E’s 2023-2025 WMP is part of the 2023-2026 system hardening plan presented in our 2023-2026 GRC application.5 Decision (D.) 23-11-069 (Decision on Test Year 2023 General Rate Case for PG&E, or GRC Decision) approved a spending cap for system hardening based on the expectation that between 2023 and 2026 PG&E would complete fewer total system hardening miles (approximately 2,000, compared to approximately 2,300 miles presented in PG&E’s 2023 WMP),6 and significantly fewer System Hardening underground miles (1,230, compared to approximately 2,000 PG&E proposed).7 The reduction in miles—and in particular, in undergrounding miles—necessitated changes to PG&E’s workplan that go beyond simple mileage reductions, because System Hardening jobs are designed in an interdependent way. That is, the design of one job may influence others, and PG&E planned to sequence work in a way that achieved efficiencies and economies of scale over the full four years. The GRC Decision also introduced cumulative annual risk reduction targets for each year of the GRC period, reaching 18% cumulative wildfire risk reduction by the end of 2026. This requirement does not align with the approved definition of high-risk miles in the WMP (top 20% risk-ranked circuit segments, PSPS projects, PSS identified projects and rebuild). As a result, we must pursue different miles than planned to address the requirement of reducing risk by 18%. While our System Hardening program is driven by wildfire risk reduction and the program has reported on risk reduction through the WMP venue starting in the 2023-2025 WMP, the program has previously focused on largescale wildfire risk reduction over a longer period of time and sequencing projects in a way that minimizes costs to ratepayers. The GRC Decision introduced short-term compliance targets for risk reduction, with complexity added by the differing definitions of high-risk miles in the WMP and GRC forums, and by the GRC system hardening hybrid scenario’s shift away from undergrounding and toward more overhead hardening, which yields lower risk reduction. To meet these new targets in the context of a workplan in which approximately 40% fewer undergrounding miles were authorized, changes to our workplan were necessary. Timing has also influenced updates to our 2023-2026 workplan. First, when the GRC decision was issued in November 2023, PG&E had completed the bulk of the 364 underground and 145 overhead hardening miles it completed in 2023. In addition, we retained jobs that were in construction or significantly ready for construction in the portfolio to avoid negative impacts to customers of stranding unfinished work and readiness efforts.8 Similarly, underground fire rebuild miles cannot be stopped and comprise approximately 110 miles within PG&E’s System Hardening 2023-2026 portfolio, largely slated for completion in 2023 and 2024. Finally, due to the significant lead time required to develop undergrounding projects, any new work that began scoping at the end of 2023 will not be completed until late in the GRC period.9 As a result of the number of miles completed in 2023, significantly progressed by the end of 2023, or dedicated to fire rebuild, we had limited room in our 2023-2026 System Hardening portfolio to scope new projects to meet the new short-term risk reduction targets. Newly scoped projects will be constructed later in the GRC period to support meeting the overall risk reduction target. Below, we discuss how these overarching factors influence our responses to each subpart of this question. i. The primary reason PG&E reduced the undergrounding miles in 2024 was to account for the reduced undergrounding miles that were authorized in the GRC – a reduction by almost 40%, from approximately 2,000 to 1,230 undergrounding miles from 2023 to 2026. As noted above, the 18% riskreduction requirement of the GRC Final Decision does not align with the approved definition of high-risk miles in the WMP (top 20% risk-ranked circuit segments, PSPS projects, PSS identified projects and rebuild) and, therefore, we must pursue different miles than planned to address the requirement of reducing risk by 18%. The primary reason PG&E slightly reduced the overhead hardening miles in 2024, was to provide adequate time to revisit the portfolio structure between overhead and underground miles and ensure the overhead miles selected for hardening are not in locations that would be identified for undergrounding in the future. ii. High-risk miles ordered in the GRC are defined as those that cumulatively build a portfolio that meet the risk reduction targets in the GRC (the final target being 18% cumulative risk reduction in the HFTD by 2026).10 iii. PG&E had originally prepared its 2023-2026 undergrounding workplan based on our approved high-risk definition in our approved 2023-2025 WMP, including: (1) the top 20% risk-ranked circuit segments, equating to approximately 8,100 highest risk overhead miles that contribute to approximately 70% of the total wildfire risk; (2) Public Safety Specialist (PSS)-identified projects; (3) PSPS reliability projects; and (4) Rebuild projects. Based on the GRC decision, PG&E revisited our 2024-2026 undergrounding workplan in order to meet the cumulative risk reduction target of 18% and to align to a hybrid structure and associated increased miles for overhead hardening and reduced undergrounding work. PG&E also had to account for the other factors noted in the introduction: the interdependence of jobs and the quantity of miles either completed or significantly progressed in 2023. For the projects that were planned in 2024-2026, approximately 1,500 miles in the program were impacted – either stopped (approximately 60 miles), paused for future consideration (approximately 1,040 miles), or paused for review and potential re-scoping to a hybrid alternative that includes both undergrounding and overhead hardening (approximately 410 undergrounding miles).11 iv. Based on the GRC decision, PG&E revisited our 2024-2026 overhead hardening workplan to achieve the cumulative risk reduction target of 18% and align to a hybrid structure and associated miles for increased overhead hardening and reduced undergrounding work. For the overhead projects that were planned in 2024-2026, approximately 90 miles in the program were impacted – either stopped (approximately 20 miles) or paused for future consideration (approximately 70 miles).12 v. PSPS Risk Reduction: The average PSPS risk reduction per undergrounded mile for the System Hardening undergrounding projects which were originally scoped for 2024 and removed from the updated workplan, including those converted from underground to overhead, is 0.003%. In other words, for every one mile undergrounded, there is a 0.003% reduction in PSPS risk. Note, the PSPS risk estimates do not use WDRM, therefore reflection of v2 and v3 is not incorporated for this analysis. Wildfire Risk Reduction: For projects initiated under WDRM v2 that PG&E intends to remove via its 2023-2025 WMP Change Order, the average wildfire risk reduction per mile of the System Hardening undergrounding projects originally scoped for 2024 and removed from the updated workplan, including those converted from underground to overhead, was 0.003%. This is calculated by dividing the total v2 risk reduction of these projects (0.09%) by the total previously planned miles of these projects (~32 miles). For projects initiated under WDRM v3 that PG&E intends to remove via its 2023- 2025 WMP Change Order, the average wildfire risk reduction per mile of the System Hardening undergrounding projects originally scoped for 2024 and removed from the updated workplan, including those that had a revised mitigation type, such as from underground to overhead, was 0.008%. This is calculated by dividing the total v3 risk reduction of these projects (1.96%) by the total previously planned miles of these projects (~232 miles). vi. PSPS Risk Reduction: The average PSPS risk reduction per undergrounded mile is 0.004% for undergrounding projects remaining scoped in 2024. In other words, for every one mile undergrounded, there is a 0.004% reduction in PSPS risk. Note, the PSPS risk estimates do not use WDRM, therefore reflection of v2 and v3 is not incorporated for this analysis. Wildfire Risk Reduction: For projects initiated under WDRM v2, the average wildfire risk reduction per mile for all System Hardening undergrounding projects (excluding Butte) that remain scoped for 2024 is 0.006%. This is calculated by dividing the total v2 risk reduction of undergrounding projects in 2024 (0.94%) by the total System Hardening Undergrounding target miles for those projects (~154 miles). For projects initiated under WDRM v3, the average wildfire risk reduction per mile for all System Hardening undergrounding projects (excluding Butte) that remain scoped for 2024 is 0.011%. This is calculated by dividing the total v3 risk reduction of undergrounding projects in 2024 (0.61%) by the total System Hardening Undergrounding target miles for those projects (~56 miles). It is important to recognize that the new projects identified and added to the portfolio to account for the GRC decision to meet the 18% risk reduction target were primarily added to years 2025 and 2026. The wildfire risk reduction per mile for undergrounded projects added to the 2023-2026 workplan (excluding Butte) is 0.011% based on WDRM v3. This estimate is calculated by dividing the total v3 risk reduction of undergrounding projects in 2023-2026 (5.68%) by the total System Hardening Undergrounding forecasted miles of those projects (~499 miles as of February 22, 2024). vii. PSPS Risk Reduction: As stated in response to ACI PG&E-22-31 in the 2023- 2025 WMP, due to our PSPS modeling approach, we would not adjust our final PSPS risk thresholds to account for covered conductor. Our Catastrophic Fire Probability model (discussed in Section 9 of the WMP) is a risk-based assessment of the probability of ignition given an outage multiplied by the probability of catastrophic fires (Fire Potential Index). Thus, we would not adjust the threshold at which PSPS is executed (each area is scoped for PSPS at the same risk threshold) based on covered conductor. Wildfire Risk Reduction: For projects initiated under WDRM v2, the average wildfire risk reduction per mile of all overhead hardening projects originally scoped for 2024 and removed from the updated workplan was 0.006%. This is calculated by dividing the total v2 risk reduction of these projects (0.1%) by the total previously planned miles of these projects (~18 miles). For projects initiated under WDRM v3, the average wildfire risk reduction per mile of all overhead hardening projects originally scoped for 2024 and were removed from the updated workplan was 0.008. This is calculated by dividing the total v3 risk reduction of these projects (0.001%) by the total previously planned miles of these projects (~.1 miles). viii. PSPS Risk Reduction: Please see the above response to Question 1, subpart vii for the requested explanation. Wildfire Risk Reduction: For projects initiated under WDRM v2 that PG&E does not intend to remove via its 2023-2025 WMP Change Order, the average wildfire risk reduction per mile for all System Hardening overhead hardening projects that remain scoped for 2024 is 0.01%. This is calculated by dividing the total v2 risk reduction of these projects (0.61%) by the total target miles of these projects (59 miles). For projects initiated under WDRM v3 that PG&E does not intend to remove via its 2023-2025 WMP Change Order, the average wildfire risk reduction per mile for all overhead hardening projects that remain scoped for 2024 is 0.007%. This is calculated by dividing the total v3 risk reduction of these projects (0.007%) by the total System Hardening Undergrounding target miles (1 mile). PG&E notes the v3 average wildfire risk reduction per mile of overhead hardening projects that were retained on the 2024 workplan is lower than the original miles that were removed (see response to subpart iv above) primarily because these projects were already significantly far along in their project lifecycle and were selected based on the high-risk definition authorized in the 2023 WMP. | Dakota Smith | 2024-02-27 | 2024-03-12 | 2024-03-12 | N/A | 0 | N/A | 8 | Section 8.1.2 - Grid Design and System Hardening | 8.1.2.2 Undergrounding of electric lines and/or equipment | N/A
2023 Change Order 05 | OEIS | Set WMP-Change Order OEIS 01 | OEIS_Set WMP-Change Order OEIS 01 | 2 | OEIS_Set WMP-Change Order OEIS 01_Q2 | Regarding risk reduction from 2023-2026 a. The GRC decision requires a cumulative risk reduction of 18% from 2023-2026.5 PG&E states that reducing its targets as described in its 2023-2025 WMP change order would reduce its risk in 2024 from 4% to 2%.6 Please provide: i. An analysis of PG&E’s ability to reach the 18% risk reduction required by GRC following the approved 2023-2025 WMP system hardening plan for 2023-2025 and completing the remaining GRC funded 55 underground and 543 covered conductor miles in 2026. ii. PG&E’s plan to reach the 18% risk reduction target required by the GRC after reducing its 2024 risk reduction from 4% to 2%. Include the actual/expected risk reduced per year for 2023, 2024, 2025, and 2026. | Please be advised that the attachment to this response contains CONFIDENTIAL information and is provided pursuant to the accompanying confidentiality declaration. a. i. For the requested analysis, please see attachment 2024WMPChangeOrderDiscovery_DR_OEIS_001-Q002Atch01_CONF.xlsx, worksheet “OEIS-01 Q2”, which includes the detailed project data demonstrating how each project contributes to achieving our risk reduction targets. The method used for calculating risk reduction in this analysis described in PG&E Advice Letter 7150-E-A, filed with the CPUC’s Safety Policy Division (SPD) on February 20, 2024.3 Please note that we combined the 2025 and 2026 risk estimates and the projects associated with each of these years are still being finalized. Some of the key fields are: • Order Number: Column A • Applicable Risk Model: Column M • Total Planned Miles by mitigation type (OH/UG/Removal): Columns Q-S • Total Applicable Risk Model Risk Reduction by mitigation type (OH/UG/Removal): Columns AG-AI. ii. The 2024 WMP Change Order filing reduced risk estimates from 4% to 2% using the v3 of the WDRM for all projects in the portfolio based on a workplan developed in December 2023. The 18% cumulative risk reduction target of the GRC uses a different method of measuring risk reduction, as described below, as well as in Advice Letter 7150-E-A. GRC Method for Measuring Risk Reduction: As discussed in Advice Letter 7150-EA, for reporting progress towards the risk reduction targets in Ordering Paragraph (OP) 23 of the GRC Decision (D.) 23-11-069, PG&E plans to report risk reduction using both WDRM v2 and v3 for the projects initiated under each risk model. PG&E interprets the cumulative risk reduction targets set forth in OP 23 to be split between WDRM v2 and v3 for compliance purposes. As discussed in Advice Letter 7150-E-A, the use of multiple WDRM versions is appropriate in this forum, for compliance with D.23-11-069, OPs 23 and 24, but WMP reporting will remain consistent with prior years. WMP Method for Measuring Risk Reduction: We will continue to use the same method of reporting risk in the WMP as we have in prior years. In PG&E’s 2024 WMP Change Order filing, PG&E reduced the risk from 4% to 2% based on the method for quantifying risk using the latest version of the risk model (WDRM V3). As described in PG&E’s Risk Baseline Advice Letter 7150-E-A,4 risk reduction forecast and reporting in the WMP calculates risk using the latest risk model (currently WDRM V3). In the Energy Safety Wildfire Mitigation Plan docket, PG&E will report on risk reduction associated with WMP System Hardening using WDRM v3 only, as this is the consistent way all other mitigations of the WMP are reported. Table 1 below—and included in the “summary” worksheet of attachment 2024WMPChangeOrderDiscovery_DR_OEIS_002_Attch01.xlsx— summarizes the estimated miles and GRC-method of risk reduction using the full workplan as provided in worksheet “OEIS-01 Q2” in the same attachment. This workplan purposefully builds in additional miles compared to the proposed targets described in the 2024 change order and forthcoming 2025 WMP Update, to account for the fact that project dependencies and construction issues may arise and delay some projects, lowering the final actual mileage and risk reduction achieved. Therefore, PG&E anticipates that the mileage and risk reduction numbers may be lower than shown in Table 1 below, but the total 2023-2026 actual risk reduction will be managed with the intent to meet or exceed the 18% risk reduction target. Table 1. 2023-2026 System Hardening Workplan Summary of Forecasted Miles and Risk Reduction Based on 2/22/24 workplan (MAT Codes 08W and 3UG only) 2023 2024 2025-2026 Total WDRM Version 2023 Total Complete SH Miles 2023 Total Risk Reduction 2024 Total Planned SH Miles 2024 Potential Risk Reduction 2025-26 Total Forecast SH Miles 2025-26 Potential Risk Reduction Total Planned SH Miles Total Potential Risk Reduction v2 396.4 2.3% 271.5 2.2% 239.0 1.5% 906.9 6.0% v3 28.5 0.1% 73.0 0.8% 1,160.0 12.6% 1,261.6 13.5% Sum of v2 + v3 Annual Miles / Risk Reduction 424.9 2.4% 344.5 3.0% 1,399.0 14.1% 2,168.4 19.5% Sum of v2 + v3 Cumulative Miles / Risk Reduction 424.9 2.4% 769.4 5.4% 2,168.4 19.5% SH miles = all system hardening miles: overhead hardening, undergrounding, and line removal. Table 2 below is the target-informed forecasted risk reduced by year, showing both the WMP WDRM v3 method and the GRC WDRM v2 and v3 method. The targetinformed risk reduction estimate utilizes project readiness data from our project pipeline each year (i.e., projects that are beyond scoping, and in permitting or construction, are more likely to completed). As shown in the table below, risk reduction of the two methods will become more similar in 2025-2026 because a majority of v2 projects in the portfolio are completed in the earlier years. Table 2. Target-Informed 2023-2026 System Hardening Workplan Summary of Forecasted Miles and Risk Reduction 2023 2024 2025-26(a) Total System Hardening Miles(b) 420 280 1,308 2,008 Risk Reduction (%) Forecast GRC version (WDRM V2/V3)(b) 2.4% 2.3% 13.7% 18.4% Risk Reduction (%) Forecast GH-01: WMP version (WDRM V3)(c) 1.3% 1.6% 13.1% 15.9% (a) Values for 2025-26 represent the highest plausible risk reductions in accordance with the GH-01 System Hardening workplan as of February 22, 2024. Results could vary by approximately 0.5%. (b) Includes overhead covered conductor, undergrounding (excluding Butte / Community Rebuild), and line removal (only MAT codes 08W and 3UG in GH-01 System Hardening workplan). (c) Includes overhead covered conductor, undergrounding (excluding Butte / Community Rebuild), and line removal (All MAT codes in GH-01 System Hardening workplan). | Dakota Smith | 2024-02-27 | 2024-03-12 | 2024-03-12 | N/A | 1 | N/A | 7 | Section 7 - Wildfire Mitigation Strategy Development | 7.2.2 Anticipated Risk Reduction | N/A
2023 Change Order 05 | OEIS | Set WMP-Change Order OEIS 01 | OEIS_Set WMP-Change Order OEIS 01 | 2(s) | OEIS_Set WMP-Change Order OEIS 01_Q2(s) | Regarding risk reduction from 2023-2026 a. The GRC decision requires a cumulative risk reduction of 18% from 2023-2026.5 PG&E states that reducing its targets as described in its 2023-2025 WMP change order would reduce its risk in 2024 from 4% to 2%.6 Please provide: i. An analysis of PG&E’s ability to reach the 18% risk reduction required by GRC following the approved 2023-2025 WMP system hardening plan for 2023-2025 and completing the remaining GRC funded 55 underground and 543 covered conductor miles in 2026. ii. PG&E’s plan to reach the 18% risk reduction target required by the GRC after reducing its 2024 risk reduction from 4% to 2%. Include the actual/expected risk reduced per year for 2023, 2024, 2025, and 2026. | ANSWER 002 SUPPLEMENTAL 01 b. Please see attachment “2024WMPChangeOrderDiscovery_DR_OEIS_001- Q002Supp01Atch01CONF.xlsx,” worksheet “OEIS-01 Q2 Supp,” for projects PG&E planned from 2023-2026 as part of the approved 2023-2025 WMP. The list of projects and associated details are as of January 3, 2023. The data is populated in the same format using the same calculation methods as the originally provided response to OEIS_001-Q002i. PG&E notes that the sub-projects (identified by orders) that are included in both the workplans provided in response to OEIS_001-Q002i (information as of February 22, 2024) and the workplan as of January 3, 3023 provided in this supplemental 1 Decision (D.) 23-11-069 (Nov. 16, 2023), page 281. 2 PG&E’s 2023-2025 Change Order, page 13. 3 Per OEIS’ supplemental request via email on March 18, 2024 due back March 21, 2024. response, which was associated with the 2023-2025 WMP at the time of filing, may have different system hardening mitigation methods (i.e., OH vs. UG), miles, and risk reduction values. This is because system hardening mitigation miles and hardening approaches may differ from the original plan (as of January 2023) as individual project scopes are refined once field conditions and execution dependencies materialize as the project is implemented. Risk reduction values may differ because of the change to the mitigation type and/or miles for the project. Since the mitigation type and/or total planned miles on a circuit segment may increase or decrease as a result of refined scoping, additional projects, or discontinuation of projects on that segment, the associated risk reduction values could vary slightly. Table 3 below — and included in the “OEIS-01 Q2 Supp Summary” worksheet of the attachment 2024WMPChangeOrderDiscovery_DR_OEIS_001- Q002Supp01Atch01CONF.xlsx — summarizes the estimated miles and GRCmethod of risk reduction using the full workplan as provided in worksheet “OEIS-01 Q2 Supp” in the same attachment. The following are the primary reasons the workplans differ: 1) The projects represented in Table 3 below do not account for the adjustments made to meet the mileage and cumulative risk reduction targets required in the November 16, 2023 GRC decision. 2) As described in the 2023 WMP ACI 22-16, the workplans purposefully build in additional miles compared to the proposed targets at that time to account for the fact that project dependencies and construction issues may arise and delay some projects. Therefore, the cumulative mileage and risk reduction associated with the workplan were overstated as compared to what would be accomplished in accordance with the target. PG&E anticipated that the mileage and associated risk reduction that would be completed would be lower than shown in Table 3 below but would be managed with the intent to meet the proposed mileage targets of that time. Table 3. 2023-2026 System Hardening Workplan Summary of Forecasted Miles and Risk Reduction Based on 1/3/23 workplan (MAT Codes 08W and 3UG only) 2023 2024 2025-2026 Total WDRM Version 2023 Total Forecast SH Miles 2023 Potential Risk Reduction 2024 Total Forecast SH Miles 2024 Potential Risk Reduction 2025-26 Total Forecast SH Miles 2025-26 Potential Risk Reduction Total Forecast SH Miles Total Potential Risk Reduction v2 629.1 3.7% 298.8 1.9% 248.7 1.1% 1,176.7 6.7% v3 55.4 0.4% 363.4 3.2% 1,483.8 13.8% 1,902.6 17.4% Sum of v2 + v3 Annual Miles / Risk Reduction 684.5 4.1% 662.3 5.1% 1,732.5 14.9% 3,079.3 24.1% Sum of v2 + v3 Cumulative Miles / Risk Reduction 684.5 4.1% 1,346.8 9.2% 3,079.3 24.1% SH miles = all system hardening miles: overhead hardening, undergrounding, and line removal. | Dakota Smith | 2024-03-18 | 2024-03-21 | 2023-03-21 | N/A | 1 | N/A | 7 | Section 7 - Wildfire Mitigation Strategy Development | 7.2.2 Anticipated Risk Reduction | N/A
2023 Change Order 06 | OEIS | Set WMP-Change Order OEIS 01 | OEIS_Set WMP-Change Order OEIS 01 | 3 | OEIS_Set WMP-Change Order OEIS 01_Q3 | 10-Year Undergrounding Plan Submission Pursuant to Public Utilities Code Section 8388.5 a. Does PG&E plan to submit a 10-Year Undergrounding Plan and a subsequent application for costs pursuant to Public Utilities Code section 8388.5 for the undergrounding work to be performed in 2026? If so, please provide the approximate miles PG&E will seek funding for. | PG&E is currently awaiting the SB 884 10-Year Plan guidelines from Energy Safety. Based on the review timeline of the legislation (i.e., nine-month review by Energy Safety, two months for electric utilities to submit to the CPUC, and nine-month review by CPUC), if final guidelines are issued mid-year 2024, the earliest we could possibly receive approval for our SB 884 Plan and cost recovery would be in mid-2026. Thus, PG&E anticipates our Plan period would begin January 1, 2027 – meaning that projects included in our SB 884 Plan would begin to be electrified in 2027. The Plan launch in January 2027 assumes Energy Safety and the CPUC approve our Plan and cost recovery without requiring significant changes to our planned program. However, given the typical undergrounding project lifecycle of approximately two or more years, electrifying projects in 2027 will require project readiness work in 2025 and 2026. Thus, PG&E would begin incurring costs in 2025 and 2026 for projects that will become used and useful in the SB 884 Plan period of 2027 and beyond. PG&E’s cost recovery application will include these costs for readiness work for projects that become operative during the SB 884 Plan period. PG&E has not yet prepared a workplan for 2027 and thus does not have a mileage estimate. | Dakota Smith | 2024-02-27 | 2024-03-12 | 2024-03-12 | N/A | 0 | N/A | Appendix D | Appendix D - Areas for Continued Improvement | Appendix D ACI PG&E-22--16 Progress and Updates on Undergrounding and Risk Prioritization | N/A
Pre-Discovery 01 | CalPA | Set WMP-01 | CalPA_Set WMP-01 | 1 | CalPA_Set WMP-01_Q1 | This data request pertains to your 2023-2025 Wildfire Mitigation Plan (WMP) and all related documents and submissions (including but not limited to data submissions, tables, GIS data, attachments, and appendices). This data request covers the entirety of calendar year 2023. Please provide a copy of each WMP-related document, submission, or report you submit to the Office of Energy Infrastructure Safety (Energy Safety) in 2023 that is related to your WMP. Provide the copy to Cal Advocates within one business day of the document’s submittal to Energy Safety. (If you have submitted the document to Energy Safety in 2023 prior to this data request, please provide a copy as soon as possible and no later than 10 business days from the issuance of this data request.) This request is limited to materials or documents that: (1) are related to work plans, initiative targets, risk models, risk spend efficiency (RSE) calculations, or WMP change orders; and (2) are provided to Energy Safety to provide additional details or context concerning information or statements in your WMP (and any subsequent revisions or change orders affecting your WMP). | GENERAL OBJECTIONS TO THIS SET OF DATA REQUESTS PG&E objects to the instructions or definitions in the set of data requests entitled CalAdvocates-PGE-2023WMP-01 that purport to impose any obligations greater than those provided by the applicable rules and decisions of the Commission or and any other statutes, orders, rules, or laws limiting the regulatory authority and jurisdiction of the Commission. In particular, PG&E objects to the instruction that purports to place a burden on the responding party to reach out to the requesting party to clarify any unclear questions, definitions, or instructions. The duty to prepare precise and wellwritten instructions, definitions, and requests is on the party seeking the information and cannot be shifted to the responding party. Additionally, PG&E objects to the instruction that PG&E must “[p]rovide the name and title of the responding individual” as burdensome and not reasonably calculated to lead to the discovery of admissible evidence. Our responses to data requests are not the product of a single individual but of numerous individuals working together from different departments of the company. If the requesting party wishes to contact PG&E with questions or concerns about a data request, it may do so by contacting the appropriate individuals in the Regulatory Relations or Law Department upon whom the request was served PG&E also objects to the following definitions: • The definitions of “[r]elate to” or “concern” which are overbroad and burdensome to the extent they request materials “mention, or be connected with, in any way” the subject of the data requests. • The definitions of the terms “document,” “documents,” and “documentary material,” which include “correspondence” and “communications,” making these terms overbroad, unduly burdensome, and not reasonably calculated to lead to the discovery of admissible evidence in this proceeding. • The definition of the phrase “state the basis,” which is overbroad and burdensome to the extent it requests “every fact, statistic, inference, supposition, estimate, consideration, conclusion, study, report, and analysis….” ANSWER 001 In addition to all general objections, PG&E specifically objects to this request on the grounds that it is unduly burdensome. PG&E further objects to this request as the information requested is vague, ambiguous, and overbroad. Lastly, PG&E objects to this request on the grounds that it seeks to impose a continuing response obligation on the responding party. Continuing discovery obligations are not permitted under California law. Biles v. Exxon Mobil Corp., 124 Cal.App.4th 1315, 1328 (2004); Code Civ. Proc. § 2030.060(g). Notwithstanding and without waiving these objections, PG&E responds as follows. We will do our best to provide the requested information within the requested timeframe, or as soon as possible thereafter. However, please note that due to the timing and voluminous nature of our submissions to Energy Safety, it may not always be possible to provide the information sought within the requested timeframe. In these instances, we will provide the requested information as soon as it is reasonably possible. Additionally, with the exception of confidential and spatial data, please note that we post our WMP-related submissions on our website, www.pge.com/wildfiremitigationplan, on the same business day that the documents are provided to Energy Safety. Furthermore, all submissions to Energy Safety are also posted to the relevant docket on the Energy Safety website, https://efiling.energysafety.ca.gov/, and are nearly always publicly available within one business day of submission. Public email notifications of the availability of these documents are sent to all parties who subscribe to the service lists for those dockets. | Holly Wehrman | 2023-02-07 | 2023-02-14 | 2023-02-14 | https://www.pge.com/pge_global/common/pdfs/safety/emergency-preparedness/natural-disaster/wildfires/wildfire-mitigation-plan/reference-docs/2023/CalAdvocates_001.zip | 0 | N/A | N/A | N/A | N/A | N/A
Pre-Discovery 02 | CalPA | Set WMP-01 | CalPA_Set WMP-01 | 2 | CalPA_Set WMP-01_Q2 | Please provide a copy of your WMP pre-submission within two business days of its submission to Energy Safety | Attachment “WMP-Discovery2023_DR_CalAdvocates_001-Q02Atch01CONF.pdf” is our WMP pre-submission to Energy Safety. Please note that this document is not our final WMP submission and may be subject to revision before the final WMP is submitted in March. Additionally, we have designated this entire submission as confidential to align with Energy Safety’s pre-submission process and guidelines which stipulate that the presubmission documents are not to be made public. | Holly Wehrman | 2023-02-07 | 2023-02-15 | 2023-02-15 | https://www.pge.com/pge_global/common/pdfs/safety/emergency-preparedness/natural-disaster/wildfires/wildfire-mitigation-plan/reference-docs/2023/CalAdvocates_001.zip | 1 | N/A | N/A | N/A | N/A | N/A
Pre-Discovery 03 | CalPA | Set WMP-01 | CalPA_Set WMP-01 | 3 | CalPA_Set WMP-01_Q3 | Provide a copy of all documents or files that are referenced in your WMP Quarterly Data Reports and submitted to Energy Safety (including but not limited to all PDFs, spatial data files, non-spatial data files, and confidential attachments) on the same business day that the document is sent to Energy Safety. | In addition to all general objections, PG&E specifically objects to this request on the grounds that it is unduly burdensome. PG&E further objects to this request as the information requested is vague, ambiguous, and overbroad. Lastly, PG&E objects to this request on the grounds that it seeks to impose a continuing response obligation on the responding party. Continuing discovery obligations are not permitted under California law. Biles v. Exxon Mobil Corp., 124 Cal.App.4th 1315, 1328 (2004); Code Civ. Proc. § 2030.060(g). Notwithstanding and without waiving these objections, PG&E responds as follows. We will do our best to provide the requested information within the requested timeframe, or as soon as possible thereafter. However, please note that due to the timing and voluminous nature of our submissions to Energy Safety, it may not always be possible to provide the information sought within the requested timeframe. In these instances, we will provide the requested information as soon as it is reasonably possible. Additionally, with the exception of confidential and spatial data, please note that we post our WMP-related submissions on our website, www.pge.com/wildfiremitigationplan, on the same business day that the documents are provided to Energy Safety. Furthermore, all submissions to Energy Safety are also posted to the relevant docket on the Energy Safety website, https://efiling.energysafety.ca.gov/, and are nearly always publicly available within one business day of submission. Public email notifications of the availability of these documents are sent to all parties who subscribe to the service lists for those dockets. | Holly Wehrman | 2023-02-07 | 2023-02-14 | 2023-02-14 | https://www.pge.com/pge_global/common/pdfs/safety/emergency-preparedness/natural-disaster/wildfires/wildfire-mitigation-plan/reference-docs/2023/CalAdvocates_001.zip | 0 | N/A | N/A | N/A | N/A | N/A
Pre-Discovery 04 | CalPA | Set WMP-01 | CalPA_Set WMP-01 | 4 | CalPA_Set WMP-01_Q4 | Provide a copy to Cal Advocates of all your confidential responses to WMP discovery requests, on the same business day that you send the documents to the issuer of the discovery request. This includes: a) Confidential responses to WMP discovery requests issued by Energy Safety. b) Confidential responses to WMP discovery requests issued by other entities. | In addition to all general objections, PG&E specifically objects to this request on the grounds that it is unduly burdensome. PG&E further objects to this request as the information requested is vague, ambiguous, and overbroad. Lastly, PG&E objects to this request on the grounds that it seeks to impose a continuing response obligation on the responding party. Continuing discovery obligations are not permitted under California law. Biles v. Exxon Mobil Corp., 124 Cal.App.4th 1315, 1328 (2004); Code Civ. Proc. § 2030.060(g). Notwithstanding and without waiving these objections, PG&E responds as follows. We will do our best to provide the requested information within the requested timeframe, or as soon as possible thereafter. However, please note that due to the timing and voluminous nature of our submissions to Energy Safety, it may not always be possible to provide the information sought within the requested timeframe. In these instances, we will provide the requested information as soon as it is reasonably possible. | Holly Wehrman | 2023-02-07 | 2023-02-14 | 2023-02-14 | https://www.pge.com/pge_global/common/pdfs/safety/emergency-preparedness/natural-disaster/wildfires/wildfire-mitigation-plan/reference-docs/2023/CalAdvocates_001.zip | 0 | N/A | N/A | N/A | N/A | N/A
Pre-Discovery 05 | CalPA | Set WMP-02 | CalPA_Set WMP-02 | 1 | CalPA_Set WMP-02_Q1 | Please identify and provide a copy of all quality assurance or quality control (QA/QC) reports conducted by internal entities that were completed since January 1, 2022 and that examined any programs, initiatives, or strategies described in your 2022 WMP Update. | PG&E understands this question to refer to reports from our internal Quality Control, Quality Assurance, and Quality Verification programs as set forth below. System Inspections Department Please see the attachment below for the System Inspections QC Department’s daily and weekly dashboards communicating Key Performance Indicators (KPIs) and analysis. • “WMP-Discovery2023_DR_CalAdvocates_002-Q001Atch01CONF.pdf” Please note the above attachment contain confidential information. Electric Compliance Quality Management • GO 165 Inspections Please see attachment listed below for the Electric Compliance Quality Management Department’s audits of GO 165 inspections. One Distribution and one Transmission system inspections audits were conducted in 2022. Please see attachments “WMP-Discovery2023_DR_CalAdvocates_002-Q001Atch02CONF.pdf” and “WMP-Discovery2023_DR_CalAdvocates_002-Q001Atch03CONF.pdf”; Please note the above attachments contain confidential information. • Vegetation Quality Verification (QV) The 2022 WMP submission for Vegetation QV is broken down to the following components: Distribution Reviews, Transmission Reviews, Vegetation Control Reviews, Enhanced Vegetation Management (EVM), and Break-In Audits. Please see the following reports for each of these components: o QVVM Work Log (attached as “xlsx”) is a comprehensive log for all QV reviews completed in 2022 including a summary of findings for each review as well as a detailed report of those findings. o 2022 EVM Report, attached as “WMPDiscovery2023_DR_CalAdvocates_002-Q001Atch05.pdf.” • Vegetation Quality Assurance (QA) The 2022 WMP submission for Vegetation QA is broken down by “bundles.” Final reports are available for bundles that have been completed to date. Please see the attached zip file for a total of 37 QA Report Packages: “WMPDiscovery2023_DR_CalAdvocates_002-Q001Atch06CONF.zip”; Please note the above attachments in the Zip folder contain confidential information. | Holly Wehrman | 2023-02-07 | 2023-03-07 | 2023-03-07 | https://www.pge.com/pge_global/common/pdfs/safety/emergency-preparedness/natural-disaster/wildfires/wildfire-mitigation-plan/reference-docs/2023/CalAdvocates_002.zip | 6 | N/A | N/A | N/A | N/A | N/A
Pre-Discovery 06 | CalPA | Set WMP-02 | CalPA_Set WMP-02 | 2 | CalPA_Set WMP-02_Q2 | Please identify and provide a copy of all quality assurance or quality control (QA/QC) reports conducted by external entities that were completed since January 1, 2022 and that examined any programs, initiatives, or strategies described in your 2022 WMP Update. External entities include, but are not limited to, consultants, contractors, auditors, court-appointed monitors, and Independent Evaluators. | The PG&E Independent Safety Monitor Status Update Report, dated October 4, 2022, discusses programs and initiatives described in our 2022 WMP. Please find the document here: https://www.cpuc.ca.gov/-/media/cpuc-website/industries andtopics/documents/pge/oversight-and-enforcement/ism-status-update-report-q3-2022.pdf. | Holly Wehrman | 2023-02-07 | 2023-03-07 | 2023-03-07 | https://www.pge.com/pge_global/common/pdfs/safety/emergency-preparedness/natural-disaster/wildfires/wildfire-mitigation-plan/reference-docs/2023/CalAdvocates_002.zip | 1 | N/A | N/A | N/A | N/A | N/A
Pre-Discovery 07 | CalPA | Set WMP-02 | CalPA_Set WMP-02 | 3 | CalPA_Set WMP-02_Q3 | Provide an Excel table of all defects in the year 2022 found by Energy Safety’s Compliance Branch (as rows) that includes the following information in separate columns. a) Associated circuit name b) Defect type c) Description of defect d) WMP initiative (from your 2022 WMP update) associated with defect e) Date that the defect was identified f) Date that the defect was corrected g) If the defect has not yet been corrected as of the issuance date of this data request, a brief explanation h) Priority level of corresponding corrective tag i) Geographic latitude of defect in decimal degrees, truncated to seven decimal places j) Geographic longitude of defect in decimal degrees, truncated to seven decimal places | Please see attachment “WMP-Discovery2023_DR_CalAdvocates_002-Q03Atch01CONF.xlsx” for a list of all alleged defects identified in December 2021 by the Office of Energy Infrastructure Safety (“Energy Safety”). Please note these defects were issued as notification of defects in March 2022. Please note the following: • The data provided for “Defect type”, “Description of defect,” and “Date that the defect was identified” are all based on Energy Safety’s inspection reports. • Not all corrective actions required Electric Corrective (EC) notifications (or “EC tags”). For example, while reviewing the alleged defects from Energy Safety, some work was addressed directly in the field (e.g., trimming of vegetation), and no EC tag was created. • This attachment contains confidential information | Holly Wehrman | 2023-02-07 | 2023-02-22 | 2023-02-22 | https://www.pge.com/pge_global/common/pdfs/safety/emergency-preparedness/natural-disaster/wildfires/wildfire-mitigation-plan/reference-docs/2023/CalAdvocates_002.zip | 1 | N/A | 8.1.3 | Asset Inspections | N/A | N/A
Pre-Discovery 08 | CalPA | Set WMP-03 | CalPA_Set WMP-03 | 1 | CalPA_Set WMP-03_Q1 | Provide an Excel table of all distribution circuits existing as of January 1, 2023 (as rows) that includes the following information in separate columns. a. Circuit name b. Circuit ID number c. Total circuit miles d. Circuit miles in Non-HFTD Areas e. Circuit miles in Other HFTD f. Circuit miles in HFTD Tier 2 g. Circuit miles in HFTD Tier 3 h. Circuit voltage i. Circuit SAIDI (System Average Interruption Duration Index) for 2021 j. Circuit SAIDI (System Average Interruption Duration Index) for 2022 k. Circuit SAIFI (System Average Interruption Frequency Index) for 2021 l. Circuit SAIFI (System Average Interruption Frequency Index) for 2022 m. Circuit MAIFI (Momentary Average Interruption Frequency Index) for 2021 n. Circuit MAIFI (Momentary Average Interruption Frequency Index) for 2022 o. Total customer-minutes of de-energization on the circuit due to PSPS events in 2021 (sum of customer-minutes across all PSPS events). p. Total customer-minutes of de-energization on the circuit due to PSPS events in 2022 (sum of customer-minutes across all PSPS events). q. Total customer-minutes of de-energization on the circuit due to fast-trip settings in 2021. r. Total customer-minutes of de-energization on the circuit due to fast-trip settings in 2022. s. Number of trees that were worked on for EVM in Non-HFTD in 2021 t. Number of trees that were worked on for EVM in Non-HFTD in 2022 u. Number of trees that were worked on for EVM in Other HFTD in 2021 v. Number of trees that were worked on for EVM in Other HFTD in 2022 w. Number of trees that were worked on for EVM in HFTD Tier 2 in 2021 x. Number of trees that were worked on for EVM in HFTD Tier 2 in 2022 y. Number of trees that were worked on for EVM in HFTD Tier 3 in 2021 z. Number of trees that were worked on for EVM in HFTD Tier 3 in 2022 aa. Miles of covered conductor installed in Non-HFTD in 2021 bb. Miles of covered conductor installed in Non-HFTD in 2022 cc. Miles of covered conductor installed in Other HFTD in 2021 dd. Miles of covered conductor installed in Other HFTD in 2022 ee. Miles of covered conductor installed in HFTD Tier 2 in 2021 ff. Miles of covered conductor installed in HFTD Tier 2 in 2022 gg. Miles of covered conductor installed in HFTD Tier 3 in 2021 hh. Miles of covered conductor installed in HFTD Tier 3 in 2022 ii. Number of poles replaced in Non-HFTD in 2021 jj. Number of poles replaced in Non-HFTD in 2022 kk. Number of poles replaced in Other HFTD in 2021 ll. Number of poles replaced in Other HFTD in 2022 mm. Number of poles replaced in HFTD Tier 2 in 2021 nn. Number of poles replaced in HFTD Tier 2 in 2022 oo. Number of poles replaced in HFTD Tier 3 in 2021 pp. Number of poles replaced in HFTD Tier 3 in 2022 qq. Miles of underground conductor installation in Non-HFTD in 2021 rr. Miles of underground conductor installation in Non-HFTD in 2022 ss. Miles of underground conductor installation in Other HFTD in 2021 tt. Miles of underground conductor installation in Other HFTD in 2022 uu. Miles of underground conductor installation in HFTD Tier 2 in 2021 vv. Miles of underground conductor installation in HFTD Tier 2 in 2022 ww. Miles of underground conductor installation in HFTD Tier 3 in 2021 xx. Miles of underground conductor installation in HFTD Tier 3 in 2022 yy. Miles of LiDAR inspection in Non-HFTD in 2021 zz. Miles of LiDAR inspection in Non-HFTD in 2022 aaa. Miles of LiDAR inspection in Other HFTD in 2021 bbb. Miles of LiDAR inspection in Other HFTD in 2022 ccc. Miles of LiDAR inspection in HFTD Tier 2 in 2021 ddd. Miles of LiDAR inspection in HFTD Tier 2 in 2022 eee. Miles of LiDAR inspection in HFTD Tier 3 in 2021 fff. Miles of LiDAR inspection in HFTD Tier 3 in 2022 ggg. Number of detailed overhead inspections in Non-HFTD in 2021 hhh. Number of detailed overhead inspections in Non-HFTD in 2022 iii. Number of detailed overhead inspections in Other HFTD in 2021 jjj. Number of detailed overhead inspections in Other HFTD in 2022 kkk. Number of detailed overhead inspections in HFTD Tier 2 in 2021 lll. Number of detailed overhead inspections in HFTD Tier 2 in 2022 mmm. Number of detailed overhead inspections in HFTD Tier 3 in 2021 nnn. Number of detailed overhead inspections in HFTD Tier 3 in 2022 ooo. Number of sectionalization devices installed in Non-HFTD in 2021 ppp. Number of sectionalization devices installed in Non-HFTD in 2022 qqq. Number of sectionalization devices installed in Other HFTD in 2021 rrr. Number of sectionalization devices installed in Other HFTD in 2022 sss. Number of sectionalization devices installed in HFTD Tier 2 in 2021 ttt. Number of sectionalization devices installed in HFTD Tier 2 in 2022 uuu. Number of sectionalization devices installed in HFTD Tier 3 in 2021 vvv. Number of sectionalization devices installed in HFTD Tier 3 in 2022 | PG&E is providing the requested distribution information at the circuit level in attachment “WMP-Discovery2023_DR_CalAdvocates_003-Q001Atch01.xlxs.” Included in the table below are notes that document assumptions in the methodology for data collection. Where we have not included any notes, the data provided did not require adaptations or assumptions in answering the request. For purposes of this request, “Other HFTD” refers to Zone 1 areas. Asset data provided in response to this request was generated from PG&E’s Geographic Information Systems (GIS) and presented in a spreadsheet format. PG&E’s Electric Transmission GIS and Electric Distribution GIS mapping systems represent assets associated with construction work when that work has been received and mapped by electric GIS mapping technicians. Construction jobs that are partially complete or fully complete may be mapped in the GIS systems once construction “asbuilt” information has been submitted and accepted by the GIS Mapping Department. Prior to being received by the GIS Mapping Department, completed job packages must undergo several processing steps including clerical review, processing, and paperwork scanning. Sometimes completed job packages require additional information from the field or post-estimating work. The processing steps take time to complete. Until a project is completed and mapped, detailed information remains in the design systems and paper job packages. Therefore, completed field work is not always reflected in the current GIS systems. Once data is mapped in PG&E’s GIS systems, it can be formatted to meet the requirements of the Office of Energy Infrastructure Safety (Energy Safety) File Geodatabase schema and included in our GIS Data Standard submissions. Data Question Notes Circuit Information a-h Some circuits can have multiple voltages. Where this occurs, the Circuit Voltage in column g reflects the voltage of the majority of the circuit (based on circuit miles). Please note, Circuit IDs and Circuit Names representing idle circuits were not included in this response. SAIDI/SAIFI/MAIFI i-n All transmission, substation, and distribution level outages as of February 22, 2023 were used to quantify the metric results as measured at the individual distribution circuit level and include Major Event Days (as defined in the IEEE 1366 Standard). The denominator used for each calculation is based on the number of customers served by each circuit (based on the system confirmation at the end of 2022 and may not represent the same circuit configuration at the time of each contributing outage event). De-Energization o-r As previously stated in our PSPS Post Event DeEnergization reports submitted to the CPUC: “The information, times and figures referenced in this report are based on the best available information available at the time of this report’s submission. The information, times and figures herein are subject to revision based on further analysis and validation.” As such, we note that there are some minor updated revisions in the data included in this submission, as compared to the data that may have been previously reported in previous submissions immediately following the events, due to further data reconciliation and analysis having been performed in the time which has elapsed between this report and any other previous submissions. In some circumstances, PG&E may conclude a PSPS event before all customers are restored. For example, when there is an ongoing fire that prohibits PG&E from restoring customers or extensive weather-related damages that require extended outages while crews safely repair the area. The outage durations for these customers are not included in Questions 1o-p and Questions 2i-j, as we do not have restoration dates and times for those customers. For information on which circuits were not restored prior to concluding the PSPS, please see the “Time, Place, Duration, and Affected Customers” appendix section of the PSPS Post-Event Reports. Please note that the sum of PSPS customer outage durations is rounded up to the whole minute for each circuit to be consistent with data included in past data responses. This data request response will reference all outages associated with a PSPS event, including those which are either indirect effects of the PSPS event and are not direct de-energizations, or brief outages occurring as a result of microgrid switching, or temporary generation used as part of PSPS mitigation solution. Most switching in a PSPS event to re-energize customers takes place, typically, between five minutes and one hour, and that re-energization occurring within four hours of deenergization or outages less than four hours, typically, can likely be attributed to switching. EVM s-z Covered Conductor aa-hh Number of Poles Replaced ii-pp PG&E’s system of record does not have a relationship between circuits and poles, and therefore we cannot provide this data in the format requested. However, we can provide the data for poles replaced in 2021 and 2022 by SAP Equipment ID. Please see “WMPDiscovery2023_DR_CalAdvocates_003-Q01Atch02.xlxs.” Underground Conductor Installation qq-xx The information for underground miles provided is based on the distribution underground cable recorded in PG&E’s mapping system (EDGIS). The total miles installed are based on the “year installed” as recorded in EDGIS for each individual circuit then added together to provide the cumulative total. These underground miles are comprised primarily of new business, capacity, reliability, cable replacement, customer requested, Rule20, and fire hardening undergrounding work. LiDAR inspection yy-fff Detailed Overhead Inspections ggg-nnn Sectionalization Devices ooo-vvv Sectionalization devices include remotely operable SCADA sectionalizing devices and manually operated sectionalizing devices (i.e., reclosers, not fuses). | Holly Wehrman | 2023-02-07 | 2023-03-10 | 2023-03-10 | https://www.pge.com/pge_global/common/pdfs/safety/emergency-preparedness/natural-disaster/wildfires/wildfire-mitigation-plan/reference-docs/2023/CalAdvocates_003.zip | 2 | N/A | 8.1.3 | Asset Inspections | Distribution | N/A
Pre-Discovery 09 | CalPA | Set WMP-03 | CalPA_Set WMP-03 | 2 | CalPA_Set WMP-03_Q2 | Provide an Excel table of all transmission circuits existing as of January 1, 2023 (as rows) that includes the following information in separate columns. a. Circuit name b. Circuit ID number c. Total circuit miles d. Circuit miles in Non-HFTD Areas e. Circuit miles in Other HFTD f. Circuit miles in HFTD Tier 2 g. Circuit miles in HFTD Tier 3 h. Circuit voltage i. Total customer-minutes of de-energization on the circuit due to PSPS events in 2021 (sum of customer-minutes across all PSPS events). j. Total customer-minutes of de-energization on the circuit due to PSPS events in 2022 (sum of customer-minutes across all PSPS events). k. Total customer-minutes of de-energization on the circuit due to fast-trip settings in 2021. l. Total customer-minutes of de-energization on the circuit due to fast-trip settings in 2022. m. Number of support structures replaced in Non-HFTD in 2021 n. Number of support structures replaced in Non-HFTD in 2022 o. Number of support structures replaced in Other HFTD in 2021 p. Number of support structures replaced in Other HFTD in 2022 q. Number of support structures replaced in HFTD Tier 2 in 2021 r. Number of support structures replaced in HFTD Tier 2 in 2022 s. Number of support structures replaced in HFTD Tier 3 in 2021 t. Number of support structures replaced in HFTD Tier 3 in 2022 u. Miles of LiDAR inspection in Non-HFTD in 2021 v. Miles of LiDAR inspection in Non-HFTD in 2022 w. Miles of LiDAR inspection in Other HFTD in 2021 x. Miles of LiDAR inspection in Other HFTD in 2022 y. Miles of LiDAR inspection in HFTD Tier 2 in 2021 z. Miles of LiDAR inspection in HFTD Tier 2 in 2022 aa. Miles of LiDAR inspection in HFTD Tier 3 in 2021 bb. Miles of LiDAR inspection in HFTD Tier 3 in 2022 cc. Number of detailed aerial inspections in Non-HFTD in 2021 dd. Number of detailed aerial inspections in Non-HFTD in 2022 ee. Number of detailed aerial inspections in Other HFTD in 2021 ff. Number of detailed aerial inspections in Other HFTD in 2022 gg. Number of detailed aerial inspections in HFTD Tier 2 in 2021 hh. Number of detailed aerial inspections in HFTD Tier 2 in 2022 ii. Number of detailed aerial inspections in HFTD Tier 3 in 2021 jj. Number of detailed aerial inspections in HFTD Tier 3 in 2022 kk. Number of detailed climbing inspections in Non-HFTD in 2021 ll. Number of detailed climbing inspections in Non-HFTD in 2022 mm. Number of detailed climbing inspections in Other HFTD in 2021 nn. Number of detailed climbing inspections in Other HFTD in 2022 oo. Number of detailed climbing inspections in HFTD Tier 2 in 2021 pp. Number of detailed climbing inspections in HFTD Tier 2 in 2022 qq. Number of detailed climbing inspections in HFTD Tier 3 in 2021 rr. Number of detailed climbing inspections in HFTD Tier 3 in 2022 ss. Number of detailed ground inspections in Non-HFTD in 2021 tt. Number of detailed ground inspections in Non-HFTD in 2022 uu. Number of detailed ground inspections in Other HFTD in 2021 vv. Number of detailed ground inspections in Other HFTD in 2022 ww. Number of detailed ground inspections in HFTD Tier 2 in 2021 xx. Number of detailed ground inspections in HFTD Tier 2 in 2022 yy. Number of detailed ground inspections in HFTD Tier 3 in 2021 zz. Number of detailed ground inspections in HFTD Tier 3 in 2022 aaa. Number of sectionalization devices installed in Non-HFTD in 2021 bbb. Number of sectionalization devices installed in Non-HFTD in 2022 ccc. Number of sectionalization devices installed in Other HFTD in 2021 ddd. Number of sectionalization devices installed in Other HFTD in 2022 eee. Number of sectionalization devices installed in HFTD Tier 2 in 2021 fff. Number of sectionalization devices installed in HFTD Tier 2 in 2022 ggg. Number of sectionalization devices installed in HFTD Tier 3 in 2021 hhh. Number of sectionalization devices installed in HFTD Tier 3 in 2022 iii. Miles of transmission ROW expansion performed in Non-HFTD in 2021 jjj. Miles of transmission ROW expansion performed in Non-HFTD in 2022 kkk. Miles of transmission ROW expansion performed in Other HFTD in 2021 lll. Miles of transmission ROW expansion performed in Other HFTD in 2022 mmm. Miles of transmission ROW expansion performed in HFTD Tier 2 in 2021 nnn. Miles of transmission ROW expansion performed in HFTD Tier 2 in 2022 ooo. Miles of transmission ROW expansion performed in HFTD Tier 3 in 2021 ppp. Miles of transmission ROW expansion performed in HFTD Tier 3 in 2022 | PG&E is providing the requested transmission information at the circuit level in the attachment named “WMP-Discovery2023_DR_CalAdvocates_003-Q001Atch01.xlxs.” Included in the table below are notes that document assumptions in the methodology for data collection. Where we have not included any notes, the data provided did not require adaptations or assumptions in answering the request. For purposes of this request, “Other HFTD” refers to Zone 1 areas. Asset data provided in response to this request was generated from PG&E’s Geographic Information Systems (GIS) and presented in a spreadsheet format. PG&E’s Electric Transmission GIS and Electric Distribution GIS mapping systems represent assets associated with construction work when that work has been received and mapped by electric GIS mapping technicians. Construction jobs that are partially complete or fully complete may be mapped in the GIS systems once construction “asbuilt” information has been submitted and accepted by the GIS Mapping Department. Prior to being received by the GIS Mapping Department, completed job packages must undergo several processing steps including clerical review, processing, and paperwork scanning. Sometimes completed job packages require additional information from the field or post-estimating work. The processing steps take time to complete. Until a project is completed and mapped, detailed information remains in the design systems and paper job packages. Therefore, completed field work is not always reflected in the current GIS systems. Once data is mapped in PG&E’s GIS systems, it can be formatted to meet the requirements of the Office of Energy Infrastructure Safety (Energy Safety) File Geodatabase schema and included in our GIS Data Standard submissions. Data Question Notes Circuit Information a.-h Some circuits can have multiple voltages. Where this occurs the Circuit Voltage in column g reflects the voltage of the majority of the circuit (based on circuit miles). De-Energization i-l As previously stated in our PSPS Post Event DeEnergization reports submitted to the CPUC: “The information, times and figures referenced in this report are based on the best available information available at the time of this report’s submission. The information, times and figures herein are subject to revision based on further analysis and validation.” As such, we note that there are some minor updated revisions in the data included in this submission, as compared to the data that may have been previously reported in previous submissions immediately following the events, due to further data reconciliation and analysis having been performed in the time which has elapsed between this report and any other previous submissions. In some circumstances, PG&E may conclude a PSPS before all customers are restored. For example, when there is an ongoing fire that prohibits PG&E from restoring customers or extensive weather-related damages that require extended outages while crews safely repair the area. The outage durations for these customers are not included in Questions 1o-p and Questions 2i-j, as we do not have restoration dates and times. For information on which circuits were not restored prior to concluding the PSPS, please see the “Time, Place, Duration, and Affected Customers” appendix section of the PSPS Post-Event Reports. Note the sum of PSPS customer outage durations is rounded up to the whole minute for each circuit to be consistent with data included in past data responses. This data request will reference all outages associated with a PSPS event, including those which are either indirect effects of the PSPS event and are not direct de-energizations, or brief outages occurring as a result of microgrid switching or temporary generation used as part of PSPS mitigation solution. Most switching in a PSPS event to re-energize customers takes place, typically, between five minutes and one hour, and that re-energization occurring within four hours of de-energization or outages less than four hours, typically, can likely be attributed to switching. Number of Support Structures Replaced m-t Data includes poles and towers. Poles were matched to a circuit by GIS radius of 15 feet. LiDAR inspection u-bb Number of detailed aerial inspections cc-jj Number of detailed climbing inspections kk-rr Number of detailed ground inspections tt-zz Sectionalization Devices aaa-zzz Sectionalization devices include remotely operable SCADA sectionalizing devices and manually operated sectionalizing devices; ie reclosers not fuses. Transmission ROW Expansion iii-ppp PG&E does have an ongoing Transmission ROW Expansion program that is focused on reliability that was initiated in 2017. That program continued in 2022, but is not directly related to wildfire mitigation. However, to the extent ROWs are being expanded, there will be incremental wildfire mitigation benefits resulting from decreased vegetation around our transmission lines. | Holly Wehrman | 2023-02-07 | 2023-03-10 | 2023-03-10 | https://www.pge.com/pge_global/common/pdfs/safety/emergency-preparedness/natural-disaster/wildfires/wildfire-mitigation-plan/reference-docs/2023/CalAdvocates_003.zip | 0 | N/A | 8.1.3 | Asset Inspections | Transmission | N/A
Pre-Discovery 10 | CalPA | Set WMP-03 | CalPA_Set WMP-03 | 3 | CalPA_Set WMP-03_Q3 | Provide an Excel table of all distribution circuits existing as of January 1, 2022 (as rows) that were removed or decommissioned in 2022, either partially or entirely. This includes permanent removal, removal of overhead lines that were moved underground, or overhead lines that were decommissioned but not physically removed. Include the following information in separate columns. a. Circuit name b. Circuit ID number c. Circuit miles removed or decommissioned in Non-HFTD Areas d. Circuit miles removed or decommissioned in Other HFTD e. Circuit miles removed or decommissioned in HFTD Tier 2 f. Circuit miles removed or decommissioned in HFTD Tier 3 g. Reason(s) for removal or decommissioning | Attached is “WMP-Discovery2023_DR_CalAdvocates_003-Q003Atch01.xlsx”, which provides information regarding removals of primary distribution lines in HFTD in 2022, which is the subset of the requested information available at this time. PG&E does not track line removals when relocating overhead to underground, removing secondary services, or removing lines in non-HFTD. Further, our GIS cannot be used to obtain this information retroactively because when mapping removals, the electric assets are removed from GIS. Below we provide additional information to clarify the data provided in the attachment in response to the request. a. Circuit name: See column C. b. Circuit ID number: See column D. c. Circuit miles removed or decommissioned in Non-HFTD Areas: N/A. As noted above, PG&E does not track line removals when relocating overhead to underground, removing secondary services, or removing lines in non-HFTD . d. Circuit miles removed or decommissioned in Other HFTD: N/A. PG&E does not track line removals when relocating overhead to underground, removing secondary services, or removing lines in non-HFTD. e. Circuit miles removed or decommissioned in HFTD Tier 2: Column E indicates if the project in the unique circuit segment is in either a Tier 2 and/or Tier 3 HFTD, and column G includes the associated circuit miles. f. Circuit miles removed or decommissioned in HFTD Tier 3: Column E indicates if the project in the unique circuit segment is in either a Tier 2 and/or Tier 3 HFTD, and column G includes the associated circuit miles. g. Reason(s) for removal or decommissioning: See Column F, which notes the name of one of three programs: (1) Fire Rebuild – Removal based on rebuilding in the aftermath of wildfires; (2) Idle Facilities – Unused facilities with no foreseeable future use; or (3) Base SH (System Hardening) – Removal based on the risk-informed criteria used in PG&E’s System Hardening Program. | Holly Wehrman | 2023-02-07 | 2023-03-10 | 2023-03-10 | https://www.pge.com/pge_global/common/pdfs/safety/emergency-preparedness/natural-disaster/wildfires/wildfire-mitigation-plan/reference-docs/2023/CalAdvocates_003.zip | 1 | N/A | 8.1.2 | Grid Design and System Hardening | Work Performed in 2022 | N/A
Pre-Discovery 11 | CalPA | Set WMP-03 | CalPA_Set WMP-03 | 4 | CalPA_Set WMP-03_Q4 | Provide an Excel table of all transmission circuits existing as of January 1, 2022 (as rows) that were removed or decommissioned in 2022, either partially or entirely. This includes permanent removal, removal of overhead lines that were moved underground, or overhead lines that were decommissioned but not physically removed. Includes the following information in separate columns. a. Circuit name b. Circuit ID number c. Circuit miles removed or decommissioned in Non-HFTD Areas d. Circuit miles removed or decommissioned in Other HFTD e. Circuit miles removed or decommissioned in HFTD Tier 2 f. Circuit miles removed or decommissioned in HFTD Tier 3 g. Reason(s) for removal or decommissioning | Please see “WMP-Discovery2023_DR_CalAdvocates_003-Q004Atch01.xlsx. | Holly Wehrman | 2023-02-07 | 2023-03-10 | 2023-03-10 | https://www.pge.com/pge_global/common/pdfs/safety/emergency-preparedness/natural-disaster/wildfires/wildfire-mitigation-plan/reference-docs/2023/CalAdvocates_003.zip | 1 | N/A | Grid Design and System Hardening | System Hardening | Work Performed in 2022 | N/A
Pre-Discovery 12 | CalPA | Set WMP-03 | CalPA_Set WMP-03 | 5 | CalPA_Set WMP-03_Q5 | For each WMP initiative listed below, please state how the modeled Wildfire Risk Scores for each circuit or circuit-segment influenced where you performed work in 2022. a. EVM b. Covered conductor installation c. Undergrounding d. Distribution pole replacement e. Grid sectionalization f. Detailed inspections of distribution assets g. Detailed inspections of transmission assets h. Aerial inspections of distribution assets i. Aerial inspections of transmission assets j. LiDAR inspections of distribution assets k. LiDAR inspections of transmission assets | a. EVM work in 2022 was informed by a modification of the 2021 Wildfire Distribution Risk Model (WDRM). The refined output from the 2021 WDRM is referred to as the EVM Tree-Weighted Prioritization. The EVM Tree-Weighted Prioritization prioritized the high risk CPZs with the associated miles and estimated tree work to produce the 2022 EVM Scope of Work as described in the 2022 WMP Section 7.1.B. In 2022, the goals for the EVM program were: (1) to perform at least 80% of our 2022 EVM work on the highest 20% of the risk-ranked miles; and (2) to perform approximately 1,800 miles of EVM work by the end of the year. b. As described in the 2022 WMP Section 7.3.3.17.1 “System Hardening –Distribution,” PG&E targeted the highest wildfire risk miles and applied various mitigations such as line removal, conversion from overhead to underground, application of remote grid alternatives, mitigation of exposure through relocation of overhead facilities, and in-place overhead system hardening (emphasis added). For 2022, the highest wildfire risk miles were separated into four categories: 1. The top 20 percent of circuit segments as defined by PG&E’s 2021 WDRM v2 for System Hardening, 2. Fire and Major Emergency rebuild within HFTD, 3. PSPS mitigation projects; and 4. Locations identified by PG&E’s Public Safety Specialist (PSS) team as presenting elevated wildfire risk. The primary approach used for selecting and prioritizing circuit segments for covered conductor installation was based on the 2021 WDRM v2. c. As described in the 2022 WMP Section 7.3.3.17.1 “System Hardening –Distribution,” PG&E targeted the highest wildfire risk miles and applied various mitigations such as line removal, conversion from overhead to underground(emphasis added), application of remote grid alternatives, mitigation of exposure through relocation of overhead facilities, and in-place overhead system hardening. For 2022, the highest wildfire risk miles are separated into four categories: 1. The top 20 percent of circuit segments as defined by PG&E’s 2021 WDRM v2 for System Hardening, 2. Fire and Major Emergency rebuild within HFTD, 3. PSPS mitigation projects; and 4. Locations identified by PG&E’s Public Safety Specialist (PSS) team as presenting elevated wildfire risk. The primary approach used for selecting and prioritizing circuit segments for converting overhead to underground was based on the 2021 WDRM v2. As described in the 2022 WMP Section 7.3.3.17.6 “Butte County Rebuild Program,” PG&E did not identify these circuit segments using a risk model. d. As described in the 2022 WMP Section 7.3.3.6, “Distribution Pole Replacement and Reinforcement, Including with Composite Poles,” PG&E leveraged the Wildfire Distribution Risk Model (WRDM) v2 to determine what pole replacement work was performed in 2022. Pole replacements are driven primarily by asset condition, namely maintenance tags found through enhanced inspections and intrusive inspections (Pole Test and Treat). These tags are then prioritized using the WRDM, which considers both wildfire ignition likelihood and consequence. In addition, pole replacements were also prioritized based on CPUC commitments, self-reports and other regulatory conditions. e. For transmission and distribution grid sectionalization, Wildfire Risk scores were not factors in determining what grid sectionalizing work was performed. Sectionalizing device prioritization in 2022 was based on circuit HFTD location, likelihood of potential de-energization during future PSPS events (based on a study of 10-years of weather data), and/or potential customer impact. f. In 2022, wildfire risk scores were not factors in determining where work was performed for detailed ground inspections on distribution facilities. Detailed ground inspections were performed on all Tier 3 assets and roughly one-third of Tier 2 assets. This was the final third of a three-year program to inspect Tier 2 distribution structures. g. In 2022, wildfire risk and wildfire consequence informed annual overhead transmission asset detailed inspection scope (in addition to other considerations such as inspection trends and a baseline frequency of every three years for HFTD/HFRA assets). Specifically, highest wildfire risk and wildfire consequence locations were included in the 2022 scope. h. In 2022, wildfire risk scores for were not factors in determining where work was performed for the pilot of aerial inspections. The pilot targeted problematic circuits already included in the ground inspection plan where aerial inspections would likely deliver the most benefit. i. In 2022, wildfire risk and wildfire consequence informed annual overhead transmission asset detailed inspection scope (in addition to other considerations such as inspection trends and a baseline frequency of every three years for HFTD/HFRA assets). Specifically, highest wildfire risk and wildfire consequence locations were included in the 2022 scope. j. PG&E does not have a stand-alone LiDAR distribution inspection program, but collects LiDAR data on distribution to support various needs, including flight planning for aerial inspections and engineering analyses, such as pole loading calculations. PG&E did not use the wildfire risk model in 2022 or 2023 to select locations or sequence LiDAR collection activities. k. PG&E does not use risk-informed prioritization for Transmission LiDAR inspections, rather, it inspects 100 percent of the system annually using LiDAR. The Transmission Routine NERC and Non-NERC Inspection cycle consists of a LiDAR inspection followed by a ground patrol based on LiDAR findings. The LiDAR inspection provides an inventory of potential vegetation for ground patrol, and the results of the ground patrol prescribe the forecasted tree work to comply with state and federal regulations. | Holly Wehrman | 2023-02-07 | 2023-03-10 | 2023-03-10 | https://www.pge.com/pge_global/common/pdfs/safety/emergency-preparedness/natural-disaster/wildfires/wildfire-mitigation-plan/reference-docs/2023/CalAdvocates_003.zip | 0 | N/A | 2022 WMP Section 7.1 | Wildfire Mitigation Strategy Development | N/A | N/A
Pre-Discovery 13 | CalPA | Set WMP-03 | CalPA_Set WMP-03 | 6 | CalPA_Set WMP-03_Q6 | For each WMP initiative listed below, please state how the modeled Wildfire Risk Scores for each circuit or circuit-segment influenced how work in 2022 was sequenced. a. EVM b. Covered conductor installation c. Undergrounding d. Distribution pole replacement e. Grid sectionalization f. Detailed inspections of distribution assets g. Detailed inspections of transmission assets h. Aerial inspections of distribution assets i. Aerial inspections of transmission assets j. LiDAR inspections of distribution assets k. LiDAR inspections of transmission assets | a. The 2022 EVM Scope of Work was based on the prioritization from the 2021 list of circuit protection zones informed by the EVM Tree Weighed Prioritization barring external factors and leveraging efficiency of bundling where possible. b. The circuit segments selected for the installation of covered conductor in the System Hardening program were based on the highest wildfire risk criteria described in response to Question 5(b). To then sequence projects, PG&E assesses the dependencies and readiness of each project based on the stage of the work (e.g., designing/estimating, permit acquisition, construction) to appropriately schedule each individual project, as the development time for each project can vary widely. Once projects are in the construction phase, schedules can continue to evolve based on various factors that impact project execution, including unanticipated weather, material availability, and customer preference of timing of re-connection. c. The circuit segments selected for the installation of underground lines in the System Hardening program were based on the highest wildfire risk criteria described in response to Question 5(c). To then sequence projects, PG&E assesses the dependencies and readiness of each project in each stage of the work (e.g., designing/estimating, permit acquisition, land rights acquisition, construction) to appropriately schedule each individual project, as the development time for each project can vary widely. Once projects are in the construction phase, schedules can continue to evolve based on various factors that impact project execution including unanticipated weather, material availability, community limitations (e.g., for road closures), customer preference of timing of re-connection, discovery of hard rock, and/or detection of unmarked existing utility infrastructure. d. After the work for 2022 was prioritized based on the process described in Q005, the pole replacement sequencing was determined based on each pole’s priority bucket, estimating and material readiness, and crew and clearance availability. Wildfire risk scores were not factors in determining sequencing after prioritization. e. For grid sectionalization, Wildfire Risk scores were not factors in determining how work was sequenced. f. In 2022, wildfire risk scores were not factors in how distribution ground inspections were sequenced. Inspections were sequenced based on field conditions including physical access, environmental restrictions, permitting constraints and customer refusals. g. In 2022, the overhead transmission assets in the work plan for inspection were each labeled with the average wildfire risk of their host circuit for consideration in inspection sequencing. Assets were typically grouped by line for execution efficiency. The sequence prioritization also considered operational field knowledge and constraints, including restricted physical access periods, to inform the schedule for completion. h. For overhead distribution aerial pilot inspections, wildfire risk scores for each circuit or circuit-segment did not influence how work in 2022 was sequenced. Sequencing was based on the scheduled ground inspection as well as operational field knowledge and constraints, including restricted physical access periods. i. In 2022, the overhead transmission assets in work plan for inspection were each labeled with the average wildfire risk of their host circuit for consideration in inspection sequencing. Assets were typically grouped by line for execution efficiency. The sequence prioritization also considered operational field knowledge and constraints, including restricted physical access periods, to inform the schedule for completion. j. PG&E does not have a stand-alone LiDAR distribution inspection program but collects LiDAR data on distribution to support various needs, including flight planning for aerial inspections and engineering analyses, such as pole loading calculations. PG&E did not use the wildfire risk model in 2022 to select locations or sequence LiDAR collection activities. k. PG&E does not use risk-informed prioritization for Transmission LiDAR inspections, rather, it inspects 100 percent of the system annually using LiDAR. The Transmission Routine NERC and Non-NERC Inspection cycle consists of a LiDAR inspection followed by a ground patrol based on LiDAR findings. The LiDAR inspection provides an inventory of potential vegetation for ground patrol, and the results of the ground patrol prescribe the forecasted tree work to comply with state and federal regulations | Holly Wehrman | 2023-02-07 | 2023-03-10 | 2023-03-10 | https://www.pge.com/pge_global/common/pdfs/safety/emergency-preparedness/natural-disaster/wildfires/wildfire-mitigation-plan/reference-docs/2023/CalAdvocates_003.zip | 0 | N/A | 2022 WMP Section 7.1 | Wildfire Mitigation Strategy Development | N/A | N/A
Pre-Discovery 14 | CalPA | Set WMP-03 | CalPA_Set WMP-03 | 7 | CalPA_Set WMP-03_Q7 | For each WMP initiative listed below, please state how the modeled Wildfire Risk Scores for each circuit or circuit-segment influence where you plan to perform work in 2023. a. EVM b. Covered conductor installation c. Undergrounding d. Distribution pole replacement e. Grid sectionalization f. Detailed inspections of distribution assets g. Detailed inspections of transmission assets h. Aerial inspections of distribution assets i. Aerial inspections of transmission assets j. LiDAR inspections of distribution assets k. LiDAR inspections of transmission assets | a. PG&E is not conducting EVM in 2023.. b. As described in the 2023 WMP Section 8.1.2.1 “Covered Conductor Installation –Distribution,” PG&E’s System Hardening program, which includes targeted CC installation, focuses on mitigating potential catastrophic wildfire risk caused by distribution overhead assets. The System Hardening Program applies various mitigations to circuit segments that have the highest wildfire risk. For 2023, the highest wildfire risk miles are identified using the following categories: 1. Top Risk Based on Wildfire Distribution Risk Models (WDRM): The primary approach for selecting system hardening miles used two risk prioritization methodologies: (1) top 20 percent circuit segments based on the 2021 WDRM v2 and (2) the Wildfire Feasibility Efficiency (WFE) ranked circuit segments based on the 2022 WDRM v3. Overhead hardening was selected where undergrounding was deemed infeasible for the WDRM v3 selection. 2. Fire Rebuilds: Rebuilding electric distribution lines within towns and communities in the aftermath of catastrophic wildfires. Overhead hardening Fire Rebuild work is identified through a decision tree to determine the type of rebuild (overhead hardening, undergrounding, or other solution) in areas that have been impacted by a wildfire and may include fire-impacted areas in both HFTD and non-HFTD; and 3. PG&E’s Public Safety Specialist (PSS) Identified: Locations identified by PG&E’s PSS team as presenting elevated wildfire risk, such as ingress/egress constraints and community risk factors. c. As described in the 2023 WMP Section 8.1.2.2 “Undergrounding of Electric Lines and/or Equipment – Distribution,” The 2023-2026 undergrounding portfolio is focused on undergrounding lines in the highest risk areas, which include the following: 1. Top Risk-Ranked Circuit Segments Based on WDRMs: The primary approach for selecting miles used two risk prioritization methodologies: (1) Top 20 percent circuit segments based on the 2021 WDRM v2; and (2) the WFE-ranked circuit segments based on the 2022 WDRM v3 and considering undergrounding feasibility. Both approaches used to select undergrounding projects represent approximately 70 percent of our total wildfire risk. 2. Fire Rebuilds: Undergrounding electric distribution lines within towns and communities that are rebuilding in the aftermath of catastrophic wildfires. Undergrounding work in Fire Rebuild areas typically results from the use of a decision tree to determine the type of asset to rebuild and occurs in areas that have been impacted by an actual wildfire that may include fire-impacted areas in both HFTD and non-HFTD. 3. PSPS Mitigation Projects: Projects identified that would reduce PSPS customer impacts. 4. PG&E’s PSS Identification: Locations identified by PG&E’s PSS team as presenting elevated wildfire risk such as ingress/egress constraints and community risk factors. d. As described in the 2023 WMP Section 8.1.2.3, “Distribution Pole Replacements and Reinforcements,” PG&E leveraged the Wildfire Distribution Risk Model (WRDM) v3 to determine what pole replacement work is planned to be performed in 2023. Pole replacements are driven primarily by asset condition, namely maintenance tags found through enhanced inspections and intrusive inspections (Pole Test and Treat). These tags are then prioritized using the WRDM, which considers both wildfire ignition likelihood and consequence. In addition, pole replacements are also prioritized based on CPUC commitments, self-reports or other regulatory conditions. Starting in 2023, PG&E began to bundle distribution pole replacements with non-pole maintenance tags to gain efficiencies and minimize customer impacts. The goal of bundling is to perform all of the corrective maintenance (pole and non-pole) on the line segment under one clearance e. For transmission line, there is no targeted work planned in 2023 for grid sectionalization. For distribution, the program was modified to install additional protective devices to mitigate reliability impacts associated with EPSS. Projects are based upon reliability risk rather than wildfire risk. f. In 2023, PG&E's detailed ground inspection plan is informed by wildfire risk and wildfire consequence as described in 2023 WMP Section 8.1.3.2.1. PG&E developed a frequency recommendation for each level of wildfire consequence: extreme and severe consequence plat maps will be inspected annually; high consequence plat maps will be inspected every other year; and all other plat maps will be inspected once every three years. Structures that constitute the top 10 percent of wildfire risk but are not already included in a plat map that is being inspected by ground or aerial are also included in the 2023 ground inspection plan. g. In 2023, wildfire risk and wildfire consequence inform the annual overhead detailed inspection scope at a structure level (in addition to other considerations such as inspection trends and a baseline frequency of every three years for HFTD/HFRA assets). Specifically, highest wildfire risk and wildfire consequence locations were included in the 2023 scope. h. In 2023, PG&E's distribution aerial inspection pilot is informed by wildfire risk and wildfire consequence as described in 2023 WMP Section 8.1.3.2.1. For aerial inspections, PG&E used the same prioritization framework with the same plat map level designation that we used for detailed ground inspections and is described in Section 8.1.3.2.1. In 2023, PG&E will prioritize the new aerial inspection where an ignition would potentially have the greatest consequences, which include the Extreme and Severe plat maps as well as some of the High consequence plat maps. i. In 2023, wildfire risk and wildfire consequence inform the annual overhead detailed inspection scope at a structure level (in addition to other considerations such as inspection trends and a baseline frequency of every three years for HFTD/HFRA assets). Specifically, highest wildfire risk and wildfire consequence locations were included in the 2023 scope. j. PG&E does not have a stand-alone LiDAR distribution inspection program but collects LiDAR data on distribution to support various needs, including flight planning for aerial inspections and engineering analyses, such as pole loading calculations. PG&E did not use the wildfire risk model in 2022 or 2023 to select locations or sequence LiDAR collection activities k. PG&E does not use risk-informed prioritization for Transmission LiDAR inspections, rather, it inspects 100 percent of the system annually using LiDAR. The Transmission Routine NERC and Non-NERC Inspection cycle consists of a LiDAR inspection followed by a ground patrol based on LiDAR findings. The LiDAR inspection provides an inventory of potential vegetation for ground patrol, and the results of the ground patrol prescribe the forecasted tree work to comply with state and federal regulations. | Holly Wehrman | 2023-02-07 | 2023-03-10 | 2023-03-10 | https://www.pge.com/pge_global/common/pdfs/safety/emergency-preparedness/natural-disaster/wildfires/wildfire-mitigation-plan/reference-docs/2023/CalAdvocates_003.zip | 0 | N/A | 7.2 | Wildfire Mitigation Strategy Development | Wildfire Mitigation Strategy | N/A
Pre-Discovery 15 | CalPA | Set WMP-03 | CalPA_Set WMP-03 | 8 | CalPA_Set WMP-03_Q8 | For each WMP initiative listed below, please state how the modeled Wildfire Risk Scores for each circuit or circuit-segment influence how work in 2023 will be sequenced. a. EVM b. Covered conductor installation c. Undergrounding d. Distribution pole replacement e. Grid sectionalization f. Detailed inspections of distribution assets g. Detailed inspections of transmission assets h. Aerial inspections of distribution assets i. Aerial inspections of transmission assets j. LiDAR inspections of distribution assets k. LiDAR inspections of transmission assets | a. PG&E is not conducting EVM in 2023. b. The circuit segments selected for the installation of covered conductor in the System Hardening program were based on the highest wildfire risk criteria described in response to Question 7(b). To then sequence projects, PG&E assesses the dependencies and readiness of each project based on the stage of the work (e.g., designing/estimating, permit acquisition, construction) to appropriately schedule each individual project, as the development time for each project can vary widely. Once projects are in the construction phase, schedules can continue to evolve based on various factors that impact project execution, including unanticipated weather, material availability, and customer preference of timing of re-connection. c. The circuit segments selected for the installation of underground lines in the System Hardening program were based on the highest wildfire risk criteria described in response to Question 7(c). To then sequence projects, PG&E assesses the dependencies and readiness of each project in each stage of the work (e.g., designing/estimating, permit acquisition, land rights acquisition, construction) to appropriately schedule each individual project, as the development time for each project can vary widely. Once projects are in the construction phase, schedules can continue to evolve based on various factors that impact project execution including unanticipated weather, material availability, community limitations (e.g., for road closures), customer preference of timing of re-connection, discovery of hard rock, and/or detection of unmarked existing utility infrastructure. d. After the work for 2023 is prioritized based on the process described in response to Q007 part d, the pole replacement sequencing is determined based on each pole’s priority bucket, estimating and material readiness, and crew and clearance availability. e. For transmission line, there is no targeted work planned in 2023 for grid sectionalization. For distribution, the 2023 additional sectionalizing and protective device installation work is prioritized by highest reliability benefit and not wildfire risk. f. In 2023, PG&E's sequencing for the ground inspection plan is informed by wildfire consequence as described in 2023 WMP Section 8.1.3.2.1. Detailed inspection activities in HFTD and HFRA are scheduled such that extreme, severe, and high consequence plat maps will be completed by July 31. Medium consequence plat maps will be completed by October 1. Low consequence plat maps will be completed by December 31. Inspections are also sequenced based on field conditions including physical access, environmental restrictions, permitting constraints and customer refusals. g. In 2023, the overhead transmission assets in scope for inspection are each labeled with the average wildfire risk of their host circuit for consideration in inspection sequencing. Assets are typically grouped by line for execution efficiency. The sequence prioritization also considers operational field knowledge and constraints, including restricted physical access periods, to inform the schedule for completion. h. In 2023, PG&E's sequencing for the pilot aerial inspections is not directly based on wildfire risk score. However, in areas of overlap with detailed ground inspections, aerial inspections are scheduled to take place in the same time frame as the scheduled ground inspection, which is based on wildfire consequence. Sequencing is based on the scheduled ground inspection as well as operational field knowledge and constraints, including restricted physical access periods. i. In 2023, the overhead transmission assets in scope for inspection are each labeled with the average wildfire risk of their host circuit for consideration in inspection sequencing. Assets are typically grouped by line for execution efficiency. The sequence prioritization also considers operational field knowledge and constraints, including restricted physical access periods, to inform the schedule for completion. j. PG&E does not have a stand-alone LiDAR distribution inspection program but collects LiDAR data on distribution to support various needs, including flight planning for aerial inspections and engineering analyses, such as pole loading calculations. PG&E did not use the wildfire risk model in 2022 or 2023 to select locations or sequence LiDAR collection activities. k. PG&E does not use risk-informed prioritization for Transmission LiDAR inspections, rather, it inspects 100 percent of the system annually using LiDAR. The Transmission Routine NERC and Non-NERC Inspection cycle consists of a LiDAR inspection followed by a ground patrol based on LiDAR findings. The LiDAR inspection provides an inventory of potential vegetation for ground patrol, and the results of the ground patrol prescribe the forecasted tree work to comply with state and federal regulations. | Holly Wehrman | 2023-02-07 | 2023-03-10 | 2023-03-10 | https://www.pge.com/pge_global/common/pdfs/safety/emergency-preparedness/natural-disaster/wildfires/wildfire-mitigation-plan/reference-docs/2023/CalAdvocates_003.zip | 0 | N/A | 7.2 | Wildfire Mitigation Strategy Development | Wildfire Mitigation Strategy | N/A
Pre-Discovery 16 | CalPA | Set WMP-03 | CalPA_Set WMP-03 | 9 | CalPA_Set WMP-03_Q9 | For each WMP initiative listed below, please state how the modeled Wildfire Risk Scores for eachcircuit or circuit-segment influence where you plan to perform work in 2024. a. EVM b. Covered conductor installation c. Undergrounding d. Distribution pole replacement e. Grid sectionalization f. Detailed inspections of distribution assets g. Detailed inspections of transmission assets h. Aerial inspections of distribution assets i. Aerial inspections of transmission assets j. LiDAR inspections of distribution assets k. LiDAR inspections of transmission assets | a. PG&E is not conducting EVM in 2024. b. Please refer to the response to Question 7b, which also applies to 2024. c. Please refer to the response to Question 7c, which also applies to 2024. d. Please refer to the response to Question 7d, which also applies to 2024. e. For transmission line, there is no targeted work planned in 2024 for grid sectionalization. For distribution, there is no targeted work planned in 2024 for grid sectionalization as future work related to EPSS reliability will be incorporated into base reliability programs. f. In 2024, PG&E’s detailed ground inspection plan will be informed by wildfire risk and wildfire consequence as described in 2023 WMP Section 8.1.3.2.1. PG&E developed a frequency recommendation for each level of wildfire consequence: extreme and severe consequence plat maps will be inspected annually; high consequence plat maps will be inspected every other year; and all other plat maps will be inspected once every three years. Structures that constitute the top 10 percent of wildfire risk but are not already included in a plat map that is being inspected by ground or aerial are also included in the 2024 ground inspection plan. g. In 2024, wildfire risk and wildfire consequence will inform the annual overhead detailed inspection scope at a structure level (in addition to other considerations such as inspection trends and a baseline frequency of every three years for HFTD/HFRA assets). Specifically, highest wildfire risk and wildfire consequence locations were included in the 2024 scope. h. In 2024, PG&E's distribution aerial inspection pilot will be informed by wildfire risk and wildfire consequence as described in 2023 WMP Section 8.1.3.2.1. For aerial inspections, PG&E used the same prioritization framework with the same plat map level designation that we used for detailed ground inspections and is described in Section 8.1.3.2.1. The specific structures and plat maps to be included for inspection in 2024 will depend on 2023 pilot results. i. In 2024, wildfire risk and wildfire consequence will inform the annual overhead detailed inspection scope at a structure level (in addition to other considerations such as inspection trends and a baseline frequency of every three years for HFTD/HFRA assets). Specifically, highest wildfire risk and wildfire consequence locations were included in the 2024 scope. j. PG&E does not have a stand-alone LiDAR distribution inspection program but collects LiDAR data on distribution to support various needs, including flight planning for aerial inspections and engineering analyses, such as pole loading calculations. PG&E did not use the wildfire risk model in 2022 or 2023 to select locations or sequence LiDAR collection activities k. PG&E does not use risk-informed prioritization for Transmission LiDAR inspections, rather, it inspects 100 percent of the system annually using LiDAR. The Transmission Routine NERC and Non-NERC Inspection cycle consists of a LiDAR inspection followed by a ground patrol based on LiDAR findings. The LiDAR inspection provides an inventory of potential vegetation for ground patrol, and the results of the ground patrol prescribe the forecasted tree work to comply with state and federal regulations. | Holly Wehrman | 2023-02-07 | 2023-03-10 | 2023-03-10 | https://www.pge.com/pge_global/common/pdfs/safety/emergency-preparedness/natural-disaster/wildfires/wildfire-mitigation-plan/reference-docs/2023/CalAdvocates_003.zip | 0 | N/A | 7.2 | Wildfire Mitigation Strategy Development | Wildfire Mitigation Strategy | N/A
Pre-Discovery 17 | CalPA | Set WMP-03 | CalPA_Set WMP-03 | 10 | CalPA_Set WMP-03_Q10 | For each WMP initiative listed below, please state how the modeled Wildfire Risk Scores for each circuit or circuit-segment influence how work in 2024 will be sequenced. a. EVM b. Covered conductor installation c. Undergrounding d. Distribution pole replacement e. Grid sectionalization f. Detailed inspections of distribution assets g. Detailed inspections of transmission assets h. Aerial inspections of distribution assets i. Aerial inspections of transmission assets j. LiDAR inspections of distribution assets k. LiDAR inspections of transmission assets | a. PG&E is not conducting EVM in 2024. b. Please refer to the response for Question 8b, which also applies to 2024. c. Please refer to the response for Question 8c, which also applies to 2024. d. Please refer to the response for Question 8d, which also applies to 2024. e. There is no targeted work planned in 2024 for grid sectionalization for both transmission or for distribution. f. In 2024, PG&E's sequencing for the ground inspection plan will be informed by wildfire consequence as described in 2023 WMP Section 8.1.3.2.1. Detailed inspection activities in HFTD and HFRA are scheduled such that extreme, severe, and high consequence plat maps will be completed by July 31. Medium consequence plat maps will be completed by October 1. Low consequence plat maps will be completed by December 31. Inspections are also sequenced based on field conditions including physical access, environmental restrictions, permitting constraints and customer refusals. g. In 2024, the overhead transmission assets in scope for inspection are each labeled with the average wildfire risk of their host circuit for consideration in inspection sequencing. Assets are typically grouped by line for execution efficiency. The sequence prioritization also considers operational field knowledge and constraints, including restricted physical access periods, to inform the schedule for completion. h. In 2024, PG&E's sequencing for the pilot aerial inspections will not be directly based on wildfire risk score. However, in areas of overlap with detailed ground inspections, aerial inspections are scheduled to take place in the same time frame as the scheduled ground inspection, which is based on wildfire consequence. Sequencing is based on the scheduled ground inspection as well as operational field knowledge and constraints, including restricted physical access periods. The specific structures and plat maps to be included for inspection in 2024 will depend on 2023 pilot results. i. In 2024, the overhead transmission assets in scope for inspection are each labeled with the average wildfire risk of their host circuit for consideration in inspection sequencing. Assets are typically grouped by line for execution efficiency. The sequence prioritization also considers operational field knowledge and constraints, including restricted physical access periods, to inform the schedule for completion. j. PG&E does not have a stand-alone LiDAR distribution inspection program but collects LiDAR data on distribution to support various needs, including flight planning for aerial inspections and engineering analyses, such as pole loading calculations. PG&E did not use the wildfire risk model in 2022 or 2023 to select locations or sequence LiDAR collection activities k. PG&E does not use risk-informed prioritization for Transmission LiDAR inspections, rather, it inspects 100 percent of the system annually using LiDAR. The Transmission Routine NERC and Non-NERC Inspection cycle consists of a LiDAR inspection followed by a ground patrol based on LiDAR findings. The LiDAR inspection provides an inventory of potential vegetation for ground patrol, and the results of the ground patrol prescribe the forecasted tree work to comply with state and federal regulations. | Holly Wehrman | 2023-02-07 | 2023-03-10 | 2023-03-10 | https://www.pge.com/pge_global/common/pdfs/safety/emergency-preparedness/natural-disaster/wildfires/wildfire-mitigation-plan/reference-docs/2023/CalAdvocates_003.zip | 0 | N/A | 7.2 | Wildfire Mitigation Strategy Development | Wildfire Mitigation Strategy | N/A
Pre-Discovery 18 | CalPA | Set WMP-04 | CalPA_Set WMP-04 | 1 | CalPA_Set WMP-04_Q1 | For each WMP initiative for which you forecast capital expenditures in 2023 to be at least two times actual capital expenditures in 2022, please provide: a) The name of the initiative as it is identified in your 2023-2025 WMP b) The WMP Initiative number in Table 11 of your 2023-2025 WMP c) The name of the initiative as it is identified in your 2022 WMP Update d) The WMP Initiative number in Table 12 of your 2022 WMP Update e) An explanation for the projected increase. | a) 2023 WMP financials are mapped per WMP Initiative Activities as laid out in Table 11 from Energy Safety. As the 2023 WMP is a new cycle with new mapping of financials by activities that align with the 2023 WMP narrative, there is not an apples-to-apples re-mapping of costs back to the 2022 WMP view. Thus, the comparison can only be made using the 2023 WMP view. Below are the 2023 WMP activities and section numbers where 2023 capital forecast is at least two times compared to the 2022 recorded costs. • Customer support in wildfire and PSPS emergencies – section 8.4.6 • Traditional Overhead Hardening Transmission – 8.1.2.5 b) See the response to part a). c) N/A. As explained in response to part a), there is not an apples-to-apples re-mapping of costs back to the 2022 WMP view. Thus, the comparison can only be made using the 2023 WMP view of 2022 recorded costs. d) N/A, please refer to part c). e) Explanations for the projected increase are below: • Customer support in wildfire and PSPS emergencies – There was a minor cost adjustment/correction in the 2022 recorded costs which resulted in a credit/negative in the 2022 recorded costs as shown in Table 11. • Traditional Overhead Hardening Transmission – We look to complete 43 miles in 2023 as compared to 38 miles in 2022. In addition, the 2022 recorded costs reported in Table 11 are too low due to missing some costs. The 2022 recorded for this initiative should be $7.9M instead of $4.9M. We will correct this item in Table 11 pursuant to the 2023-2025 WMP Guidelines from Energy Safety. | Holly Wehrman | 2023-02-07 | 2023-03-07 | 2023-03-07 | https://www.pge.com/pge_global/common/pdfs/safety/emergency-preparedness/natural-disaster/wildfires/wildfire-mitigation-plan/reference-docs/2023/CalAdvocates_004.zip | 0 | N/A | 4.3 | Proposed Expenditures | N/A | N/A
Pre-Discovery 19 | CalPA | Set WMP-04 | CalPA_Set WMP-04 | 2 | CalPA_Set WMP-04_Q2 | For each WMP initiative for which you forecast capital expenditures in 2024 to be at least two times actual capital expenditures in 2022, please provide: a) The name of the initiative as it is identified in your 2023-2025 WMP b) The WMP Initiative number in Table 11 of your 2023-2025 WMP c) The name of the initiative as it is identified in your 2022 WMP Update d) The WMP Initiative number in Table 12 of your 2022 WMP Update e) An explanation for the projected increase. | a) 2023 WMP financials are mapped per WMP Initiative Activities as laid out in Table 11 from Energy Safety. As the 2023 WMP is a new cycle with new mapping of financials by activities that align with the 2023 WMP narrative, there is not an apples-to-apples re-mapping of costs back to the 2022 WMP view. Thus, the comparison can only be made using the 2023 WMP view. Below are the 2023 WMP activities and section number where the 2024 capital forecast is at least two times compared to the 2022 recorded costs. • Customer support in wildfire and PSPS emergencies – section 8.4.6 b) See the response to part a). c) N/A. As explained in part a) there is not an apples-to-apples re-mapping of costs back to the 2022 WMP view. Thus, the comparison can only be made using the 2023 WMP view of 2022 recorded costs. d) N/A, please refer to the response to part c). e) Explanations for the projected increase are below: • Customer support in wildfire and PSPS emergencies – There was a minor cost adjustment/correction in the 2022 recorded costs which resulted in a credit/negative in the 2022 recorded costs as shown in Table 11. | Holly Wehrman | 2023-02-07 | 2023-03-07 | 2023-03-07 | https://www.pge.com/pge_global/common/pdfs/safety/emergency-preparedness/natural-disaster/wildfires/wildfire-mitigation-plan/reference-docs/2023/CalAdvocates_004.zip | 0 | N/A | 4.3 | Proposed Expenditures | N/A | N/A
Pre-Discovery 20 | CalPA | Set WMP-04 | CalPA_Set WMP-04 | 3 | CalPA_Set WMP-04_Q3 | For each WMP initiative for which you forecast operating expenditures in 2023 to be at least two times actual operating expenditures in 2022, please provide: a) The name of the initiative as it is identified in your 2023-2025 WMP b) The WMP Initiative number in Table 11 of your 2023-2025 WMP c) The name of the initiative as it is identified in your 2022 WMP Update d) The WMP Initiative number in Table 12 of your 2022 WMP Update e) An explanation for the projected increase. | a) 2023 WMP financials are mapped per WMP Initiative Activities as laid out in Table 11 from Energy Safety. As the 2023 WMP is a new cycle with new mapping of financials by activities that align with the 2023 WMP narrative, there is not an apples-to-apples re-mapping of costs back to the 2022 WMP view. Thus, the comparison can only be made using the 2023 WMP view. Below are the 2023 WMP activities and section numbers where 2023 operating expense forecasts are at least two times compared to the 2022 recorded costs. • Other technologies and systems not listed above – section 8.1.2.12 • Environmental monitoring systems – 8.3.2 • Fall-in mitigation 8.2.3.4 b) See the response to part a). c) N/A. As explained in part a) there is not an apples-to-apples re-mapping of costs back to the 2022 WMP view. Thus, the comparison can only be made using the 2023 WMP view of 2022 recorded costs. d) N/A, please refer to the response to part c). e) Explanations for the projected increases are below: • Other technologies and systems not listed above – The 2022 recorded costs in Table 11 are too low due to missing some costs. The 2022 recorded costs need to be adjusted to pull in recorded costs for Substation animal abatement. We will correct this item in Table 11 pursuant to the 2023-2025 WMP Guidelines from Energy Safety. • Environmental monitoring systems – The forecast increase in 2023 is mainly driven by anticipated weather station maintenance work such as calibrations. • Fall-in mitigation – The forecast increase is due to implementing three new VM programs starting in 2023 that support fall-in mitigations (VM for Operational Mitigations, Tree Removal Inventory, Focused Tree Inspections). Please refer to the 2023 WMP narrative in section 8.2.3.4 for additional details. | Holly Wehrman | 2023-02-07 | 2023-03-07 | 2023-03-07 | https://www.pge.com/pge_global/common/pdfs/safety/emergency-preparedness/natural-disaster/wildfires/wildfire-mitigation-plan/reference-docs/2023/CalAdvocates_004.zip | 0 | N/A | 4.3 | Proposed Expenditures | N/A | N/A
Pre-Discovery 21 | CalPA | Set WMP-04 | CalPA_Set WMP-04 | 4 | CalPA_Set WMP-04_Q4 | For each WMP initiative for which you forecast operating expenditures in 2024 to be at least two times actual operating expenditures in 2022, please provide: a) The name of the initiative as it is identified in your 2023-2025 WMP b) The WMP Initiative number in Table 11 of your 2023-2025 WMP c) The name of the initiative as it is identified in your 2022 WMP Update d) The WMP Initiative number in Table 12 of your 2022 WMP Update e) An explanation for the projected increase. | a) 2023 WMP financials are mapped per WMP Initiative Activities as laid out in Table 11 from Energy Safety. As the 2023 WMP is a new cycle with new mapping of financials by activities that align with the 2023 narrative, there is not an apples-to-apples re-mapping of costs back to the 2022 WMP view. Thus, the comparison can only be made using the 2023 WMP view. Below are the 2023 WMP activities and section numbers where 2024 operating expense forecasts are at least two times the 2022 recorded costs. • Other technologies and systems not listed above – section 8.1.2.12 • Microgrids – section 8.1.2.7 • Environmental monitoring systems – 8.3.2 • Fall-in mitigation 8.2.3.4 b) See the response to part a). c) N/A. As explained in part a), there is not an apples-to-apples re-mapping of costs back to the 2022 WMP view. Thus, the comparison can only be made using the 2023 WMP view of 2022 recorded costs. d) N/A. Please refer to the response to part c). e) Explanations for the projected increases are below: • Other technologies and systems not listed above – The 2022 recorded costs are too low by anticipated weather station maintenance work such as calibrations. • Fall-in mitigation – The forecast increase is due to implementing three new VM programs that support fall-in mitigations (VM for Operational Mitigations, Tree Removal Inventory, Focused Tree Inspections). Please refer to the narrative in section 8.2.3.4 of the 2023 WMP for more details due to missing some costs. The 2022 recorded costs need to be adjusted to pull in recorded costs for Substation animal abatement. We will correct this item in Table 11 pursuant to the 2023-2025 WMP Guidelines from Energy Safety. • Microgrids – The projected increase is based on forecast and anticipated projects put forward to the CPUC in PG&E's Microgrids Incentive Program Implementation Plan. The plan is currently awaiting a CPUC Decision. • Environmental monitoring systems – The forecast increase in 2023/2024 is mainly driven. | Holly Wehrman | 2023-02-07 | 2023-03-07 | 2023-03-07 | https://www.pge.com/pge_global/common/pdfs/safety/emergency-preparedness/natural-disaster/wildfires/wildfire-mitigation-plan/reference-docs/2023/CalAdvocates_004.zip | 0 | N/A | 4.3 | Proposed Expenditures | N/A | N/A
Pre-Discovery 22 | CalPA | Set WMP-05 | CalPA_Set WMP-05 | 1 | CalPA_Set WMP-05_Q1 | In response to Data Request CalAdvocates-PGE-2022WMP-31 on September 8, 2022, PG&E provided information regarding its Wildfire Distribution Risk Model version 3 (WDRM v3). Please provide an updated response to questions 1-7 of the above-referenced data request, including any new or changed information since PG&E’s original response. If the response to a question has not changed, please so indicate. | No changes have been made to WDRM v3 since the September 8, 2022 response. | Holly Wehrman | 2023-02-10 | 2023-03-10 | 2023-03-10 | https://www.pge.com/pge_global/common/pdfs/safety/emergency-preparedness/natural-disaster/wildfires/wildfire-mitigation-plan/reference-docs/2023/CalAdvocates_005.zip | 0 | N/A | 2022 WMP Section 4.5 | Model Metrics and Calculation Methodologies | WDRM v3 | N/A
Pre-Discovery 23 | CalPA | Set WMP-05 | CalPA_Set WMP-05 | 2 | CalPA_Set WMP-05_Q2 | a) Have you identified transportation corridors within your service territory where falling or failing lines or poles could currently limit egress and/or ingress during an emergency? b) If the answer to part (a) is yes, please describe how you identify such transportation corridors. c) If available, please provide a geospatial data file that contains all current identified transportation corridors with ingress and egress hazards. | a) The potential of falling or failing lines or poles near identified transportation corridors is not currently reflected in our risk modeling. PG&E Public Safety Specialists with experience as career wildland firefighters have reviewed general egress and/or ingress concerns when evaluating circuits or circuit segments for potential system hardening work. b) Not applicable c) Not applicable | Holly Wehrman | 2023-02-10 | 2023-03-10 | 2023-03-10 | https://www.pge.com/pge_global/common/pdfs/safety/emergency-preparedness/natural-disaster/wildfires/wildfire-mitigation-plan/reference-docs/2023/CalAdvocates_005.zip | 0 | N/A | 8.1.3 | Asset Inspections | N/A | N/A
Pre-Discovery 24 | CalPA | Set WMP-05 | CalPA_Set WMP-05 | 3 | CalPA_Set WMP-05_Q3 | Please fill out the attached spreadsheet, CalAdvocates-PGE-2023WMP-05 Attachment 1, requesting information regarding your asset inspections in 2022. | Please see attachment “WMP-Discovery2023_DR_CalAdvocates_005-Q003Atch01.xlsx” for the requested information | Holly Wehrman | 2023-02-10 | 2023-03-10 | 2023-03-10 | https://www.pge.com/pge_global/common/pdfs/safety/emergency-preparedness/natural-disaster/wildfires/wildfire-mitigation-plan/reference-docs/2023/CalAdvocates_005.zip | 1 | N/A | 8.1.3 | Asset Inspections | Inspections completed in 2022 | N/A
Pre-Discovery 25 | CalPA | Set WMP-05 | CalPA_Set WMP-05 | 4 | CalPA_Set WMP-05_Q4 | Please augment Table 13 of the non-spatial data tables in your WMP Quarterly Data Report for Q4 of 2022, which reports asset-related corrective notifications on electric circuits that were open at the end of the quarter, as follows. a. Add the following information in separate columns: i. Name of the associated circuit ii. ID number of the associated circuit iii. Geographic latitude in decimal degrees, truncated to seven decimal places iv. Geographic longitude in decimal degrees, truncated to seven decimal places v. Priority of the original notification, using PG&E’s internal priority level codes vi. Object/damage code or other internal description of defect b. Please complete column b (“Equipment type”) of Table 13. c. Please complete or explain why each of the below columns is not applicable: i. Column i ii. Column j iii. Column k iv. Column l | a-b. Please see attachments “WMP-Discovery2023_DR_CalAdvocates_005-Q004Atch01.xlsb” for the requested Distribution information and “WMPDiscovery2023_DR_CalAdvocates_005-Q004Atch02.xlsx” for the requested Transmission information. c. Please note that columns i, j, k, and l will not be available for Distribution and Transmission circuits until the 2023 Q1 Quarterly Data Report (QDR) because the data is not ready, and due to recent changes to the standard that resulted in a substantial reassessment of our notification data. | Holly Wehrman | 2023-02-10 | 2023-03-10 | 2023-03-10 | https://www.pge.com/pge_global/common/pdfs/safety/emergency-preparedness/natural-disaster/wildfires/wildfire-mitigation-plan/reference-docs/2023/CalAdvocates_005.zip | 2 | N/A | QDR | N/A | N/A | N/A
Pre-Discovery 26 | CalPA | Set WMP-06 | CalPA_Set WMP-06 | 1 | CalPA_Set WMP-06_Q1 | Provide your workplan that describes where you will undertake EVM projects in 2023. This workplan should be in an Excel format, with circuit-segments as rows. Please include the following information in separate columns in the Excel spreadsheet at a minimum: a) Circuit name b) Circuit ID number c) Circuit-segment name d) Circuit-segment ID number e) EVM miles to be completed in 2023 f) Risk ranking(s) for the circuit segment. | The EVM program concluded at the end of 2022. There is no EVM workplan for 2023 | Holly Wehrman | 2023-02-10 | 2023-03-29 | 2023-03-29 | https://www.pge.com/pge_global/common/pdfs/safety/emergency-preparedness/natural-disaster/wildfires/wildfire-mitigation-plan/reference-docs/2023/CalAdvocates_006.zip | 0 | N/A | 8.2.3 | Vegetation Management | EVM | N/A
Pre-Discovery 27 | CalPA | Set WMP-06 | CalPA_Set WMP-06 | 2 | CalPA_Set WMP-06_Q2 | Provide your workplan that describes where you will undertake EVM projects in 2024. This workplan should be in an Excel format, with circuit-segments as rows. Please include the following information in separate columns in the Excel spreadsheet at a minimum: a) Circuit name b) Circuit ID number c) Circuit-segment name d) Circuit-segment ID number e) EVM miles to be completed in 2024 f) Risk ranking(s) for the circuit segment. | The EVM program concluded at the end of 2022. There is no EVM workplan for 2024. | Holly Wehrman | 2023-02-10 | 2023-03-29 | 2023-03-29 | https://www.pge.com/pge_global/common/pdfs/safety/emergency-preparedness/natural-disaster/wildfires/wildfire-mitigation-plan/reference-docs/2023/CalAdvocates_006.zip | 0 | N/A | 8.2.3 | Vegetation Management | EVM | N/A
Pre-Discovery 28 | CalPA | Set WMP-06 | CalPA_Set WMP-06 | 3 | CalPA_Set WMP-06_Q3 | In response to Data Request CalAdvocates-PGE-2022WMP-11, Question 2, March 3, 2022, PG&E provided its 2022 EVM workplan. Please provide an updated version of this workplan that lists the actual EVM mileage performed in each circuit-segment in 2022 as a new column. Rows should be added as needed to cover all circuit-segments where you performed EVM work in 2022 (even if those circuit-segments were not included in the original workplan). | Please see “WMP-Discovery2023_DR_CalAdvocates_006-Q003Atch01.xlsx” for actual 2022 EVM mileage data broken down by circuit segment. Column G on tab ‘2022 EVM Miles Planned’ contains the number of miles planned for EVM work in 2022. Column G on tab ‘2022 EVM Miles Completed’ contains the number of miles that were completed and work verified in 2022. | Holly Wehrman | 2023-02-10 | 2023-03-29 | 2023-03-29 | https://www.pge.com/pge_global/common/pdfs/safety/emergency-preparedness/natural-disaster/wildfires/wildfire-mitigation-plan/reference-docs/2023/CalAdvocates_006.zip | 1 | N/A | 2022 WMP 7.3.5.2 | Vegetation Management and Inspections | Enhanced Vegetation Management | N/A
Pre-Discovery 29 | CalPA | Set WMP-06 | CalPA_Set WMP-06 | 4 | CalPA_Set WMP-06_Q4 | In response to Data Request CalAdvocates-PGE-2022WMP-16, Question 11, March 23, 2022, PG&E stated the following: “Through 2022, the EVM program includes strike trees evaluation and hazard trees mitigation, overhang clearing and radial clearance. Starting in 2023, Enhanced VM only includes overhang clearing.” a) Is the statement above still accurate as of the date of this request? b) If the answer to part (a) is no, please update the above statement to reflect PG&E’s vegetation management strategy for 2023. c) If the answer to part (a) is no, please update the above statement to reflect PG&E’s vegetation management strategy for 2024. | a) To maximize reduction of wildfire risk effectively and efficiently, the Enhanced Vegetation Management (EVM) program concluded at the end of 2022. b) Three new VM programs will be incorporated into the 2023 workplan. These programs for VM are Focused Tree Inspections, VM for Operational Mitigations, and Tree Removal Inventory. • Focused Tree Inspections: We developed specific areas of focus (referred to as Areas of Concern (AOC)), primarily in the HFRA, where we will concentrate our efforts to inspect and address high-risk locations, such as those that have experienced higher volumes of vegetation damage during PSPS events, outages, and/or ignitions. • VM for Operational Mitigations: This program is intended to help reduce outages and potential ignitions using a risk informed, targeted plan to mitigate potential vegetation contacts based on historic vegetation caused outages on EPSSenabled circuits. We will initially focus on mitigating potential vegetation contacts in circuit protection zones that have experienced vegetation caused outages. Scope of work will be developed by using EPSS and historical outage data and vegetation failure from the WDRM v3 risk model. EPSS-enabled devices vegetation outages extent of condition inspections may generate additional tree work. • Tree Removal Inventory: This is a long-term program intended to systematically work down trees that were previously identified through EVM inspections. We will develop annual risk-ranked work plans and mitigate the highest risk-ranked areas first and will continue monitor the condition of these trees through our established inspection programs. c) The three programs identified above will continue in 2024. These combined three programs are also referred to as EVM Transitional programs. | Holly Wehrman | 2023-02-10 | 2023-03-29 | 2023-03-29 | https://www.pge.com/pge_global/common/pdfs/safety/emergency-preparedness/natural-disaster/wildfires/wildfire-mitigation-plan/reference-docs/2023/CalAdvocates_006.zip | 0 | N/A | 2022 WMP 7.3.5 | Vegetation Management and Inspections | Program Costs | N/A
Pre-Discovery 30 | CalPA | Set WMP-06 | CalPA_Set WMP-06 | 5 | CalPA_Set WMP-06_Q5 | In response to Data Request CalAdvocates-PGE-2022WMP-15, Question 16, March 18, 2022, PG&E provided the following table, which shows spending on vegetation management programs in thousands of dollars (actual figures for 2019-2021 and forecast figures for 2022-2023): Please update this table as follows: a) Update the 2022 column to state actual spending in 2022. b) Update the 2023 column to show PG&E’s current forecasts for 2023. c) Add a column that shows PG&E’s current forecasts for 2024. d) Please add rows as necessary, if any changes in PG&E’s vegetation management strategy have created new initiatives or categories of spending. | Please see updated table below with 2022 Actuals, and our current forecasts for 2023 and 2024. | Holly Wehrman | 2023-02-10 | 2023-03-29 | 2023-03-29 | https://www.pge.com/pge_global/common/pdfs/safety/emergency-preparedness/natural-disaster/wildfires/wildfire-mitigation-plan/reference-docs/2023/CalAdvocates_006.zip | 0 | N/A | Vegetation Management | N/A | N/A | N/A
Pre-Discovery 31 | CalPA | Set WMP-06 | CalPA_Set WMP-06 | 6 | CalPA_Set WMP-06_Q6 | Please provide a list of any incidents in 2022 where the actions of a VM contractor posed a safety risk to workers and/or the public. “Safety risk” here is defined as any occurrence on a worksite where the contractor's actions created a safety hazard for either workers or the general public. For each instance, please provide: a) The date you were informed of the safety issue b) The date that the original work that created the safety issue was performed c) Whether the safety issue concerned a transmission or distribution circuit d) The vegetation management initiative involved in the original work e) A brief description of the safety issue involved. | Please refer to Attachment “WMP-Discovery2023_DR_CalAdvocates_006-Q006Atch01CONF.xlsx” for a list of all contractors involved safety incidents that took place in 2022. This data includes, but is not limited to: • Contractor Name/ParentCo: The contractor/parent company involved in the incident. • IncDate: The date of the incident. • Date EN: The date the incident was formally reported and logged. • Division: The division where the incident took place. • Inc Types: The incident type (ie line strike) • Incident Description: A brief description of the incident. • Program: Description on which initiative a contractor was working on, on the date of incident. • Corrective Action: A description of the action(s) PG&E took to prevent recurrence. Please note, both Distribution and Transmission contractor incidents are included in the attachment. These records are pulled from the Enterprise Contractor Incident Records Tool (ECIRT) database. The ECIRT database incident recording process does not have a space for inputting Distribution or Transmission circuit information, therefore we are unable to provide that information on the spreadsheet because our system does not track the incidents that way. | Holly Wehrman | 2023-02-10 | 2023-03-29 | 2023-03-29 | https://www.pge.com/pge_global/common/pdfs/safety/emergency-preparedness/natural-disaster/wildfires/wildfire-mitigation-plan/reference-docs/2023/CalAdvocates_006.zip | 1 | N/A | Vegetation Management | N/A | N/A | N/A
Pre-Discovery 32 | CalPA | Set WMP-06 | CalPA_Set WMP-06 | 7 | CalPA_Set WMP-06_Q7 | In response to Data Request CalAdvocates-PGE-2022WMP-14, Question 13, March 15, 2022, PG&E provided its 2022 system hardening workplan for the categories referred to in parts (a)-(d) below. Please provide an updated version of this workplan with additional columns to show the actual system hardening work performed in each circuit-segment in 2022 for each of these categories. Please add rows as needed to cover all circuit-segments where PG&E performed system hardening work in 2022 (even if those circuit-segments were not included in the original workplan). a) Installation of covered conductor b) Installation of underground conductor c) Removal of overhead conductor d) Removal of overhead conductor associated with remote grid work. | Note, for CalAdvocates-PGE-2022WMP-14, Question 13, the projects listed in the 2022 columns were only for projects that overlapped with 2021 completed miles. It did not represent a comprehensive list of 2022 projects. Similarly, the 2020 columns were only for projects that overlapped with 2021 completed miles. It did not represent a comprehensive list of 2020 projects. See “WMP-Discovery2023_DR_CalAdvocates_006-Q007Atch01CONF.xlsx.” This file includes the 2022 system hardening completed work in the below columns: a. Installation of covered conductor: See column O b. Installation of underground conductor: See column P c. Removal of overhead conductor: See column Q. Note, this removal work is not associated with the lines removed from overhead for installation of underground projects. It is strictly overhead conductor completely de-energized and removed. d. Removal of overhead conductor associated with remote grid work: N/A. There are no removals from remote grid work in 2022. Since the installation of remote grid generating units work occurred late in 2022, the associated line removal of de-energized conductor will take place in 2023. Similar to the response to CalAdvocates-PGE-2022WMP-14, Question 13, the data includes project information from 2021 and 2023 only where projects overlap with those years. Thus, the 2021 and 2023 data is not comprehensive. Additionally, because this question is associated with the System Hardening workplan only, this data does not include undergrounding mileage associated with the Butte Rebuild. | Holly Wehrman | 2023-02-10 | 2023-03-29 | 2023-03-29 | https://www.pge.com/pge_global/common/pdfs/safety/emergency-preparedness/natural-disaster/wildfires/wildfire-mitigation-plan/reference-docs/2023/CalAdvocates_006.zip | 1 | N/A | 2022 WMP Section 7.3.3.17 | Grid Design and System Hardening | System Hardening | N/A
Pre-Discovery 33 | CalPA | Set WMP-06 | CalPA_Set WMP-06 | 8 | CalPA_Set WMP-06_Q8 | Provide your workplan that describes where and when you will perform system hardening on distribution circuits in 2023. For projects that you expect to partially complete in 2023 (i.e., projects that started before 2023 and are expected to continue in 2023, or projects that are expected to be completed after 2023), please include the project and report the work that you forecast will actually be performed in calendar year 2023. For each project, include the following information in separate columns, at a minimum: a) Order number b) MAT code c) Program d) Circuit ID number e) Circuit-segment name or ID number (if the project affects more than one circuit-segment, please identify each one) f) Relevant wildfire risk score(s) from the wildfire risk model that you are using to estimate distribution risk in your 2023-2025 WMP filing g) The expected or actual start date of the project. h) The expected completion date of the project. i) Length (in circuit miles) of covered conductor to be installed in 2023. j) Length (in circuit miles) of underground conductor to be installed in 2023. k) Length (in circuit miles) of overhead conductor to be permanently removed in 2023 and replaced by underground conductor (note that this may differ slightly from the previous section due to differing overhead and underground routes). l) Length (in circuit miles) of overhead conductor to be permanently removed in 2023 and not replaced with covered conductor or undergrounded) m) Length (in circuit miles) of any other type of system hardening project to be installed in 2023 (if this is greater than zero, please describe the type of system hardening project). | Please see attachment “WMP-Discovery2023_DR_CalAdvocates_006-Q008Atch01CONF.xlsx.” a. See columns A (order number), and B (order description) b. See column C c. See column D d. See columns E e. See column F f. See columns G, I and K Column G shows the Applicable Risk Model that was used for selecting the project and putting it into scope. Risk Rank scores, shown in Columns I and K, are based on the Wildfire Distribution Risk Model (WDRM) for Version 2 and Version 3, respectively. The Risk ranking outcomes are the results of the relevant risk model (e.g., WDRM v2, WDRM v3) where circuit segments are ranked on a 1 to N basis, where 1 is the highest risk circuit segment, and N is the lowest risk. g. See column L h. See column M i. See column Z j. See column AA k. N/A – PG&E does not track length (in circuit miles) of overhead conductor to be permanently removed and replaced by underground. l. See column AB m. N/A The data includes project information from prior to 2022 and 2022 where projects overlap with these years. Data is provided in the same file for 2024 that is responsive to Question Q009. Additionally, because this question is associated with the System Hardening workplan only, this data does not include undergrounding mileage associated with the Butte Rebuild. | Holly Wehrman | 2023-02-10 | 2023-03-29 | 2023-03-29 | https://www.pge.com/pge_global/common/pdfs/safety/emergency-preparedness/natural-disaster/wildfires/wildfire-mitigation-plan/reference-docs/2023/CalAdvocates_006.zip | 1 | N/A | 8.1.2.5 | System Hardening | N/A | N/A
Pre-Discovery 34 | CalPA | Set WMP-06 | CalPA_Set WMP-06 | 9 | CalPA_Set WMP-06_Q9 | Provide your workplan that describes where and when you will perform system hardening on distribution circuits in 2024. For projects that you expect to partially complete in 2024 (i.e., projects that are expected to start before 2024 and are expected to continue in 2024, or projects that are expected to be completed after 2024), please include the project and report the work that you forecast will actually be performed in calendar year 2024. For each project, include the following information in separate columns, at a minimum: a) Order number b) MAT code c) Program d) Circuit ID number e) Circuit-segment name or ID number (if the project affects more than one circuit-segment, please identify each one) f) Relevant wildfire risk score(s) from the wildfire risk model that you are using to estimate distribution risk in your 2023-2025 WMP filing g) The expected or actual start date of the project. h) The expected completion date of the project. i) Length (in circuit miles) of covered conductor to be installed in 2024. j) Length (in circuit miles) of underground conductor to be installed in 2024. k) Length (in circuit miles) of overhead conductor to be permanently removed in 2024 and replaced by underground conductor (note that this may differ slightly from the previous section due to differing overhead and underground routes). l) Length (in circuit miles) of overhead conductor to be permanently removed in 2024 and not replaced with covered conductor or undergrounded) m) Length (in circuit miles) of any other type of system hardening project to be installed in 2024 (if this is greater than zero, please describe the type of system hardening project). | Please see “WMP-Discovery2023_DR_CalAdvocates_006-Q008Atch01CONF.xlsx.” a. See columns A (order number), and B (order description) b. See column C c. See column D d. See columns E e. See column F f. See columns G, I and K Column G shows the Applicable Risk Model that was used for selecting the project and putting it into scope. Risk Rank scores, shown in Columns I and K, are based on the Wildfire Distribution Risk Model (WDRM) for Version 2 and Version 3, respectively. The Risk ranking outcomes are the results of the relevant risk model (e.g., WDRM v2, WDRM v3) where circuit segments are ranked on a 1 to N basis, where 1 is the highest risk circuit segment, and N is the lowest risk. g. See column L h. See column M i. See column AD j. See column AE k. N/A – PG&E does not track length (in circuit miles) of overhead conductor to be permanently removed and replaced by underground. l. See column AF m. N/A The data includes project information from prior to 2022, 2022, and 2023 where projects overlap with these years. Data is provided in the same file for 2023 that is responsive to Question Q008. Additionally, because this question is associated with the System Hardening workplan only, this data does not include undergrounding mileage associated with the Butte Rebuild. | Holly Wehrman | 2023-02-10 | 2023-03-29 | 2023-03-29 | https://www.pge.com/pge_global/common/pdfs/safety/emergency-preparedness/natural-disaster/wildfires/wildfire-mitigation-plan/reference-docs/2023/CalAdvocates_006.zip | 0 | N/A | 8.1.2.5 | System Hardening | N/A | N/A
Pre-Discovery 35 | CalPA | Set WMP-06 | CalPA_Set WMP-06 | 10 | CalPA_Set WMP-06_Q10 | For each of your 2023-2025 WMP system hardening initiatives, please provide disaggregated information related to expenditures and circuit miles treated in the attached table, CalAdvocatesPGE-2023WMP-06 Attachment 1. Add columns as needed. | Please see details on the cost and mileage breakouts in attached file “WMPDiscovery2023_DR_CalAdvocates_006-Q010Atch01.xlsx. | Holly Wehrman | 2023-02-10 | 2023-03-29 | 2023-03-29 | https://www.pge.com/pge_global/common/pdfs/safety/emergency-preparedness/natural-disaster/wildfires/wildfire-mitigation-plan/reference-docs/2023/CalAdvocates_006.zip | 1 | N/A | 4.3 | Proposed Expenditures | System Hardening | N/A
Pre-Discovery 36 | CalPA | Set WMP-06 | CalPA_Set WMP-06 | 11 | CalPA_Set WMP-06_Q11 | Please provide a spreadsheet listing (as rows) each undergrounding project completed during the period of January 1, 2022, through December 31, 2022. For each project, please provide the following information (as columns): a) Project ID number or other identifier b) Circuit ID c) ID of each circuit segment that was entirely undergrounded in the project d) ID of each circuit segment that was partially undergrounded in the project e) County or counties where undergrounding took place f) Project start date g) Project completion date h) Total circuit-miles undergrounded i) Total miles of trenching required j) Total life-cycle electric costs5 of the project (i.e., costs attributed to your electric facilities), including costs for planning, design, permitting, and construction k) Total life-cycle costs of the project, including costs attributed to non-electric utilities, including costs for planning, design, permitting, and construction l) Whether this was a Rule 20 project6 (yes/no) m) Whether this was a WMP project (yes/no) n) Whether this was a post-wildfire rebuild project (yes/no) o) Whether you shared trenches for this project with any telecommunications utilities (yes/no) p) Whether you shared trenches for this project with gas facilities (yes/no). | See “WMP-Discovery2023_DR_CalAdvocates_006-Q011Atch01CONF.xlsx.” a) Project ID number or other identifier – See columns A (order Number) and B (Order Description) b) Circuit ID – See column C c) ID of each circuit segment that was entirely undergrounded in the project – Our undergrounding projects are split into multiple phases within a given circuit protection zone (CPZ) shown in Column E. The undergrounding of complete CPZs is a multi-year effort that cannot be captured in the data shown for a single year. d) ID of each circuit segment that was partially undergrounded in the project – Per response to (c), our undergrounding projects are split into multiple phases within a given circuit protection zone (CPZ). By reviewing data solely from a single year, it is not possible to determine completion of an entire CPZ. e) County or counties where undergrounding took place – See column I f) Project start date – see column J g) Project completion date – See column K h) Total circuit-miles undergrounded – Column U i) Total miles of trenching required – This information is not tracked by PG&E. j) Total life-cycle electric costs4 of the project (i.e., costs attributed to your electric facilities), including costs for planning, design, permitting, and construction – See column X k) Total life-cycle costs of the project, including costs attributed to non-electric utilities, including costs for planning, design, permitting, and construction. – There is no nonelectric utility work in the scope of system hardening undergrounding l) Whether this was a Rule 20 project5 (yes/no) – See column F m) Whether this was a WMP project (yes/no) – See column G n) Whether this was a post-wildfire rebuild project (yes/no) – See column H o) PG&E did not share trenches for any projects identified in “WMPDiscovery2023_DR_CalAdvocates_006-Q011Atch01CONF.xlsx p) Whether you shared trenches for this project with gas facilities (yes/no) – No. For system hardening, we do not share trenches with gas. The data includes project information from 2021 where projects overlap with 2022. Because this question is associated with the System Hardening workplan only, this data does not include undergrounding mileage associated with the Butte Rebuild. 3 Constructed in accordance with The CPUC’s Electric Tariff Rule 20. 4 For the purposes of this question and the following question, “life-cycle costs” refers to the start-to-finish costs to complete the capital project, from planning to the end of construction. This does not include maintenance or operational costs after the underground infrastructure is complete and in use. 5 Constructed in accordance with The CPUC’s Electric Tariff Rule 20 | Holly Wehrman | 2023-02-10 | 2023-03-29 | 2023-03-29 | https://www.pge.com/pge_global/common/pdfs/safety/emergency-preparedness/natural-disaster/wildfires/wildfire-mitigation-plan/reference-docs/2023/CalAdvocates_006.zip | 1 | N/A | 8.1.2.2 | Grid Design and System Hardening | Undergrounding of Electric Lines and/or Equipment – Distribution | N/A
Pre-Discovery 37 | CalPA | Set WMP-06 | CalPA_Set WMP-06 | 12 | CalPA_Set WMP-06_Q12 | Please provide a geodatabase file with a polyline feature for each undergrounding project completed during the period of January 1, 2022 through December 31, 2022. In addition to the spatial location, please provide the following attributes for each project: a) Project ID number or other identifier, matching part (a) of the previous question b) Circuit ID c) Project completion date. | See attachment “WMP-Discovery2023_DR_CalAdvocates_006-Q012Atch01CONF.zip.” Please note that the data reflected in this GIS geospatial file will not match the data set from Q11 due to the process time lag between construction completion and being fully mapped in GIS. | Holly Wehrman | 2023-02-10 | 2023-03-29 | 2023-03-29 | https://www.pge.com/pge_global/common/pdfs/safety/emergency-preparedness/natural-disaster/wildfires/wildfire-mitigation-plan/reference-docs/2023/CalAdvocates_006.zip | 1 | N/A | 8.1.2.2 | Grid Design and System Hardening | Undergrounding of Electric Lines and/or Equipment – Distribution | N/A
Pre-Discovery 38 | CalPA | Set WMP-06 | CalPA_Set WMP-06 | 13 | CalPA_Set WMP-06_Q13 | Identify any ignitions in 2022 associated with assets where you had an existing corrective notification at the time of the ignition. Please provide a spreadsheet listing each such ignition (as rows) with the following information in separate columns: a) Unique ignition ID b) Date of ignition c) Cause of ignition d) Type of asset associated with the ignition e) Acres burned f) Number of structures burned, if any g) Number of injuries associated with ignition, if any h) Asset ID of asset associated with ignition i) Circuit ID number of circuit associated with ignition j) Notification number(s) for the existing maintenance tag on the asset in question. | Please see the table below identifying 2022 CPUC reportable ignitions where the asset involved in the ignition was associated with an existing open corrective maintenance notification at the time of the event. Ignition ID Date of Ignition Suspected Cause Equipment Type Associated With Ignition Fire Size Structures Destroyed Injuries Asset ID Circuit ID Existing Maintenance Notifications 20220374 4/6/2022 Equipment Failure Conductor - Primary 0.26- 9.99 Acres 0 0 101894229 MESA 1103 121931783 20220613 5/17/2022 Equipment Failure Splice/ Clamp/ Connector 1 meter - <3 meters 0 0 102242348 SAN RAFAEL 1104 119372723 20220740 6/2/2022 Equipment Failure Service Drop 1 meter - <3 meters 0 0 103319095 MC CALL 1101 123226356 20221200 7/19/2022 Equipment Failure Conductor - Primary <1 Acre 0 0 101710681 WATSONVILLE 2101 123651178 20221314 8/3/2022 Equipment Failure Splice/Clamp /Connector 1 Acre 0 0 101850483 FOOTHILL 2101 123700083 20221278 7/28/2022 Equipment Failure Pole <0.25 Acre 0 0 101137014 MADERA 1118 118429275 20222013 11/16/2022 Equipment Failure Crossarm <0.25 Acre 0 0 101424195 FAIRVIEW 2207 123866774 | Holly Wehrman | 2023-02-10 | 2023-03-29 | 2023-03-29 | https://www.pge.com/pge_global/common/pdfs/safety/emergency-preparedness/natural-disaster/wildfires/wildfire-mitigation-plan/reference-docs/2023/CalAdvocates_006.zip | 0 | N/A | 2022 WMP Section 7.3.4 | Asset Management and Inspections | N/A | N/A
Pre-Discovery 39 | CalPA | Set WMP-06 | CalPA_Set WMP-06 | 14 | CalPA_Set WMP-06_Q14 | a) Has PG&E’s Asset Failure Analysis Team causally connected any ignitions that occurred in 2022 to assets with existing asset or vegetation corrective notifications at the time of ignition? b) If the answer to part (a) is yes, please provide the following information on each such ignition: i. Unique ignition ID (matching the previous question) ii. Date of ignition iii. Cause(s) identified by the Asset Failure Analysis Team iv. The type of corrective notification that was linked to the ignition (i.e., the priority level and whether it related to asset management or vegetation management). v. Copies of associated reports or investigations performed by the Asset Failure Analysis Team. | a) Yes, please see below. b) Two ignitions have been identified that meet these criteria: Ignition ID Date of Ignition Cause Type of Corrective Notification Copies of Associated Reports 20221278 7/28/2022 The cause of this ignition is still being finalized. EC Notification 118429275 – Pole Replacement The report in question is still being finalized and can be provided upon completion. 20222013 11/16/2022 Broken crossarm EC Notification 123866774 – Crossarm replacement (later updated to pole replacement) The report in question is still being finalized and can be provided upon completion. | Holly Wehrman | 2023-02-10 | 2023-03-29 | 2023-03-29 | https://www.pge.com/pge_global/common/pdfs/safety/emergency-preparedness/natural-disaster/wildfires/wildfire-mitigation-plan/reference-docs/2023/CalAdvocates_006.zip | 0 | N/A | 2022 WMP 7.3.7 | Data Governance | Asset Failure Analysis | N/A
Pre-Discovery 40 | CalPA | Set WMP-06 | CalPA_Set WMP-06 | 15 | CalPA_Set WMP-06_Q15 | Per PG&E’s response to Data Request CalAdvocates-PGE-2022WMP-17, Question 13, March 24, 2022, PG&E’s inspection strategy in 2022 was to complete detailed inspections on all assets in HFTD Tier 3 and Zone 1, and approximately one-third of assets in HFTD Tier 2. a) Please describe any changes to the above strategy for PG&E’s detailed distribution inspections in 2023. b) Please describe any changes to the above strategy for PG&E’s detailed transmission inspections in 2023. c) Please describe any changes to the above strategy for PG&E’s detailed distribution inspections in 2024. d) Please describe any changes to the above strategy for PG&E’s detailed transmission inspections in 2024. | a) Beginning in 2023, PG&E’s detailed inspections of distribution structures in high fire areas will be informed by wildfire consequence as provided PG&E’s Wildfire Distribution Risk Model v3. PG&E will complete a detailed inspection on each structure every one to three years. For additional details on this strategy, please refer to Section 8.1.3.2 of our 2023 WMP. This differs from our 2022 strategy where we inspected all of Tier 3 and one-third of Tier 2. b) There are no major changes in our strategy compared to last year. Transmission detailed inspections in 2023 are informed by predictive models of asset health and wildfire consequence. HFTD (Tier 3, Tier 2, and Zone 1) and HFRA structures have a baseline inspection frequency of once every three years. In addition to this baseline frequency, structures may be added to the detailed inspection scope annually based on the following considerations: • Wildfire Risk, which is informed by the asset health Transmission Composite Model V1 (TCM) annualized probability of failure and the Wildfire Consequence Model V3.4. • Other factors involving data not currently integrated into the Wildfire Transmission Risk Model V1 (ex: inspection result trends, historic fire locations etc.) For additional details on this strategy, please refer to Section 8.1.3.1 of our 2023 WMP. c) No major changes are anticipated to the detailed distribution ground inspections strategy in 2024. However, as PG&E’s risk models and understanding of the distribution system continues to mature, we may adjust the strategy described above or establish additional criteria to define the structures for inspection each year. d) There is no major anticipated change to detailed inspection scoping strategy in 2024. However, the considerations or thresholds used to define the additional structures may vary each year as the risk models mature and the overall risk of the transmission system evolves. | Holly Wehrman | 2023-02-10 | 2023-03-29 | 2023-03-29 | https://www.pge.com/pge_global/common/pdfs/safety/emergency-preparedness/natural-disaster/wildfires/wildfire-mitigation-plan/reference-docs/2023/CalAdvocates_006.zip | 0 | N/A | 2022 WMP 7.3.4.1 and 7.3.4.14 | Asset Management and Inspections | N/A | N/A
Pre-Discovery 41 | CalPA | Set WMP-06 | CalPA_Set WMP-06 | 16 | CalPA_Set WMP-06_Q16 | Regarding your PSPS circuit modeling capabilities: a) Please describe your present circuit modeling capabilities with regard to PSPS decisionmaking (“PSPS circuit modeling capabilities”), including with what level of granularity they are able to determine how circuit hardening efforts or other changes to a line segment will affect PSPS thresholds. b) Please describe any improvements to the present PSPS circuit modeling capabilities that you expect to implement in 2023. c) Please describe any improvements to the present PSPS circuit modeling capabilities that you expect to implement in 2024. d) Please describe the expected state of your PSPS circuit modeling capabilities at the conclusion of the 2023-2025 WMP cycle. | a) For all questions below, PG&E understands circuit modeling to mean the level of granularity at which a utility can model the configuration of its electrical assets and de-energize them as such. PG&E models and de-energizes circuits utilizing all switching devices on the system that do not pose ignition risks. The effects of hardening and other changes to lines will be accounted for by our IPW model which uses machine learning to quantify past outages and ignitions and uses those as a basis for ignition and outage potential going forward which feeds into our PSPS modeling. Thus, any improvements to the system or changes would be incorporated as their historical performance changes. b) As mentioned, PG&E models circuits at the most granular level for de-energization taking into account all devices on the system that do not pose an ignition risk. c) As mentioned, PG&E models circuits at the most granular level for de-energization taking into account all devices on the system that do not pose an ignition risk. d) As mentioned, PG&E models circuits at the most granular level for de-energization taking into account all devices on the system that do not pose an ignition risk | Holly Wehrman | 2023-02-10 | 2023-03-29 | 2023-03-29 | https://www.pge.com/pge_global/common/pdfs/safety/emergency-preparedness/natural-disaster/wildfires/wildfire-mitigation-plan/reference-docs/2023/CalAdvocates_006.zip | 0 | N/A | PSPS | N/A | N/A | N/A
Pre-Discovery 42 | CalPA | Set WMP-06 | CalPA_Set WMP-06 | 17 | CalPA_Set WMP-06_Q17 | a) Have you developed Public Safety Power Shutoff (PSPS) risk scores at the circuit-segment level? b) Have you developed Enhanced Powerline Safety Settings (EPSS) risk scores at the circuitsegment level? c) If the answer to either parts (a) or (b) is yes, please provide a geodatabase file containing, as line features, the most recent spatial data for all circuit segments for which you have modeled PSPS or EPSS risk scores. Include the following attributes for each circuit segment: i. Circuit Identification Number ii. Circuit Name iii. Circuit Segment Identification Number iv. Circuit segment-level PSPS Risk Score (if applicable) v. Circuit segment-level EPSS Risk Score (if applicable). d) If the answer to either parts (a) or (b) is yes, please provide a spreadsheet that lists (as rows) each circuit-segment for which you have modeled PSPS or EPSS risk scores. Include the following attributes for each circuit segment: i. Circuit Identification Number ii. Circuit Name iii. Circuit Segment Identification Number iv. Circuit segment-level PSPS Risk Score (if applicable) v. Circuit segment-level EPSS Risk Score (if applicable) e) If the answer to part (a) is no, does PG&E intend to develop PSPS risk scores for circuit segments? f) If the answer to part (b) is no, does PG&E intend to develop EPSS risk scores for circuit segments? | a) Yes. This is cited in Section 6.2.1, figure 6.2.1-3. b) No. c) Please see “WMP-Discovery2023_DR_CalAdvocates_006-Q017Atch01CONF.zip” which is a geodatabase file containing the circuit segments along with PSPS risk values and Circuit Segment names. Due to the different circuit segment vintages approximately 400 of the circuit segments are not mapped. d) Yes, please see “WMP-Discovery2023_DR_CalAdvocates_006-Q017Atch02CONF.xlsx” which provides the circuit segment PSPS risk values. e) Not applicable. f) PG&E produces an annual reliability study of EPSS outage activity, which informs reliability mitigation actions. Furthermore, PG&E is exploring incorporating this data into an “EPSS reliability risk” score for circuit segments. | Holly Wehrman | 2023-02-10 | 2023-03-29 | 2023-03-29 | https://www.pge.com/pge_global/common/pdfs/safety/emergency-preparedness/natural-disaster/wildfires/wildfire-mitigation-plan/reference-docs/2023/CalAdvocates_006.zip | 2 | N/A | PSPS/EPSS | N/A | N/A | N/A
Pre-Discovery 43 | CPUC - SPD (Safety Policy Division) | 001 | CPUC - SPD (Safety Policy Division)_001 | 1 | CPUC - SPD (Safety Policy Division)_001_Q1 | REFCL Inquiries: • REFCL Pilot at Calistoga Circuit Segment ID 1102131531 o Describe various active settings profiles. o Describe how staged fault testing is planned to be conducted. o Explain how REFCL rides through momentary faults & when REFCL deenergizes line for permanent faults. • Substation Configuration – Describe any substation and/or circuit configuration issues to deploy REFCL • Availability of REFCL – Describe any known barriers to increasing deployment in CA • Explain which risk drivers per Table PG&E-7.1.4-1 REFCL mitigates. • Explain why REFCL is not preferred mitigation for broader deployment and confirm PG&E no longer plans to install REFCL at 2 substations per year per GRC filing. | a. i. The REFCL equipment installed in the substation protects all the primary lines on both Calistoga circuits. Three settings profiles allow for changing fault sensitivity and tripping behavior on the fly based on field conditions/risk. Setting 1 is for low risk with a three second delay before switching the neutral to solid grounding for line protection to clear the fault. Setting 2 is for medium risk with a three second fault ride through before directly tripping the faulted feeder circuit breaker for a sustained fault. Setting 3 is for high risk with no time delay and greatest fault sensitivity and tripping the faulted feeder circuit breaker. ii. Staged fault testing was performed in 2022 with preliminary data collected. A mobile high voltage resistor bank is momentarily connected to stage a fault on the circuit. Normally the system rides through the neutral shift with no service outage from the test. Due to greater line to ground voltages during the testing, the possibility of unplanned outage of line equipment failing is slightly increased. iii. All service transformers on REFCL circuits are connected line to line, so service voltage is maintained during the ground fault. If setting 1 or 2 is active, once a ground fault is detected, a three second time delay elapses before the fault confirmation is performed. If the fault confirmation determines that the fault vanished (momentary fault), then the neutral voltage is returned to normal with no service interruption. If the fault confirmation determines that it is a sustained fault, then the tripping is handled based on the active setting group described in 1ai. b. Due to equipment failures in the substation and on the line in the REFCL demonstration project, PG&E is still evaluating the technology and gaining operational experience with it. In order to deploy REFCL, the primary considerations for deployment are: • Substation voltage regulators: Replace wye-ground connected regulators with line-line connected regulators • Substation feeder breakers: High accuracy current transformers retrofitted • Substation secondary neutral: clearance of substation transformer bank and installation of grounding switch and cable connections to arc suppression coil • Substation physical space: Enough room within the substation for an 16 ft x 28 ft footprint per Ground Fault Neutralizer (GFN). Some substations may require 2 GFNs right away for deploying REFCL • Distribution circuits: 3-wire uni-grounded neutral only • Distribution circuits: Maximum of approximately 50 circuit miles of underground cable per transformer bank • Distribution circuits: Primary connected customers – requires large isolation transformer depending on complexity of customer-owned equipment • Distribution circuits: Long single phase underground cable causes increased neutral current and requires capacitive balancing units (CBUs) c. Each distribution circuit in California is unique. REFCL deployment needs to be evaluated on a circuit-by-circuit basis. Present lead time for certain types of substation equipment to support REFCL deployment exceeds 60 weeks. d. REFCL mitigates the following risk drivers from the table: • Vegetation contact, Equipment/Facility failure • Contact from object • Unknown • Other • Vandalism/Theft • Contamination • CC – seismic scenario e. Staged fault testing is planned in first half of 2023 and if testing is successful the REFCL technology will be put into normal operation to gain experience and quantify the benefits of the technology on PG&E’s distribution system. Potential REFCL deployments will be explored after evaluation of the demonstration site. No additional REFCL deployments are planned under the GRC filing at this time. | Wendy Al-Mukdad | 2023-02-23 | 2023-03-09 | 2023-03-09 | https://www.pge.com/pge_global/common/pdfs/safety/emergency-preparedness/natural-disaster/wildfires/wildfire-mitigation-plan/reference-docs/2023/SPD_001.zip | 0 | N/A | 8.1.8.1.3 | Grid Operations and Procedures | Settings of Other Emerging Technologies (e.g., Rapid Earth Fault Current Limiters) | N/A
Pre-Discovery 44 | CPUC - SPD (Safety Policy Division) | 001 | CPUC - SPD (Safety Policy Division)_001 | 2 | CPUC - SPD (Safety Policy Division)_001_Q2 | EPSS & Supporting Technologies (DCD & Partial Voltage Detection) Inquiries: • Explain all activities planned to mitigate EPSS reliability impacts. o Are customer support programs (e.g., battery backup) distinct from or linked to those in place for PSPS implementation? • Explain Sensitive Ground Fault settings for EPSS enabled circuit segments. • Explain Downed Conductor Detection (DCD) technology and how it isolates high impedance faults with EPSS. o Explain DCD 2023-2025 Targets (i.e. 500, 400 & 250 protective device controllers or relays) and whether they will cover all HFTD and buffer EPSS circuits. Explain why says To Be Updated. o Explain how many DCD are currently installed including on top 5% risk circuit segments. • Explain Partial Voltage Detection using SmartMeters and how supplements DCD and EPSS. | a. The following incudes activities on-going and planned to mitigate EPSS reliability impacts: Enhanced Outage Review Team (ORT) process that includes additional review of circuit/Circuit Protection Zone (CPZ) performance that when multiple outages occur triggers a Multiple Outage Review (MORE) to drive additional actions if needed to reduce repeat outages going forward. • Continuing Proactive Vegetation Trimming on the Top 12 circuit segments that were identified last year based on number of outages experienced and a projected enablement of over 50% for the fire season. For 2023 we looked at CEMI (customers experiencing multiple outages) impacted customers and evaluated vegetation outages and identified 9 additional circuit protection zones to be added to this approach. • Continuing Extent of Condition assessment and trimming. When a vegetation related EPSS outage occurs the incident location and 5 spans in all directions is inspected by our vegetation management team to identify trimming opportunities to prevent an outage from occurring near the previous location reducing risk and improving reliability. • EPSS CEMI 8+ Targeted customers: 1. Vegetation clearing for CPZ’s with multiple veg caused outages as covered above 2. Developing an animal mitigation strategy for animal interaction reduction due to high animal-caused outages when EPSS is enabled. • Fault Indicator Installations Proactively installing 1360 Fault Indicators on EPSS Circuits to expedite outage restoration and assist in finding the cause of outages to be addressed to prevent future unknown outages i. In general, customer support programs for EPSS are linked to those in place for PSPS implementation. In most cases, such as with PG&E’s Portable Battery Program (PBP), Disability and Disaster Access and Resource Program (DDAR), and Generator and Battery Rebate Program (GBRP), the programs are the same; PG&E simply expanded eligibility criteria such that programs initially targeting PSPS customer outages now also include the most impacted EPSS customers. One notable exception is the new residential Fixed Power Solutions offering (aka, the Residential Storage Initiative or RSI), which was launched in late 2022. As a new offering, RSI was targeted at EPSS-impacted customers, which happen to overlap with areas historically impacted by PSPS events. b. The Sensitive Ground Fault (SGF) protective element, which was expanded to systemwide use in 2021 and 2022 on 3-wire circuits as a part of EPSS, is a low set non-directional ground overcurrent element typically set at 15A with a 15-20 second delay. Prior to 2021, SGF was in use in limited usage throughout the system. SGF is enabled year-round given the public safety benefit of detecting and isolating wire on ground faults. SGF is only implemented on reclosers and circuit breakers protecting 3-wire or phase-to-phase load connected downstream line sections. c. Down Conductor Detection (DCD) technology is an industry term used to describe different protective relay algorithms that are focused on detection and isolation of high impedance ground faults. The specific algorithm currently in deployment at PG&E is proprietary to the manufacturer and relay being used but at a high-level leverages high sensitivity ground current measurements, current rate of change detection, and harmonic signatures to provide the proper sensitivity and restraint –tripping only when necessary to clear a high impedance fault but not in response to normal fluctuations on the grid - required to detect conditions beyond the capability of traditional protective relay elements. i. DCD 2023-2025 targets are determined and prioritized according to the highest Wildfire Risk Composite Score that covers all High Fire Risk Area (HFRA) and EPSS Buffer Areas as well as capturing the most HFRA miles where existing or upgradable DCD controllers are available. The top 500 highest risk scores are targeted for 2023, followed by 400 next highest risk scores in 2024 and remaining balance in 2025. Targets in 2024-2025 are subject to change or updated due to future potential changes in conditions (e.g., strategy, scope, priority, new information/discoveries/technology). 54 of the targeted 500 DCD installations completed through February 2023, in addition to 410 DCD installations completed in 2022. We’ve completed 5 DCD installations on the top 5% risk circuit segments through February, with 7 additional installations scheduled to be completed in 2023. d. To support the identification and response to very-low initial current (highimpedance) faults, PG&E is utilizing new data-driven capabilities leveraging our SmartMeter network for Partial Voltage (PV) Detection. PV Alerts work for the 3-wire distribution system with Line-to-Line connected transformers. PV Alert indicates low SmartMeter Voltage (25 - 75% of nominal 240V). Network Interface Card (NIC) remains on and able to return pings down to 25% Voltage, while metrology turns off at 75% voltage. New PV alert configuration settings prevent nuisance alerts from transient conditions: i. Partial Voltage Detection Alert (after 45 seconds of persistence + 20 second trap send wait time) ii. Partial Voltage Repeat Alert (repeats every 20 minute) iii. Partial Voltage Clear Alert (after 90 seconds of normal Voltage persistence) Partial voltage alarms are aggregated and brought into the outage management system where they indicate to the system operator the general location of the fault based upon the affected meters and their alarms. During periods of EPSS enablement, operational protocol will then proceed to manually de-energize the affected area using the closest upstream SCADA remote controllable device to mitigate the potential hazard which is then followed up with a field patrol response. The primary purpose of partial voltage detection is to mitigate a certain type of high impedance fault that can occur during a wire down fault event and there exists line to line connected transformers (3-wire) present that can backfeed current from the load side of the fault and create a very high impedance fault path. The amount of fault current supplied from the backfeed condition can be extremely low (< 1A) and at these low levels is not capable of being detected with SGF, DCD, or other traditional protection. This technology adds another layer of defense to detect and respond to high impedance fault conditions in addition to SGF, DCD, and the gang trip operations objectives with EPSS. | Wendy Al-Mukdad | 2023-02-23 | 2023-03-09 | 2023-03-09 | https://www.pge.com/pge_global/common/pdfs/safety/emergency-preparedness/natural-disaster/wildfires/wildfire-mitigation-plan/reference-docs/2023/SPD_001.zip | 0 | N/A | 8.1.8.1.1 | Grid Operations and Procedures | Protective Equipment and Device Settings | N/A
Pre-Discovery 45 | CPUC - SPD (Safety Policy Division) | 001 | CPUC - SPD (Safety Policy Division)_001 | 3 | CPUC - SPD (Safety Policy Division)_001_Q3 | EPSS & REFCL Inquiries: • EPSS vs REFCL – Describe the major similarities and differences. o What are advantages and disadvantages?  In terms of capability, sectionalization, safety, and reliability? • Phase-to-Ground Faults vs Complex (Multiphase) Faults – What is the risk profile of existing ignitions on PG&E’s system and how does REFCL & EPSS mitigate these risks? • Combination of REFCL with EPSS & Other Mitigations – Explain how these could work together, and if PG&E has quantified combined risk-reduction benefits. • Explain the differences in fault energy for EPSS vs REFCL including for low and high impedance faults. o Explain why EPSS is preferred if REFCL fault energy is less than 10% of EPSS fault energy for low impedance faults. o Explain the effectiveness of DCD vs REFCL on high impedance faults | a. In concept, EPSS and REFCL are two very different approaches that share a common goal of attempting to reduce risk associated with ignitions on primary electric distribution systems. i. EPSS – advantages: • Can be implemented on mostly existing equipment and relays • Reduces incident fault energy across all types of faults (Three-phase, line-toline, line-to-ground, etc.) • Reduces incident fault energy through fault clearing time reduction • Helps to reduce backfeed issues associated with 3-wire distribution system by prioritizing gang trip behavior versus single phase fuse operation • Incorporates various technologies for high impedance fault detection (Sensitive Ground Fault (SGF), Downed Conductor Detection (DCD), etc.) • Does not require extensive field high speed measurements or communication beyond traditional SCADA and remote access. (I.e. does not rely on synchrophasor technology) • Does not require changes to system grounding configuration or load connections to implement REFCL – advantages: • Potential for 90% ignition probability reduction for single line to ground faults (Victorian ignition testing). Considering all fault types, an overall ignition probability reduction can be calculated to approximately a 59% reduction. • Fault current limited to 1 Amp for single line to ground faults based on 2022 field testing • Greater sensitivity to high impedance faults ( > 5k ohm fault resistance) • Lower short circuit forces for line equipment for ground faults EPSS – disadvantages: • Less capability to sectionalize the system during fault events as compared to traditional protective settings due to the minimal coordination time provided in which can result in lower reliability performance • Fault current is not limited - fault energy is reduced by faster clearing times -and remains a function of existing system configuration. Re-energization after a fault event requires disabling of EPSS to avoid inrush trips • Susceptible to trips associated with customer load inrush, CT error, capacitor bank switching, and other non-fault grid disturbances. REFCL – disadvantages: • No risk reduction for line-line faults or three-phase ground faults • Complicated to install and operate • Limits operational flexibility / switching for the distribution circuits • Fault location is more difficult • Increased line-ground voltage stress on equipment during fault • Requires tuning, stress testing, and some proactive equipment replacement b. PG&E will need to evaluate the occurrences of different types of faults at locations within HFRA to determine the risk profile of existing ignitions and risk mitigation for REFCL and EPSS. c. i. EPSS and REFCL can be effective companion technologies as they both augment the other technologies shortfalls in some areas. For example, EPSS can reduce fault incident energy associated with line-to-line and three-phase faults which REFCL does not provide any benefit for. On a similar point, REFCL can potentially reduce energy associated with high impedance and provide greater detectability of these conditions. At this time, PG&E does not believe there are any negative implications of having both systems online at the same time and plans to do so in 2023. ii. PG&E has not assessed the combined risk-reduction benefits of REFCL with EPSS & Other Mitigations. Having actual operational data associated with operating REFCL will allow better understanding of the risk vs. benefits associated with the systems independently as well as combined. d. i. PG&E’s REFCL demonstration project has not been in full operation yet due to equipment failures during testing and the need for more testing to finalize settings. EPSS does not require the same new complex hardware, system conditioning, and testing and tuning periods to implement on a circuit, as compared to REFCL. Once REFCL is online, its advantages will be limited to line-to-ground faults only. Therefore, EPSS will continue to be a part of the protection strategy regardless of REFCL being implemented. ii. REFCL can be performance tested to dial in settings with staged fault testing, and fault sensitivity is expected to be approximately 1 Amp of fault current. DCD can be enabled in software in certain types of existing line recloser controllers to detect high impedance fault conditions down to approximately 1 Amp. Both technologies will continue to be evaluated to determine their effectiveness. | Wendy Al-Mukdad | 2023-02-23 | 2023-03-09 | 2023-03-09 | https://www.pge.com/pge_global/common/pdfs/safety/emergency-preparedness/natural-disaster/wildfires/wildfire-mitigation-plan/reference-docs/2023/SPD_001.zip | 0 | N/A | 8.1.8.1 | Grid Operations and Procedures | Equipment Settings to Reduce Wildfire Risk | N/A
Pre-Discovery 46 | CPUC - SPD (Safety Policy Division) | 001 | CPUC - SPD (Safety Policy Division)_001 | 4 | CPUC - SPD (Safety Policy Division)_001_Q4 | General risk reduction inquiry: • What’s PG&E’s goal for long-term risk reduction, particularly reduction of likelihood of ignition and also reduction of consequences, for circuits in HFTDs that are not undergrounded? | PG&E's long term goal is to maximize risk reduction by undergrounding high wildfire risk locations. For locations that will not be undergrounded, we will continue to deploy our suite of Operational Mitigations and other System Resilience Mitigations. Operational Mitigations include programs such as EPSS, equipment maintenance and repair, vegetation management for operational mitigations, and PSPS. System Resilience Mitigations include programs such as covered conductor installation, transmission conductor replacement, line removal, and distribution and transmission HFTD and HFRA open tag reduction. We will also manage system risk through our Comprehensive Monitoring and Data Collection programs include detailed distribution and transmission asset inspection programs, vegetation inspection programs, and monitoring programs such as Distribution Fault Anticipation Installations, Early Fault Detection Sensors and our network of wildfire cameras and weather stations. A complete listing of PG&E’s mitigation programs is included in Section 7.2.1. of PG&E’s WMP. Table 7.4 in PG&E’s WMP shows how we layer different mitigation programs at the circuit segment level to provide system protection and reduce risk. While Table 7.4 shows only PG&E’s top risk circuit segments, we apply this approach across all the circuits in the HFTD and HFRA. PG&E will continue to explore new technologies to reduce the risk of ignitions and the consequences of wildfires and may incorporate new technologies into our mitigation portfolio. | Wendy Al-Mukdad | 2023-02-23 | 2023-03-09 | 2023-03-09 | https://www.pge.com/pge_global/common/pdfs/safety/emergency-preparedness/natural-disaster/wildfires/wildfire-mitigation-plan/reference-docs/2023/SPD_001.zip | 0 | N/A | 7.2.1 | Wildfire Mitigation Strategy Development | Overview of Mitigation Initiatives and Activities | N/A
Pre-Discovery 47 | Green Power Institute (GPI) | 001 | Green Power Institute (GPI)_001 | 1 | Green Power Institute (GPI)_001_Q1 | Please provide PG&E’s Pre-submission 2023-2025 WMP Base Plan filed on February 13, 2023, with the OEIS per the 2023 WMP Guidelines and Schedule document. Including all attachments and associated supporting documents required for the Pre-submission 2023-2025 WMP Base Plan filing. | PG&E has designated the entire pre-submission as confidential to align with Energy Safety’s pre-submission process and guidelines which stipulate that the pre-submission documents are not to be made public. In addition, the pre-submission contains contact information for individuals that is considered confidential. As noted in our correspondences to you on March 8th and March 10th, we can provide you with a copy of the pre-submission documents that were submitted upon execution of a non-disclosure agreement. Alternatively, we will be submitting our final 2023-2025 Wildfire Mitigation Plan (WMP) for public review on March 27, 2023 if you would prefer to wait for a copy of the completed WMP following Energy Safety’s completeness check. Please feel free to reach out to us to discuss how you would prefer to move forward with this request. | Zoe Harrold | 2023-03-01 | 2023-03-14 | 2023-03-14 | https://www.pge.com/pge_global/common/pdfs/safety/emergency-preparedness/natural-disaster/wildfires/wildfire-mitigation-plan/reference-docs/2023/GPI_001.zip | 0 | N/A | All | All | All | N/A
Pre-Discovery 48 | CalPA | Set WMP-37 | CalPA_Set WMP-37 | 1 | CalPA_Set WMP-37_Q1 | Please provide a copy of each WMP Update-related document, submission, or report you submit to the Office of Energy Infrastructure Safety (Energy Safety) in 2024 or 2025 that is related to your 2025 WMP Update. Provide the copy to Cal Advocates within one business day of the document’s submittal to Energy Safety. (If you have submitted a document to Energy Safety prior to this data request, please provide a copy as soon as possible and no later than 10 business days from the issuance of this data request.) This request is limited to materials or documents that (1) are related to work plans, initiative targets, risk models, risk spend efficiency (RSE) calculations, cost-benefit ratio (CBR) calculations, or WMP change orders; and (2) are provided to Energy Safety to provide additional details or context concerning information or statements in your WMP (and any subsequent revisions or change orders affecting your WMP). | GENERAL OBJECTIONS TO THIS SET OF DATA REQUESTS PG&E objects to the instructions or definitions in the set of data requests entitled CalAdvocates-PGE-2025WMP-01 that purport to impose any obligations greater than those provided by the applicable rules and decisions of the Commission or and any other statutes, orders, rules, or laws limiting the regulatory authority and jurisdiction of the Commission. In particular, PG&E objects to the instruction that purports to place a burden on the responding party to reach out to the requesting party to clarify any unclear questions, definitions, or instructions. The duty to prepare precise and wellwritten instructions, definitions, and requests is on the party seeking the information and cannot be shifted to the responding party. Additionally, PG&E objects to the instruction that PG&E must “[p]rovide the name and title of the responding individual” as burdensome and not reasonably calculated to lead to the discovery of admissible evidence. Our responses to data requests are not the product of a single individual but of numerous individuals working together from different departments of the company. If the requesting party wishes to contact PG&E with questions or concerns about a data request, it may do so by contacting the appropriate individuals in the Regulatory Relations or Law Department upon whom the request was served. PG&E also objects to the following definitions: • The definitions of “[r]elate to” or “concern” which are overbroad and burdensome to the extent they request materials that “mention, or be connected with, in any WMP-Discovery2023-2025_DR_CalAdvocates_037-Q001 Page 2 way” the subject of the data requests. • The definitions of the terms “document,” “documents,” and “documentary material,” which include “correspondence” and “communications,” making these terms overbroad, unduly burdensome, and not reasonably calculated to lead to the discovery of admissible evidence in this proceeding. • The definition of the phrase “state the basis,” which is overbroad and burdensome to the extent it requests “every fact, statistic, inference, supposition, estimate, consideration, conclusion, study, report, and analysis….” ANSWER 001 In addition to all general objections, PG&E specifically objects to this request on the grounds that it is unduly burdensome. PG&E further objects to this request as the information requested is vague, ambiguous, and overbroad. Lastly, PG&E objects to this request on the grounds that it seeks to impose a continuing response obligation on the responding party. Continuing discovery obligations are not permitted under California law. Biles v. Exxon Mobil Corp., 124 Cal.App.4th 1315, 1328 (2004); Code Civ. Proc. § 2030.060(g). Notwithstanding and without waiving these objections, PG&E responds as follows: We will do our best to provide the requested information within the requested timeframe, or as soon as possible thereafter. However, please note that due to the timing and voluminous nature of our submissions to Energy Safety, it may not always be possible to provide the information sought within the requested timeframe. In these instances, we will provide the requested information as soon as it is reasonably possible. Additionally, with the exception of confidential and spatial data, please note that we post our WMP-related submissions on our website, www.pge.com/wildfiremitigationplan, generally on the same business day that the documents are provided to Energy Safety. Furthermore, all submissions to Energy Safety are also posted to the relevant docket on the Energy Safety website, https://efiling.energysafety.ca.gov/, and are nearly always publicly available within one business day of submission. Public email notifications of the availability of these documents are sent to all parties who subscribe to the service lists for those dockets. | Holly Wehrman | 2023-03-20 | 2024-04-03 | 2024-04-03 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_037.zip | 0 | N/A | N/A | N/A | N/A | N/A
Pre-Discovery 49 | CalPA | Set WMP-37 | CalPA_Set WMP-37 | 2 | CalPA_Set WMP-37_Q2 | Provide a copy of all documents or files that are referenced in your WMP Quarterly Data Reports and submitted to Energy Safety (including but not limited to all PDFs, spatial data files, non-spatial data files, and confidential attachments), within one business day of the document’s submission to Energy Safety. | In addition to all general objections, PG&E specifically objects to this request on the grounds that it is unduly burdensome. PG&E further objects to this request as the information requested is vague, ambiguous, and overbroad. Lastly, PG&E objects to this request on the grounds that it seeks to impose a continuing response obligation on the responding party. Continuing discovery obligations are not permitted under California law. Biles v. Exxon Mobil Corp., 124 Cal.App.4th 1315, 1328 (2004); Code Civ. Proc. § 2030.060(g). Notwithstanding and without waiving these objections, PG&E responds as follows: We will do our best to provide the requested information within the requested timeframe, or as soon as possible thereafter. However, please note that due to the timing and voluminous nature of our submissions to Energy Safety, it may not always be possible to provide the information sought within the requested timeframe. In these instances, we will provide the requested information as soon as it is reasonably possible. Additionally, with the exception of confidential and spatial data, please note that we post our WMP-related submissions on our website, www.pge.com/wildfiremitigationplan, generally on the same business day that the documents are provided to Energy Safety. Furthermore, all submissions to Energy Safety are also posted to the relevant docket on the Energy Safety website, https://efiling.energysafety.ca.gov/, and are nearly always publicly available within one business day of submission. Public email notifications of the availability of these documents are sent to all parties who subscribe to the service lists for those dockets. | Holly Wehrman | 2023-03-20 | 2024-04-03 | 2024-04-03 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_037.zip | 0 | N/A | N/A | N/A | N/A | N/A
Pre-Discovery 50 | CalPA | Set WMP-37 | CalPA_Set WMP-37 | 3 | CalPA_Set WMP-37_Q3 | Provide a copy to Cal Advocates of all your confidential responses to WMP discovery requests, on the same business day that you send the documents to the issuer of the discovery request. This includes: a) Confidential responses to WMP discovery requests issued by Energy Safety. b) Confidential responses to WMP discovery requests issued by other entities. | In addition to all general objections, PG&E specifically objects to this request on the grounds that it is unduly burdensome. PG&E further objects to this request as the information requested is vague, ambiguous, and overbroad. Lastly, PG&E objects to this request on the grounds that it seeks to impose a continuing response obligation on the responding party. Continuing discovery obligations are not permitted under California law. Biles v. Exxon Mobil Corp., 124 Cal.App.4th 1315, 1328 (2004); Code Civ. Proc. § 2030.060(g). Notwithstanding and without waiving these objections, PG&E responds as follows: We will do our best to provide the requested information within the requested timeframe, or as soon as possible thereafter. However, please note that due to the timing and voluminous nature of our submissions to Energy Safety, it may not always be possible to provide the information sought within the requested timeframe. In these instances, we will provide the requested information as soon as it is reasonably possible. | Holly Wehrman | 2023-03-20 | 2024-04-03 | 2024-04-03 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_037.zip | 0 | N/A | N/A | N/A | N/A | N/A
Pre-Discovery 51 | CalPA | Set WMP-38 | CalPA_Set WMP-38 | 1 | CalPA_Set WMP-38_Q1 | Provide an Excel table of all distribution circuit-segments existing as of January 1, 2024 (as rows) that includes the below information in separate columns. If PG&E is unable to provide some or all of the requested information at the circuit-segment level, provide such data at the circuit level instead and explain why PG&E is unable to provide circuit-segment level data. a) Circuit-segment name b) Circuit name c) Circuit ID number d) Total circuit miles e) Circuit miles in Non-HFTD f) Circuit miles in Other HFTD g) Circuit miles in HFTD Tier 2 h) Circuit miles in HFTD Tier 3 i) Circuit voltage j) Circuit SAIDI (System Average Interruption Duration Index) for 2023 k) Circuit SAIFI (System Average Interruption Frequency Index) for 2023 l) Circuit MAIFI (Momentary Average Interruption Frequency Index) for 2023 m) Total customer-minutes of de-energization on the circuit due to PSPS events in 2023 (sum of customer-minutes across all PSPS events) n) Total customer-minutes of de-energization on the circuit due to fast-trip settings in 2023 o) Miles of covered conductor installed in Non-HFTD in 2023 p) Miles of covered conductor installed in Other HFTD in 2023 q) Miles of covered conductor installed in HFTD Tier 2 in 2023 r) Miles of covered conductor installed in HFTD Tier 3 in 2023 s) Number of poles replaced in Non-HFTD in 2023 t) Number of poles replaced in Other HFTD in 2023 u) Number of poles replaced in HFTD Tier 2 in 2023 v) Number of poles replaced in HFTD Tier 3 in 2023 w) Miles of underground conductor installation in Non-HFTD in 2023 x) Miles of underground conductor installation in Other HFTD in 2023 y) Miles of underground conductor installation in HFTD Tier 2 in 2023 z) Miles of underground conductor installation in HFTD Tier 3 in 2023 aa) Miles of LiDAR inspection in Non-HFTD in 2023 bb) Miles of LiDAR inspection in Other HFTD in 2023 cc) Miles of LiDAR inspection in HFTD Tier 2 in 2023 dd) Miles of LiDAR inspection in HFTD Tier 3 in 2023 ee) Number of detailed ground-based inspections in Non-HFTD in 2023 ff) Number of detailed ground-based inspections in Other HFTD in 2023 gg) Number of detailed ground-based inspections in HFTD Tier 2 in 2023 hh) Number of detailed ground-based inspections in HFTD Tier 3 in 2023 ii) Number or miles of detailed aerial inspections in Non-HFTD in 2023 (specify units) jj) Number or miles of detailed aerial inspections in Other HFTD in 2023 (specify units) kk) Number or miles of detailed aerial inspections in HFTD Tier 2in 2023 (specify units) ll) Number or miles of detailed aerial inspections in HFTD Tier 3 in 2023 (specify units) mm) Number of sectionalization devices installed in Non-HFTD in 2023 nn) Number of sectionalization devices installed in Other HFTD in 2023 oo) Number of sectionalization devices installed in HFTD Tier 2 in 2023 pp) Number of sectionalization devices installed in HFTD Tier 3 in 2023 qq) Number of trees worked under VM for Operational Mitigations in Non-HFTD in 2023 rr) Number of trees worked under VM for Operational Mitigations in Other HFTD in 2023 ss) Number of trees worked under VM for Operational Mitigations in HFTD Tier 2 in 2023 tt) Number of trees worked under VM for Operational Mitigations in HFTD Tier 3 in 2023 uu) Number of trees worked under Focused Tree Inspections in Non-HFTD in 2023 vv) Number of trees worked under Focused Tree Inspections in Other HFTD in 2023 ww) Number of trees worked under Focused Tree Inspections in HFTD Tier 2 in 2023 xx) Number of trees worked under Focused Tree Inspections in HFTD Tier 3 in 2023. | PG&E is providing the requested distribution information at the circuit level in attachment “WMP-Discovery2023-2025_DR_CalAdvocates_038-Q001Atch01.xlsx.” Included in the table below are notes that document assumptions in the methodology for data collection. Where we have not included any notes, the data provided did not require adaptations or assumptions in answering the request. For purposes of this request, “Other HFTD” refers to Zone 1 areas. Please note that our SAIDI, SAIFI, and MAIFI data is not available at this time. The data will be available following the finalization of our Annual Reliability Report on July 15, 2024. Asset data provided in response to this request was generated from PG&E’s Geographic Information Systems (GIS) and presented in a spreadsheet format. PG&E’s Electric Transmission GIS and Electric Distribution GIS mapping systems represent assets associated with construction work when that work has been received and mapped by electric GIS mapping technicians. Construction jobs that are partially complete or fully complete may be mapped in the GIS systems once construction “asbuilt” information has been submitted and accepted by the GIS Mapping Department. Prior to being received by the GIS Mapping Department, completed job packages must undergo several processing steps including clerical review, processing, and paperwork scanning. Sometimes completed job packages require additional information from the field or post-estimating work. The processing steps take time to complete. Until a project is completed and mapped, detailed information remains in the design systems and paper job packages. Therefore, completed field work is not always reflected in the current GIS systems. Please note that circuit-segments are not defined on an enterprise level such that the asset information produced from EDGIS can be produced on a circuit-segment level. Once data is mapped in PG&E’s GIS systems, it can be formatted to meet the requirements of the Office of Energy Infrastructure Safety (Energy Safety) File Geodatabase schema and included in our GIS Data Standard submissions. Data Question Notes Circuit Information a-i Some circuits can have multiple voltages. Where this occurs, the Circuit Voltage in column g reflects the voltage of the majority of the circuit (based on circuit miles). Please note, Circuit IDs and Circuit Names representing idle circuits were not included in this response. SAIDI/SAIFI/MAIFI j-l N/A De-Energization - PSPS m Please see WMP-Discovery2023- 2025_DR_CalAdvocates_038-Q001Atch02.xlsx for the Data Question Notes requested information provided on a circuit-segment level. Please note that PSPS defines a “circuit segment” to be bounded by the nearest upstream and downstream protective devices. Circuit segments may change over time due to changes to our assets and protective devices. This data is provided using the circuit segments as they existed on January 1, 2024. For outage minutes not attributable to a circuit segment that existed as of January 1, 2024, circuit segments from the start of the month closest to the event were used. A [NULL] category is included to show PSPS outage minutes that cannot be attributed to circuit segments that existed as of January 1, 2024 or the start of the month closest to the event. As previously stated in our PSPS Post Event DeEnergization reports submitted to the CPUC: “The information, times and figures referenced in this report are based on the best available information available at the time of this report’s submission. The information, times and figures herein are subject to revision based on further analysis and validation.” As such, we note that there are some minor updated revisions in the data included in this submission, as compared to the data that may have been previously reported in previous submissions immediately following the events, due to further data reconciliation and analysis having been performed in the time which has elapsed between this report and any other previous submissions. Please note that the sum of PSPS customer outage durations is rounded up to the whole minute for each circuit segment to be consistent with data included in past data responses. This data request response will reference all outages associated with a PSPS event, including those which are either indirect effects of the PSPS event and are not direct de-energizations, or brief outages occurring as a result of microgrid switching, or temporary generation used as part of PSPS mitigation solution. Most switching in a PSPS event to re-energize customers takes place, typically, between five minutes and one hour, and that re-energization occurring within four hours of deenergization or outages less than four hours, typically, can likely be attributed to switching. De-Energization - EPSS n Please see WMP-Discovery2023- 2025_DR_CalAdvocates_038-Q001Atch03.xlsx for the requested information provided on a circuit-segment level. Please note, the circuit segment reported here reflects the circuit segment of the EPSS-enabled protective device the originating fault occurred on. Circuit segments may change over time due to changes to our assets and protective devices. This data is Data Question Notes provided using the circuit segments as they existed on February 2, 2024. Covered Conductor o-r Number of Poles Replaced s-v PG&E’s system of record does not have a relationship between circuits and poles, and therefore we cannot provide this data in the format requested. However, we can provide the data for poles replaced in 2023 by SAP Equipment ID. Please see “WMP-Discovery2023- 2025_DR_CalAdvocates_038-Q01Atch04xlxs.” Underground Conductor Installation w-z The information for underground miles provided is based on the distribution underground cable recorded in PG&E’s mapping system (EDGIS). The total miles installed are based on the “year installed” as recorded in EDGIS for each individual circuit then added together to provide the cumulative total. These underground miles are comprised primarily of new business, capacity, reliability, cable replacement, customer requested, Rule20, and fire hardening undergrounding work. LiDAR inspection aa-dd LiDAR is a supplemental source of data to support various lines of business including vegetation management, mapping, engineering, and inspections. Please note that the provided LiDAR data is associated only with PG&E's work on above-ground electric assets. Please note that LiDAR data is not stored or categorized by circuit-segment. Detailed Ground Inspections ee-hh Please note that System Inspections data is not stored or categorized by circuit-segment. Detailed Aerial Inspections ii-ll Please note that System Inspections data is not stored or categorized by circuit-segment. Sectionalization Devices mm-pp Sectionalization devices include remotely operable SCADA sectionalizing devices and manually operated sectionalizing devices (i.e., reclosers, not fuses). Tree Work under VM for Operational Mitigations qq-tt Please note that VM data is not stored or categorized by circuit-segment. Tree Work under Focused Tree Inspections uu-xx Please note that VM data is not stored or categorized by circuit-segment. | Holly Wehrman | 2023-03-20 | 2024-04-19 | 2024-04-19 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_038.zip | 4 | N/A | 8 | Section 8.1.3 - Asset Inspection | 8.1.3.2 Asset Inspections - Distribution | ACI 23-09 – Decrease in Detailed Distribution Inspections
Pre-Discovery 52 | CalPA | Set WMP-38 | CalPA_Set WMP-38 | 2 | CalPA_Set WMP-38_Q2 | Provide an Excel table of all transmission circuits existing as of January 1, 2024 (as rows) that includes the following information in separate columns: a) Circuit name b) Circuit ID number c) Total circuit miles d) Circuit miles in Non-HFTD e) Circuit miles in Other HFTD f) Circuit miles in HFTD Tier 2 g) Circuit miles in HFTD Tier 3 h) Circuit voltage i) Total customer-minutes of de-energization on the circuit due to PSPS events in 2023 (sum of customer-minutes across all PSPS events) j) Total customer-minutes of de-energization on the circuit due to fast-trip settings in 2023 k) Number of support structures replaced in Non-HFTD in 2023 l) Number of support structures replaced in Other HFTD in 2023 m) Number of support structures replaced in HFTD Tier 2 in 2023 n) Number of support structures replaced in HFTD Tier 3 in 2023 o) Miles of LiDAR inspection in Non-HFTD in 2023 p) Miles of LiDAR inspection in Other HFTD in 2023 q) Miles of LiDAR inspection in HFTD Tier 2 in 2023 r) Miles of LiDAR inspection in HFTD Tier 3 in 2023 s) Number or miles of detailed aerial inspections in Non-HFTD in 2023 (specify units) t) Number or miles of detailed aerial inspections in Other HFTD in 2023 (specify units) u) Number or miles of detailed aerial inspections in HFTD Tier 2 in 2023 (specify units) v) Number or miles of detailed aerial inspections in HFTD Tier 3 in 2023 (specify units) w) Number of detailed climbing inspections in Non-HFTD in 2023 x) Number of detailed climbing inspections in Other HFTD in 2023 y) Number of detailed climbing inspections in HFTD Tier 2 in 2023 z) Number of detailed climbing inspections in HFTD Tier 3 in 2023 aa) Number of detailed ground-based inspections in Non-HFTD in 2023 bb) Number of detailed ground-based inspections in Other HFTD in 2023 cc) Number of detailed ground-based inspections in HFTD Tier 2 in 2023 dd) Number of detailed ground-based inspections in HFTD Tier 3 in 2023 ee) Number of sectionalization devices installed in Non-HFTD in 2023 ff) Number of sectionalization devices installed in Other HFTD in 2023 gg) Number of sectionalization devices installed in HFTD Tier 2 in 2023 hh) Number of sectionalization devices installed in HFTD Tier 3 in 2023. | PG&E is providing the requested transmission information at the circuit level in attachment “WMP-Discovery2023-2025_DR_CalAdvocates_038-Q01Atch01.xlsx.” Included in the table below are notes that document assumptions in the methodology for data collection. Where we have not included any notes, the data provided did not require adaptations or assumptions in answering the request. For purposes of this request, “Other HFTD” refers to Zone 1 areas. Asset data provided in response to this request was generated from PG&E’s Geographic Information Systems (GIS) and presented in a spreadsheet format. PG&E’s Electric Transmission GIS and Electric Distribution GIS mapping systems represent assets associated with construction work when that work has been received and mapped by electric GIS mapping technicians. Construction jobs that are partially complete or fully complete may be mapped in the GIS systems once construction “asbuilt” information has been submitted and accepted by the GIS Mapping Department. Prior to being received by the GIS Mapping Department, completed job packages must undergo several processing steps including clerical review, processing, and paperwork scanning. Sometimes completed job packages require additional information from the field or post-estimating work. The processing steps take time to complete. Until a project is completed and mapped, detailed information remains in the design systems and paper job packages. Therefore, completed field work is not always reflected in the current GIS systems. Once data is mapped in PG&E’s GIS systems, it can be formatted to meet the requirements of the Office of Energy Infrastructure Safety (Energy Safety) File Geodatabase schema and included in our GIS Data Standard submissions. Data Question Notes Circuit Information a-h Some circuits can have multiple voltages. Where this occurs, the Circuit Voltage in column g reflects the voltage of the majority of the circuit (based on circuit miles). De-Energization - PSPS i As previously stated in our PSPS Post Event DeEnergization reports submitted to the CPUC: “The information, times and figures referenced in this report are based on the best available information available at the time of this report’s submission. The information, times and figures herein are subject to revision based on further analysis and validation.” As such, we note that there are some minor updated revisions in the data included in this submission, as compared to the data that may have been previously reported in previous submissions immediately following the events, due to further data reconciliation and analysis having been performed in the time which has elapsed between this report and any other previous submissions. In some circumstances, PG&E may conclude a PSPS event before all customers are restored. For example, when there is an ongoing fire that prohibits PG&E from restoring customers or extensive weather-related damages that require extended outages while crews safely repair the area. The outage durations for these customers are not included in Questions 1o-p and Questions 2i-j, as we do not have restoration dates and times for those customers. For information on which circuits were not restored prior to concluding the PSPS, please see the “Time, Place, Duration, and Affected Customers” appendix section of the PSPS Post-Event Reports. Please note that the sum of PSPS customer outage durations is rounded up to the whole minute for each circuit to be consistent with data included in past data responses. This data request response will reference all outages associated with a PSPS event, including those which are either indirect effects of the PSPS event and are not direct de-energizations, or brief outages occurring as a result of microgrid Data Question Notes switching, or temporary generation used as part of PSPS mitigation solution. Most switching in a PSPS event to re-energize customers takes place, typically, between five minutes and one hour, and that re-energization occurring within four hours of de-energization or outages less than four hours, typically, can likely be attributed to switching. De-Energization – EPSS j Please note that this data only shows distribution customer outage minutes resulting from outages that occurred on transmission circuits while EPSS fast-trip settings were enabled. Number of Support Structures Replaced k-n Data includes poles and towers. Poles were matched to a circuit by GIS radius of 15 feet. LiDAR inspection o-r LiDAR is a supplemental source of data to support various lines of business including vegetation management, mapping, engineering, and inspections. Please note that the provided LiDAR data is associated only with PG&E's work on above-ground electric assets. Please note that some miles flown were performed on circuits that were subsequently removed from our system. Those inspections are not included here. Number of detailed aerial inspections s-v Please note that some inspections were performed on circuits are no longer in our system. Those inspections are not included here. Number of detailed climbing inspections w-z Please note that some inspections were performed on circuits are no longer in our system. Those inspections are not included here. Number of detailed ground inspections aa-dd Please note that some inspections were performed on circuits are no longer in our system. Those inspections are not included here. Sectionalization Devices ee-hh Sectionalization devices include remotely operable SCADA sectionalizing devices and manually operated sectionalizing devices (i.e., reclosers, not fuses). | Holly Wehrman | 2023-03-20 | 2024-04-19 | 2024-04-19 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_038.zip | 0 | N/A | 8 | Section 8.1.3 - Asset Inspection | 8.1.3.1 Asset Inspections - Transmission | 2.1.4.1 GH-11 Traditional Overhead Hardening Conductor
Pre-Discovery 53 | CalPA | Set WMP-38 | CalPA_Set WMP-38 | 3 | CalPA_Set WMP-38_Q3 | Provide an Excel table of all distribution circuits existing as of January 1, 2023 (as rows) that were removed or decommissioned in 2023, either partially or entirely. This includes permanent removal, removal of overhead lines that were moved underground, or overhead lines that were decommissioned but not physically removed. Include the following information in separate columns: a) Circuit name b) Circuit ID number c) Circuit miles removed or decommissioned in Non-HFTD d) Circuit miles removed or decommissioned in Other HFTD e) Circuit miles removed or decommissioned in HFTD Tier 2 f) Circuit miles removed or decommissioned in HFTD Tier 3 g) Reason(s) for removal or decommissioning. | Please see attachment WMP-Discovery2023-2025_DR_CalAdvocates_038- Q003Atch01.xlsx, which provides information regarding removal of primary distribution lines in HFTD in 2023, as well as the underground miles installed, which is a subset of the requested information available at this time. This response is generally consistent with the one we provided last year in response to the same question (CalAdvocatesPGE-2023WMP-03). The information provided is specific to projects within PG&E’s 2023-2025 WMP Initiative GH-01 (System Hardening). However, there may be additional circuits that were removed or decommissioned, either partially or entirely, outside of the System Hardening program (e.g. via maintenance and construction). Historically, PG&E did not track line removals when relocating overhead to underground, removing secondary services, or removing lines in non-HFTD. However, based on the 2023 GRC Decision (D.) 23-11-069 OP23, PG&E is preparing to report the 2023 miles of overhead lines removed during underground projects in the annual System Hardening Accountability Report, which will be distributed to the GRC service list by July 1, 2024. For transparency in this response, we have included the Undergrounding miles installed by project in 2023. A conversion factor of one (1) mile of overhead miles removed to 1.25 miles of undergrounding installed may be applied to estimate the overhead miles removed. This conversion factor was adopted by the CPUC in GRC D.23-11-069, Conclusion of Law 80 (page 862). Below we provide additional information to clarify the data provided in the attachment in response to the request. a) Circuit name: please see column C. b) Circuit ID number: please see column D. c) Distribution circuit miles removed or decommissioned in non-HFTD Areas: column E indicates the HFTD Tier by project, including Tier 1 (see definition tab for the definitions of the HFTD tiers included). Column G includes the associated line removal circuit miles, and column H includes the underground miles installed (see note above regarding the overhead to underground conversion factor). d) Distribution circuit miles removed or decommissioned in other HFTD: column E indicates the HFTD Tier by project, including HFTD Buffer Zone and Zone 1 (see definition tab for the definitions of the HFTD tiers included). Column G includes the associated line removal circuit miles, and column H includes the underground miles installed (see note above regarding the overhead to underground conversion factor). e) Distribution circuit miles removed or decommissioned in HFTD Tier 2: column E indicates the HFTD Tier by project, including Tier 2 (see definition tab for the definitions of the HFTD tiers included). Column G includes the associated line removal circuit miles, and column H includes the underground miles installed (see note above regarding the overhead to underground conversion factor). f) Distribution circuit miles removed or decommissioned in HFTD Tier 3: column E indicates the HFTD Tier by project, including Tier 3 (see definition tab for the definitions of the HFTD tiers included). Column G includes the associated line removal circuit miles, and column H includes the underground miles installed (see note above regarding the overhead to underground conversion factor). g) Reason(s) for removal or decommissioning: please see Column F, which notes the name of one of the program / reasons for removal or decommission that is associated with the project (see definition tab for the definitions of the Program included). ATTACHMENT: WMP-Discovery2023-2025_DR_CalAdvocates_038-Q003Atch01.xlsx | Holly Wehrman | 2023-03-20 | 2024-04-19 | 2024-04-15 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_038.zip | 1 | N/A | 8 | Section 8.1.3 - Asset Inspection | 8.1.3.2 Asset Inspections - Distribution | ACI 23-09 – Decrease in Detailed Distribution Inspections
Pre-Discovery 54 | CalPA | Set WMP-38 | CalPA_Set WMP-38 | 4 | CalPA_Set WMP-38_Q4 | Provide an Excel table of all transmission circuits existing as of January 1, 2023 (as rows) that were removed or decommissioned in 2023, either partially or entirely. This includes permanent removal, removal of overhead lines that were moved underground, or overhead lines that were decommissioned but not physically removed. Include the following information in separate columns: a) Circuit name b) Circuit ID number c) Circuit miles removed or decommissioned in Non-HFTD d) Circuit miles removed or decommissioned in Other HFTD e) Circuit miles removed or decommissioned in HFTD Tier 2 f) Circuit miles removed or decommissioned in HFTD Tier 3 g) Reason(s) for removal or decommissioning. | Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_038- Q004Atch01.xlsx” for the requested information. ATTATCHMENT: WMP-Discovery2023-2025_DR_CalAdvocates_038-Q004Atch01.xlsx | Holly Wehrman | 2023-03-20 | 2024-04-19 | 2024-04-15 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_038.zip | 1 | N/A | 8 | Section 8.1.3 - Asset Inspection | 8.1.3.1 Asset Inspections - Transmission | 2.1.4.1 GH-11 Traditional Overhead Hardening Conductor
Pre-Discovery 55 | MGRA | 008 | MGRA_008 | 1 | MGRA_008_Q1 | GIS Data: Please provide the GIS data set provided to the Office of Energy Infrastructure Safety for Q1-Q4 2023. Please remove any confidential attributes that may have been added to the requested records. Please provide for Asset Point data for Camera, Fuse, Support Structure, and Weather Station. | GENERAL STATEMENT REGARDING RESPONSES TO QUESTIONS 1 THROUGH 6 In response to questions 1 through 6 of this set of data requests, PG&E is providing non-confidential data from the 2023 Office of Energy Infrastructure and Safety (Energy Safety) Geographic Information System (GIS) Data Standard submission, as instructed by the requesting party. Due to the high volume of records in our submission (approximately 13.5 million records each quarter), individual record review for confidential data is neither feasible nor practical. The feature classes and related tables included in the submission are not static and change each quarter. Additionally, the interconnected aspect of feature class data and the geospatial representation of the data creates complexities in identifying the confidentiality of individual records and introduces additional risk for error. PG&E is applying confidentiality designations at the feature class and field level, dependent on the subject data, to help mitigate against the risk of mislabeling individual records. Batch analysis was used to identify nonconfidential records. PG&E respectfully requests that MGRA use this data for internal purposes only and restrict access to a need-to-know basis. In response to this request, PG&E is providing Camera and Weather Station data, as delivered in the 2023 Energy Safety GIS Data Standard Submissions. PG&E is also providing non-confidential data from the Support Structure feature class. As requested, WMP-Discovery2023-2025_DR_MGRA_008-Q001 Page 2 PG&E is not providing data for the Fuse feature class as this data is confidential critical energy infrastructure information (CEII). Please see attachment “WMP-Discovery2023-2025_DR_MGRA_008-Q001Atch01.zip,” for the data provided in response to this data request. | Joseph Mitchell | 2023-03-21 | 2024-04-05 | 2024-04-05 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_008.zip | 1 | N/A | Appendix D | Appendix D - Areas for Continued Improvement | Appendix D ACI PG&E-22--33 Progress on Filling Asset Inventory Data Gaps | N/A
Pre-Discovery 55 | MGRA | Data Request No. 8 | MGRA_Data Request No. 8 | 1(s) | MGRA_Data Request No. 8_Q1(s) | GIS Data: Please provide the GIS data set provided to the Office of Energy Infrastructure Safety for Q1-Q4 2023. Please remove any confidential attributes that may have been added to the requested records. Please provide for Asset Point data for Camera, Fuse, Support Structure, and Weather Station. | Please see “WMP-Discovery2023-2025_DR_MGRA_008-Q001Supp01Atch01.gdb.zip” for the information requested during PG&E’s discussion with MGRA on Friday, April 12, 2024. | Joseph Mitchell | 2023-03-21 | 2024-04-22 | 2024-04-22 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_008.zip | 1 | N/A | Appendix D | Appendix D - Areas for Continued Improvement | Appendix D ACI PG&E-22--33 Progress on Filling Asset Inventory Data Gaps | N/A
Pre-Discovery 56 | MGRA | 008 | MGRA_008 | 2 | MGRA_008_Q2 | Provide Asset Line data for Transmission Line (as permitted as non-confidential), Primary Distribution Line, and Secondary Distribution Line. | In response to this request, PG&E is providing non-confidential data for the Primary and Secondary Distribution Line Feature Classes, as delivered in the 2023 Energy Safety GIS Data Standard Submissions. As requested, PG&E is not providing the Transmission Line feature class because it is confidential CEII. Please see attachment “WMP-Discovery2023-2025_DR_MGRA_008-Q001Atch01.zip,” for the data provided in response to this data request. | Joseph Mitchell | 2023-03-21 | 2024-04-05 | 2024-04-05 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_008.zip | 0 | N/A | Appendix D | Appendix D - Areas for Continued Improvement | Appendix D ACI PG&E-22--33 Progress on Filling Asset Inventory Data Gaps | N/A
Pre-Discovery 56 | MGRA | Data Request No. 8 | MGRA_Data Request No. 8 | 2(s) | MGRA_Data Request No. 8_Q2(s) | Provide Asset Line data for Transmission Line (as permitted as non-confidential), Primary Distribution Line, and Secondary Distribution Line. | Please see “WMP-Discovery2023-2025_DR_MGRA_008-Q001Supp01Atch01.gdb.zip” for the information requested during PG&E’s discussion with MGRA on Friday, April 12, 2024. | Joseph Mitchell | 2023-03-21 | 2024-04-22 | 2024-04-22 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_008.zip | 1 | N/A | Appendix D | Appendix D - Areas for Continued Improvement | Appendix D ACI PG&E-22--33 Progress on Filling Asset Inventory Data Gaps | N/A
Pre-Discovery 57 | MGRA | 008 | MGRA_008 | 3 | MGRA_008_Q3 | Provide PSPS Event data. Include Event Log, Event Line, Event Polygon data. Please exclude customer meter data. Provide all PSPS Event Asset Damage data including photos. | In response to this request, PG&E is unable to provide Public Safety Power Shutoff (PSPS) Event data for the Quarter (Q)1, Q2, and Q3 2023 submissions as no PSPS Events took place those quarters. Two PSPS events occurred during the third quarter in 2023. As requested, our non-confidential data is included in this response. Please see attachment “WMP-Discovery2023-2025_DR_MGRA_008-Q001Atch01.zip,” for the data provided in response to this data request. | Joseph Mitchell | 2023-03-21 | 2024-04-05 | 2024-04-05 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_008.zip | 0 | N/A | Appendix D | Appendix D - Areas for Continued Improvement | Appendix D ACI PG&E-22--33 Progress on Filling Asset Inventory Data Gaps | N/A
Pre-Discovery 57 | MGRA | Data Request No. 8 | MGRA_Data Request No. 8 | 3(s) | MGRA_Data Request No. 8_Q3(s) | Provide PSPS Event data. Include Event Log, Event Line, Event Polygon data. Please exclude customer meter data. Provide all PSPS Event Asset Damage data including photos. | Please see “WMP-Discovery2023-2025_DR_MGRA_008-Q001Supp01Atch01.gdb.zip” for the information requested during PG&E’s discussion with MGRA on Friday, April 12, 2024. | Joseph Mitchell | 2023-03-21 | 2024-04-22 | 2024-04-22 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_008.zip | 1 | N/A | Appendix D | Appendix D - Areas for Continued Improvement | Appendix D ACI PG&E-22--33 Progress on Filling Asset Inventory Data Gaps | N/A
Pre-Discovery 58 | MGRA | 008 | MGRA_008 | 4 | MGRA_008_Q4 | Provide Risk Event Point data, including Wire Down, Ignition, Transmission unplanned outage (as classified non-confidential), Distribution Unplanned Outage data, Distribution Vegetation Caused Unplanned Outage, Risk Event Asset Log. | In response to this request, PG&E is providing non-confidential data for the Wire Down, Ignition, Unplanned Outage, and Risk Event Asset Log feature classes, as delivered in the 2023 Energy Safety GIS Data Standard Submissions. Energy Safety changed its schema for version 3.1 of the Data Standard and combined all Outage feature classes into a single feature class. Please see attachment “WMP-Discovery2023-2025_DR_MGRA_008-Q001Atch01.zip,” for the data provided in response to this data request. | Joseph Mitchell | 2023-03-21 | 2024-04-05 | 2024-04-05 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_008.zip | 0 | N/A | Appendix D | Appendix D - Areas for Continued Improvement | Appendix D ACI PG&E-22--33 Progress on Filling Asset Inventory Data Gaps | N/A
Pre-Discovery 58 | MGRA | Data Request No. 8 | MGRA_Data Request No. 8 | 4(s) | MGRA_Data Request No. 8_Q4(s) | Please provide for Asset Point data for Camera, Fuse, Support Structure, and Weather Station. | Please see “WMP-Discovery2023-2025_DR_MGRA_008-Q001Supp01Atch01.gdb.zip” for the information requested during PG&E’s discussion with MGRA on Friday, April 12, 2024. | Joseph Mitchell | 2023-03-21 | 2024-04-22 | 2024-04-22 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_008.zip | 1 | N/A | Appendix D | Appendix D - Areas for Continued Improvement | Appendix D ACI PG&E-22--33 Progress on Filling Asset Inventory Data Gaps | N/A
Pre-Discovery 59 | MGRA | 008 | MGRA_008 | 5 | MGRA_008_Q5 | Under Initiatives, please provide Grid Hardening data, including Hardening Log, Hardening Point, and Hardening Line data. Inspection data is not requested at this time. | In response to this request, PG&E is providing non-confidential data for the Grid Hardening Point and Grid Hardening Line feature classes, as delivered in the 2023 Energy Safety GIS Data Standard Submissions. Energy Safety changed its schema for version 3.1 of the Data Standard which removed the Grid Hardening Log feature class. Please see attachment “WMP-Discovery2023-2025_DR_MGRA_008-Q001Atch01.zip,” for the data provided in response to this data request. | Joseph Mitchell | 2023-03-21 | 2024-04-05 | 2024-04-05 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_008.zip | 0 | N/A | Appendix D | Appendix D - Areas for Continued Improvement | Appendix D ACI PG&E-22--33 Progress on Filling Asset Inventory Data Gaps | N/A
Pre-Discovery 59 | MGRA | Data Request No. 8 | MGRA_Data Request No. 8 | 5(s) | MGRA_Data Request No. 8_Q5(s) | Under Initiatives, please provide Grid Hardening data, including Hardening Log, Hardening Point, and Hardening Line data. Inspection data is not requested at this time. | Please see “WMP-Discovery2023-2025_DR_MGRA_008-Q001Supp01Atch01.gdb.zip” for the information requested during PG&E’s discussion with MGRA on Friday, April 12, 2024. | Joseph Mitchell | 2023-03-21 | 2024-04-22 | 2024-04-22 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_008.zip | 1 | N/A | Appendix D | Appendix D - Areas for Continued Improvement | Appendix D ACI PG&E-22--33 Progress on Filling Asset Inventory Data Gaps | N/A
Pre-Discovery 60 | MGRA | 008 | MGRA_008 | 6 | MGRA_008_Q6 | Under Other Required Data, please provide Red Flag Warning Day polygon data. | In response to this request, PG&E is providing non-confidential data for the Red Flag Warning Day polygon data for Q2-Q4 2023 feature class as delivered in the 2023 Energy Safety GIS Data Standard Submissions. PG&E is unable to provide the Red Flag Warning Day polygon data for the Q1 2023 submission as there were no Red Flag Warning days to report. Please see attachment “WMP-Discovery2023-2025_DR_MGRA_008-Q001Atch01.zip,” for the data provided in response to this data request. | Joseph Mitchell | 2023-03-21 | 2024-04-05 | 2024-04-05 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_008.zip | 0 | N/A | Appendix D | Appendix D - Areas for Continued Improvement | Appendix D ACI PG&E-22--33 Progress on Filling Asset Inventory Data Gaps | N/A
Pre-Discovery 60 | MGRA | Data Request No. 8 | MGRA_Data Request No. 8 | 6(s) | MGRA_Data Request No. 8_Q6(s) | Under Other Required Data, please provide Red Flag Warning Day polygon data. | Please see “WMP-Discovery2023-2025_DR_MGRA_008-Q001Supp01Atch01.gdb.zip” for the information requested during PG&E’s discussion with MGRA on Friday, April 12, 2024. | Joseph Mitchell | 2023-03-21 | 2024-04-22 | 2024-04-22 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_008.zip | 1 | N/A | Appendix D | Appendix D - Areas for Continued Improvement | Appendix D ACI PG&E-22--33 Progress on Filling Asset Inventory Data Gaps | N/A
Pre-Discovery 61 | MGRA | 008 | MGRA_008 | 7 | MGRA_008_Q7 | Please provide a layer indicating calculated circuit-level risk using the methodology presented in the WMP. a. If independent probability and consequence layers exist, please provide these independently as well. | The requested circuit segment-level risk model results that correspond with this request for 2023 Q1-Q4 data are the Wildfire Distribution Risk Model (WDRM) v3 results that were provided previously in WMP-Discovery2023_DR_MGRA_001-Q001 and submitted to the Mussey Grade Road Alliance on April 7, 2023. In PG&E’s 2025 WMP Update, the next iteration of the Wildfire Risk model (WDRM v4) is outlined.1 At this time the model has recently been internally approved for use in developing future workplans. WDRM v4 influenced workplans will be first introduced in the 2026 WMP. | Joseph Mitchell | 2023-03-21 | 2024-04-05 | 2024-04-05 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_008.zip | 0 | N/A | Appendix D | Appendix D - Areas for Continued Improvement | Appendix D ACI PG&E-22--30 Response Operations for Potential Fault/Outages in its Highest Risk Areas | N/A
Pre-Discovery 61 | MGRA | Data Request No. 8 | MGRA_Data Request No. 8 | 7(s) | MGRA_Data Request No. 8_Q7(s) | Please provide a layer indicating calculated circuit-level risk using the methodology presented in the WMP. a. If independent probability and consequence layers exist, please provide these independently as well. | Please see “WMP-Discovery2023-2025_DR_MGRA_008-Q001Supp01Atch01.gdb.zip” for the information requested during PG&E’s discussion with MGRA on Friday, April 12, 2024. | Joseph Mitchell | 2023-03-21 | 2024-04-22 | 2024-04-22 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/MGRA_008.zip | 1 | N/A | Appendix D | Appendix D - Areas for Continued Improvement | Appendix D ACI PG&E-22--30 Response Operations for Potential Fault/Outages in its Highest Risk Areas | N/A
Pre-Discovery 62 | CalPA | Set WMP-39 | CalPA_Set WMP-39 | 1 | CalPA_Set WMP-39_Q1 | Please identify and provide a copy of all quality assurance or quality control (QA/QC) reports conducted by internal entities that have been completed since January 1, 2023 and that examined any programs, initiatives, or strategies described in your 2023-2025 Base WMP. | PG&E historically has managed Quality Assurance (QA)/Quality Control (QC) within our individualized functional areas. In 2023, PG&E formalized its independent quality management system in support of the System Inspections and Vegetation Management functional areas. As a result, the response provided for 2023 aligns with data produced to validate 2023 commitments. Please see the eight attachments identified below for data/reports of QA/QC performed for the following programs: • Vegetation Management Routine Distribution; • Vegetation Management Routine Transmission; • Vegetation Management Pole Clearing; • System Inspections Distribution; and • System Inspections Transmission. ATTACHMENTS WMP-Discovery2023-2025_DR_CalAdvocates_039-Q001Atch01.xlsx WMP-Discovery2023-2025_DR_CalAdvocates_039-Q001Atch02.xlsx WMP-Discovery2023-2025_DR_CalAdvocates_039-Q001Atch03.xlsx WMP-Discovery2023-2025_DR_CalAdvocates_039-Q001Atch04.xlsx WMP-Discovery2023-2025_DR_CalAdvocates_039-Q001Atch05.xlsx WMP-Discovery2023-2025_DR_CalAdvocates_039-Q001Atch06.xlsx WMP-Discovery2023-2025_DR_CalAdvocates_039-Q001Atch07.xlsx WMP-Discovery2023-2025_DR_CalAdvocates_039-Q001Atch08.xlsx | Holly Wehrman | 2024-03-22 | 2024-04-05 | 2024-04-05 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_039.zip | 8 | N/A | 8 | Section 8.1.6 - Quality Assurance and Quality Control | 8.1.6.1 Quality Assurance (QA) | N/A
Pre-Discovery 63 | CalPA | Set WMP-39 | CalPA_Set WMP-39 | 2 | CalPA_Set WMP-39_Q2 | Please identify and provide a copy of all quality assurance or quality control (QA/QC) reports conducted by external entities that have been completed since January 1, 2023 and that examined any programs, initiatives, or strategies described in your 2023-2025 Base WMP. External entities include, but are not limited to, consultants, contractors, auditors, court-appointed monitors, and Independent Evaluators. | Similar to PG&E’s response to this request last year, a new report from the Independent Safety Monitor was provided to the CPUC on March 29, 2024, and published by the CPUC on April 4, 2024. All reports from the Independent Safety Monitor, including this most recent report, can be found at the following link: https://www.cpuc.ca.gov/industries-and-topics/pge/independent-safety-monitor. The reports discuss a number of functional areas and programs, including programs and initiatives described in our 2023-2025 WMP. | Holly Wehrman | 2024-03-22 | 2024-04-05 | 2024-04-05 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_039.zip | 0 | N/A | 8 | Section 8.1.6 - Quality Assurance and Quality Control | 8.1.6.1 Quality Assurance (QA) | N/A
Pre-Discovery 64 | CalPA | Set WMP-39 | CalPA_Set WMP-39 | 3 | CalPA_Set WMP-39_Q3 | Provide an Excel table of all defects in the year 2023 found by Energy Safety’s Compliance Branch (as rows) that includes the following information in separate columns: a) Associated circuit name b) Defect type c) Description of defect d) WMP initiative (from your 2023-2025 WMP) associated with defect e) Date that the defect was identified f) Date that the defect was corrected g) If the defect has not yet been corrected as of the issuance date of this data request, a brief explanation h) Priority level of corresponding corrective tag i) Geographic latitude of defect in decimal degrees, truncated to seven decimal places j) Geographic longitude of defect in decimal degrees, truncated to seven decimal places. | Please note the attachment to this response contains CONFIDENTIAL information provided pursuant to the accompanying confidentiality declaration. Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_039- Q003Atch01CONF.xlsx” for the requested information. | Holly Wehrman | 2024-03-22 | 2024-04-05 | 2024-04-05 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_039.zip | 1 | N/A | 11 | Section 11 - Corrective Action Program | 11.3 Corrective Action Program - Address finding from Energy Safety’s Compliance Assurance Division (i.e., audits and notices of defect and violation) | N/A
Pre-Discovery 65 | CalPA | Set WMP-39 | CalPA_Set WMP-39 | 4 | CalPA_Set WMP-39_Q4 | For each WMP initiative for which you forecast capital expenditures in 2025 to be at least two times actual capital expenditures in 2023, please provide: a) The name of the initiative as it is identified in your 2025 WMP Update. b) The WMP Initiative number in Table 11 of your 2025 WMP Update. c) The name of the initiative as it is identified in your 2023-2025 Base WMP d) The WMP Initiative number in Table 11 of your 2023-2025 Base WMP e) An explanation for the projected increase. | ``There are two WMP initiatives that fall in the population requested above, where the forecast capital expenditures in 2025 are at least two times the actual capital expenditures in 2023: (1) customer support in wildfire and PSPS emergencies; and (2) traditional overhead hardening. (1) Customer support in wildfire and PSPS emergencies (2) Traditional Overhead Hardening a) Name of initiative: Emergency Preparedness – Customer Support in Wildfire and PSPS Emergencies Grid Design, Operations, and Maintenance – Traditional Overhead Hardening b) PG&E is providing the name of the activity category in lieu of the initiative number for PG&E is providing the name of the activity category in lieu of the initiative number for (1) Customer support in wildfire and PSPS emergencies (2) Traditional Overhead Hardening ease of reference as Table 11 includes activity categories. The WMP activity category for this initiative is “Customer Support in Wildfire and PSPS Emergencies.” ease of reference as Table 11 includes activity categories. The WMP activity category for this initiative is “Traditional Overhead Hardening.” c) Same as above in part a. Same as above in part a. d) Same as above in part b. Same as above in part b. e) This difference is due to PG&E having fewer than forecasted PSPS activations in 2023 and, therefore, the need to replace capital hardware (for example, phones, laptops, etc.) for this type of response work was reduced. The 2025 forecast represents costs associated with our current estimate of PSPS events that may occur The projected increase is due to the continuation of the shunt splice program, reconductor program, and the addition of the segment replacement program. Please refer to 2025 WMP section B.2.2.2.2 Traditional Overhead Hardening for additional information. | Holly Wehrman | 2024-03-22 | 2024-04-05 | 2024-04-05 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_039.zip | 0 | N/A | 4 | Section 4 - Overview of WMP | 4.3 Proposed Expenditures | 2.3 Expenditures
Pre-Discovery 66 | CalPA | Set WMP-39 | CalPA_Set WMP-39 | 5 | CalPA_Set WMP-39_Q5 | For each WMP initiative for which you forecast operating expenditures in 2025 to be at least two times actual operating expenditures in 2023, please provide: a) The name of the initiative as it is identified in your 2025 WMP Update. b) The WMP Initiative number in Table 11 of your 2025 WMP Update. c) The name of the initiative as it is identified in your 2023-2025 Base WMP d) The WMP Initiative number in Table 11 of your 2023-2025 Base WMP e) An explanation for the projected increase. | There are three WMP initiatives that fall in the population requested above, where the forecast operating expenditures in 2025 are at least two times actual operating expenditures in 2023: (1) fall-in mitigation; (2) microgrids; and (3) fire-resilient right-ofways. 1. Fall-In Mitigation 2. Microgrid 3. Fire-Resilient Right-ofWays a) Vegetation Management and Inspection- Fall-In Mitigation. Grid Design, Operations, and MaintenanceMicrogrids Vegetation Management and Inspection – Fire Resilient Right-of-Ways. 1. Fall-In Mitigation 2. Microgrid 3. Fire-Resilient Right-ofWays b) PG&E is providing the name of the activity category in lieu of the initiative number for ease of reference as Table 11 includes activity categories. The WMP activity category for this initiative is “Fall-In Mitigation.” PG&E is providing the name of the activity category in lieu of the initiative number for ease of reference as Table 11 includes activity categories. The WMP activity category for this initiative is “Microgrids.” PG&E is providing the name of the activity category in lieu of the initiative number for ease of reference as Table 11 includes activity categories. The WMP activity category for this initiative is “Fire Resilient right-ofways.” c) Same as above in part a. Same as above in 2. Microgrids, part a. Same as above in 3. FireResilient Right-of-Ways, part a. d) Same as above in part b. Same as above in 2. Microgrids, part b. Same as above in 3. FireResilient Right-of-Ways, part b. e) The 2025 WMP increase is due to the expanded scope and increased maturity of the Tree Removal Inventory (TRI), Vegetation Management for Operational Mitigation (VMOM), and Focused Tree Inspection (FTI) programs since the original filing. Please refer to the “B.2.2.2.6 Fall-in Mitigation” section of our 2025 WMP filing for a detailed description of this work. The projected increase for 2025 (versus 2023) is comparable to the increase originally forecasted for this work in the Base 2023–2025 WMP. The forecasted increase aligns with the Microgrids Incentive Program approved by the CPUC in Decision 23-04-024. This difference is due to an inadvertent error. We are in the process of filing errata to the information provided in our Quarterly Data Report (QDR), which will provide corrected 2023 actuals. After the correction, this section would not fall under the above criteria. As noted in PG&E response to CalAdvocates_036-Q004, submitted to CalAdvocates on March 29, 2024, PG&E will submit a corrected QDR to Energy Safety’s QDR docket. | Holly Wehrman | 2024-03-22 | 2024-04-05 | 2024-04-05 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_039.zip | 0 | N/A | 4 | Section 4 - Overview of WMP | 4.3 Proposed Expenditures | 2.3 Expenditures
Pre-Discovery 67 | CalPA | Set WMP-39 | CalPA_Set WMP-39 | 6 | CalPA_Set WMP-39_Q6 | Please fill out the attached spreadsheet, CalAdvocates-PGE-2025WMP-03 Attachment 1, requesting information regarding your asset inspections in 2023. | Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_039- Q006Atch01.xlsx” for the requested information. | Holly Wehrman | 2024-03-22 | 2024-04-05 | 2024-04-05 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_039.zip | 1 | N/A | 8 | Section 8.1.3 - Asset Inspection | 8.1.3 Asset Inspections | N/A
Pre-Discovery 68 | CalPA | Set WMP-39 | CalPA_Set WMP-39 | 7 | CalPA_Set WMP-39_Q7 | Please provide a list of any incidents in 2023 where the actions of a VM contractor posed a safety risk to workers and/or the public. “Safety risk” here is defined as any occurrence on a worksite where the contractor's actions created a safety hazard for either workers or the general public. For each instance, please provide: a) The date you were informed of the safety issue b) The date the original work that created the safety issue was performed c) Whether the safety issue concerned a transmission or distribution circuit d) The vegetation management initiative involved in the original work e) A brief description of the safety issue involved. | Please note the attachment to this response contains CONFIDENTIAL information provided pursuant to the accompanying confidentiality declaration. Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_039- Q007Atch01CONF.xlsx” for the requested information. Please note that both Distribution and Transmission contractor incidents are included in the attachment. These records are pulled from the Enterprise Contractor Incident Records Tool (ECIRT) database. | Holly Wehrman | 2024-03-22 | 2024-04-05 | 2024-04-05 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_039.zip | 1 | N/A | 8 | Section 8.2 - Vegetation Management and Inspections | 8.2 Vegetation Management and Inspections | ACI 23-19 Continued Progresion of Vegatation Management Maturity
Pre-Discovery 69 | CalPA | Set WMP-39 | CalPA_Set WMP-39 | 8 | CalPA_Set WMP-39_Q8 | In response to Data Request CalAdvocates-PGE-2023WMP-06, Question 8, March 29, 2023, PG&E provided its 2023 system hardening workplan for the categories referred to in parts (a)-(d) below. Please provide an updated version of this workplan with additional columns to show the actual system hardening work performed in each circuit-segment in 2023 for each of these categories. Please add rows as needed to cover all circuit-segments where PG&E performed system hardening work in 2023 (even if those circuit-segments were not included in the original workplan). a) Installation of covered conductor b) Installation of underground conductor c) Removal of overhead conductor d) Removal of overhead conductor associated with remote grid work. | Please not the attachment to this response contains CONFIDENTIAL information provided pursuant to the accompanying confidentiality declaration. Please see attachment WMP-Discovery2023-2025_DR_CalAdvocates_039- Q008Atch01CONF.xlsx for the requested information. This attachment contains our 2024–2026 System Hardening workplan as well as the projects with completed system hardening work in 2023. The work associated with projects completed in 2023 can be found in the columns noted below: a) Column Y: OH – 2023 Complete Miles. b) Column Z: UG – 2023 Complete Miles. c) Column AA: Removal – 2023 Complete Miles. This includes all line removal projects, including those associated with remote grid work. Additionally, the following three projects listed below are associated with removal of overhead conductor with remote grid work: • Order 35229051 on CPZ Corning 110253184 in Tehama County; • Order 35238088 on CPZ Mariposa 210135244 in Mariposa County; and • Order 35246501 on CPZ Fulton 1107604 in Sonoma County. For further details associated with these projects, please filter column A by the order numbers identified above. | Holly Wehrman | 2024-03-22 | 2024-04-05 | 2024-04-05 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_039.zip | 1 | N/A | 8.1.2.5 | System Hardening | N/A | 2.1.4.1 GH-11 Traditional Overhead Hardening Conductor
Pre-Discovery 70 | CalPA | Set WMP-39 | CalPA_Set WMP-39 | 9 | CalPA_Set WMP-39_Q9 | Provide your workplan that describes where and when you will perform system hardening on distribution circuits in 2025. For projects that you expect to partially complete in 2025 (i.e., projects that started before 2025 and are expected to continue in 2025, or projects that are expected to be completed after 2025), please include the project and describe the work that you forecast will actually be performed in calendar year 2025. For each project, include the following information in separate columns, at a minimum: a) Order number b) MAT code c) Program d) Circuit ID number e) Circuit-segment name or ID number (if the project affects more than one circuit-segment, please identify each one) f) Relevant wildfire risk score(s) from the wildfire risk model that you are using to estimate distribution risk in your 2025 WMP Update filing g) The expected or actual start date of the project h) The expected completion date of the project i) Length (in circuit miles) of covered conductor to be installed in 2025 j) Length (in circuit miles) of underground conductor to be installed in 2025 k) Length (in circuit miles) of overhead conductor to be permanently removed in 2025 and replaced by underground conductor (note that this may differ slightly from the previous section due to differing overhead and underground routes) l) Length (in circuit miles) of overhead conductor to be permanently removed in 2025 and not replaced with covered conductor or undergrounded) m) Length (in circuit miles) of any other type of system hardening project to be installed in 2025 (if this is greater than zero, please describe the type of system hardening project) n) Location-specific undergrounding effectiveness4 o) Location-specific effectiveness of alternative mitigations. | Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_039- Q008Atch01CONF.xlsx” for a list of PG&E’s system hardening projects for the years 2023-2026. Please note that we combined years 2025 and 2026 as the projects associated with each year are still being finalized. The requested information can be found in the following locations: a) See column A (Order). b) See column D (MAT Code). c) See column C (Category). d) See column N (Circuit ID) and column O (Circuit Name). e) See column P (Circuit Protection Zone). f) See column M (Applicable Risk Model) for the risk model used at the time the project was selected for the program and see columns AK-AZ for the current estimated risk reduction values by year and mitigation type based on a project’s applicable risk model. g) See column S (Construction Start Date). This date represents the time construction was initiated on the project, recognizing there are additional phases prior to the construction start (e.g., planning, design, estimating, permitting). As noted above, the 2025-2026 portfolio is still being finalized; therefore, construction start and end dates are placeholders and are subject to change. h) See column T (Est. Construction End). This year represents when the newly installed undergrounded lines are forecasted to be electrified and the project is considered complete. Actual construction end dates may shift through the lifecycle of a project based on project dependencies. As noted above, the 2025-2026 portfolio is still being finalized; therefore, construction start and end dates are placeholders and are subject to change. i) See column AG (OH – 2025-2026 Forecast Miles) for circuit miles of planned overhead hardening in 2025-2026. j) See column AH (UG – 2025-2026 Forecast Miles) for circuit miles of planned undergrounding in 2025-2026. k) This information is not provided in this response because PG&E currently does not have complete tabular data to provide the total overhead circuit-miles removed relating to the undergrounding project. This information is actively being consolidated and will be available in PG&E’s System Hardening Accountability Report in accordance with the requirements of GRC D.23-11-069 (OP 20–23). l) See column AI (Removal – 2025-2026 Forecast Miles) for circuit miles of planned line removal in 2025-2026. m) Not applicable. n) PG&E does not calculate location-specific undergrounding effectiveness. As described in PG&E’s 2023-2025 WMP R4 (pages 418-419), the undergrounding effectiveness is 97.7%. o) Not applicable. PG&E will provide the location-specific effectiveness scores using the Wildfire Benefit Cost Analysis (WBCA) tool that is under development for our SB884 10 Year Undergrounding Plan. This information will be used for projects planned for completion in 2027 and beyond. | Holly Wehrman | 2024-03-22 | 2024-04-05 | 2024-04-05 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_039.zip | 0 | N/A | 8.1.2.5 | System Hardening | N/A | 2.1.4.1 GH-11 Traditional Overhead Hardening Conductor
Pre-Discovery 71 | CalPA | Set WMP-39 | CalPA_Set WMP-39 | 10 | CalPA_Set WMP-39_Q10 | For each of your 2023-2025 WMP system hardening initiatives, please provide disaggregated information related to expenditures and circuit miles treated in the attached table, CalAdvocates-PGE-2023WMP-03 Attachment 2. Add columns as needed. | Circuit Miles: Please see Table 1 below for PG&E’s system hardening circuit miles for the years 2023-2025. Provided are both the target miles and the actual or projected miles for each year. Please note that while the current System Hardening workplan (WMP initiative GH-01) includes planned miles exceeding the annual targets for 2024 and 2025 to account for project dependencies and construction issues that may arise and delay some projects, PG&E intends to manage the system hardening portfolio to meet or nearly exceed the target miles. Therefore, the projected miles included below for 2024 and 2025 are equivalent to the targets. Additionally, the 2023 actual miles have been separated by MAT codes: • 08W/3UG: System Hardening projects funded by the GRC WMBA. • Non-08W/3UG: System Hardening projects in an HFTD that are funded by other programs outside of the GRC Wildfire Mitigation Balancing Account (WMBA) (e.g., work requested by others (WRO), idle facilities, Rule 20). Expenditures: Please see Table 2 below for costs related to 2023-2025 system hardening. Table 1: 2023-2025 Target, Actual, and Projected System Hardening Circuit Miles (WMP Initiative GH-01) Total Line Removal Relocation of Overhead to Undergrounda Overhead Hardening (Covered Conductor) Other Target Actual/ Projecteda Target Actual/ Projecteda Target Actual/ Projecteda Target Actual/ Projecteda Target Actual/ Projecteda 2023 circuit miles (actual) - 08W/3UGb 420 424.7 10 7.1 280 284.8 130 132.8 0 0 2023 circuit miles (actual) – Non-08W/3UGb N/A 21.8 N/A 5.7 N/A 4.1 N/A 12 N/A 0 2024 circuit miles (projected)c 280 280 10 10 210 210 60 60 0 0 2025 circuit miles (projected)c 520 520 10 10 310 310 200 200 0 0 ______________________________________________ (a) Included here are the System Hardening costs associated with WMP Initiative GH-01; therefore, undergrounding costs do not include Butte Community Rebuild. (b) The data for 2023 actuals is as of January 9, 2024. (c) While the current System Hardening workplan (WMP initiative GH-01) includes planned miles exceeding the annual targets for 2024 and 2025 to account for project dependencies and construction issues that may arise and delay some projects, PG&E intends to manage the system hardening portfolio to meet or nearly exceed the target miles. Therefore, the projected miles for 2024 and 2025 are equivalent to the targets. Table 2: 2023-2025 Actual and Projected System Hardening Costs ($ thousands) Total Line Removala Relocation of Overhead to Undergroundb Overhead Hardening (Covered Conductor) Other 2023 expenditures (actual)c $1,095,110 $15,378 $954,702 $125,029 - 2024 expenditures (projected)d,e $944,000 - $833,000 $111,000 - 2025 expenditures (projected)d,e,f $1,408,091 - $1,166,453 $241,638 - ______________________________________________ (a) Projected costs associated with line removal will be managed within the overhead hardening cost forecasts. Actual expenditures in 2023 are included and will be reported as they are realized. (b) Included here are the System Hardening costs associated with WMP Initiative GH-01; therefore, undergrounding costs do not include Butte Community Rebuild. (c) The data for 2023 actuals is as of January 9, 2024. (d) The projected values for 2024 and 2025 are based on target (not forecasted) miles and include readiness costs for projects in 2024-2026. (e) The updated financial forecasts provided above for 2024 and 2025 have not been updated in PG&E's QDR. These updated forecasts will not be reflected in the QDR unless the respective change order or update proceeding has been approved, in alignment with WMP guidelines. (f) Data for 2025 projections are based on PG&E’s 2025 WMP Update (https://www.pge.com/assets/pge/docs/outages-and-safety/outagepreparedness-and-support/pge-wmp-r0-update-040224.pdf), see B.2.2.1 Table of Expenditure Changes (pg. 29); however, this excludes Butte Community rebuild expenditures given these are separate from the System Hardening program. | Holly Wehrman | 2024-03-22 | 2024-04-05 | 2024-04-05 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_039.zip | 0 | N/A | 8.1.2.5 | System Hardening | N/A | 2.1.4.1 GH-11 Traditional Overhead Hardening Conductor
Pre-Discovery 72 | CalPA | Set WMP-39 | CalPA_Set WMP-39 | 11 | CalPA_Set WMP-39_Q11 | On page 406 of PG&E’s 2023-2025 WMP R4, January 8, 2024, PG&E provided Table PG&E-8.1.2-3, shown below. Please provide an updated version of this table (preferably in Excel format) with actuals from 2023 and updated estimates for 2024, 2025, and 2026. | Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_039- Q011Atch01.xlsx” for an updated version of the requested table as of February 22, 2024. As described in response to CalAdvocates_039-Q09, PG&E combined years 2025 and 2026 because the construction timelines associated with these projects are still being finalized. | Holly Wehrman | 2024-03-22 | 2024-04-05 | 2024-04-05 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_039.zip | 1 | N/A | 8.1.2.5 | System Hardening | N/A | 2.1.4.1 GH-11 Traditional Overhead Hardening Conductor
Pre-Discovery 73 | CalPA | Set WMP-39 | CalPA_Set WMP-39 | 12 | CalPA_Set WMP-39_Q12 | On October 3, 2023, the Wildfire Safety Advisory Board held a meeting. Four documents related to PG&E’s ground-level distribution system pilot are listed in the meeting materials (see https://energysafety.ca.gov/events-and-meetings/events/wildfire-safety-advisory-board-meeting-10-2-2023/). Please provide confidential (i.e., unredacted) copies of these four documents: a) Experimental Installation Letter b) Project Pilot Scope c) Product Information d) Pilot Construction Sketch | a) Please see attachment WMP-Discovery2023-2025_DR_CalAdvocates_039- Q012Atch01CONF.pdf for the Experimental Installation Letter. b) Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_039- Q012Atch02CONF.pdf” for the GLDS Project Pilot Scope. c) Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_039- Q012Atch03.pdf” for the GLDS Product Information. d) Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_039- Q012Atch04CONF.pdf” for our most recent Pilot Construction Sketch. Please note that the GLDS Pilot Construction Sketch includes redlines which reflect updates to the GLDS Project. Additionally, please note that these attachments contain confidential information. | Holly Wehrman | 2024-03-22 | 2024-04-05 | 2024-04-05 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_039.zip | 4 | N/A | 8.1.2.5 | System Hardening | N/A | 2.1.4.1 GH-11 Traditional Overhead Hardening Conductor
Pre-Discovery 74 | CalPA | Set WMP-39 | CalPA_Set WMP-39 | 13 | CalPA_Set WMP-39_Q13 | Identify any ignitions in 2023 associated with assets where you had an existing corrective notification at the time of the ignition. Please provide a spreadsheet listing each such ignition (as rows) with the following information in separate columns: a) Unique ignition ID b) Date of ignition c) Cause of ignition d) Type of asset associated with the ignition e) Acres burned f) Number of structures burned, if any g) Number of injuries associated with ignition, if any h Asset ID of asset associated with ignition i) Circuit ID number of circuit associated with ignition j) Notification number(s) for the existing maintenance tag on the asset in question. | Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_039- Q013Atch01.xlsx” for a list of CPUC-reportable ignitions that occurred in 2023 where the closest support structure has an open corrective notification at the time of the ignition event. | Holly Wehrman | 2024-03-22 | 2024-04-05 | 2024-04-05 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_039.zip | 1 | N/A | 8 | Section 8.3 - Situational Awareness and Forecasting | 8.3.4.1 Existing Ignition Detection Sensors and Systems | ACI 23-25 Fire Potential Index and Ignition Probability Weather Enhancements
Pre-Discovery 75 | CalPA | Set WMP-39 | CalPA_Set WMP-39 | 14 | CalPA_Set WMP-39_Q14 | a) Has PG&E’s Asset Failure Analysis Team causally connected any ignitions that occurred in 2023 to assets with existing asset or vegetation corrective notifications at the time of ignition? b) If the answer to part (a) is yes, please provide the following information for each such ignition: i. Unique ignition ID (matching the previous question) ii. Date of ignition iii. Cause(s) identified by the Asset Failure Analysis Team iv. The type of corrective notification that was linked to the ignition (i.e., the priority level and whether it related to asset management or vegetation management). v. Copies of associated reports or investigations performed by the Asset Failure Analysis Team. | Please note the attachments to this response contain CONFIDENTIAL information provided pursuant to the accompanying confidentiality declaration. a) Yes, PG&E has connected ignitions that occurred in 2023 to assets with existing asset or vegetation corrective notifications at the time of ignition. b) Please see the table below for links to the requested information. Ignition ID Ignition Date Apparent Cause(s) Corrective Notification (Type and Description) Attachment Name 20230175 3/1/23 Wire down due to potential re-test and conductor fatigue failure EC Notification 121485810 (E Priority): Vibration dampener falling off WMP-Discovery2023- 2025_DR_CalAdvocates_039- Q014Atch01CONF.pdf 20231057N 9/15/23 3rd party fence touching steel pole ignited a small brush fire. LC Notification 125508471 (E Priority): Encroachment – fence too close. Please note, Notification 123913712 is included in PG&E’s response to Q013 of this request, for this Ignition ID, however, is not identified as being causally connected to the ignition. WMP-Discovery2023- 2025_DR_CalAdvocates_039- Q014Atch02CONF.pdf 20230148 2/21/2023 Connector failure - wire down EC Notification 116872537 (E Priority): Secondary connector on primary jumper WMP-Discovery2023- 2025_DR_CalAdvocates_039- Q014Atch03CONF.pdf 20230700 7/15/2023 Gray AWAC Service Drop at PG Connector veg contact EC Notification 124052678 (E Priority): Strain/Abrasion on the AWAC between the two poles Please note, Notification 117191710 is included in PG&E’s response to Q013 of this request, for this Ignition ID, however, is not identified as being causally connected to the ignition. WMP-Discovery2023- 2025_DR_CalAdvocates_039- Q014Atch04CONF.pdf | Holly Wehrman | 2024-03-22 | 2024-04-05 | 2024-04-05 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_039.zip | 4 | N/A | 8 | Section 8.3 - Situational Awareness and Forecasting | 8.3.4.1 Existing Ignition Detection Sensors and Systems | ACI 23-25 Fire Potential Index and Ignition Probability Weather Enhancements
Pre-Discovery 75 | CalPA | Set WMP-39 | CalPA_Set WMP-39 | 14(a) | CalPA_Set WMP-39_Q14(a) | a) Has PG&E’s Asset Failure Analysis Team causally connected any ignitions that occurred in 2023 to assets with existing asset or vegetation corrective notifications at the time of ignition? b) If the answer to part (a) is yes, please provide the following information for each such ignition: i. Unique ignition ID (matching the previous question) ii. Date of ignition iii. Cause(s) identified by the Asset Failure Analysis Team iv. The type of corrective notification that was linked to the ignition (i.e., the priority level and whether it related to asset management or vegetation management). v. Copies of associated reports or investigations performed by the Asset Failure Analysis Team. | Please note the attachments to this response contain CONFIDENTIAL information provided pursuant to the accompanying confidentiality declaration. a) Yes, PG&E has connected ignitions that occurred in 2023 to assets with existing asset or vegetation corrective notifications at the time of ignition. b) Please see the table below for links to the requested information. Ignition ID Ignition Date Apparent Cause(s) Corrective Notification (Type and Description) Attachment Name 20230175 3/1/23 Wire down due to potential re-test and conductor fatigue failure EC Notification 121485810 (E Priority): Vibration dampener falling off WMP-Discovery2023- 2025_DR_CalAdvocates_039- Q014Atch01CONF.pdf 20231057N 9/15/23 3rd party fence touching steel pole ignited a small brush fire. LC Notification 125508471 (E Priority): Encroachment – fence too close. Please note, Notification 123913712 is included in PG&E’s response to Q013 of this request, for this Ignition ID, however, is not identified as being causally connected to the ignition. WMP-Discovery2023- 2025_DR_CalAdvocates_039- Q014Atch02CONF.pdf 20230148 2/21/2023 Connector failure - wire down EC Notification 116872537 (E Priority): Secondary connector on primary jumper WMP-Discovery2023- 2025_DR_CalAdvocates_039- Q014Atch03CONF.pdf 20230700 7/15/2023 Gray AWAC Service Drop at PG Connector veg contact EC Notification 124052678 (E Priority): Strain/Abrasion on the AWAC between the two poles Please note, Notification 117191710 is included in PG&E’s response to Q013 of this request, for this Ignition ID, however, is not identified as being causally connected to the ignition. WMP-Discovery2023- 2025_DR_CalAdvocates_039- Q014Atch04CONF.pdf | Holly Wehrman | 2024-05-15 | 2024-05-16 | 2024-05-16 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_039.zip | 4 | N/A | N/A | Section 8.3 - Situational Awareness and Forecasting | 8.3.4.1 Existing Ignition Detection Sensors and Systems | ACI 23-25 Fire Potential Index and Ignition Probability Weather Enhancements
Pre-Discovery 76 | CalPA | Set WMP-39 | CalPA_Set WMP-39 | 15 | CalPA_Set WMP-39_Q15 | On page 548 of PG&E’s 2023-2025 WMP R4, January 8, 2024, PG&E stated that it was revising its field safety reassessment procedure (TD-8123P-200) and expected to publish the revised procedure by the end of 2023. a) Has PG&E published the revised TD-8123P-200 procedure? b) If the answer to part (a) is yes, briefly describe the substance of the changes to the procedure. c) If the answer to part (a) is yes, please provide a copy of the updated version of TD-8123P-200. d) If the answer to part (a) is no, please explain the delay. e) If the answer to part (a) is no, please state when PG&E currently expects to published the revised TD-8123P-200 procedure. | Please note the attachment to this response contains CONFIDENTIAL information provided pursuant to the accompanying confidentiality declaration. a) Yes, PG&E published the revised TD-81239-200 procedure on December 29, 2023. b) Per the response to “DRU11767_1_Citation_Corrective Action Compliance - Follow Up - Brewer Fire.pdf”, submitted to the CPUC on February 9, 2024, the TD-8123P200 procedure was updated to reflect: i. Neither Pole Test & Treat (PT&T) nor Infrared (IR) Electric Corrective (EC) notifications require a Field Safety Reassessment (FSR). ii. Quality control (QC) review to remove any PT&T or IR inspections from FSR list. iii. A mid-year validation process to check for cancellation of notifications created by either PT&T or IR inspections. iv. SAP and Inspect App enhancements allowing inspectors to note that additional asset health conditions have been identified in the field so that tags that require updates are flagged for review. c) Please see attachment “WMP-Discovery2023-2025_DR_CalAdvocates_039- Q015Atch01CONF.pdf” for the requested information. Please note that this attachment contains confidential information. d) Not applicable. e) Not applicable. | Holly Wehrman | 2024-03-22 | 2024-04-05 | 2024-04-05 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_039.zip | 1 | N/A | 8 | Section 8.1.7 - Open Work Orders | 8.1.7.2 Open Work Orders - Distribution Tags | ACI PG&E-23-12 -Distribution Backlog Open Tag Reduction Targets
Pre-Discovery 77 | CalPA | Set WMP-39 | CalPA_Set WMP-39 | 16 | CalPA_Set WMP-39_Q16 | In response to data request CalAdvocates-PGE-2023WMP-19 question 15, April 28, 2023, PG&E stated that it was actively analyzing the effectiveness of both covered conductor and bare conductor in combination with EPSS and DCD/PV. PG&E stated that it anticipated completing this analysis in 2023. a) Has PG&E completed the analysis mentioned above? b) If the answer to part (a) is yes, please provide a copy of any reports or other output from the analysis. c) If the answer to part (a) is no, please explain the delay. d) If the answer to part (a) is no, please state when PG&E currently expects to complete this analysis. | a) No. The initial analysis has been drafted but is not yet complete. b) Not applicable. c) PG&E is still internally validating the results for quality review in preparation for the SB 884 10 Year Undergrounding Plan. d) This analysis will be included in our SB 884 10-year undergrounding plan, which is expected to be filed later this year. The timing of the filing, however, is dependent on when we receive the necessary guidelines from Energy Safety. | Holly Wehrman | 2024-03-22 | 2024-04-05 | 2024-04-05 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_039.zip | 0 | N/A | 8.1.2 | Grid Design and System Hardening | Various | ACI 23-08 Covered Conductor Inspection and Maintenance
Pre-Discovery 78 | CalPA | Set WMP-39 | CalPA_Set WMP-39 | 17 | CalPA_Set WMP-39_Q17 | In response to data request CalAdvocates-PGE-2023WMP-27 question 5, August 18, 2023, PG&E stated that it expected to complete its Substation Animal Abatement Effectiveness Study in partnership with Electric Power Research Institute by Q1 of 2024. a) Has PG&E completed the Substation Animal Abatement Effectiveness Study? b) If the answer to part (a) is yes, please provide a copy of any reports or other output from the Substation Animal Abatement Effectiveness Study. c) If the answer to part (a) is no, please explain the delay. d) If the answer to part (a) is no, please state when PG&E currently expects to complete the Substation Animal Abatement Effectiveness Study. | a) No, PG&E has not yet completed the Substation Animal Abatement Effectiveness Study being conducted in partnership with the Electric Power Research Institute (EPRI). b) Not applicable. c) At the end of January 2024, EPRI requested more data and a deadline extension of six months in order to complete their work on the study. d) PG&E currently hopes to have the EPRI Substation Animal Abatement Effectiveness report by end of July 2024, based on EPRI’s request for an extension of time. | Holly Wehrman | 2024-03-22 | 2024-04-05 | 2024-04-05 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_039.zip | 0 | N/A | 8.1.2.12.2 | Grid Design and System Hardening | Other Technologies and Systems – Substation Animal Abatement | ACI 23-07 – Deployment of New Technologies
Pre-Discovery 79 | CalPA | Set WMP-39 | CalPA_Set WMP-39 | 18 | CalPA_Set WMP-39_Q18 | In response to data request CalAdvocates-PGE-2023WMP-27 question 6, August 18, 2023, PG&E stated that it was finalizing a study to assess the recorded reliability improvements at locations that have been undergrounded and/or have been hardened with covered conductor. PG&E stated that it anticipated completing this analysis in October of 2023. a) Has PG&E completed the study mentioned above? b) If the answer to part (a) is yes, please provide a copy of any reports or other output from the study. c) If the answer to part (a) is no, please explain the delay. d) If the answer to part (a) is no, please state when PG&E currently expects to complete this study. | a) No. The initial analysis has been drafted but is not yet complete. b) Not applicable. c) PG&E is still internally validating the results for quality review in preparation for the SB 884 10 Year Undergrounding Plan. d) This analysis will be included in our SB 884 10-year undergrounding plan, which is expected to be filed later this year. The timing of the filing, however, is dependent on when we receive the necessary guidelines from Energy Safety. | Holly Wehrman | 2024-03-22 | 2024-04-05 | 2024-04-05 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_039.zip | 0 | N/A | Appendix D | Appendix D - Areas for Continued Improvement | Appendix D ACI PG&E-22--16 Progress and Updates on Undergrounding and Risk Prioritization | 2.1.1.2 GH-04 Undergrounding
Pre-Discovery 80 | CalPA | Set WMP-39 | CalPA_Set WMP-39 | 19 | CalPA_Set WMP-39_Q19 | In response to data request CalAdvocates-PGE-2023WMP-29 question 5, September 27, 2023, PG&E stated that it expected to publish its 2023 Electric Asset Management Plan by the end of 2023. a) Has PG&E completed the 2023 Electric Asset Management Plan? b) If the answer to part (a) is yes, please provide a copy of the 2023 Electric Asset Management Plan. c) If the answer to part (a) is no, please explain the delay. d) If the answer to part (a) is no, please state when PG&E currently expects to publish the 2023 Electric Asset Management Plan. | a) PG&E is working on completing final updates to the 2023 Electric Asset Management Plan and tentatively plans to publish this document in June 2024. PG&E will provide the completed document once it is finalized and published. b) Not applicable. c) The 2023 Electric Asset Management Plan has been reviewed and approved by PG&E leadership. However, the document is still going through the technical writer formatting and processing, along with the other functional areas’ asset management plans. d) PG&E tentatively expects to publish the 2023 Electric Asset Management Plan in June 2024. | Holly Wehrman | 2024-03-22 | 2024-04-05 | 2024-04-05 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_039.zip | 0 | N/A | N/A | N/A | N/A | N/A
Pre-Discovery 80 | CalPA | Set WMP-39 | CalPA_Set WMP-39 | 19(s) | CalPA_Set WMP-39_Q19(s) | In response to data request CalAdvocates-PGE-2023WMP-29 question 5, September 27, 2023, PG&E stated that it expected to publish its 2023 Electric Asset Management Plan by the end of 2023. a) Has PG&E completed the 2023 Electric Asset Management Plan? b) If the answer to part (a) is yes, please provide a copy of the 2023 Electric Asset Management Plan. c) If the answer to part (a) is no, please explain the delay. d) If the answer to part (a) is no, please state when PG&E currently expects to publish the 2023 Electric Asset Management Plan. | a) Please see “WMP-Discovery2023-2025_DR_CalAdvocates_039-Q019Supp01Atch01CONF.pdf” for the completed 2023 Electric Asset Management Plan. | Holly Wehrman | 2024-03-22 | 2024-06-21 | 2024-06-18 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_039.zip | 1 | N/A | N/A | N/A | N/A | N/A
Pre-Discovery 81 | CalPA | Set WMP-39 | CalPA_Set WMP-39 | 20 | CalPA_Set WMP-39_Q20 | In response to data request CalAdvocates-PGE-2023WMP-29 question 6, September 27, 2023, PG&E stated the following: “We will evaluate the history of response to wire down conditions in the HFRA/HFTD, occurring during the traditional peak wildfire season of [between] May 1 and November 1, going back to 2020. We can complete that analysis by December 31, 2023.” a) Has PG&E completed the analysis mentioned above? b) If the answer to part (a) is yes, briefly describe your findings. c) If the answer to part (a) is yes, please provide a copy of any reports or other output from the analysis. d) If the answer to part (a) is no, please explain the delay. e) If the answer to part (a) is no, please state when PG&E currently expects to complete this analysis. | a) PG&E has not yet completed its evaluation. PG&E is currently evaluating outages in High Fire Risk Areas (HFRA) / High Fire Threat District (HFTD) areas with wire down conditions during peak wildfire season between May 1 and November 1 at this time. b) Not applicable, please see the response to subpart (a). c) Not applicable, please see the response to subpart (a). d) The HFRA / HFTD Wire-Down Outage Response time analysis has been delayed due to resource constraints driven by the extended 2023 wildfire season and the 2024 wildfire season planning activities. e) PG&E expects to complete the analysis by May 2024. | Holly Wehrman | 2024-03-22 | 2024-04-05 | 2024-04-05 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_039.zip | 0 | N/A | 8.2.3.4 | Vegetation Management and Inspections | Fall-In Mitigation | ACI 23-19 Continued Progresion of Vegatation Management Maturity
754 | CalPA | 058 | CalPA_058 | 1 | CalPA_058_Q1 | Attachment One of this data request contains a subset of transmission projects identified in PG&E’s Transmission Project Review (TPR) data as “a measure identified in the Wildfire Mitigation Plan”.1 Please provide an updated version of attachment one with additional columns containing the following information: • Wildfire Mitigation Plan (WMP) in which measure was identified (e.g. PG&E’s 2021WMP, 2022 WMP, etc.); • WMP initiative this project is related to; • Cost recovery venue (include applicable CPUC or FERC docket number); • Current status of project (complete, in progress, deferred, etc.); • Pre-mitigated risk of project per PG&E’s Wildfire Transmission Risk Model; • Forecast post-mitigated risk of project per PG&E’s Wildfire Transmission Risk Model; • Actual post-mitigated risk of project per PG&E’ Wildfire Transmission Risk Model (if project completed); • Total risk points reduced per PG&E’s Wildfire Transmission Risk Model; • Benefit-Cost Ratio (BCR) of the project; and • Cost impact on monthly bill for a typical residential non-CARE customer. | Attachment 1 is a subset of projects in the Public version of PG&E’s May 2024 TPR Project Spreadsheet. Each of these projects was flagged as TRUE for measures identified in the Wildfire Mitigation Plan in Data Field 17 (Wildfire Related). PG&E has 1 PG&E 2024 TPR data submission, May 1st, 2024. Available at: “https://pgera.azurewebsites.net/Regulation/ValidateDocAccess?docID=792173. WMP-Discovery2023-2025_DR_CalAdvocates_058-Q001 Page 2 provided the following language for mapping WMP programs to TPR projects for Data Field 17: “Replacement and/or upgrades of transmission line assets for Projects in programs as defined in PG&E’s Wildfire Mitigation Plan (MWC 60, 70, 71, 82, 92, 93, and 94) with an in-service date of 2019 or later and assets with Fire Threat Tiers 2 or 3 or Zone 1 were designated as Wildfire Mitigation Plan. A small subset of MWC 2F and 65 Projects were designated as WMP on a project basis.” Please note that Data Field 17 in TPR Project Spreadsheet is a mapping of WMP programs to unique projects. Please see the updated November 2024 TPR Project Spreadsheet, “WMPDiscovery2023-2025_DR_CalAdvocates_058-Q001Atch01.xlsx”, along with the corresponding Transmittal Letter, “WMP-Discovery2023-2025_DR_CalAdvocates_058- Q001Atch02.pdf”. All projects in the TPR PS are FERC jurisdictional. Data Field 66 (Cost-Benefit Analysis) states that PG&E is still in process of evaluating and developing the value framework and reviewing Cost Benefit Ratios (CBRs) for transmission projects. At this time, PG&E cannot provide pre-mitigated risk, post-mitigated risk, and risk points at a project level that can be used to inform prioritization or represents the true total benefits of the projects. PG&E continues to develop its Transmission project framework and hopes to have refreshed CBRs for the November 2025 TPR submission. Columns “WMP Version” and “WMP Initiative” were added to the TPR spreadsheet to address bullets 1 & 2 of Question No. 001. Per the above, mapping for the TPR to the WMP section was done at a financial grouping level, and not per individual line item. For WMP targets, individual investments may be identified. We do not have the cost impact on monthly bills for a typical residential non-CARE customer information readily available and thus do not have information readily available to provide on this item. | Miles Gordon | 2025-04-08 | 2025-04-22 | 2025-04-22 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_058.zip | 2 | N/A | 8 | 8.1.2.4 | 8.1.2.4 | Transmission Pole/Tower Replacements and Reinforcements
755 | CalPA | 058 | CalPA_058 | 2 | CalPA_058_Q2 | Please fill out the following table with information regarding PG&E’s total forecast and actual capital expenditures for its wildfire-related transmission projects for 2018 through 2024: | PG&E is populating the above table based solely on the projects provided in “WMPDiscovery2023-2025_DR_CalAdvocates_058-Q001Atch01.xlsx” of this data request. For “forecast wildfire transmission capital expenditures” in the table above, PG&E provides the total forecast capital expenditures from the Transmission Owner Rate Case filing listed in “cost recover venue” column relative to the subset of transmission projects identified in Attachment One from Question No. 001 above. The forecast costs only include the amounts forecast in the rate year of the listed Transmission Owner filing. Actual wildfire transmission capital expenditures are a summation of projects provided in “WMP-Discovery2023-2025_DR_CalAdvocates_058-Q001Atch01.xlsx” based on an April 14, 2025 data pull. These actuals may vary with prior TPR submissions as those pulls were pulled on various prior dates. “Actual wildfire transmission capital expenditures” are total project expenditures, whereas “forecast wildfire transmission capital expenditures” are only expenditures forecast in the respective Rate Year, as described in the paragraph above. | Miles Gordon | 2025-04-08 | 2025-04-22 | 2025-04-22 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/CalAdvocates_058.zip | 0 | N/A | 4 | 4.3 | 4.3 | Proposed Expenditures
| CPUC - SPD (Safety Policy Division) | 014 | CPUC - SPD (Safety Policy Division)_014 | 005Rev3 | CPUC - SPD (Safety Policy Division)_014_Q005Rev3 | Provide number of A, B, X, E, F for Aerial, Ground and Pole Test and Treat finds during inspections in 2023, and 2024 broken down by HFTD and non‐HFTD. Include number of inspections and find rate for each tag type. Submit the same information in the same format as Table RN‐PG&E‐23‐04‐7 (attached in email) for 2023 and 2024 from PG&E’s 2023‐2025 Wildfire Mitigation Plan Supplemental Response to Revision Notice, except provide the actual tag finds, rather than “Forecast Tag Finds.” Indicate if helicopters or planes were used for any of the aerial inspections. | 1. Inspection count data is pulled from our inspection attainment reports. Inspection totals reflect only those where the asset was accessed; “CGI” inspections are excluded. 2. PTT inspection HFRA/Non-HFRA locations reflect current designations of assets, not the designation at time of inspection. 3. Priority A notifications include major and routine emergency. Please note that the Ground A-Priority notification count from 2023 adds to 4,823, which is slightly higher than 4,817 (the value previously reported in WMP 2026-2028 Discovery SPD_014- Q002). Five notifications were removed from the previous total because they were generated by other programs. Eleven notifications were added to the previous total because they were generated by Ground Inspections but lacked corresponding identification in SAP. 4. Aerial emergency tags include notifications identified in the field and during desktop inspection. The notifications are in SAP but not identified as from aerial inspection in SAP. “Refer to table in data request response” as public versions of DR responses will have the initial question and response tables. |  | 2024-05-28 | 2025-09-28 | 2025-09-28 | https://www.pge.com/assets/pge/docs/outages-and-safety/outage-preparedness-and-support/SPD_014.zip