## Sheet2
IR | IR
Notification User Status | (Multiple Items)
Count of Notification No | Column Labels
Row Labels | B | Grand Total |  | Tier | Cycle | Inspect Miles
T0 | 53 | 53 | T0 | 55300 | 10 | 5530
T2 | 6 | 6 | T2 | 18310 | 3 | 6103.3333
T3 | 6 | 6 | T3 | 7100 | 3 | 2366.6667
UNK. No SAP ID | 1 | 1 | Total | 25410 |  | 14000
ZONE 1 | 1 | 1 |  |  | cost per mile | 155
Grand Total | 67 | 67 |  |  | total cost | 2170000
[5 empty] | cost in HFTD | 1312850
Cost/Benefit Analysis
B tag failure estimate | 50%
Total potential failures avoided | 33.5
Outage Cost | 5000 | <-- RAMP Filing
Outage to Ignition Cost | 91000 | <-- RAMP Filing
Outage Cost Saving | 96000
Avoided Failures Cost Saving | 3216000
Cost of Program | -2170000
Cost Benefit | 1046000
IR Inspection OH Mile | 14000
Cost Benefit / Inspection OH Mile | 74.7143

## Sheet1
Tier | IR | Div | Work Center Text | Notification No | Notification type | Work Type Code | Order | MaintActivityType | Order User Status | Priority | Sub Priority | Notification User Status | Required End | Funded Repair Date | Object Code text | Damage Code text | Activity Code text | Description | Notification Sytem Status | Functional Location | Plat Map | Circuit | Source Side Device | Technical identification no. | Equipment | Latitude | Longitude | Street | City | Gate Keeper | GateKeeper Date | Code group | Reported by | Notification date | Created By | Created On | Reference date | Completed On | Completed By | Completion by date | Item | Notification Tracking | Recommended Priority | County Code | Status
T0 | IR | SA | Vacaville | 119836621 | S9 | 511 |  |  |  | E |  | POHW OH CNCL ESTR PROG TER0 | 2021-09-22 |  | Transformer | Broken/Damaged | Replace | TRAN_BROK_REPL - 3 W\O 5887 HAY RD. VACA | NOCO ATCO | ED.48-R150000000.STRU.POLE | R15 | 06364-2105, PEABODY | 9641 |  | 101663157 | 38.3153 | -121.875 | 3 W\O 5887 HAY RD. | VACAVILLE | GJME | 2020-10-01 | ECFOH | BODENHAMER | 2020-09-22 | LMMY | 2020-10-01 | 2020-10-01 |  |  | 2020-10-01 | 1 |  | E | 048
T0 | IR | SA | Vacaville | 119836627 | EC | 540 | 44485175 | KAA | UNSC srdy | B |  | RELW OH TER0 | 2020-12-21 |  | Cutout | Broken/Damaged | Replace | CUTO_BROK_REPL - 346 EAST TRAVIS BLVD FA | NOPR ORAS ATCO | ED.48-S111700000.STRU.POLE | S1117 | 06213-1102, SUISUN | 9439 | 120195390 | 103926844 | 38.2583 | -122.0311 | 346 EAST TRAVIS BLVD | FAIRFIELD | J6AG | 2020-10-01 | ECFOH | JOINER | 2020-09-21 | LMMY | 2020-10-01 | 2020-09-21 |  |  |  | 2 | NAV3 1/2 CNCL DUP EC | E | 048
T0 | IR | SA | Vacaville | 119836885 | EC | 540 | 44485177 | KAA | DOCC srdy | B |  | RELW OH COMP CPGE PROG CPGD TER0 | 2020-10-22 |  | Riser/Pothead | Broken/Damaged | Replace | RISE_BROK_REPL - W/S SUNSET AVE. S/O TRA | ORAS NOCO ATCO | ED.48-S111800000.STRU.POLE | S1118 | 06213-1105, SUISUN | 8773 |  | 101559889 | 38.2571 | -122.0201 | W/S SUNSET AVE. S/O TRAVIS BLVD. N/O RAILROAD AVE. | FAIRFIELD | J6AG | 2020-10-01 | ECFOH | JOINER | 2020-09-22 | LMMY | 2020-10-01 | 2020-12-23 | 2020-12-23 | KRT0 | 2020-12-24 | 1 |  | B | 048
T0 | IR | ST | Manteca | 119871302 | EC | 511 | 35206395 | 2AA | DOCC | B |  | RELW OH CNCL ESTR OTRG PROG CPGD TER0 | 2020-11-01 |  | Capacitor | Broken/Damaged | Replace | CAPR_BROK_REPL - 703 E WILLIAMSON RD. MA | ORAS NOCO ATCO | ED.93-Y102300000.STRU.POLE | Y1023 | 16270-1707, VIERRA | 14197 | 110453175 | 103568649 | 37.7735 | -121.2984 | 703 E WILLIAMSON RD. | MANTECA | J6AG | 2020-10-09 | ECFOH | CHAMBERS | 2020-10-01 | LMMY | 2020-10-08 | 2020-12-22 |  |  | 2020-12-22 | 2 |  | B | 039
T0 | IR | ST | Stockton | 119871893 | EC | 511 | 35206435 | 2AA | MAPP srdy | B |  | RELW OH COMP ESTR CPGE PROG CPGD TER0 | 2020-10-30 |  | Transformer | Leaks/Seeps/Weeps | Replace | TRAN_SEEP_REPL - ACCESS ROAD NEAR 21348 | ORAS NOCO NOPT ATCO | ED.91-X170000000.STRU.POLE | X17 | 16357-1701, AVENA | D1317 | 120375521 | 102105192 | 37.8452 | -121.0356 | ACCESS ROAD NEAR 21348 AVENA RD | STOCKTON | J6AG | 2020-10-09 | ECFOH | ARAUJO | 2020-09-30 | LMMY | 2020-10-08 | 2020-12-08 | 2020-12-08 | ACD7 | 2020-12-10 | 2 | CMPLT 12/8 ACD7 IN 12/9 | B | 039
T0 | IR | ST | Stockton | 119872021 | EC | 605 | 31515785 | 2AA | MAPP srdy | B |  | RELW OH COMP CCNT TER0 | 2020-12-29 |  | Cutout | Broken/Damaged | Replace | CUTO_BROK_REPL - 0.2 MI W/O N99 FRONTAGE | ORAS NOCO ATCO | ED.93-PP11080000.STRU.POLE | PP1108 | 16211-1102, LODI | D3185 | 120402702 | 103569929 | 38.2039 | -121.269 | 0.2 MI W/O N99 FRONTAGE AND E JAHANT RD I/F/O LODI | ACAMPO | J6AG | 2020-10-09 | ECFOH | BUENROSTRO | 2020-09-29 | LMMY | 2020-10-08 | 2020-12-18 | 2020-12-18 | CONT | 2020-12-24 | 1 |  | B | 039
T0 | IR | SA | Vacaville | 119872806 | EC | 540 | 44586968 | KAA | DOCC srdy | B |  | RELW OH COMP CPGE CPGD TER0 | 2020-12-28 |  | Cutout | Broken/Damaged | Repair | CUTO_BROK_REPA - 101 FOOTHILL DR. SWC/O | ORAS NOCO NOPT ATCO | ED.48-Q111500000.STRU.POLE | Q1115 | 06360-1108, VACAVILLE | 11507 | 0 | 101570040 | 38.358 | -122.0114 | 101 FOOTHILL DR. SWC/O FOOTHILL DR & MONTE VISTA A | VACAVILLE | J6AG | 2020-10-09 | ECFOH | WILSON | 2020-09-28 | LMMY | 2020-10-08 | 2020-11-30 | 2020-11-30 | RFSI | 2020-12-14 | 1 |  | B | 048
T2 | IR | SA | Vacaville | 119872934 | EC | 540 | 44495199 | KAA | DOCC srdy | B |  | RELW OH COMP CPGE PROG CPGD TER2 | 2020-12-29 |  | Switch | Broken/Damaged | Repair | SWIT_BROK_REPA - W/S PLEASANT VALLEY RD, | ORAS NOCO ATCO | ED.48-Q112300000.STRU.POLE | Q1123 | 06360-1104, VACAVILLE | 2811 |  | 101662283 | 38.3426 | -122.0247 | W/S PLEASANT VALLEY RD, 2 POLES S/O 5989 PLEASANTS | VACAVILLE | J6AG | 2020-10-09 | ECFOH | WILSON | 2020-09-29 | LMMY | 2020-10-08 | 2020-11-30 | 2020-11-30 | RFSI | 2020-12-01 | 2 |  | B | 048
T0 | IR | ST | Manteca | 119874298 | EC | 511 |  |  |  | E |  | POHW OH ESTR PROG TER0 | 2021-10-01 |  | Transformer | Broken/Damaged | Replace | TRAN_BROK_REPL - 528 SAN JUAN ST MANTECA | OSNO ATCO | ED.93-Y120800000.STRU.POLE | Y1208 | 16261-1704, MANTECA | 20115 |  | 102087837 | 37.802 | -121.2221 | 528 SAN JUAN ST | MANTECA | J6AG | 2020-10-09 | ECFOH | WITKOWSKI | 2020-10-01 | LMMY | 2020-10-09 | 2020-10-01 |  |  |  | 2 |  | E | 039
T0 | IR | YO | Newman | 119874703 | EC | 540 |  |  |  | E |  | POHW OH MINR JAR TER0 | 2021-10-01 |  | Lightning Arrester | Broken/Damaged | Replace | LITN_BROK_REPL - S/S CANAL RD (BOLADO RD | OSNO ATCO | ED.91-LL16000000.STRU.POLE | LL16 | 16311-1102, GUSTINE | 6215 |  | 101232356 | 37.2076 | -121.0492 | S/S CANAL RD (BOLADO RD), 0.2 MILES S/O PFITZER RD | GUSTINE | J6AG | 2020-10-09 | ECFOH | WILSON | 2020-10-01 | LMMY | 2020-10-09 | 2020-10-01 |  |  |  | 2 |  | E | 024
T0 | IR | YO | Newman | 119875795 | EC | 540 |  |  |  | E |  | POHW OH PROG TER0 | 2021-09-30 |  | Switch | Broken/Damaged | Repair | SWIT_BROK_REPA - W/S HWY 33, 4 POLES N/O | OSNO ATCO | ED.91-MM17000000.STRU.POLE | MM17 | 16311-1102, GUSTINE | 8649 |  | 101232102 | 37.1898 | -121.0129 | W/S HWY 33, 4 POLES N/O COTTONWOOD RD | GUSTINE | J6AG | 2020-10-09 | ECFOH | WILSON | 2020-09-30 | LMMY | 2020-10-09 | 2020-09-30 |  |  |  | 2 |  | E | 024
T0 | IR | YO | Madera | 119911210 | EC | 540 | 44509418 | KAA | UNSC srdy | B |  | RELW OH PROG TER0 | 2021-01-06 |  | Switch | Broken/Damaged | Repair | SWIT_BROK_REPA - 2 POLES S/O 12806 RD 26 | NOPR ORAS ATCO | ED.72-11175D0000.STRU.POLE | 11175D | 25276-1119, MADERA | 5202 |  | 103220732 | 36.9318 | -120.0739 | 2 POLES S/O 12806 RD 26, | MADERA | GJME | 2020-10-16 | ECFOH | WILSON | 2020-10-06 | LMMY | 2020-10-15 | 2020-10-06 |  |  |  | 2 | SABQ PRINTED | B | 020
T0 | IR | YO | Madera | 119911282 | EC | 511 | 35207384 | 2AA | CLSD canc | B |  | RELW OH CNCL ESTR PROG CPGI TER0 | 2021-01-06 |  | Transformer | Broken/Damaged | Replace | TRAN_BROK_REPL - R/O 12806 RD 26, MADERA | ORAS NOCO ATCO | ED.72-11175D0000.STRU.POLE | 11175D | 25276-1119, MADERA | 6497 | 120065517 | 101134874 | 36.9338 | -120.0766 | R/O 12806 RD 26, | MADERA | GJME | 2020-10-16 | ECFOH | WILSON | 2020-10-06 | LMMY | 2020-10-15 | 2020-11-23 |  |  | 2020-11-23 | 1 |  | B | 020
T0 | IR | FR | Selma | 119911350 | EC | 511 | 35207385 | 2AA | FICL crdy srdy | B |  | RELW OH COMP ESTR CPGD TER0 | 2021-01-05 |  | Transformer | Leaks/Seeps/Weeps | Replace | TRAN_SEEP_REPL - 0.9 MILES S/O E ELKHORN | ORAS NOCO NOPT ATCO | ED.70-1721100000.STRU.POLE | 17211 | 25224-1116, KINGSBURG | 6178F | 110408483 | 103127782 | 36.4805 | -119.6586 | 0.9 MILES S/O E ELKHORN AVE | SELMA | GJME | 2020-10-16 | ECFOH | BUENROSTRO | 2020-10-05 | LMMY | 2020-10-15 | 2020-11-20 | 2020-11-20 | JBG0 | 2020-11-25 | 2 |  | B | 010
T0 | IR | ST | Stockton | 119912339 | EC | 540 |  |  |  | E |  | POHW OH PROG TER0 | 2021-04-07 |  | Switch | Broken/Damaged | Repair | SWIT_BROK_REPA - A/F 16359 N TULLY RD. L | OSNO ATCO | ED.93-Q142400000.STRU.POLE | Q1424 | 16368-2102, LOCKEFORD | 9497 | 120117487 | 103803819 | 38.1305 | -121.1331 | A/F 16359 N TULLY RD. | LODI | GJME | 2020-10-16 | ECFOH | JERNIGAN | 2020-10-07 | LMMY | 2020-10-15 | 2020-10-07 |  |  |  | 2 |  | E | 039
T0 | IR | SI | Placerville | 119914152 | EC | 605 |  |  |  | E |  | POHW OH MINR JAR TER0 | 2021-04-08 |  | Lightning Arrester | Flashed | Replace | LITN_FLSH_REPL - 3610 RAVENWOOD LN. SHIN | OSNO ATCO | ED.21-J361500000.STRU.POLE | J3615 | 15365-2108, SHINGLE SPRINGS | 13129 |  | 101381196 | 38.666 | -121.0044 | 3610 RAVENWOOD LN. | SHINGLE SPRINGS | GJME | 2020-10-16 | ECFOH | JOINER | 2020-10-08 | LMMY | 2020-10-16 | 2020-10-08 |  |  |  | 2 |  | E | 009
T0 | IR | KE | Bakersfield | 119941823 | EC | 511 | 35209915 | 2AA | MAPP crdy srdy redl | B |  | RELW OH COMP ESTR CPGE PROG CPGD TER0 | 2020-11-13 |  | Transformer | Broken/Damaged | Replace | TRAN_BROK_REPL - I/B/O ALLEY 1015 E 18TH | ORAS NOCO NOPT ATCO | ED.66-2928295000.STRU.POLE | 2928295 | 25337-2106, BAKERSFIELD | 13528 | 120432542 | 100164531 | 35.3719 | -118.9887 | I/B/O ALLEY 1015 E 18TH ST | BAKERSFIELD | J6AG | 2020-10-23 | ECFOH | BUENROSTRO | 2020-10-13 | LMMY | 2020-10-23 | 2020-12-21 | 2020-12-21 | WGM6 | 2020-12-22 | 2 |  | B | 015
T0 | IR | FR | Fresno | 119942009 | EC | 540 | 44517049 | KAA | DOCC crdy srdy | B |  | RELW OH COMP PROG CPGD TER0 | 2021-01-15 |  | Switch | Broken/Damaged | Repair | SWIT_BROK_REPA - 1714 N BLYTHE AVE FRESN | ORAS NOCO ATCO | ED.70-1319351000.STRU.POLE | 1319351 | 25373-1112, WEST FRESNO | D12313 |  | 100708326 | 36.7628 | -119.8712 | 1714 N BLYTHE AVE | FRESNO | GJME | 2020-10-23 | ECFOH | WILSON | 2020-10-15 | LMMY | 2020-10-23 | 2020-12-03 | 2020-12-03 | MAAT | 2020-12-04 | 2 | RSGG 111020 | B | 010
T0 | IR | KE | Bakersfield | 119942054 | EC | 511 | 35209972 | 2AA | CONS srdy | B |  | RELW OH ESTR PROG TER0 | 2021-01-12 |  | Transformer | Broken/Damaged | Replace | TRAN_BROK_REPL - B/O 1815 BELLE TERR BAK | NOPR ORAS NOPT ATCO | ED.66-3027014000.STRU.POLE | 3027014 | 25370-1108, WESTPARK | 15622 | 120958987 | 100144053 | 35.3464 | -119.0228 | B/O 1815 BELLE TERR | BAKERSFIELD | J6AG | 2020-10-23 | ECFOH | BUENROSTRO | 2020-10-12 | LMMY | 2020-10-23 | 2020-10-12 |  |  |  | 2 |  | B | 015
T0 | IR | KE | Bakersfield | 119942411 | EC | 511 | 35209887 | 2AA | CONS srdy | B |  | RELW OH ESTR PROG TER0 | 2020-11-15 |  | Transformer | Leaks/Seeps/Weeps | Replace | TRAN_SEEP_REPL - I/B/O 604 CURTIS DR BAK | NOPR ORAS NOPT ATCO | ED.66-3028071000.STRU.POLE | 3028071 | 25337-2109, BAKERSFIELD | 14632 | 120389662 | 100155219 | 35.3371 | -119.0088 | I/B/O 604 CURTIS DR | BAKERSFIELD | J6AG | 2020-10-23 | ECFOH | BUENROSTRO | 2020-10-15 | LMMY | 2020-10-23 | 2020-10-15 |  |  |  | 2 |  | B | 015
T0 | IR | EB | Richmond | 119946953 | EC | 540 |  |  |  | E |  | POHW OH PROG TER0 | 2021-04-15 |  | Switch | Broken/Damaged | Repair | SWIT_BROK_REPA - R/O 291 CALAIS DR. HERC | OSNO ATCO | ED.28-B040900000.STRU.POLE | B0409 | 01392-1103, FRANKLIN | P123 | 110432996 | 101444859 | 38.0103 | -122.2921 | R/O 291 CALAIS DR. | HERCULES | GJME | 2020-10-27 | ECFOH | LAND | 2020-10-15 | LMMY | 2020-10-26 | 2020-10-15 |  |  |  | 2 |  | E | 007
T0 | IR | FR | Fresno | 119960613 | EC | 311 | 35211121 | 07D | DOCC crdy idoc redl cdoc cdpr | B |  | RELW OH COMP ESTR PROG CPGD TER0 | 2020-11-19 |  | Pole | Decayed/Rotten | Replace | POLE_DECA_REPL - R/O 615 E OLIVE AVE FRE | ORAS NOCO NOPT ATCO | ED.70-1320333000.STRU.POLE | 1320333 | 25392-1108, MANCHESTER | D9989 | 120419173 | 100863833 | 36.758 | -119.804 | R/O 615 E OLIVE AVE | FRESNO HIGH ROEDING | J6AG | 2020-10-29 | ECFOH | WILSON | 2020-10-19 | LMMY | 2020-10-29 | 2020-12-21 | 2020-12-21 | J2H2 | 2020-12-22 | 2 |  | B | 010
T3 | IR | ST | Jackson | 119960737 | EC | 605 |  |  |  | E |  | POHW OH TER3 | 2021-04-21 |  | Cutout | Broken/Damaged | Replace | CUTO_BROK_REPL - 2651 BALD MOUNTIAN RD W | OSNO ATCO | ED.95-L310000000.STRU.POLE | L31 | 16320-1102, WEST POINT | L3751 | 110527483 | 101251737 | 38.3964 | -120.4815 | 2651 BALD MOUNTIAN RD | WEST POINT | J6AG | 2020-10-29 | ECFOH | WITKOWSKI | 2020-10-21 | LMMY | 2020-10-29 | 2020-10-21 |  |  |  | 1 |  | E | 005
T2 | IR | SI | Placerville | 119960931 | EC | 605 | 31517764 | 2AA | UNSC srdy | B |  | RELW OH PROG TER2 | 2020-11-22 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 3181 CORRAL TRAIL RD. S | NOPR ORAS ATCO | ED.21-L440000000.STRU.POLE | L44 | 15366-2102, APPLE HILL | 18835 |  | 101396145 | 38.5857 | -120.7027 | 3181 CORRAL TRAIL RD. | SOMERSET | J6AG | 2020-10-29 | ECFOH | JERNIGAN | 2020-10-22 | LMMY | 2020-10-29 | 2020-10-22 |  |  |  | 1 | ARW8 1/2 CHG UNSC SRDY | B | 009
T2 | IR | SI | Grass Valley | 119998009 | EC | 511 |  |  |  | E |  | POHW OH ESTR PROG TER2 | 2021-04-28 |  | Switch | Broken/Damaged | Replace | SWIT_BROK_REPL - ACROSS STREET FROM 2186 | OSNO ATCO | ED.22-Q081900000.STRU.POLE | Q0819 | 15269-1103, HIGGINS | 2295 |  | 100018477 | 39.058 | -121.0878 | ACROSS STREET FROM 21866 IRON HORSE DR | GRASS VALLEY | GJME | 2020-11-09 | ECFOH | WITKOWSKI | 2020-10-29 | LMMY | 2020-11-09 | 2020-10-29 |  |  |  | 1 |  | B | 029
T2 | IR | SI | Grass Valley | 120048648 | EC | 540 |  |  |  | E |  | POHW OH MINR JAR TER2 | 2021-11-06 |  | Lightning Arrester | Broken/Damaged | Replace | LITN_BROK_REPL - 14179 BEITLER RD., GPS | OSNO ATCO | ED.22-M060000000.STRU.POLE | M06 | 15313-2102, NARROWS | 4759 |  | 100113350 | 39.2423 | -121.1812 | 14179 BEITLER RD., GPS COORDINATES 39.2437627,-121 | ROUGH AND READY | J6AG | 2020-11-17 | ECFOH | JOINER | 2020-11-06 | LMMY | 2020-11-17 | 2020-11-06 |  |  |  | 2 |  | E | 029
T2 | IR | SI | Grass Valley | 120049099 | EC | 540 |  |  |  | E |  | POHW OH MINR JAR TER2 | 2021-11-02 |  | Lightning Arrester | Broken/Damaged | Replace | LITN_BROK_REPL - I/F/O 13644 LITTLE BIRD | OSNO ATCO | ED.22-O061500000.STRU.POLE | O0615 | 15313-2105, NARROWS | 4713 |  | 100114010 | 39.1621 | -121.156 | I/F/O 13644 LITTLE BIRD LN | PENN VALLEY | J6AG | 2020-11-17 | ECFOH | BUENROSTRO | 2020-11-02 | LMMY | 2020-11-17 | 2020-11-02 |  |  |  | 2 |  | E | 029
T3 | IR | SI | Auburn | 120049174 | EC | 605 | 31519000 | 2AA | MAPP srdy | B |  | RELW OH COMP CCNT TER3 | 2021-02-05 |  | Cutout | Broken/Damaged | Replace | CUTO_BROK_REPL - 33990 ALTA BONNYNOOK RD | ORAS NOCO ATCO | ED.20-N150800000.STRU.POLE | N1508 | 15230-1102, BONNIE NOOK | 3473 |  | 100010084 | 39.2074 | -120.8097 | 33990 ALTA BONNYNOOK RD, | ALTA | J6AG | 2020-11-17 | ECFOH | GONZALES-NAT | 2020-11-05 | LMMY | 2020-11-17 | 2020-12-10 | 2020-12-10 | K3PC | 2020-12-13 | 1 | DPB9 | B | 031
T0 | IR | SI | Placerville | 120049176 | EC | 511 |  |  |  | E |  | POHW OH ESTR PROG TER0 | 2021-11-03 |  | Transformer | Broken/Damaged | Replace | TRAN_BROK_REPL - 3720 WILSON LOOP PLACER | OSNO ATCO | ED.21-I440000000.STRU.POLE | I44 | 15366-2102, APPLE HILL | 10933 |  | 101421733 | 38.6947 | -120.6996 | 3720 WILSON LOOP | PLACERVILLE | J6AG | 2020-11-17 | ECFOH | JERNIGAN | 2020-11-03 | LMMY | 2020-11-17 | 2020-11-03 |  |  |  | 2 |  | E | 009
T3 | IR | SI | Auburn | 120049177 | EC | 511 | 35214176 | 2AA | PEND | B |  | RELW OH ESTR PROG TER3 | 2021-02-03 |  | Transformer | Broken/Damaged | Replace | TRAN_BROK_REPL - 3206 BAUER RD. GEORGETO | NOPR ORAS ATCO | ED.20-T152000000.STRU.POLE | T1520 | 15308-2106, PLACERVILLE | 9321 | 120083600 | 100040443 | 38.9209 | -120.7982 | 3206 BAUER RD. | GEORGETOWN | J6AG | 2020-11-17 | ECFOH | LAND | 2020-11-03 | LMMY | 2020-11-17 | 2020-11-03 |  |  |  | 2 |  | B | 009
T0 | IR | SI | Grass Valley | 120049179 | EC | 511 | 35214177 | 2AA | MAPP crdy srdy redl | B |  | RELW OH COMP ESTR PROG CPGD TER0 | 2021-01-05 |  | Transformer | Broken/Damaged | Replace | TRAN_BROK_REPL - 17647 FOXTAIL DR. PENN | ORAS NOCO NOPT ATCO | ED.22-M061100000.STRU.POLE | M0611 | 15313-2102, NARROWS | 7739 |  | 100007037 | 39.2492 | -121.1901 | 17647 FOXTAIL DR. | PENN VALLEY | J6AG | 2020-11-17 | ECFOH | JOINER | 2020-11-05 | LMMY | 2020-11-17 | 2020-12-09 | 2020-12-09 | JPRI | 2020-12-15 | 2 |  | B | 029
T2 | IR | SI | Grass Valley | 120049460 | EC | 511 | 35214178 | 2AA | MAPP srdy redl | B |  | RELW OH COMP ESTR PROG CPGD TER2 | 2021-02-02 |  | Transformer | Broken/Damaged | Replace | TRAN_BROK_REPL - 11796 PALOMINO PL. GRAS | ORAS NOCO NOPT ATCO | ED.22-Q090000000.STRU.POLE | Q09 | 15269-1104, HIGGINS | 30483 |  | 100098417 | 39.0882 | -121.0536 | 11796 PALOMINO PL. | GRASS VALLEY | J6AG | 2020-11-17 | ECFOH | JOINER | 2020-11-02 | LMMY | 2020-11-17 | 2020-12-16 | 2020-12-16 | BAHE | 2020-12-19 | 1 |  | B | 029
T0 | IR | NV | Oroville | 120086514 | EC | 511 | 35218939 | 2AA | DOCC | B |  | RELW OH COMP PROG CPGD TER0 | 2021-02-13 |  | Switch | Broken/Damaged | Replace | SWIT_BROK_REPL - 5 MELANDJO CT OROVILLE | ORAS NOCO NOPT ATCO | ED.13-H240800000.STRU.POLE | H2408 | 10291-1109, WYANDOTTE | 23303 |  | 100370399 | 39.4821 | -121.5317 | 5 MELANDJO CT | OROVILLE | GJME | 2020-11-23 | ECFOH | GONZALES-NAT | 2020-11-13 | LMMY | 2020-11-23 | 2020-12-06 | 2020-12-06 | KESG | 2020-12-28 | 2 |  | E | 004
T0 | IR | NV | Oroville | 120086941 | EC | 605 | 31519909 | 2AA | CONS srdy | B |  | RELW OH TER0 | 2021-02-02 |  | Cutout | Broken/Damaged | Replace | CUTO_BROK_REPL - 2490 ITHACA ST. OROVILL | NOPR ORAS ATCO | ED.13-H240200000.STRU.POLE | H2402 | 10291-1102, WYANDOTTE | 90255 |  | 100429530 | 39.4932 | -121.544 | 2490 ITHACA ST. | OROVILLE | RXHV | 2020-11-23 | ECFOH | BODENHAMER | 2020-11-09 | LMMY | 2020-11-23 | 2020-11-09 |  |  |  | 1 |  | B | 004
T0 | IR | SA | Sacramento | 119777867 | EC | 540 |  |  |  | E |  | POHW OH PROG TER0 | 2021-03-10 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 429 FIRST ST WOODLAND | OSNO ATCO | ED.50-J170900000.STRU.POLE | J1709 | 06203-1104, WOODLAND | 2599 |  | 101602975 | 38.6764 | -121.7731 | 429 FIRST ST | WOODLAND | GJME | 2020-09-18 | ECFOH | BOAK | 2020-09-10 | LMMY | 2020-09-17 | 2020-09-10 |  |  |  | 1 |  | E | 057
T0 | IR | SA | Woodland | 119778082 | EC | 540 | 44475005 | KAA | DOCC crdy srdy | B |  | RELW OH SEC COMP CPGE PROG CPGD TER0 | 2020-12-11 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 419 ELM ST WOODLAND DO | ORAS NOCO ATCO | ED.50-J170900000.STRU.POLE | J1709 | 06203-1104, WOODLAND | 8669 |  | 101641024 | 38.6769 | -121.7762 | 419 ELM ST | WOODLAND | GJME | 2020-09-18 | ECFOH | BOAK | 2020-09-11 | LMMY | 2020-09-17 | 2020-11-05 | 2020-11-05 | CAVO | 2020-11-09 | 1 |  | E | 057
T0 | IR | SA | Sacramento | 119778129 | EC | 540 |  |  |  | E |  | POHW OH SEC PROG TER0 | 2021-03-11 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 205 CROSS ST WOODLAND | OSNO ATCO | ED.50-J171300000.STRU.POLE | J1713 | 06203-1107, WOODLAND | 5431 | 120350624 | 101610809 | 38.6722 | -121.7815 | 205 CROSS ST | WOODLAND | GJME | 2020-09-18 | ECFOH | BOAK | 2020-09-11 | LMMY | 2020-09-17 | 2020-09-11 |  |  |  | 1 |  | E | 057
T0 | IR | SA | Woodland | 119778293 | EC | 540 | 44475006 | KAA | DOCC crdy srdy | B |  | RELW OH SEC COMP CPGE PROG CPGD TER0 | 2020-10-11 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 454 COLLEGE AVE WOODLAN | ORAS NOCO ATCO | ED.50-J170900000.STRU.POLE | J1709 | 06203-1104, WOODLAND | 7183 |  | 101641029 | 38.6762 | -121.7748 | 454 COLLEGE AVE | WOODLAND | GJME | 2020-09-18 | ECFOH | BOAK | 2020-09-11 | LMMY | 2020-09-17 | 2020-11-06 | 2020-11-06 | JEV9 | 2020-11-09 | 1 |  | B | 057
T0 | IR | SA | Woodland | 119822402 | EC | 540 | 44485181 | KAA | DOCC srdy | B |  | RELW OH COMP CCNT PROG TER0 | 2020-12-15 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 510 RUTGERS DR. CENTRAL | ORAS NOCO ATCO | ED.50-M180100000.STRU.POLE | M1801 | 06204-1105, DAVIS | 8903 |  | 101646442 | 38.5543 | -121.7545 | 510 RUTGERS DR. | DAVIS | J6AG | 2020-09-28 | ECFOH | CHAMBERS | 2020-09-15 | LMMY | 2020-09-28 | 2020-11-30 | 2020-11-30 | TEUSCHER | 2020-12-09 | 1 |  | B | 057
T0 | IR | SA | Woodland | 119822408 | EC | 540 |  |  |  | E |  | POHW OH PROG TER0 | 2021-09-16 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 445 LAWSON LN. WOODLAND | OSNO ATCO | ED.50-J171400000.STRU.POLE | J1714 | 06203-1107, WOODLAND | 7459 | 120350557 | 101609961 | 38.6697 | -121.7759 | 445 LAWSON LN. | WOODLAND | J6AG | 2020-09-28 | ECFOH | BOAK | 2020-09-16 | LMMY | 2020-09-28 | 2020-09-16 |  |  |  | 1 |  | E | 057
T0 | IR | SA | Vacaville | 119836765 | EC | 540 | 44485176 | KAA | DOCC srdy | B |  | RELW OH COMP JAR CCNT TER0 | 2020-10-22 |  | Cutout | Broken/Damaged | Repair | CUTO_BROK_REPA - 350 TRAVIS BLVD. SOLANO | ORAS NOCO ATCO | ED.48-S111600000.STRU.POLE | S1116 | 06213-1102, SUISUN | 15709 | 120559491 | 101665722 | 38.2585 | -122.0376 | 350 TRAVIS BLVD. SOLANO STORAGE CENTER | FAIRFIELD | GJME | 2020-10-01 | ECFOH | JOINER | 2020-09-22 | LMMY | 2020-10-01 | 2020-12-04 | 2020-12-04 | TLWV | 2020-12-09 | 2 |  | B | 048
T0 | IR | SA | Vacaville | 119837029 | EC | 540 | 44485178 | KAA | DOCC srdy | B |  | RELW OH COMP CPGE PROG CPGD TER0 | 2020-10-23 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 715 2ND ST FAIRFIELD, C | ORAS NOCO ATCO | ED.48-S102400000.STRU.POLE | S1024 | 06213-1108, SUISUN | 19485 |  | 101556846 | 38.25 | -122.0553 | 715 2ND ST FAIRFIELD, CA 94533 | FAIRFIELD | J6AG | 2020-10-01 | ECFOH | JOINER | 2020-09-23 | LMMY | 2020-10-01 | 2020-12-04 | 2020-12-04 | R1WI | 2020-12-07 | 1 |  | B | 048
T0 | IR | SA | Woodland | 119837207 | EC | 540 |  |  |  | E |  | POHW OH PROG TER0 | 2021-03-22 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - R/O 1624 DELAWARE AVE W | OSNO ATCO | ED.50-L232400000.STRU.POLE | L2324 | 06313-1107, WEST SACRAMENTO | 2277 |  | 101657972 | 38.5679 | -121.5311 | R/O 1624 DELAWARE AVE | WEST SACRAMENTO | GJME | 2020-10-01 | ECFOH | WILSON | 2020-09-21 | LMMY | 2020-10-01 | 2020-09-21 |  |  |  | 1 |  | E | 057
T0 | IR | SA | Vacaville | 119871300 | EC | 540 | 44495197 | KAA | DOCC srdy | B |  | RELW OH COMP CCNT PROG TER0 | 2020-11-01 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 15949 SUTTER ISLAND RD. | ORAS NOCO ATCO | ED.48-R220000000.STRU.POLE | R22 | 06246-2227, GRAND ISLAND | 8787 |  | 101572419 | 38.3049 | -121.5764 | 15949 SUTTER ISLAND RD. | COURTLAND | J6AG | 2020-10-09 | ECFOH | LAND | 2020-10-01 | LMMY | 2020-10-08 | 2020-11-21 | 2020-11-21 | J2B8 | 2020-12-07 | 1 |  | B | 048
T0 | IR | ST | Stockton | 119871500 | EC | 540 | 44491923 | KAA | DOCC srdy | B |  | RELW OH COMP JAR CCNT TER0 | 2021-01-01 |  | Cutout | Broken/Damaged | Repair | CUTO_BROK_REPA - 2207 POCK LANE STOCKTON | ORAS NOCO ATCO | ED.93-V111000000.STRU.POLE | V1110 | 16348-1114, WEBER | 2265 |  | 103965277 | 37.9358 | -121.2478 | 2207 POCK LANE | STOCKTON | J6AG | 2020-10-09 | ECFOH | WITKOWSKI | 2020-10-01 | LMMY | 2020-10-08 | 2020-11-16 | 2020-11-16 | CONT | 2020-11-20 | 2 |  | B | 039
T0 | IR | YO | Newman | 119871503 | EC | 540 | 44491478 | KAA | DOCC crdy srdy | B |  | RELW OH COMP CPGE PROG CPGD TER0 | 2021-01-01 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - W/S HWY 33, 3 POLES S/O | ORAS NOCO ATCO | ED.91-KK17000000.STRU.POLE | KK17 | 16311-1102, GUSTINE | 9100 |  | 101219098 | 37.2434 | -121.0128 | W/S HWY 33, 3 POLES S/O SULLIVAN RD | GUSTINE | GJME | 2020-10-09 | ECFOH | WILSON | 2020-10-01 | LMMY | 2020-10-08 | 2020-12-03 | 2020-12-03 | JWB8 | 2020-12-03 | 1 |  | B | 024
T0 | IR | SA | Vacaville | 119871789 | EC | 540 | 44495198 | KAA | DOCC srdy | B |  | RELW OH COMP CCNT PROG TER0 | 2020-10-29 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 302 RIVER RD. RIO VISTA | ORAS NOCO NOPT ATCO | ED.48-U200000000.STRU.POLE | U20 | 06246-2226, GRAND ISLAND | 270613 | 120113002 | 103812767 | 38.1651 | -121.6823 | 302 RIVER RD. RIO VISTA | RIO VISTA | J6AG | 2020-10-09 | ECFOH | BODENHAMER | 2020-09-29 | LMMY | 2020-10-08 | 2020-12-09 | 2020-12-09 | TEUSCHER | 2020-12-14 | 1 |  | B | 048
T0 | IR | ST | Manteca | 119872320 | EC | 540 | 44491924 | KAA | DOCC srdy | B |  | RELW OH COMP CPGE PROG CPGD TER0 | 2020-10-29 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 14500 LONE TREE RD RIPO | ORAS NOCO ATCO | ED.93-X140000000.STRU.POLE | X14 | 16357-1701, AVENA | 19355 | 120485485 | 102102609 | 37.8268 | -121.1351 | 14500 LONE TREE RD | RIPON | J6AG | 2020-10-09 | ECFOH | ARAUJO | 2020-09-29 | LMMY | 2020-10-08 | 2020-11-25 | 2020-11-25 | TXGR | 2020-12-02 | 1 |  | B | 039
T0 | IR | ST | Stockton | 119872342 | EC | 540 | 44491925 | KAA | DOCC srdy | B |  | RELW OH COMP CCNT PROG TER0 | 2021-01-01 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - I/F/O 5400 CA-12 LODI, | ORAS NOCO ATCO | ED.93-R080800000.STRU.POLE | R0808 | 16391-2101, EIGHT MILE | D1219 | 120531870 | 102049431 | 38.1153 | -121.3823 | I/F/O 5400 CA-12 LODI, CA 95242 | LODI | J6AG | 2020-10-09 | ECFOH | BUENROSTRO | 2020-10-01 | LMMY | 2020-10-08 | 2020-11-18 | 2020-11-18 | DCPC | 2020-11-20 | 1 | CMPLT. 11-18-20 DCPC | B | 039
T0 | IR | YO | Newman | 119872876 | EC | 540 | 44491477 | KAA | DOCC crdy srdy | B |  | RELW OH COMP CPGE PROG CPGD TER0 | 2021-01-01 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 5TH AVE @ ALLEY, WEST O | ORAS NOCO ATCO | ED.91-KK17150000.STRU.POLE | KK1715 | 16311-1102, GUSTINE | 90260 |  | 101220273 | 37.2547 | -120.9998 | 5TH AVE @ ALLEY, WEST OF 5TH ST | GUSTINE | GJME | 2020-10-09 | ECFOH | WILSON | 2020-10-01 | LMMY | 2020-10-08 | 2020-12-01 | 2020-12-01 | JWB8 | 2020-12-02 | 1 |  | B | 024
T0 | IR | ST | Stockton | 119872939 | EC | 540 | 44491926 | KAA | DOCC srdy | B |  | RELW OH COMP CCNT PROG TER0 | 2020-11-01 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - N/E/C KETTLEMAN & STOCK | ORAS NOCO ATCO | ED.93-R110000000.STRU.POLE | R11 | 16211-1102, LODI | 1103 | 120531293 | 102102633 | 38.1157 | -121.2694 | N/E/C KETTLEMAN & STOCKTON | LODI | J6AG | 2020-10-09 | ECFOH | BUENROSTRO | 2020-10-01 | LMMY | 2020-10-08 | 2020-11-17 | 2020-11-17 | CONT | 2020-11-20 | 1 |  | B | 039
T0 | IR | SA | Vacaville | 119873031 | EC | 540 | 44496080 | KAA | DOCC srdy | B |  | RELW OH COMP CPGE PROG CPGD TER0 | 2020-12-30 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 5814 PEDRICK RD. HOT SP | ORAS NOCO ATCO | ED.48-Q160000000.STRU.POLE | Q16 | 06364-2107, PEABODY | 47023 |  | 101567098 | 38.3373 | -121.8043 | 5814 PEDRICK RD. HOT SPOT IS 500 YARDS NORTH OF AD | DIXON | J6AG | 2020-10-09 | ECFOH | CHAMBERS | 2020-09-30 | LMMY | 2020-10-08 | 2020-10-21 | 2020-10-21 | DXHL | 2020-10-22 | 1 |  | B | 048
T0 | IR | ST | Stockton | 119873147 | EC | 540 | 44491927 | KAA | DOCC srdy | B |  | RELW OH COMP CCNT PROG TER0 | 2020-10-29 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 1138 S NETHERTON AVE ST | ORAS NOCO ATCO | ED.93-U122100000.STRU.POLE | U1221 | 16313-1102, EAST STOCKTON | 8133 |  | 102095512 | 37.9509 | -121.2409 | 1138 S NETHERTON AVE | STOCKTON | J6AG | 2020-10-09 | ECFOH | WITKOWSKI | 2020-09-29 | LMMY | 2020-10-08 | 2020-11-16 | 2020-11-16 | CONT | 2020-11-20 | 1 |  | B | 039
T0 | IR | ST | Stockton | 119873421 | EC | 540 | 44491928 | KAA | DOCC crdy srdy | B |  | RELW OH COMP CCNT PROG TER0 | 2020-11-01 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 2P S/O 22201 FRAZIER RD | ORAS NOCO ATCO | ED.93-S170000000.STRU.POLE | S17 | 16368-2102, LOCKEFORD | 410085 |  | 102124330 | 38.0737 | -121.042 | 2P S/O 22201 FRAZIER RD | LINDEN | GJME | 2020-10-09 | ECFOH | JERNIGAN | 2020-10-01 | LMMY | 2020-10-08 | 2020-11-12 | 2020-11-12 | CONT | 2020-11-17 | 1 |  | B | 039
T0 | IR | YO | Newman | 119874299 | EC | 540 |  |  |  | E |  | POHW OH PROG TER0 | 2021-10-01 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 1091 WEST AVE GUSTINE | OSNO ATCO | ED.91-KK17200000.STRU.POLE | KK1720 | 16311-1102, GUSTINE | S1015 |  | 101220533 | 37.2495 | -121.0035 | 1091 WEST AVE | GUSTINE | J6AG | 2020-10-09 | ECFOH | WILSON | 2020-10-01 | LMMY | 2020-10-09 | 2020-10-01 |  |  |  | 1 |  | E | 024
T0 | IR | SA | Vacaville | 119874700 | EC | 540 |  |  |  | E |  | POHW OH PROG TER0 | 2021-09-29 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - R/O 713 MERCHANT ST VAC | OSNO ATCO | ED.48-Q121700000.STRU.POLE | Q1217 | 06360-1104, VACAVILLE | 54085 |  | 101572658 | 38.3493 | -121.9946 | R/O 713 MERCHANT ST | VACAVILLE | J6AG | 2020-10-09 | ECFOH | WILSON | 2020-09-29 | LMMY | 2020-10-09 | 2020-09-29 |  |  |  | 1 |  | E | 048
T0 | IR | SA | Vacaville | 119874705 | EC | 540 |  |  |  | E |  | POHW OH PROG TER0 | 2021-09-29 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - R/O 5075 RYER RD. E. WA | OSNO ATCO | ED.48-S210000000.STRU.POLE | S21 | 06246-2227, GRAND ISLAND | 34577 |  | 101583889 | 38.2858 | -121.608 | R/O 5075 RYER RD. E. | WALNUT GROVE | J6AG | 2020-10-09 | ECFOH | LAND | 2020-09-29 | LMMY | 2020-10-09 | 2020-09-29 |  |  |  | 1 |  | E | 048
T0 | IR | YO | Los Banos | 119874905 | EC | 540 |  |  |  | E |  | POHW OH PROG TER0 | 2021-09-30 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - P/P, 0.2 MILES E/O WHIT | OSNO ATCO | ED.72-09092C0000.STRU.POLE | 09092C | 16311-1102, GUSTINE | 3279 |  | 101202128 | 37.1701 | -121.0271 | P/P, 0.2 MILES E/O WHITWORTH RD, 0.2 MILES S/O BUN | LOS BANOS | J6AG | 2020-10-09 | ECFOH | WILSON | 2020-09-30 | LMMY | 2020-10-09 | 2020-09-30 |  |  |  | 1 |  | E | 024
T0 | IR | YO | Newman | 119874907 | EC | 540 |  |  |  | E |  | POHW OH PROG TER0 | 2021-10-01 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - R/O 351 5TH ST IN ALLEY | OSNO ATCO | ED.91-KK17150000.STRU.POLE | KK1715 | 16311-1102, GUSTINE | 90260 |  | 101220256 | 37.2565 | -121.0006 | R/O 351 5TH ST IN ALLEY. SWITCH #3513 | GUSTINE | J6AG | 2020-10-09 | ECFOH | WILSON | 2020-10-01 | LMMY | 2020-10-09 | 2020-10-01 |  |  |  | 1 |  | E | 024
T0 | IR | YO | Oakdale | 119874909 | EC | 540 |  |  |  | E |  | POHW OH PROG TER0 | 2021-10-02 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 1550 MAIN ST ESCALON M | OSNO ATCO | ED.91-Y181200000.STRU.POLE | Y1812 | 16319-1713, RIVERBANK | S853 |  | 102327910 | 37.7966 | -120.9946 | 1550 MAIN ST | ESCALON | J6AG | 2020-10-09 | ECFOH | WITKOWSKI | 2020-10-02 | LMMY | 2020-10-09 | 2020-10-02 |  |  |  | 1 |  | E | 039
T0 | IR | ST | Stockton | 119875023 | EC | 540 |  |  |  | E |  | POHW OH PROG TER0 | 2021-10-01 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - .5 MI N/O E VICTOR RD & | OSNO ATCO | ED.93-Q121600000.STRU.POLE | Q1216 | 16211-1102, LODI | 14169 | 120374551 | 102115096 | 38.141 | -121.2388 | .5 MI N/O E VICTOR RD &N KENNISON LN | LODI | J6AG | 2020-10-09 | ECFOH | BUENROSTRO | 2020-10-01 | LMMY | 2020-10-09 | 2020-10-01 |  |  |  | 1 |  | E | 039
T0 | IR | SA | Vacaville | 119875026 | EC | 540 |  |  |  | E |  | POHW OH PROG TER0 | 2021-09-29 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 518 BOYD ST VACAVILLE | OSNO ATCO | ED.48-Q121700000.STRU.POLE | Q1217 | 06360-1104, VACAVILLE | 40409 |  | 101572732 | 38.3533 | -121.9888 | 518 BOYD ST | VACAVILLE | J6AG | 2020-10-09 | ECFOH | WILSON | 2020-09-29 | LMMY | 2020-10-09 | 2020-09-29 |  |  |  | 1 |  | E | 048
T0 | IR | YO | Oakdale | 119875027 | EC | 540 |  |  |  | E |  | POHW OH PROG TER0 | 2021-04-02 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 1603 2ND ST ESCALON 2N | OSNO ATCO | ED.91-Y181200000.STRU.POLE | Y1812 | 16319-1713, RIVERBANK | 4061 |  | 102337294 | 37.7952 | -120.9914 | 1603 2ND ST | ESCALON | GJME | 2020-10-09 | ECFOH | WITKOWSKI | 2020-10-02 | LMMY | 2020-10-09 | 2020-10-02 |  |  |  | 1 |  | E | 039
T0 | IR | ST | Stockton | 119875716 | EC | 540 |  |  |  | E |  | POHW OH PROG TER0 | 2021-04-01 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 1619 E 10TH ST STOCKTON | OSNO ATCO | ED.93-V110800000.STRU.POLE | V1108 | 16348-1105, WEBER | 2335 |  | 102108825 | 37.9304 | -121.2605 | 1619 E 10TH ST | STOCKTON | GJME | 2020-10-09 | ECFOH | WITKOWSKI | 2020-10-01 | LMMY | 2020-10-09 | 2020-10-01 |  |  |  | 1 |  | E | 039
T0 | IR | SA | Woodland | 119875790 | EC | 540 |  |  |  | E |  | POHW OH PROG TER0 | 2021-03-30 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 50720 BABEL SLOUGH RD. | OSNO ATCO | ED.50-O220000000.STRU.POLE | O22 | 06246-2227, GRAND ISLAND | 1849 |  | 101576209 | 38.4622 | -121.5686 | 50720 BABEL SLOUGH RD. | CLARKSBURG | GJME | 2020-10-09 | ECFOH | LAND | 2020-09-30 | LMMY | 2020-10-09 | 2020-09-30 |  |  |  | 1 |  | E | 057
T0 | IR | ST | Stockton | 119875794 | EC | 540 |  |  |  | E |  | POHW OH PROG TER0 | 2021-04-01 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - I/F/O 12730 N DE VRIES | OSNO ATCO | ED.93-R091700000.STRU.POLE | R0917 | 16391-2101, EIGHT MILE | 14399 | 110422888 | 103817483 | 38.0924 | -121.3509 | I/F/O 12730 N DE VRIES RD LODI, CA 95242 | LODI | GJME | 2020-10-09 | ECFOH | BUENROSTRO | 2020-10-01 | LMMY | 2020-10-09 | 2020-10-01 |  |  |  | 1 |  | E | 039
T0 | IR | NV | Willows | 119877250 | EC | 540 |  |  |  | E |  | REGW OH PRI INSP FLAG BTKA FMOB TER0 | 2021-10-09 |  | Connector | Incorrectly Installed | Replace | CONN_INCR_REPL - 4860 RD N ORLAND | OSNO ATCO | ED.14-S200000000.STRU.POLE | S20 | 10260-1101, GLENN | 423 |  | 100352358 | 39.7858 | -122.1595 | 4860 RD N | Orland | S7HB | 2020-10-21 | ECFOH | CZBE | 2020-10-09 | INSPECTCPIC | 2020-10-09 | 2020-10-09 |  |  |  | 2 |  | E | 011 | INSP
T0 | IR | ST | Stockton | 119911033 | EC | 540 | 44499916 | KAA | DOCC crdy srdy | B |  | RELW OH COMP CPGE PROG CPGD TER0 | 2020-11-05 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - A/F 13852 E PELTIER RD. | ORAS NOCO ATCO | ED.93-PP14000000.STRU.POLE | PP14 | 16368-2102, LOCKEFORD | D6863 | 0 | 103762012 | 38.1944 | -121.1466 | A/F 13852 E PELTIER RD. | ACAMPO | GJME | 2020-10-16 | ECFOH | JERNIGAN | 2020-10-05 | LMMY | 2020-10-15 | 2020-11-03 | 2020-11-03 | J9MP | 2020-11-09 | 1 | CMPLT 11/3 J9MP IN 11/4 | B | 039
T0 | IR | YO | Merced | 119911037 | EC | 540 | 44509589 | KAA | DOCC crdy srdy | B |  | RELW OH SEC COMP CPGE PROG CPGD TER0 | 2020-11-05 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 557 CONE AVE MERCED BE | ORAS NOCO NOPT ATCO | ED.72-0714311000.STRU.POLE | 0714311 | 25280-2101, MERCED | 22545 | 120011675 | 101018785 | 37.2844 | -120.4735 | 557 CONE AVE | MERCED | GJME | 2020-10-16 | ECFOH | ARAUJO | 2020-10-05 | LMMY | 2020-10-15 | 2020-11-23 | 2020-11-23 | D3SD | 2020-11-25 | 1 |  | B | 024
UNK. No SAP ID | IR | YO | Merced | 119911114 | EC | 540 | 44509590 | KAA | DOCC crdy srdy | B |  | RELW OH COMP JAR CPGE CPGD | 2020-11-07 |  | Cutout | Broken/Damaged | Repair | CUTO_BROK_REPA - 8201 MONTE CRISTO AVE M | ORAS NOCO NOPT ATCO | ED.72-06123C0000.STRU.POLE | 06123C | 25226-1106, LIVINGSTON | 7319 |  |  | 37.4039 | -120.6905 | 8201 MONTE CRISTO AVE | MERCED | GJME | 2020-10-16 | ECFOH | ARAUJO | 2020-10-07 | LMMY | 2020-10-15 | 2020-11-24 | 2020-11-24 | D3SD | 2020-11-25 | 2 |  | B | 024
T0 | IR | YO | Madera | 119911216 | EC | 540 | 44509591 | KAA | DOCC srdy | B |  | RELW OH COMP CPGE PROG CPGD TER0 | 2020-11-08 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - ACCESS FROM AVENUE 9 MA | ORAS NOCO ATCO | ED.70-1219500000.STRU.POLE | 12195 | 25455-2112, FIGARDEN | 23519 |  | 101127459 | 36.8641 | -119.8663 | ACCESS FROM AVENUE 9 | MADERA | GJME | 2020-10-16 | ECFOH | ARAUJO | 2020-10-08 | LMMY | 2020-10-15 | 2020-11-13 | 2020-11-13 | PRMJ | 2020-11-17 | 1 | SABQ PRINTED | B | 020
T0 | IR | ST | Stockton | 119911283 | EC | 540 | 44499917 | KAA | DOCC srdy | B |  | RELW OH COMP CCNT PROG TER0 | 2021-01-06 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 7P S/O E HARNEY LN | ORAS NOCO ATCO | ED.93-R160000000.STRU.POLE | R16 | 16368-2102, LOCKEFORD | D4261 |  | 102074839 | 38.0996 | -121.0464 | 7P S/O E HARNEY LN | LODI | GJME | 2020-10-16 | ECFOH | JERNIGAN | 2020-10-06 | LMMY | 2020-10-15 | 2020-11-12 | 2020-11-12 | CONT | 2020-11-17 | 1 |  | B | 039
T0 | IR | SA | Vacaville | 119911356 | EC | 540 | 44499821 | KAA | DOCC srdy | B |  | RELW OH COMP JAR CPGE CPGD TER0 | 2020-11-05 |  | Cutout | Broken/Damaged | Repair | CUTO_BROK_REPA - 400 ORANGE DR. 150 FEET | ORAS NOCO ATCO | ED.48-Q130200000.STRU.POLE | Q1302 | 06359-1104, VACA DIXON | 15240 |  | 101571029 | 38.3729 | -121.953 | 400 ORANGE DR. 150 FEET NORTH OF I-80 EASTBOUND ON | VACAVILLE | GJME | 2020-10-16 | ECFOH | BODENHAMER | 2020-10-05 | LMMY | 2020-10-15 | 2020-12-09 | 2020-12-09 | DXHL | 2020-12-10 | 2 |  | B | 048
T0 | IR | ST | Angels Camp | 119911402 | EC | 540 | 44499918 | KAA | DOCC srdy | B |  | RELW OH COMP CPGE PROG CPGD TER0 | 2021-01-08 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 584 ANGELS RD. ANGELS C | ORAS NOCO ATCO | ED.95-P261700000.STRU.POLE | P2617 | 16221-1101, CALAVERAS CEMENT | L5289 |  | 101251126 | 38.1885 | -120.675 | 584 ANGELS RD. | SAN ANDREAS | GJME | 2020-10-16 | ECFOH | JERNIGAN | 2020-10-08 | LMMY | 2020-10-15 | 2020-11-24 | 2020-11-24 | JWAA | 2020-11-30 | 1 |  | B | 005
T2 | IR | ST | Angels Camp | 119911409 | EC | 540 | 44499919 | KAA | DOCC srdy | B |  | RELW OH SERV COMP CPGE PROG CPGD TER2 | 2020-11-08 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 1465 FRENCH GULCH RD. A | ORAS NOCO ATCO | ED.95-Q310000000.STRU.POLE | Q31 | 16345-1702, FROGTOWN | L6029 |  | 101276325 | 38.1395 | -120.4828 | 1465 FRENCH GULCH RD. | ANGELS CAMP | GJME | 2020-10-16 | ECFOH | LAND | 2020-10-08 | LMMY | 2020-10-15 | 2020-11-20 | 2020-11-20 | JWAA | 2020-11-23 | 1 |  | B | 005
T0 | IR | FR | Selma | 119911461 | EC | 540 | 44499775 | KAA | DOCC srdy | B |  | RELW OH COMP PROG CPGD TER0 | 2020-11-05 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 150FT N/W/O 6461 E ELKH | ORAS NOCO ATCO | ED.70-1721100000.STRU.POLE | 17211 | 25224-1116, KINGSBURG | 4443F |  | 100834166 | 36.4852 | -119.6764 | 150FT N/W/O 6461 E ELKHORN AVE | SELMA | GJME | 2020-10-16 | ECFOH | BUENROSTRO | 2020-10-05 | LMMY | 2020-10-15 | 2020-11-12 | 2020-11-12 | A0S2 | 2020-11-17 | 1 |  | B | 010
T0 | IR | YO | Merced | 119911462 | EC | 540 | 44509592 | KAA | DOCC crdy srdy | B |  | RELW OH COMP CPGE PROG CPGD TER0 | 2020-11-05 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 17 CONE AVE MERCED LOS | ORAS NOCO ATCO | ED.72-0714312000.STRU.POLE | 0714312 | 25280-2101, MERCED | 90270 | 120471905 | 101156737 | 37.2845 | -120.4866 | 17 CONE AVE | MERCED | GJME | 2020-10-16 | ECFOH | ARAUJO | 2020-10-05 | LMMY | 2020-10-15 | 2020-11-23 | 2020-11-23 | D3SD | 2020-11-24 | 1 |  | B | 024
T0 | IR | SA | Vacaville | 119911743 | EC | 540 | 44499822 | KAA | DOCC srdy | B |  | RELW OH COMP CCNT PROG TER0 | 2021-01-05 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 17523 GRAND ISLAND RD. | ORAS NOCO ATCO | ED.48-U212400000.STRU.POLE | U2124 | 06246-2224, GRAND ISLAND | 4307 |  | 101573332 | 38.1647 | -121.613 | 17523 GRAND ISLAND RD. | WALNUT GROVE | GJME | 2020-10-16 | ECFOH | JOINER | 2020-10-05 | LMMY | 2020-10-15 | 2020-11-21 | 2020-11-21 | J2B8 | 2020-12-07 | 1 |  | B | 048
T0 | IR | FR | Selma | 119911978 | EC | 540 | 44499776 | KAA | DOCC srdy | B |  | RELW OH COMP PROG CPGD TER0 | 2020-11-06 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 0.2MI E/O 16508 S CLOVI | ORAS NOCO NOPT ATCO | ED.70-1621600000.STRU.POLE | 16216 | 25224-1116, KINGSBURG | 315909 |  | 103233789 | 36.4963 | -119.6903 | 0.2MI E/O 16508 S CLOVIS AVE | SELMA | GJME | 2020-10-16 | ECFOH | BUENROSTRO | 2020-10-06 | LMMY | 2020-10-15 | 2020-11-12 | 2020-11-12 | A0S2 | 2020-11-17 | 1 |  | B | 010
T0 | IR | SA | Woodland | 119912337 | EC | 540 | 44499218 | KAA | UNSC srdy | E |  | RELW OH PROG TER0 | 2021-04-05 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 50285 CLARKSBURG RD. CL | NOPR ORAS ATCO | ED.50-P220000000.STRU.POLE | P22 | 06246-2227, GRAND ISLAND | 20731 |  | 101579942 | 38.4143 | -121.5792 | 50285 CLARKSBURG RD. | CLARKSBURG | GJME | 2020-10-16 | ECFOH | LAND | 2020-10-05 | LMMY | 2020-10-15 | 2020-10-05 |  |  |  | 1 |  | E | 057
T0 | IR | YO | Madera | 119912462 | EC | 540 |  |  |  | E |  | POHW OH SEC PROG TER0 | 2021-04-06 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - N/S AVE 13, 1 POLE WEST | OSNO ATCO | ED.72-11176D0000.STRU.POLE | 11176D | 25276-1119, MADERA | 5281 | 110462332 | 101127732 | 36.9383 | -120.1105 | N/S AVE 13, 1 POLE WEST OF RD 24. | MADERA | GJME | 2020-10-16 | ECFOH | WILSON | 2020-10-06 | LMMY | 2020-10-15 | 2020-10-06 |  |  |  | 1 |  | E | 020
T0 | IR | YO | Merced | 119913921 | EC | 540 |  |  |  | E |  | POHW OH PROG TER0 | 2021-04-05 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 150 W 24TH ST MERCED | OSNO ATCO | ED.72-0714195000.STRU.POLE | 0714195 | 25280-2101, MERCED | 21019 | 120073519 | 101166600 | 37.306 | -120.4745 | 150 W 24TH ST | MERCED | GJME | 2020-10-16 | ECFOH | ARAUJO | 2020-10-05 | LMMY | 2020-10-16 | 2020-10-05 |  |  |  | 1 |  | E | 024
T0 | IR | YO | Oakdale | 119913922 | EC | 540 |  |  |  | E |  | POHW OH PROG TER0 | 2021-04-05 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 31251 ROSSIER RD OAKDAL | OSNO ATCO | ED.91-Y191000000.STRU.POLE | Y1910 | 16319-1713, RIVERBANK | 20199 | 110309953 | 103168549 | 37.8044 | -120.9299 | 31251 ROSSIER RD | ESCALON | GJME | 2020-10-16 | ECFOH | WITKOWSKI | 2020-10-05 | LMMY | 2020-10-16 | 2020-10-05 |  |  |  | 1 |  | E | 039
T0 | IR | SA | Vacaville | 119914084 | EC | 540 |  |  |  | E |  | POHW OH PROG TER0 | 2021-04-06 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 1.2 MILES NORTHEAST OF | OSNO ATCO | ED.48-V200000000.STRU.POLE | V20 | 06246-2225, GRAND ISLAND | 40319 |  | 101665853 | 38.1566 | -121.6605 | 1.2 MILES NORTHEAST OF HIGHWAY 12 AND HIGHWAY 160 | ISLETON | GJME | 2020-10-16 | ECFOH | BODENHAMER | 2020-10-06 | LMMY | 2020-10-16 | 2020-10-06 |  |  |  | 1 |  | E | 034
T0 | IR | FR | Selma | 119914115 | EC | 540 |  |  |  | E |  | POHW OH PROG TER0 | 2021-04-07 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 100FT N/O 15444 S FOWLE | OSNO ATCO | ED.70-1621500000.STRU.POLE | 16215 | 25224-1116, KINGSBURG | 746675 | 120136980 | 103836992 | 36.5126 | -119.6828 | 100FT N/O 15444 S FOWLER AVE | SELMA | GJME | 2020-10-16 | ECFOH | BUENROSTRO | 2020-10-07 | LMMY | 2020-10-16 | 2020-10-07 |  |  |  | 1 |  | E | 010
T0 | IR | FR | Selma | 119914151 | EC | 540 |  |  |  | E |  | POHW OH PROG TER0 | 2021-04-06 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 400FT N/E/O VINEYARD WA | OSNO ATCO | ED.70-1621500000.STRU.POLE | 16215 | 25224-1116, KINGSBURG | 746675 | 110408443 | 100819518 | 36.5074 | -119.6779 | 400FT N/E/O VINEYARD WAY | SELMA | GJME | 2020-10-16 | ECFOH | BUENROSTRO | 2020-10-06 | LMMY | 2020-10-16 | 2020-10-06 |  |  |  | 1 |  | E | 010
T0 | IR | YO | Oakdale | 119914342 | EC | 540 |  |  |  | E |  | POHW OH PROG TER0 | 2021-04-06 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - .7 MI NORTH ON COBBLEST | OSNO ATCO | ED.91-Y230000000.STRU.POLE | Y23 | 16371-1702, COTTLE | 26314 | 110473216 | 103155685 | 37.8163 | -120.803 | .7 MI NORTH ON COBBLESTONE RD | OAKDALE | GJME | 2020-10-16 | ECFOH | WITKOWSKI | 2020-10-06 | LMMY | 2020-10-16 | 2020-10-06 |  |  |  | 1 |  | E | 050
T0 | IR | FR | Selma | 119941560 | EC | 540 | 44517147 | KAA | DOCC srdy | B |  | RELW OH COMP PROG CPGD TER0 | 2021-01-15 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - A/F IN FIELD, 4 POLES S | ORAS NOCO ATCO | ED.70-16222A0000.STRU.POLE | 16222A | 25412-1102, MC CALL | 6998F |  | 100880522 | 36.5734 | -119.5839 | A/F IN FIELD, 4 POLES S/O 11567 E FLORAL AVE | SELMA | GJME | 2020-10-23 | ECFOH | WILSON | 2020-10-15 | LMMY | 2020-10-23 | 2020-11-27 | 2020-11-27 | A0S2 | 2020-11-30 | 1 | RSGG 111020 | B | 010
T0 | IR | KE | Bakersfield | 119941565 | EC | 540 | 44506029 | KAA | CONS srdy | B |  | RELW OH PROG TER0 | 2021-01-15 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - ACCESS OF BOLTHOUSE DR | NOPR ORAS ATCO | ED.66-3026135000.STRU.POLE | 3026135 | 25532-2104, TEVIS | 919041 | 120489914 | 100236895 | 35.3149 | -119.1369 | ACCESS OF BOLTHOUSE DR | BAKERSFIELD | J6AG | 2020-10-23 | ECFOH | ARAUJO | 2020-10-15 | LMMY | 2020-10-23 | 2020-10-15 |  |  |  | 1 |  | B | 015
T0 | IR | FR | Fresno | 119941567 | EC | 540 | 44505644 | KAA | DOCC srdy | B |  | RELW OH COMP PROG CPGD TER0 | 2020-11-12 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 4222 W ALAMOS AVE BULLA | ORAS NOCO ATCO | ED.70-1319141000.STRU.POLE | 1319141 | 25455-2102, FIGARDEN | 42907 | 120370263 | 100632978 | 36.8054 | -119.8672 | 4222 W ALAMOS AVE | FRESNO | J6AG | 2020-10-23 | ECFOH | WITKOWSKI | 2020-10-12 | LMMY | 2020-10-23 | 2020-11-07 | 2020-11-07 | J2ML | 2020-11-09 | 1 | RSGG 102920 | B | 010
T0 | IR | KE | Bakersfield | 119941691 | EC | 540 | 44505878 | KAA | DOCC crdy srdy | B |  | RELW OH COMP CPGE PROG CPGD TER0 | 2020-11-13 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - I/B/O SUPER Q MARKET 72 | ORAS NOCO ATCO | ED.66-2928341000.STRU.POLE | 2928341 | 25337-2106, BAKERSFIELD | 14721 | 120309397 | 100252337 | 35.3646 | -118.9581 | I/B/O SUPER Q MARKET 723 QUANTICO AVE | BAKERSFIELD | J6AG | 2020-10-23 | ECFOH | BUENROSTRO | 2020-10-13 | LMMY | 2020-10-23 | 2020-11-09 | 2020-11-09 | RXVR | 2020-11-10 | 1 |  | B | 015
T0 | IR | KE | Bakersfield | 119941698 | EC | 540 | 44506023 | KAA | DOCC srdy | B |  | RELW OH COMP CPGE PROG CPGD TER0 | 2020-11-15 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - I/B/O 1500 S UNION AVE | ORAS NOCO ATCO | ED.66-3028082000.STRU.POLE | 3028082 | 25337-2104, BAKERSFIELD | 13016 | 120300329 | 100255944 | 35.3367 | -119.0012 | I/B/O 1500 S UNION AVE B | BAKERSFIELD | GJME | 2020-10-23 | ECFOH | BUENROSTRO | 2020-10-15 | LMMY | 2020-10-23 | 2020-12-21 | 2020-12-21 | SCTB | 2020-12-23 | 1 |  | B | 015
T0 | IR | KE | Bakersfield | 119941821 | EC | 540 | 44506020 | KAA | DOCC crdy | B |  | RELW OH COMP CPGE PROG CPGD TER0 | 2020-11-14 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - B/O 235 KINCAID ST BAKE | ORAS NOCO ATCO | ED.66-2928325000.STRU.POLE | 2928325 | 25337-2104, BAKERSFIELD | 13296 | 120299960 | 100241535 | 35.3587 | -118.9925 | B/O 235 KINCAID ST | BAKERSFIELD | J6AG | 2020-10-23 | ECFOH | BUENROSTRO | 2020-10-14 | LMMY | 2020-10-23 | 2020-11-20 | 2020-11-20 | SCTB | 2020-12-02 | 1 |  | B | 015
T0 | IR | FR | Selma | 119941826 | EC | 540 | 44517148 | KAA | DOCC srdy | B |  | RELW OH COMP PROG CPGD TER0 | 2021-01-14 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - W/S MCCALL AVE, 2 POLES | ORAS NOCO ATCO | ED.70-1522314000.STRU.POLE | 1522314 | 25412-1102, MC CALL | 310426 |  | 100896821 | 36.5829 | -119.6108 | W/S MCCALL AVE, 2 POLES N/O BARBARA ST | SELMA | GJME | 2020-10-23 | ECFOH | WILSON | 2020-10-14 | LMMY | 2020-10-23 | 2020-11-28 | 2020-11-28 | A0S2 | 2020-11-30 | 1 | RSGG 111020 | B | 010
T0 | IR | KE | Bakersfield | 119942000 | EC | 540 | 44506021 | KAA | DOCC | B |  | RELW OH COMP CPGE PROG CPGD TER0 | 2020-11-14 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 328 S BROWN ST BAKERSFI | ORAS NOCO ATCO | ED.66-2928333000.STRU.POLE | 2928333 | 25337-2104, BAKERSFIELD | 13437 | 120300149 | 100146793 | 35.3607 | -118.9834 | 328 S BROWN ST | BAKERSFIELD | J6AG | 2020-10-23 | ECFOH | BUENROSTRO | 2020-10-14 | LMMY | 2020-10-23 | 2020-12-14 | 2020-12-14 | DOR2 | 2020-12-15 | 1 |  | B | 015
T0 | IR | FR | Dinuba | 119942052 | EC | 540 | 44517149 | KAA | DOCC srdy | B |  | RELW OH COMP PROG CPGD TER0 | 2021-01-12 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 80FT N/W/O 20866 E PARL | ORAS NOCO ATCO | ED.70-15234D0000.STRU.POLE | 15234D | 25453-1110, WAHTOKE | 64934 |  | 100830145 | 36.6119 | -119.415 | 80FT N/W/O 20866 E PARLIER AVE | REEDLEY | J6AG | 2020-10-23 | ECFOH | BUENROSTRO | 2020-10-12 | LMMY | 2020-10-23 | 2020-11-30 | 2020-11-30 | G2BG | 2020-12-01 | 1 |  | B | 010
T3 | IR | SI | Placerville | 119942053 | EC | 540 | 44506357 | KAA | DOCC srdy | B |  | RELW OH COMP CCNT PROG TER3 | 2020-11-13 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 3383 MEDER RD CAMERON P | ORAS NOCO ATCO | ED.21-J370400000.STRU.POLE | J3704 | 15365-2105, SHINGLE SPRINGS | 11869 | 120548201 | 101415083 | 38.6826 | -120.9649 | 3383 MEDER RD | CAMERON PARK | J6AG | 2020-10-23 | ECFOH | JOINER | 2020-10-12 | LMMY | 2020-10-23 | 2020-11-15 | 2020-11-15 | N3M6 | 2020-11-18 | 1 | DPB9 | B | 009
T0 | IR | FR | Fresno | 119942056 | EC | 540 | 44505645 | KAA | DOCC crdy srdy | B |  | RELW OH COMP PROG CPGD TER0 | 2020-11-12 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 1166 S BRAWLEY AVE FRES | ORAS NOCO ATCO | ED.70-14194A0000.STRU.POLE | 14194A | 25373-1112, WEST FRESNO | D2832 |  | 100656267 | 36.7182 | -119.8623 | 1166 S BRAWLEY AVE | FRESNO | GJME | 2020-10-23 | ECFOH | WILSON | 2020-10-12 | LMMY | 2020-10-23 | 2020-11-20 | 2020-11-20 | BRCB | 2020-11-23 | 1 | RSGG 102920 | B | 010
T0 | IR | FR | Fresno | 119942058 | EC | 540 | 44505647 | KAA | DOCC crdy srdy | B |  | RELW OH COMP PROG CPGD TER0 | 2020-11-12 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 1589 N GARFIELD AVE FRE | ORAS NOCO ATCO | ED.70-13196D0000.STRU.POLE | 13196D | 25270-1110, KEARNEY | D9117 |  | 100628476 | 36.7587 | -119.925 | 1589 N GARFIELD AVE | FRESNO | J6AG | 2020-10-23 | ECFOH | WILSON | 2020-10-12 | LMMY | 2020-10-23 | 2020-11-23 | 2020-11-23 | BRCB | 2020-11-24 | 1 | RSGG 102920 | B | 010
T0 | IR | KE | Bakersfield | 119942412 | EC | 540 | 44505879 | KAA | DOCC crdy srdy | B |  | RELW OH COMP CPGE PROG CPGD TER0 | 2020-11-13 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - I/B/O KISCO SALEES ALLE | ORAS NOCO ATCO | ED.66-2928293000.STRU.POLE | 2928293 | 25337-2106, BAKERSFIELD | 15543 | 120290602 | 100163672 | 35.3776 | -118.9985 | I/B/O KISCO SALEES ALLEY WAY 301 SUMNER ST | BAKERSFIELD | J6AG | 2020-10-23 | ECFOH | BUENROSTRO | 2020-10-13 | LMMY | 2020-10-23 | 2020-11-12 | 2020-11-12 | M1V6 | 2020-11-19 | 1 |  | B | 015
T0 | IR | KE | Bakersfield | 119942413 | EC | 540 | 44506022 | KAA | DOCC crdy | B |  | RELW OH COMP CPGE PROG CPGD TER0 | 2020-11-14 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - I/F/O 633 WILLIAMS ST B | ORAS NOCO ATCO | ED.66-2928286000.STRU.POLE | 2928286 | 25337-2106, BAKERSFIELD | 15564 | 120432576 | 100244864 | 35.3714 | -118.9792 | I/F/O 633 WILLIAMS ST | BAKERSFIELD | GJME | 2020-10-23 | ECFOH | BUENROSTRO | 2020-10-14 | LMMY | 2020-10-23 | 2020-11-30 | 2020-11-30 | SCTB | 2020-12-02 | 1 |  | B | 015
T0 | IR | FR | Fresno | 119942414 | EC | 540 | 44505648 | KAA | DOCC crdy srdy | B |  | RELW OH COMP PROG CPGD TER0 | 2020-11-15 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 2039 N KATY LN FRESNO | ORAS NOCO ATCO | ED.70-1319266000.STRU.POLE | 1319266 | 25373-1112, WEST FRESNO | D9124 |  | 100636981 | 36.7653 | -119.8751 | 2039 N KATY LN | FRESNO | GJME | 2020-10-23 | ECFOH | WILSON | 2020-10-15 | LMMY | 2020-10-23 | 2020-11-23 | 2020-11-23 | BRCB | 2020-11-24 | 1 | RSGG 102920 | B | 010
T0 | IR | FR | Fresno | 119942415 | EC | 540 | 44517150 | KAA | DOCC srdy | B |  | RELW OH COMP PROG CPGD TER0 | 2021-01-12 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 1253 S TURNEY AVE SANG | ORAS NOCO ATCO | ED.70-1422400000.STRU.POLE | 14224 | 25444-1106, RAINBOW | 2802 |  | 100814755 | 36.7172 | -119.5316 | 1253 S TURNEY AVE | SANGER | J6AG | 2020-10-23 | ECFOH | ARAUJO | 2020-10-12 | LMMY | 2020-10-23 | 2020-12-04 | 2020-12-04 | MWS0 | 2020-12-07 | 1 |  | B | 010
T2 | IR | ST | Stockton | 119946724 | EC | 540 |  |  |  | E |  | POHW OH CNCL JAR CPGD TER2 | 2021-04-13 |  | Cutout | Broken/Damaged | Repair | CUTO_BROK_REPA - 8039 WARREN RD. VALLEY | NOCO ATCO | ED.93-Q192500000.STRU.POLE | Q1925 | 16299-1101, CORRAL | 965803 | 120513917 | 102040219 | 38.1317 | -120.9266 | 8039 WARREN RD. | VALLEY SPRINGS | GJME | 2020-10-27 | ECFOH | CHAMBERS | 2020-10-13 | LMMY | 2020-10-26 | 2020-12-02 |  |  | 2020-12-02 | 2 |  | E | 005
T2 | IR | ST | Stockton | 119946727 | EC | 540 |  |  |  | E |  | POHW OH PROG TER2 | 2021-04-14 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 7777 SOUTHWORTH RD. VAL | OSNO ATCO | ED.93-Q191300000.STRU.POLE | Q1913 | 16299-1101, CORRAL | 11655 | 120514228 | 102040061 | 38.1484 | -120.9421 | 7777 SOUTHWORTH RD. | VALLEY SPRINGS | GJME | 2020-10-27 | ECFOH | CHAMBERS | 2020-10-14 | LMMY | 2020-10-26 | 2020-10-14 |  |  |  | 1 |  | E | 005
T0 | IR | FR | Fresno | 119946791 | EC | 540 |  |  |  | E |  | POHW OH PROG TER0 | 2021-04-12 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 494 N FAIRBANKS AVE SAN | OSNO ATCO | ED.70-14221C0000.STRU.POLE | 14221C | 25444-1106, RAINBOW | 36552 | 110351424 | 103145820 | 36.7275 | -119.5697 | 494 N FAIRBANKS AVE | SANGER | GJME | 2020-10-27 | ECFOH | ARAUJO | 2020-10-12 | LMMY | 2020-10-26 | 2020-10-12 |  |  |  | 1 |  | E | 010
T0 | IR | EB | Richmond | 119946798 | EC | 540 |  |  |  | E |  | POHW OH PROG TER0 | 2021-04-12 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 2274 ORLEANS DR. PINOLE | OSNO ATCO | ED.28-B040900000.STRU.POLE | B0409 | 01392-1103, FRANKLIN | R6397 | 110433935 | 101444836 | 38.0102 | -122.296 | 2274 ORLEANS DR. | PINOLE | GJME | 2020-10-27 | ECFOH | LAND | 2020-10-12 | LMMY | 2020-10-26 | 2020-10-12 |  |  |  | 1 |  | E | 007
T0 | IR | FR | Fresno | 119946892 | EC | 540 |  |  |  | E |  | POHW OH PROG TER0 | 2021-04-12 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 14400 E CALIFORNIA AVE | OSNO ATCO | ED.70-1422400000.STRU.POLE | 14224 | 25444-1106, RAINBOW | 2818 |  | 100814779 | 36.721 | -119.5327 | 14400 E CALIFORNIA AVE | SANGER | GJME | 2020-10-27 | ECFOH | ARAUJO | 2020-10-12 | LMMY | 2020-10-26 | 2020-10-12 |  |  |  | 1 |  | E | 010
T0 | IR | KE | Bakersfield | 119946899 | EC | 540 | 44592843 | KAA | UNSC | E |  | RELW OH PROG TER0 | 2021-04-15 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - I/F/O 2214 S O ST SOUTH | NOPR ORAS ATCO | ED.66-3028073000.STRU.POLE | 3028073 | 25337-2109, BAKERSFIELD | 64867 | 120389445 | 100155621 | 35.334 | -119.0129 | I/F/O 2214 S O ST | SOUTHGATE | GJME | 2020-10-27 | ECFOH | BUENROSTRO | 2020-10-15 | LMMY | 2020-10-26 | 2020-10-15 |  |  |  | 1 |  | E | 015
T0 | IR | KE | Bakersfield | 119947004 | EC | 540 | 44592844 | KAA | UNSC | E |  | RELW OH PROG TER0 | 2021-04-15 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 12500 E PANAMA LN BAKER | NOPR ORAS ATCO | ED.66-3029216000.STRU.POLE | 3029216 | 25391-1106, LAMONT | 1106/2 |  | 103227738 | 35.2963 | -118.8769 | 12500 E PANAMA LN | BAKERSFIELD | GJME | 2020-10-27 | ECFOH | ARAUJO | 2020-10-15 | LMMY | 2020-10-26 | 2020-10-15 |  |  |  | 1 |  | E | 015
BUFFER | IR | SI | Placerville | 119947290 | EC | 540 |  |  |  | E |  | POHW OH PROG BUFF | 2021-04-12 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 3640 LARIAT RD., SHINGL | OSNO ATCO | ED.21-J372500000.STRU.POLE | J3725 | 15365-1103, SHINGLE SPRINGS | 8317 | 120508500 | 101374509 | 38.6494 | -120.959 | 3640 LARIAT RD., | CAMERON PARK | GJME | 2020-10-27 | ECFOH | JOINER | 2020-10-12 | LMMY | 2020-10-26 | 2020-10-12 |  |  |  | 1 |  | E | 009
T0 | IR | KE | Bakersfield | 119947293 | EC | 540 | 44592845 | KAA | UNSC | E |  | RELW OH PROG TER0 | 2021-04-14 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 2.1 MI E/O FAIRFAX RD B | NOPR ORAS ATCO | ED.66-3028246000.STRU.POLE | 3028246 | 25277-2108, MAGUNDEN | 14991 | 120329376 | 100144467 | 35.2996 | -118.9255 | 2.1 MI E/O FAIRFAX RD | BAKERSFIELD | GJME | 2020-10-27 | ECFOH | BUENROSTRO | 2020-10-14 | LMMY | 2020-10-26 | 2020-10-14 |  |  |  | 1 |  | E | 015
T0 | IR | KE | Bakersfield | 119947330 | EC | 540 | 44592846 | KAA | UNSC | E |  | RELW OH PROG TER0 | 2021-04-12 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - W/O SIMON DR COTTONWOOD | NOPR ORAS ATCO | ED.66-3028042000.STRU.POLE | 3028042 | 25277-2108, MAGUNDEN | 16953 |  | 100135103 | 35.3508 | -118.9788 | W/O SIMON DR | BAKERSFIELD | GJME | 2020-10-27 | ECFOH | BUENROSTRO | 2020-10-12 | LMMY | 2020-10-26 | 2020-10-12 |  |  |  | 1 |  | E | 015
T0 | IR | KE | Bakersfield | 119947335 | EC | 540 | 44592847 | KAA | UNSC | E |  | RELW OH PROG TER0 | 2021-04-14 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - I/B/O 3140 NILES ST BAK | NOPR ORAS ATCO | ED.66-2928263000.STRU.POLE | 2928263 | 25277-1101, MAGUNDEN | 16716 | 120491980 | 100141175 | 35.3764 | -118.948 | I/B/O 3140 NILES ST | BAKERSFIELD | GJME | 2020-10-27 | ECFOH | BUENROSTRO | 2020-10-14 | LMMY | 2020-10-26 | 2020-10-14 |  |  |  | 1 |  | E | 015
T0 | IR | KE | Bakersfield | 119947434 | EC | 540 | 44592848 | KAA | UNSC | E |  | RELW OH PROG TER0 | 2021-04-13 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - I/B/O 819 S HALEY ST BA | NOPR ORAS ATCO | ED.66-2928332000.STRU.POLE | 2928332 | 25337-2106, BAKERSFIELD | 13489 | 120428146 | 100146931 | 35.3657 | -118.9833 | I/B/O 819 S HALEY ST | BAKERSFIELD | GJME | 2020-10-27 | ECFOH | BUENROSTRO | 2020-10-13 | LMMY | 2020-10-26 | 2020-10-13 |  |  |  | 1 |  | E | 015
T2 | IR | SI | Placerville | 119947461 | EC | 540 |  |  |  | E |  | POHW OH PROG TER2 | 2021-04-13 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 3898 DE SABLA RD CAMERO | OSNO ATCO | ED.21-J371800000.STRU.POLE | J3718 | 15365-1103, SHINGLE SPRINGS | 8717 | 120257342 | 101376898 | 38.6625 | -120.9767 | 3898 DE SABLA RD | CAMERON PARK | GJME | 2020-10-27 | ECFOH | JOINER | 2020-10-13 | LMMY | 2020-10-26 | 2020-10-13 |  |  |  | 1 |  | E | 009
T0 | IR | FR | Fresno | 119947466 | EC | 540 |  |  |  | E |  | POHW OH PROG TER0 | 2021-04-13 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - R/O 3647 E HUNTINGTON B | OSNO ATCO | ED.70-1420025000.STRU.POLE | 1420025 | 25228-1114, CALIFORNIA AVE | D10922 | 120456954 | 100864116 | 36.7401 | -119.7632 | R/O 3647 E HUNTINGTON BLVD IN ALLEY. | FRESNO | GJME | 2020-10-27 | ECFOH | WILSON | 2020-10-13 | LMMY | 2020-10-26 | 2020-10-13 |  |  |  | 1 |  | E | 010
T0 | IR | FR | Fresno | 119947623 | EC | 540 |  |  |  | E |  | POHW OH PROG TER0 | 2021-04-15 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - A/F 2811 W CALIFORNIA A | OSNO ATCO | ED.70-1420076000.STRU.POLE | 1420076 | 25373-1112, WEST FRESNO | 87339 | 110423282 | 103152682 | 36.7213 | -119.8416 | A/F 2811 W CALIFORNIA AVE. N/S CALIFORNIA AVE, 5 P | FRESNO | GJME | 2020-10-27 | ECFOH | WILSON | 2020-10-15 | LMMY | 2020-10-26 | 2020-10-15 |  |  |  | 1 |  | E | 010
T0 | IR | KE | Bakersfield | 119947627 | EC | 540 | 44592849 | KAA | UNSC | E |  | RELW OH PROG TER0 | 2021-04-14 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - S/O 201 DONNA AVE BAKER | NOPR ORAS ATCO | ED.66-2928315000.STRU.POLE | 2928315 | 25337-2109, BAKERSFIELD | 390355 | 120388005 | 100243885 | 35.3572 | -119.0075 | S/O 201 DONNA AVE | BAKERSFIELD | GJME | 2020-10-27 | ECFOH | BUENROSTRO | 2020-10-14 | LMMY | 2020-10-26 | 2020-10-14 |  |  |  | 1 |  | E | 015
T3 | IR | ST | Jackson | 119947667 | EC | 605 | 31518110 | 2AA | FICL srdy | B |  | RELW OH COMP JAR CPGE CPGD TER3 | 2021-01-14 |  | Cutout | Broken/Damaged | Replace | CUTO_BROK_REPL - 4511 N RAILROAD FLAT RD | ORAS NOCO NOPT ATCO | ED.95 | NOMAP | 16320-1102, WEST POINT | 4790 |  | 102316344 | 38.3825 | -120.5252 | 4511 N RAILROAD FLAT RD | WEST POINT | GJME | 2020-10-27 | ECFOH | WITKOWSKI | 2020-10-14 | LMMY | 2020-10-26 | 2020-11-10 | 2020-11-10 | M7B0 | 2020-11-13 | 2 |  | E | 005
T2 | IR | SI | Placerville | 119959853 | EC | 540 | 44515566 | KAA | DOCC srdy | B |  | RELW OH COMP PROG CPGD TER2 | 2021-01-22 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 3040 WINTER CREEK RD. S | ORAS NOCO ATCO | ED.21-L440000000.STRU.POLE | L44 | 15366-2102, APPLE HILL | 18829 |  | 101417064 | 38.5797 | -120.7115 | 3040 WINTER CREEK RD. | SOMERSET | J6AG | 2020-10-29 | ECFOH | JERNIGAN | 2020-10-22 | LMMY | 2020-10-29 | 2020-11-24 | 2020-11-24 | TXV6 | 2020-11-25 | 1 | AXFT | B | 009
T0 | IR | FR | Fresno | 119959898 | EC | 540 |  |  |  | E |  | POHW OH PROG TER0 | 2021-10-19 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - R/O 923 E BREMER AVE IN | OSNO ATCO | ED.70-1320336000.STRU.POLE | 1320336 | 25392-1108, MANCHESTER | D8538 | 120408764 | 100865421 | 36.7533 | -119.7996 | R/O 923 E BREMER AVE IN ALLEY TO NORTH | FRESNO | J6AG | 2020-10-29 | ECFOH | WILSON | 2020-10-19 | LMMY | 2020-10-29 | 2020-10-19 |  |  |  | 1 |  | E | 010
T3 | IR | ST | Stockton | 119960230 | EC | 540 |  |  |  | E |  | POHW OH PROG TER3 | 2021-04-23 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 17709 ANTELOPE CT PIONE | OSNO ATCO | ED.95-J292200000.STRU.POLE | J2922 | 16375-1102, PINE GROVE | L3299 |  | 101253235 | 38.4628 | -120.5435 | 17709 ANTELOPE CT | PIONEER | J6AG | 2020-10-29 | ECFOH | ARAUJO | 2020-10-23 | LMMY | 2020-10-29 | 2020-10-23 |  |  |  | 1 |  | E | 003
T3 | IR | ST | Angels Camp | 119960272 | EC | 540 | 44510188 | KAA | DOCC srdy | B |  | RELW OH COMP CPGE PROG CPGD TER3 | 2021-01-19 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 3025 EVERGREEN DR. ARNO | ORAS NOCO ATCO | ED.95-O331900000.STRU.POLE | O3319 | 16282-1701, STANISLAUS | L2687 |  | 101280325 | 38.2325 | -120.3748 | 3025 EVERGREEN DR. | ARNOLD | J6AG | 2020-10-29 | ECFOH | LAND | 2020-10-19 | LMMY | 2020-10-29 | 2020-11-19 | 2020-11-19 | RJOF | 2020-11-20 | 1 |  | B | 005
T2 | IR | SI | Placerville | 119960312 | EC | 540 |  |  |  | E |  | POHW OH PROG TER2 | 2021-10-21 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 3170 GOLD NUGGET WAY PL | OSNO ATCO | ED.21-I410200000.STRU.POLE | I4102 | 15308-1111, PLACERVILLE | 41379 |  | 101406926 | 38.7258 | -120.8215 | 3170 GOLD NUGGET WAY | PLACERVILLE | J6AG | 2020-10-29 | ECFOH | BUENROSTRO | 2020-10-21 | LMMY | 2020-10-29 | 2020-10-21 |  |  |  | 1 |  | E | 009
T2 | IR | FR | Dinuba | 119960469 | EC | 540 |  |  |  | E |  | POHW OH PROG TER2 | 2021-10-20 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - GPS COORDINATES = 36.72 | OSNO ATCO | ED.70-1428054000.STRU.POLE | 1428054 | 25406-1102, DUNLAP | 7605F |  | 103072764 | 36.737 | -118.9568 | #1 N/O LILY/WILLOW/NIF | Kings Canyon National Pk | J6AG | 2020-10-29 | ECFOH | WILSON | 2020-10-20 | LMMY | 2020-10-29 | 2020-10-20 |  |  |  | 1 |  | E | 054
T2 | IR | SI | Placerville | 119960650 | EC | 540 |  |  |  | E |  | POHW OH PROG TER2 | 2021-10-22 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 7101 DORADO CANYON RD. | OSNO ATCO | ED.21-K440000000.STRU.POLE | K44 | 15366-2102, APPLE HILL | 10303 |  | 101394595 | 38.5993 | -120.6973 | 7101 DORADO CANYON RD. | SOMERSET | J6AG | 2020-10-29 | ECFOH | JERNIGAN | 2020-10-22 | LMMY | 2020-10-29 | 2020-10-22 |  |  |  | 1 |  | E | 009
T0 | IR | FR | Fresno | 119960659 | EC | 540 |  |  |  | E |  | POHW OH PROG TER0 | 2021-10-19 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - R/O IN COMPLEX PARKING | OSNO ATCO | ED.70-1320275000.STRU.POLE | 1320275 | 25392-1106, MANCHESTER | 263575 | 120300764 | 100854653 | 36.7693 | -119.7799 | R/O IN COMPLEX PARKING LOT - 2667 E WELDON AVE | MCLANE | J6AG | 2020-10-29 | ECFOH | WILSON | 2020-10-19 | LMMY | 2020-10-29 | 2020-10-19 |  |  |  | 1 |  | E | 010
T3 | IR | ST | Jackson | 119960854 | EC | 540 | 44510189 | KAA | DOCC crdy srdy | B |  | RELW OH COMP CCNT PROG TER3 | 2021-01-23 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 26150 OXBOW RD PIONEER | ORAS NOCO NOPT ATCO | ED.95-K290700000.STRU.POLE | K2907 | 16375-1102, PINE GROVE | L1761 |  | 101266279 | 38.4468 | -120.5425 | 26150 OXBOW RD | PIONEER | J6AG | 2020-10-29 | ECFOH | ARAUJO | 2020-10-23 | LMMY | 2020-10-29 | 2020-11-19 | 2020-11-19 | CONT | 2020-11-23 | 1 |  | B | 003
T3 | IR | ST | Angels Camp | 119960891 | EC | 540 | 44510190 | KAA | DOCC srdy | B |  | RELW OH COMP PROG CPGD TER3 | 2021-01-21 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 2867 NEW MCKAYS DAM RD. | ORAS NOCO ATCO | ED.95-O331400000.STRU.POLE | O3314 | 16282-1702, STANISLAUS | L2681 |  | 101278830 | 38.2389 | -120.3745 | 2867 NEW MCKAYS DAM RD. | ARNOLD | J6AG | 2020-10-29 | ECFOH | LAND | 2020-10-21 | LMMY | 2020-10-29 | 2020-11-19 | 2020-11-19 | RJOF | 2020-11-20 | 1 |  | B | 005
T3 | IR | ST | Angels Camp | 119998000 | EC | 540 |  |  |  | E |  | POHW OH PROG TER3 | 2021-04-28 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - A/F 995 SHOSHONE DR. DO | OSNO ATCO | ED.95-MM36220000.STRU.POLE | MM3622 | 16369-2102, SALT SPRINGS | 81017 |  | 101279927 | 38.3102 | -120.2689 | A/F 995 SHOSHONE DR. | ARNOLD | GJME | 2020-11-09 | ECFOH | LAND | 2020-10-28 | LMMY | 2020-11-09 | 2020-10-28 |  |  |  | 1 |  | E | 005
T3 | IR | ST | Angels Camp | 119998001 | EC | 540 |  |  |  | E |  | POHW OH CNCL PROG CPGD TER3 | 2021-04-28 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - A/F 1359 SHOSHONE DR. A | NOCO ATCO | ED.95-MM36230000.STRU.POLE | MM3623 | 16369-2102, SALT SPRINGS | 81017 |  | 101279302 | 38.3114 | -120.2643 | A/F 1359 SHOSHONE DR. | ARNOLD | GJME | 2020-11-09 | ECFOH | LAND | 2020-10-28 | LMMY | 2020-11-09 | 2020-11-25 |  |  | 2020-11-25 | 1 |  | E | 005
ZONE 1 | IR | SI | Grass Valley | 119998003 | EC | 540 | 44521460 | KAA | DOCC srdy | B |  | RELW OH COMP PROG CPGD ZNE1 | 2021-01-30 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 12364 FRANCIS DR. GRASS | ORAS NOCO ATCO | ED.22-O091900000.STRU.POLE | O0919 | 15248-1106, BRUNSWICK | 32821 |  | 100071087 | 39.1476 | -121.0462 | 12364 FRANCIS DR. | GRASS VALLEY | GJME | 2020-11-09 | ECFOH | JOINER | 2020-10-30 | LMMY | 2020-11-09 | 2020-11-23 | 2020-11-23 | DBE4 | 2020-11-24 | 1 | AXFT | B | 029
T3 | IR | SI | Placerville | 119998005 | EC | 540 | 44522966 | KAA | DOCC srdy | B |  | RELW OH CNCL PROG CPGD TER3 | 2020-11-30 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 4500 SLY PARK RD POLLOC | ORAS NOCO ATCO | ED.21-H472300000.STRU.POLE | H4723 | 15276-2101, EL DORADO PH | 11823 |  | 101392607 | 38.7382 | -120.5729 | 4500 SLY PARK RD | POLLOCK PINES | J6AG | 2020-11-09 | ECFOH | ARAUJO | 2020-10-30 | LMMY | 2020-11-09 | 2020-11-25 |  |  | 2020-12-02 | 1 | AXFT | B | 009
T3 | IR | SI | Placerville | 119998006 | EC | 540 |  |  |  | E |  | POHW OH CNCL PROG CPGD TER3 | 2021-04-30 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 7031 PIONEER DR GRIZZLY | NOCO ATCO | ED.21-K480100000.STRU.POLE | K4801 | 15276-2101, EL DORADO PH | 2825 | 120559610 | 101399884 | 38.6321 | -120.5467 | 7031 PIONEER DR | GRIZZLY FLATS | GJME | 2020-11-09 | ECFOH | ARAUJO | 2020-10-31 | LMMY | 2020-11-09 | 2020-12-08 |  |  | 2020-12-08 | 1 |  | E | 009
T2 | IR | SI | Grass Valley | 119998007 | EC | 540 |  |  |  | E |  | POHW OH PROG TER2 | 2021-04-28 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 16684 SCOPAR RD GRASS V | OSNO ATCO | ED.22-P080400000.STRU.POLE | P0804 | 15269-1103, HIGGINS | 31467 |  | 100013936 | 39.1298 | -121.0852 | 16684 SCOPAR RD | GRASS VALLEY | GJME | 2020-11-09 | ECFOH | WITKOWSKI | 2020-10-28 | LMMY | 2020-11-09 | 2020-10-28 |  |  |  | 1 |  | E | 029
T0 | IR | SI | Grass Valley | 119998221 | EC | 540 | 44522968 | KAA | DOCC srdy | B |  | RELW OH CNCL PROG CPGD TER0 | 2020-12-30 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 11495 ALTA SIERRA DR., | ORAS NOCO ATCO | ED.22-O092300000.STRU.POLE | O0923 | 15269-1104, HIGGINS | 9543 |  | 100071179 | 39.1402 | -121.0543 | 11495 ALTA SIERRA DR., | GRASS VALLEY | J6AG | 2020-11-09 | ECFOH | JOINER | 2020-10-30 | LMMY | 2020-11-09 | 2020-11-18 |  |  | 2020-11-23 | 1 | AXFT | B | 029
T2 | IR | SI | Placerville | 119998223 | EC | 540 | 44522970 | KAA | DOCC srdy | B |  | RELW OH COMP PROG CPGD TER2 | 2021-01-28 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 400 RESERVOIR ST PLACER | ORAS NOCO ATCO | ED.21-I410500000.STRU.POLE | I4105 | 15308-1112, PLACERVILLE | 52141 |  | 101404586 | 38.7291 | -120.8001 | 400 RESERVOIR ST | PLACERVILLE | J6AG | 2020-11-09 | ECFOH | ARAUJO | 2020-10-28 | LMMY | 2020-11-09 | 2020-11-23 | 2020-11-23 | RLTL | 2020-11-24 | 1 | AXFT | B | 009
T2 | IR | SI | Placerville | 119998225 | EC | 540 |  |  |  | E |  | POHW OH PROG TER2 | 2021-10-28 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 400 RESERVOIR ST PLACER | OSNO ATCO | ED.21-I410500000.STRU.POLE | I4105 | 15308-1112, PLACERVILLE | 52141 |  | 101404583 | 38.7285 | -120.8009 | 400 RESERVOIR ST | PLACERVILLE | J6AG | 2020-11-09 | ECFOH | ARAUJO | 2020-10-28 | LMMY | 2020-11-09 | 2020-10-28 |  |  |  | 1 |  | E | 009
T2 | IR | SI | Grass Valley | 119998227 | EC | 540 |  |  |  | E |  | POHW OH PROG TER2 | 2021-04-30 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 6030 JOHNSTOWN CREEK RD | OSNO ATCO | ED.20-V142100000.STRU.POLE | V1421 | 15308-2106, PLACERVILLE | 18875 |  | 100056017 | 38.8231 | -120.8694 | 6030 JOHNSTOWN CREEK RD. | GRASS VALLEY | GJME | 2020-11-09 | ECFOH | LAND | 2020-10-31 | LMMY | 2020-11-09 | 2020-10-31 |  |  |  | 1 |  | E | 029
T2 | IR | SI | Auburn | 119998228 | EC | 540 | 44521461 | KAA | DOCC srdy | B |  | RELW OH COMP PROG CPGD TER2 | 2020-12-01 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 5131 MARSHALL RD. GARDE | ORAS NOCO ATCO | ED.20-V141200000.STRU.POLE | V1412 | 15308-2106, PLACERVILLE | 4271 |  | 100108730 | 38.8486 | -120.8638 | 5151 MARSHALL RD. | GARDEN VALLEY | GJME | 2020-11-09 | ECFOH | LAND | 2020-10-31 | LMMY | 2020-11-09 | 2020-12-07 | 2020-12-07 | RLTL | 2020-12-07 | 1 | DPB9 | B | 009
T2 | IR | SI | Auburn | 119998444 | EC | 540 |  |  |  | E |  | POHW OH PROG TER2 | 2021-04-29 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 9205 WISE RD AUBURN | OSNO ATCO | ED.20-U070300000.STRU.POLE | U0703 | 15227-1102, WISE | 531 |  | 100085720 | 38.9058 | -121.1315 | 9205 WISE RD | AUBURN | GJME | 2020-11-09 | ECFOH | GONZALES-NAT | 2020-10-29 | LMMY | 2020-11-09 | 2020-10-29 |  |  |  | 1 |  | E | 031
T2 | IR | SI | Auburn | 119998446 | S9 | 540 |  |  |  | E |  | POHW OH CNCL PROG TER2 | 2021-10-30 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 3020 AYRES HOLMES RD, A | NOCO ATCO | ED.20-T061800000.STRU.POLE | T0618 | 15227-1102, WISE | 531 |  | 100073241 | 38.927 | -121.176 | 3020 AYRES HOLMES RD, AUBURN | AUBURN | GJME | 2020-11-09 | ECFOH | GONZALES-NAT | 2020-10-30 | LMMY | 2020-11-09 | 2020-11-09 |  |  | 2020-11-09 | 1 |  | E | 031
T2 | IR | SI | Placerville | 120048645 | EC | 540 |  |  |  | E |  | POHW OH PROG TER2 | 2021-11-03 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 6030 OUTINGDALE RD. SOM | OSNO ATCO | ED.21-K430000000.STRU.POLE | K43 | 15366-2102, APPLE HILL | 19809 |  | 101401914 | 38.6184 | -120.7192 | 6030 OUTINGDALE RD. | SOMERSET | J6AG | 2020-11-17 | ECFOH | JERNIGAN | 2020-11-03 | LMMY | 2020-11-17 | 2020-11-03 |  |  |  | 1 |  | E | 009
T0 | IR | SI | Grass Valley | 120049090 | EC | 540 |  |  |  | E |  | POHW OH PROG TER0 | 2021-11-04 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 12802 LOMA RICA DR GRAS | OSNO ATCO | ED.22-N100300000.STRU.POLE | N1003 | 15248-1102, BRUNSWICK | 8997 |  | 100036914 | 39.2214 | -121.0058 | 12802 LOMA RICA DR | GRASS VALLEY | J6AG | 2020-11-17 | ECFOH | ARAUJO | 2020-11-04 | LMMY | 2020-11-17 | 2020-11-04 |  |  |  | 1 |  | E | 029
T2 | IR | SI | Grass Valley | 120049173 | EC | 540 |  |  |  | E |  | POHW OH PROG TER2 | 2021-11-03 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 227 NEVADA ST NEVADA CI | OSNO ATCO | ED.22-M100200000.STRU.POLE | M1002 | 15248-1103, BRUNSWICK | 1963 |  | 100072967 | 39.2644 | -121.015 | 227 NEVADA ST | NEVADA CITY | J6AG | 2020-11-17 | ECFOH | WITKOWSKI | 2020-11-03 | LMMY | 2020-11-17 | 2020-11-03 |  |  |  | 1 |  | E | 029
T3 | IR | SI | Auburn | 120049461 | EC | 540 |  |  |  | E |  | POHW OH PROG TER3 | 2021-05-04 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 912 STOCKTON ST, DUTCH | OSNO ATCO | ED.20-N141400000.STRU.POLE | N1414 | 15230-1101, BONNIE NOOK | 4513 |  | 100009196 | 39.2039 | -120.8375 | 912 STOCKTON ST, | DUTCH FLAT | J6AG | 2020-11-17 | ECFOH | GONZALES-NAT | 2020-11-04 | LMMY | 2020-11-17 | 2020-11-04 |  |  |  | 1 |  | E | 031
T3 | IR | SI | Auburn | 120049464 | EC | 540 |  |  |  | E |  | POHW OH PROG TER3 | 2021-05-04 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 908 SACRAMENTO, DUTCH F | OSNO ATCO | ED.20-N141400000.STRU.POLE | N1414 | 15230-1101, BONNIE NOOK | 6377 |  | 100009287 | 39.2037 | -120.8385 | 908 SACRAMENTO, | DUTCH FLAT | J6AG | 2020-11-17 | ECFOH | GONZALES-NAT | 2020-11-04 | LMMY | 2020-11-17 | 2020-11-04 |  |  |  | 1 |  | E | 031
T2 | IR | SI | Grass Valley | 120049465 | EC | 540 |  |  |  | E |  | POHW OH PROG TER2 | 2021-11-06 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 200 FT S/O 15291 LAKEWO | OSNO ATCO | ED.22-O111400000.STRU.POLE | O1114 | 15248-1106, BRUNSWICK | 8949 |  | 100012810 | 39.161 | -120.959 | 200 FT S/O 15291 LAKEWOOD LN | GRASS VALLEY | J6AG | 2020-11-17 | ECFOH | BUENROSTRO | 2020-11-06 | LMMY | 2020-11-17 | 2020-11-06 |  |  |  | 1 |  | E | 029
T0 | IR | NV | Oroville | 120086270 | EC | 540 | 44571306 | KAA | DOCC srdy | B |  | RELW OH COMP PROG CPGD TER0 | 2020-12-10 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 228 STIMPSON RD OROVILL | ORAS NOCO ATCO | ED.13-J231600000.STRU.POLE | J2316 | 10291-1106, WYANDOTTE | 5591 |  | 100382041 | 39.3738 | -121.5953 | 228 STIMPSON RD | OROVILLE | RXHV | 2020-11-23 | ECFOH | BUENROSTRO | 2020-11-10 | LMMY | 2020-11-23 | 2020-12-10 | 2020-12-10 | KESG | 2020-12-17 | 1 |  | B | 004
T0 | IR | NV | Oroville | 120086278 | EC | 540 |  |  |  | E |  | POHW OH PROG TER0 | 2021-05-10 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 2900 DALY AVE, OROVILLE | OSNO ATCO | ED.13-I241900000.STRU.POLE | I2419 | 10291-1109, WYANDOTTE | 5997 |  | 100394280 | 39.4214 | -121.5242 | 2900 DALY AVE, | OROVILLE | GJME | 2020-11-23 | ECFOH | GONZALES-NAT | 2020-11-10 | LMMY | 2020-11-23 | 2020-11-10 |  |  |  | 1 |  | E | 004
T0 | IR | NV | Oroville | 120086380 | EC | 540 |  |  |  | E |  | POHW OH JAR TER0 | 2021-05-12 |  | Cutout | Broken/Damaged | Repair | CUTO_BROK_REPA - C/O PINECREST AND UPPER | OSNO ATCO | ED.13-H242300000.STRU.POLE | H2423 | 10291-1109, WYANDOTTE | 1501 |  | 100371407 | 39.459 | -121.5319 | C/O PINECREST AND UPPER PALERMO RD | OROVILLE | GJME | 2020-11-23 | ECFOH | GONZALES-NAT | 2020-11-12 | LMMY | 2020-11-23 | 2020-11-12 |  |  |  | 2 |  | E | 004
T2 | IR | SI | Grass Valley | 120086510 | EC | 540 | 44565282 | KAA | DOCC srdy | B |  | RELW OH CNCL JAR CPGD TER2 | 2020-12-09 |  | Cutout | Broken/Damaged | Repair | CUTO_BROK_REPA - 13444 HOPEFUL HILL RD N | ORAS NOCO ATCO | ED.22-M080000000.STRU.POLE | M08 | 15313-2102, NARROWS | 31481 | 120031794 | 100088919 | 39.2504 | -121.1044 | 13444 HOPEFUL HILL RD | NEVADA CITY | GJME | 2020-11-23 | ECFOH | JOINER | 2020-11-09 | LMMY | 2020-11-23 | 2020-12-01 |  |  | 2020-12-02 | 2 | DPB9 | B | 029
T2 | IR | SI | Grass Valley | 120086516 | S9 | 540 |  |  |  | E |  | POHW OH CNCL PROG TER2 | 2021-11-09 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 13856 MYSTIC MINE RD. N | NOCO ATCO | ED.22-M071800000.STRU.POLE | M0718 | 15313-2102, NARROWS | 9073 | 110350830 | 100106134 | 39.2391 | -121.1264 | 13856 MYSTIC MINE RD. | NEVADA CITY | GJME | 2020-11-23 | ECFOH | JOINER | 2020-11-09 | LMMY | 2020-11-23 | 2020-11-23 |  |  | 2020-11-23 | 1 |  | E | 029
T0 | IR | NV | Oroville | 120086518 | EC | 540 | 44571307 | KAA | DOCC srdy | B |  | RELW OH COMP PROG CPGD TER0 | 2020-12-10 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 2590 S FIFTH AVE OROVIL | ORAS NOCO ATCO | ED.13-H230400000.STRU.POLE | H2304 | 10291-1106, WYANDOTTE | 13835 |  | 100412875 | 39.4962 | -121.5656 | 2590 S FIFTH AVE | OROVILLE | RXHV | 2020-11-23 | ECFOH | BUENROSTRO | 2020-11-10 | LMMY | 2020-11-23 | 2020-12-10 | 2020-12-10 | KESG | 2020-12-17 | 1 |  | B | 004
T0 | IR | NV | Oroville | 120086611 | EC | 540 | 44579673 | KAA | CONS srdy | B |  | RELW OH PROG TER0 | 2021-02-08 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 2043 PALEMERO RD PALEME | NOPR ORAS ATCO | ED.13-I240600000.STRU.POLE | I2406 | 10291-1109, WYANDOTTE | 40608 |  | 100431025 | 39.4351 | -121.5507 | 2043 PALEMERO RD | PALEMERO | RXHV | 2020-11-23 | ECFOH | GONZALES-NAT | 2020-11-09 | LMMY | 2020-11-23 | 2020-11-09 |  |  |  | 1 |  | B | 004
T0 | IR | SI | Marysville | 120086616 | EC | 540 |  |  |  | E |  | POHW OH PROG TER0 | 2021-05-09 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - A/F 646 SILVA AVE. (ON | OSNO ATCO | ED.11-O230100000.STRU.POLE | O2301 | 15233-1105, EAST MARYSVILLE | 1704 | 120348209 | 101312474 | 39.1808 | -121.5921 | A/F 646 SILVA AVE. (ON OROVILLE HWY.) | MARYSVILLE | GJME | 2020-11-23 | ECFOH | JERNIGAN | 2020-11-09 | LMMY | 2020-11-23 | 2020-11-09 |  |  |  | 1 |  | E | 058
T0 | IR | NV | Oroville | 120086711 | EC | 540 | 44571308 | KAA | DOCC srdy | B |  | RELW OH COMP PROG CPGD TER0 | 2020-12-09 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 1827 PALERMO RD PALERMO | ORAS NOCO ATCO | ED.13-I231000000.STRU.POLE | I2310 | 10291-1109, WYANDOTTE | 23687 |  | 100379770 | 39.435 | -121.557 | 1827 PALERMO RD | PALERMO | RXHV | 2020-11-23 | ECFOH | GONZALES-NAT | 2020-11-09 | LMMY | 2020-11-23 | 2020-12-10 | 2020-12-10 | KESG | 2020-12-22 | 1 |  | B | 004
T0 | IR | NV | Oroville | 120086788 | EC | 540 | 44579674 | KAA | CONS srdy | B |  | RELW OH PROG TER0 | 2021-02-02 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 2970 S VILLA AVE OROVIL | NOPR ORAS ATCO | ED.13-I241300000.STRU.POLE | I2413 | 10291-1109, WYANDOTTE | 79932 |  | 100394076 | 39.4313 | -121.532 | 2970 S VILLA AVE | OROVILLE | RXHV | 2020-11-23 | ECFOH | GONZALES-NAT | 2020-11-10 | LMMY | 2020-11-23 | 2020-11-10 |  |  |  | 1 |  | B | 004
T0 | Hotshot | LP | San Luis Obispo | 119727116 | EC | 540 | 44462076 | KAA | DOCC crdy srdy | B |  | RELW OH COMP CPGE PROG CPGD TER0 | 2020-11-28 |  | Switch | Broken/Damaged | Repair | SWIT_BROK_REPA - 1091 S HALCYON RD OCEAN | ORAS NOCO ATCO | ED.02-QQ35220000.STRU.POLE | QQ3522 | 18260-1105, OCEANO | 5117 | 120472770 | 101879903 | 35.101 | -120.5917 | 1091 S HALCYON RD | OCEANO | CBB6 | 2020-09-09 | ECFOH | LEWIS DAN | 2020-08-28 | LMMY | 2020-09-08 | 2020-10-22 | 2020-10-22 | DEFK | 2020-10-26 | 1 |  | E | 040
T0 | Hotshot | LP | San Luis Obispo | 119727212 | EC | 540 | 44462077 | KAA | DOCC crdy srdy | B |  | RELW OH COMP CPGE CPGD TER0 | 2020-10-08 |  | Cutout | Broken/Damaged | Replace | CUTO_BROK_REPL - 561 AIR PARK DR OCEANO | ORAS NOCO ATCO | ED.02-QQ34180000.STRU.POLE | QQ3418 | 18260-1106, OCEANO | 11061 | 110535587 | 101910080 | 35.1046 | -120.6249 | 561 AIR PARK DR | OCEANO | J6AG | 2020-09-09 | ECFOH | LEWIS DAN | 2020-09-08 | LMMY | 2020-09-08 | 2020-10-05 | 2020-10-05 | J2H4 | 2020-10-06 | 2 |  | E | 040
T0 | Hotshot | LP | San Luis Obispo | 119778819 | EC | 605 | 31516138 | 2AA | MAPP srdy | B |  | RELW OH COMP PROG CPGD TER0 | 2020-12-01 |  | Switch | Broken/Damaged | Repair | SWIT_BROK_REPA - 131 SURBAN ROAD SAN LUI | ORAS NOCO ATCO | ED.02-NN33170000.STRU.POLE | NN3317 | 18263-1107, SAN LUIS OBISPO | 10847 |  | 101849232 | 35.244 | -120.673 | 131 SURBAN ROAD | SAN LUIS OBISPO | GJME | 2020-09-18 | ECFOH | LEWIS DAN | 2020-09-01 | LMMY | 2020-09-17 | 2020-10-19 | 2020-10-19 | RAPS | 2020-10-23 | 1 |  | E | 040
BUFFER | Hotshot | LP | San Luis Obispo | 119779349 | EC | 540 | 44474869 | KAA | DOCC srdy | B |  | RELW OH COMP PROG CPGD BUFF | 2020-10-02 |  | Switch | Broken/Damaged | Repair | SWIT_BROK_REPA - 6344 ORCUTT RD SAN LUIS | ORAS NOCO ATCO | ED.02-OO35070000.STRU.POLE | OO3507 | 18263-1104, SAN LUIS OBISPO | 9129 | 120015271 | 101844521 | 35.2133 | -120.591 | 6344 ORCUTT RD | SAN LUIS OBISPO | GJME | 2020-09-18 | ECFOH | LEWIS DAN | 2020-09-02 | LMMY | 2020-09-17 | 2020-09-23 | 2020-09-23 | rwso | 2020-09-25 | 1 |  | E | 040
T0 | Hotshot | LP | San Luis Obispo | 119779494 | EC | 540 |  |  |  | E |  | POHW OH PROG TER0 | 2021-03-03 |  | Switch | Broken/Damaged | Repair | SWIT_BROK_REPA - UNKNOWN ON PRICE ST PIS | OSNO ATCO | ED.02-PP33180000.STRU.POLE | PP3318 | 18260-1105, OCEANO | 10191 | 120426573 | 101854216 | 35.1519 | -120.6586 | UNKNOWN ON PRICE ST | PISMO BEACH | GJME | 2020-09-18 | ECFOH | LEWIS DAN | 2020-09-03 | LMMY | 2020-09-17 | 2020-09-03 |  |  |  | 1 |  | E | 040
T0 | Hotshot | LP | San Luis Obispo | 119779641 | EC | 540 | 44474875 | KAA | DOCC srdy | B |  | RELW OH COMP PROG CPGD TER0 | 2020-10-03 |  | Cutout | Broken/Damaged | Repair | CUTO_BROK_REPA - 2575 PRICE ST PISMO BEA | ORAS NOCO ATCO | ED.02-PP33190000.STRU.POLE | PP3319 | 18260-1105, OCEANO | 10191 | 120426563 | 101854080 | 35.1497 | -120.6541 | 2575 PRICE ST | PISMO BEACH | GJME | 2020-09-18 | ECFOH | LEWIS DAN | 2020-09-03 | LMMY | 2020-09-17 | 2020-09-25 | 2020-09-25 | RWSO | 2020-10-03 | 2 |  | E | 040
T0 | Hotshot | LP | San Luis Obispo | 119779643 | EC | 311 |  |  |  | E |  | POHW OH ESTR TER0 | 2021-09-03 |  | Pole | Broken/Damaged | Replace | POLE_BROK_REPL - 240 SAN LUIS AVE PISMO | OSNO ATCO | ED.02-PP33250000.STRU.POLE | PP3325 | 18260-1105, OCEANO | 9431 | 120428289 | 101853995 | 35.1434 | -120.6445 | 240 SAN LUIS AVE | PISMO BEACH | GJME | 2020-09-18 | ECFOH | LEWIS DAN | 2020-09-03 | LMMY | 2020-09-17 | 2020-09-03 |  |  |  | 3 |  | E | 040
T2 | Hotshot | LP | San Luis Obispo | 119779870 | EC | 540 |  |  |  | E |  | POHW OH PROG TER2 | 2021-03-10 |  | Switch | Broken/Damaged | Repair | SWIT_BROK_REPA - MORRO BAY RAMP EXIT 278 | OSNO ATCO | ED.02-KK29160000.STRU.POLE | KK2916 | 18301-1102, MORRO BAY | 9571 | 120323822 | 101938917 | 35.368 | -120.8399 | MORRO BAY RAMP EXIT 278 | MORRO BAY | GJME | 2020-09-18 | ECFOH | LEWIS DAN | 2020-09-10 | LMMY | 2020-09-17 | 2020-09-10 |  |  |  | 1 |  | E | 040
BUFFER | Hotshot | LP | San Luis Obispo | 119780262 | EC | 540 | 44474872 | KAA | CLSD srdy canc | B |  | RELW OH CNCL PROG CPGD BUFF | 2020-12-10 |  | Cutout | Broken/Damaged | Repair | CUTO_BROK_REPA - 330 FAIRVIEW AVE MORRO | ORAS NOCO ATCO | ED.02-KK29210000.STRU.POLE | KK2921 | 18301-1101, MORRO BAY | 64675 | 120509095 | 101937809 | 35.3581 | -120.8364 | 330 FAIRVIEW AVE | MORRO BAY | GJME | 2020-09-18 | ECFOH | LEWIS DAN | 2020-09-10 | LMMY | 2020-09-17 | 2020-10-01 |  |  | 2020-10-12 | 1 |  | E | 040
T2 | Hotshot | LP | San Luis Obispo | 119780268 | EC | 540 |  |  |  | E |  | POHW OH PROG TER2 | 2021-03-11 |  | Switch | Broken/Damaged | Repair | SWIT_BROK_REPA - 33B MAGUERITE DR LOS OS | OSNO ATCO | ED.02-MM29030000.STRU.POLE | MM2903 | 18301-1102, MORRO BAY | 571241 | 120399076 | 101854947 | 35.3057 | -120.8201 | 33B MAGUERITE DR | LOS OSOS | GJME | 2020-09-18 | ECFOH | LEWIS DAN | 2020-09-11 | LMMY | 2020-09-17 | 2020-09-11 |  |  |  | 1 |  | E | 040
T0 | Hotshot | LP | San Luis Obispo | 119780341 | EC | 540 |  |  |  | E |  | POHW OH PROG TER0 | 2021-03-11 |  | Switch | Broken/Damaged | Repair | SWIT_BROK_REPA - MORRO BAY SUBSTATION MO | OSNO ATCO | ED.02-KK28140000.STRU.POLE | KK2814 | 18301-1101, MORRO BAY | 43725 | 110288407 | 103012584 | 35.3754 | -120.8543 | MORRO BAY SUBSTATION | MORRO BAY | GJME | 2020-09-18 | ECFOH | LEWIS DAN | 2020-09-11 | LMMY | 2020-09-17 | 2020-09-11 |  |  |  | 1 |  | E | 040
T0 | Hotshot | LP | Templeton | 119780346 | EC | 540 | 44474871 | KAA | DOCC srdy | B |  | RELW OH COMP PROG CPGD TER0 | 2020-10-14 |  | Switch | Broken/Damaged | Repair | SWIT_BROK_REPA - 9300 PINO SOLO AVE ATAS | ORAS NOCO ATCO | ED.03-II34110000.STRU.POLE | II3411 | 18254-1102, ATASCADERO | 2317 |  | 103405127 | 35.468 | -120.6489 | 9300 PINO SOLO AVE | ATASCADERO | GJME | 2020-09-18 | ECFOH | LEWIS DAN | 2020-09-14 | LMMY | 2020-09-17 | 2020-11-11 | 2020-11-11 | TJGB | 2020-11-11 | 1 |  | E | 040
T0 | Hotshot | LP | Santa Maria | 119791312 | EC | 540 | 44477073 | KAA | DOCC crdy srdy | B |  | RELW OH COMP CPGE CPGD TER0 | 2020-12-17 |  | Cutout | Broken/Damaged | Replace | CUTO_BROK_REPL - N BLOSSER RD SANTA MARI | ORAS NOCO ATCO | ED.01-TT38240000.STRU.POLE | TT3824 | 18267-1105, SANTA MARIA | 6057 |  | 103827858 | 34.9658 | -120.4535 | N BLOSSER RD | SANTA MARIA | J6AG | 2020-09-21 | ECFOH | LEWIS DAN | 2020-09-17 | LMMY | 2020-09-21 | 2020-10-16 | 2020-10-16 | BAHG | 2020-10-20 | 3 |  | B | 042
T2 | Hotshot | CC | Monterey | 119876162 | EC | 605 |  |  |  | E |  | POHW OH MINR JAR TER2 | 2021-04-06 |  | Lightning Arrester | Broken/Damaged | Replace | LITN_BROK_REPL - HIGHWAY 1 BIG SUR | OSNO ATCO | ED.07-S070000000.STRU.POLE | S07 | 18294-1102, OTTER | 647 |  | 101674994 | 36.1766 | -121.6975 | HIGHWAY 1 | BIG SUR | GJME | 2020-10-09 | ECFOH | PERKINS | 2020-10-06 | LMMY | 2020-10-09 | 2020-10-06 |  |  |  | 2 |  | E | 027
T0 | Hotshot | CC | Salinas | 119928352 | EC | 605 | 31516907 | 2AA | CONS crdy srdy | B |  | RELW OH COMP CCNT TER0 | 2021-01-16 |  | Cutout | Broken/Damaged | Replace | CUTO_BROK_REPL - BRIDGE STREET SALINAS | ORAS NOCO ATCO | ED.05-G0923B0000.STRU.POLE | G0923B | 18201-1104, SALINAS | 25547 |  | 101716568 | 36.6818 | -121.6524 | BRIDGE STREET | SALINAS | J6AG | 2020-10-20 | ECFOH | HEAGERTY | 2020-10-16 | LMMY | 2020-10-20 | 2020-12-17 | 2020-12-17 | CONTR | 2020-12-29 | 2 |  | B | 027
T0 | Hotshot | CC | Salinas | 119928357 | EC | 605 | 31518395 | 2AA | CNCL srdy canc | B |  | RELW OH CNCL CPGD TER0 | 2021-01-16 |  | Cutout | Broken/Damaged | Replace | CUTO_BROK_REPL - BRIDGE STREET SALINAS E | ORAS NOCO ATCO | ED.05-G0923B0000.STRU.POLE | G0923B | 18201-1106, SALINAS | 3297 |  | 101787761 | 36.6807 | -121.6528 | BRIDGE STREET | SALINAS | J6AG | 2020-10-20 | ECFOH | HEAGERTY | 2020-10-16 | LMMY | 2020-10-20 | 2020-12-04 |  |  | 2020-12-04 | 2 |  | B | 027
T0 | Hotshot | NB | Salinas | 119928398 | EC | 540 |  |  |  | E |  | POHW OH PROG TER0 | 2021-10-16 |  | Switch | Broken/Damaged | Repair | SWIT_BROK_REPA - BRIDGE STREET SALINAS | OSNO ATCO | ED.05-G0923B0000.STRU.POLE | G0923B | 18201-1106, SALINAS | 25547 |  | 101716570 | 36.6817 | -121.6525 | BRIDGE STREET | SALINAS | J6AG | 2020-10-20 | ECFOH | HEAGERTY | 2020-10-16 | LMMY | 2020-10-20 | 2020-10-16 |  |  |  | 1 |  | E | 027
T0 | Hotshot | CC | Salinas | 119947755 | EC | 540 | 44507293 | KAA | DOCC crdy srdy | B |  | RELW OH CREW COMP CPGE PROG CPGD TER0 | 2021-01-22 |  | Cutout | Broken/Damaged | Repair | CUTO_BROK_REPA - CASTRO CASTROVILLE WALS | ORAS NOCO NOPT ATCO | ED.05-F070200000.STRU.POLE | F0702 | 18235-2103, CASTROVILLE | 5149 |  | 101715154 | 36.7607 | -121.7465 | CASTRO | CASTROVILLE | GJME | 2020-10-27 | ECFOH | HEAGERTY | 2020-10-22 | LMMY | 2020-10-26 | 2020-12-03 | 2020-12-03 | ACGA | 2020-12-04 | 2 |  | E | 027 | CREW
ZONE 1 | Hotshot | DI | Concord | 119727304 | EC | 540 |  |  |  | E |  | POHW OH JAR ZNE1 | 2021-08-26 |  | Cutout | Broken/Damaged | Replace | CUTO_BROK_REPL - 518 MARSHALL DR WALNUT | OSNO ATCO | ED.30-D112100000.STRU.POLE | D1121 | 01220-0404, WALNUT CREEK | 26244 | 110167402 | 100482651 | 37.902 | -122.0336 | 518 MARSHALL DR | WALNUT CREEK | J6AG | 2020-09-09 | ECFOH | LEWIS DAN | 2020-08-26 | LMMY | 2020-09-08 | 2020-08-26 |  |  |  | 1 |  | E | 007
T2 | Hotshot | LP | San Luis Obispo | 119778924 | EC | 540 |  |  |  | E |  | POHW OH PROG TER2 | 2021-09-01 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 6588 ONTARIO RD SAN LUI | OSNO ATCO | ED.02-OO32180000.STRU.POLE | OO3218 | 18263-1107, SAN LUIS OBISPO | 10803 | 110293728 | 101845516 | 35.1948 | -120.7007 | 6588 ONTARIO RD | SAN LUIS OBISPO | GJME | 2020-09-18 | ECFOH | LEWIS DAN | 2020-09-01 | LMMY | 2020-09-17 | 2020-09-01 |  |  |  | 1 |  | E | 040
T0 | Hotshot | LP | San Luis Obispo | 119779347 | EC | 540 |  |  |  | E |  | POHW OH PROG TER0 | 2021-03-01 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 990 INDUSTRIAL WAY SAN | OSNO ATCO | ED.02-NN34110000.STRU.POLE | NN3411 | 18263-1107, SAN LUIS OBISPO | 10899 | 120763727 | 103954565 | 35.2535 | -120.6388 | 990 INDUSTRIAL WAY | SAN LUIS OBISPO | GJME | 2020-09-18 | ECFOH | LEWIS DAN | 2020-09-01 | LMMY | 2020-09-17 | 2020-09-01 |  |  |  | 1 |  | E | 040
T0 | Hotshot | LP | San Luis Obispo | 119779646 | EC | 540 | 44474870 | KAA | DOCC crdy srdy | B |  | RELW OH COMP MINR JAR CPGD TER0 | 2020-12-09 |  | Connector | Corroded | Repair | CONN_CORR_REPA - 1065 KENNEDY WAY MORRO | ORAS NOCO ATCO | ED.02-KK28200000.STRU.POLE | KK2820 | 18301-1101, MORRO BAY | 69027 |  | 101851501 | 35.3691 | -120.8452 | 1065 KENNEDY WAY | MORRO BAY | GJME | 2020-09-18 | ECFOH | LEWIS DAN | 2020-09-09 | LMMY | 2020-09-17 | 2020-11-16 | 2020-11-16 | raps | 2020-11-18 | 1 |  | E | 040
T0 | Hotshot | LP | San Luis Obispo | 119779872 | EC | 540 |  |  |  | E |  | POHW OH PROG TER0 | 2021-03-10 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 911 MORRO BAY BLVD MORR | OSNO ATCO | ED.02-KK29160000.STRU.POLE | KK2916 | 18301-1101, MORRO BAY | 10879 |  | 101852702 | 35.3668 | -120.8416 | 911 MORRO BAY BLVD | MORRO BAY | GJME | 2020-09-18 | ECFOH | LEWIS DAN | 2020-09-10 | LMMY | 2020-09-17 | 2020-09-10 |  |  |  | 1 |  | E | 040
T0 | Hotshot | LP | San Luis Obispo | 119779879 | EC | 605 | 31515591 | 2AA | MAPP srdy idoc idcr | B |  | RELW OH COMP JAR CPGD TER0 | 2020-10-10 |  | Crossarm | Decayed/Rotten | Replace | CRSS_DECA_REPL - 1129 MARKET AVE MORRO B | ORAS NOCO ATCO | ED.02-KK28190000.STRU.POLE | KK2819 | 18301-1101, MORRO BAY | 82361 |  | 101848460 | 35.3693 | -120.8526 | 1129 MARKET AVE | MORRO BAY | GJME | 2020-09-18 | ECFOH | LEWIS DAN | 2020-09-10 | LMMY | 2020-09-17 | 2020-10-08 | 2020-10-08 | LJMF | 2020-10-09 | 2 |  | E | 040
T0 | Hotshot | LP | San Luis Obispo | 119780265 | EC | 540 | 44474874 | KAA | DOCC srdy | B |  | RELW OH COMP JAR CPGD TER0 | 2020-10-10 |  | Cutout | Broken/Damaged | Repair | CUTO_BROK_REPA - PECHO VALLEY RD LOS OSO | ORAS NOCO ATCO | ED.02-LL28240000.STRU.POLE | LL2824 | 18301-1102, MORRO BAY | 3483 | 120412942 | 101846791 | 35.3116 | -120.8533 | PECHO VALLEY RD | LOS OSOS | GJME | 2020-09-18 | ECFOH | LEWIS DAN | 2020-09-10 | LMMY | 2020-09-17 | 2020-09-27 | 2020-09-27 | JCHW | 2020-10-03 | 2 |  | E | 040
T0 | Hotshot | LP | Santa Maria | 119798659 | EC | 540 |  |  |  | E |  | POHW OH PROG TER0 | 2021-03-15 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 2691 SANTA MARIA WAY SA | OSNO ATCO | ED.01-VV39020000.STRU.POLE | VV3902 | 18206-1108, FAIRWAY | 11121 | 110288254 | 101868743 | 34.9108 | -120.4345 | 2691 SANTA MARIA WAY | SANTA MARIA | GJME | 2020-09-22 | ECFOH | LEWIS DAN | 2020-09-15 | LMMY | 2020-09-22 | 2020-09-15 |  |  |  | 1 |  | E | 040
T0 | Hotshot | LP | Santa Maria | 119822501 | EC | 540 |  |  |  | E |  | POHW OH PROG TER0 | 2021-03-18 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - GUADALUPE RD NIPOMO DIV | OSNO ATCO | ED.01-TT35000000.STRU.POLE | TT35 | 18282-1102, MESA | 6677 |  | 101885554 | 34.9925 | -120.5708 | GUADALUPE RD | NIPOMO | AAO8 | 2020-09-28 | ECFOH | LEWIS DAN | 2020-09-18 | LMMY | 2020-09-28 | 2020-09-18 |  |  |  | 3 |  | B | 040
T0 | Hotshot | LP | Santa Maria | 119822573 | EC | 540 | 44482814 | KAA | DOCC srdy | B |  | RELW OH COMP CPGE PROG CPGD TER0 | 2020-10-28 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - MIDDLE OF FIELD NIPOMO | ORAS NOCO ATCO | ED.01-TT37000000.STRU.POLE | TT37 | 18267-1105, SANTA MARIA | 6131 |  | 101922412 | 34.9952 | -120.4856 | MIDDLE OF FIELD | NIPOMO | AAO8 | 2020-09-28 | ECFOH | LEWIS DAN | 2020-09-18 | LMMY | 2020-09-28 | 2020-10-20 | 2020-10-20 | BAHG | 2020-10-26 | 1 |  | B | 040
T0 | Hotshot | LP | Santa Maria | 119822648 | EC | 540 |  |  |  | E |  | POHW OH PROG TER0 | 2021-03-18 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - SOUTH SIDE OF FIELD NIP | OSNO ATCO | ED.01-TT37000000.STRU.POLE | TT37 | 18267-1105, SANTA MARIA | 602829 |  | 101922417 | 34.9925 | -120.4861 | SOUTH SIDE OF FIELD | NIPOMO | AAO8 | 2020-09-28 | ECFOH | LEWIS DAN | 2020-09-18 | LMMY | 2020-09-28 | 2020-09-18 |  |  |  | 1 |  | E | 040
T0 | Hotshot | LP | Templeton | 119836122 | EC | 540 |  |  |  | E |  | POHW OH PROG TER0 | 2021-09-28 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - NEAL SPRINGS ROAD TEMPL | OSNO ATCO | ED.03-GG34020000.STRU.POLE | GG3402 | 18305-2109, TEMPLETON | 2339 |  | 101912929 | 35.5751 | -120.643 | NEAL SPRINGS ROAD | TEMPLETON | J6AG | 2020-10-01 | ECFOH | PERKINS | 2020-09-28 | LMMY | 2020-10-01 | 2020-09-28 |  |  |  | 1 |  | E | 040
T0 | Hotshot | LP | Templeton | 119836124 | EC | 540 |  |  |  | E |  | POHW OH PROG TER0 | 2021-09-29 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - LOTHAR LANE TEMPLETON | OSNO ATCO | ED.03-GG34010000.STRU.POLE | GG3401 | 18305-2109, TEMPLETON | 6123 |  | 101935226 | 35.5797 | -120.6506 | LOTHAR LANE | TEMPLETON | J6AG | 2020-10-01 | ECFOH | PERKINS | 2020-09-29 | LMMY | 2020-10-01 | 2020-09-29 |  |  |  | 1 |  | E | 040
T0 | Hotshot | CC | King City | 119876160 | S9 | 540 |  |  |  | E |  | POHW OH CNCL PROG TER0 | 2021-10-05 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - ELM AVENUE GREENFIELD | NOCO ATCO | ED.04-P190500000.STRU.POLE | P1905 | 18208-2101, LOS OSITOS | 2201 |  | 101755003 | 36.3197 | -121.2377 | ELM AVENUE | GREENFIELD | GJME | 2020-10-09 | ECFOH | PERKINS | 2020-10-05 | LMMY | 2020-10-09 | 2020-10-09 |  |  | 2020-10-09 | 1 |  | E | 027
T0 | Hotshot | CC | Monterey | 119876164 | EC | 540 | 44496600 | KAA | DOCC srdy | B |  | RELW OH COMP JAR CPGE CPGD TER0 | 2020-11-06 |  | Cutout | Broken/Damaged | Repair | CUTO_BROK_REPA - YANKEE POINT DRIVE CARM | ORAS NOCO ATCO | ED.07-L020100000.STRU.POLE | L0201 | 18294-1101, OTTER | 6995 |  | 101776674 | 36.4826 | -121.9389 | YANKEE POINT DRIVE | CARMEL | GJME | 2020-10-09 | ECFOH | PERKINS | 2020-10-06 | LMMY | 2020-10-09 | 2020-11-05 | 2020-11-05 | S3CZ | 2020-11-10 | 2 |  | E | 027
T0 | Hotshot | CC | Monterey | 119908777 | EC | 540 |  |  |  | E |  | POHW OH PROG TER0 | 2021-04-08 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - WEST CARMEL VALLEY ROAD | OSNO ATCO | ED.07-K062400000.STRU.POLE | K0624 | 18237-1112, LAURELES | 2768SB | 110293200 | 101774682 | 36.5028 | -121.759 | WEST CARMEL VALLEY ROAD | CARMEL VALLEY | GJME | 2020-10-15 | ECFOH | PERKINS | 2020-10-08 | LMMY | 2020-10-15 | 2020-10-08 |  |  |  | 1 |  | E | 027
T0 | Hotshot | CC | Monterey | 119908890 | EC | 540 | 44499827 | KAA | DOCC crdy srdy | B |  | RELW OH COMP CPGE PROG CPGD TER0 | 2021-01-09 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - FOAM STREET MONTEREY | ORAS NOCO ATCO | ED.07-I030700000.STRU.POLE | I0307 | 18222-2105, DEL MONTE | 10637 |  | 101780971 | 36.6131 | -121.8999 | FOAM STREET | MONTEREY | GJME | 2020-10-15 | ECFOH | PERKINS | 2020-10-09 | LMMY | 2020-10-15 | 2020-11-10 | 2020-11-10 | CMJ1 | 2020-11-13 | 1 |  | B | 027
T0 | Hotshot | CC | Salinas | 119928232 | EC | 540 | 44507289 | KAA | DOCC srdy | B |  | RELW OH CREW COMP JAR CPGE CPGD TER0 | 2021-01-14 |  | Cutout | Broken/Damaged | Repair | CUTO_BROK_REPA - DAVIS ROAD SALINAS FOST | ORAS NOCO NOPT ATCO | ED.05-H081200000.STRU.POLE | H0812 | 18201-1104, SALINAS | 3017 |  | 101725019 | 36.6509 | -121.6987 | DAVIS ROAD | SALINAS | GJME | 2020-10-21 | ECFOH | HEAGERTY | 2020-10-14 | LMMY | 2020-10-20 | 2020-12-03 | 2020-12-03 | S3CZ | 2020-12-07 | 2 |  | B | 027 | CREW
T0 | Hotshot | CC | Salinas | 119928303 | EC | 540 | 44517144 | KAA | PREC srdy canc | B |  | RELW OH CNCL PROG CPGD TER0 | 2020-12-14 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 92 HITCHCOCK RD SALINAS | ORAS NOCO NOPT ATCO | ED.05-H081500000.STRU.POLE | H0815 | 18201-1104, SALINAS | 25633 |  | 101725659 | 36.6526 | -121.6802 | 92 HITCHCOCK RD | SALINAS | J6AG | 2020-10-20 | ECFOH | HEAGERTY | 2020-10-14 | LMMY | 2020-10-20 | 2020-12-03 |  |  | 2020-12-07 | 2 |  | B | 027
T0 | Hotshot | CC | Salinas | 119928308 | EC | 540 | 44517145 | KAA | CLSD srdy canc | B |  | RELW OH CNCL PROG CPGD TER0 | 2020-11-15 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - 1261 MAIN STREET SALINA | ORAS NOCO NOPT ATCO | ED.05-H091300000.STRU.POLE | H0913 | 18201-1106, SALINAS | 3822 | 0 | 103846395 | 36.6562 | -121.6578 | 1261 MAIN STREET | SALINAS | J6AG | 2020-10-20 | ECFOH | HEAGERTY | 2020-10-15 | LMMY | 2020-10-20 | 2020-12-03 |  |  | 2020-12-07 | 1 |  | B | 027
T0 | Hotshot | CC | Salinas | 119947738 | EC | 540 | 44506199 | KAA | DOCC crdy srdy | B |  | RELW OH CREW COMP CPGE PROG CPGD TER0 | 2020-11-22 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - MONTE RD CASTROVILLE N | ORAS NOCO NOPT ATCO | ED.05-F061400000.STRU.POLE | F0614 | 18235-2103, CASTROVILLE | 5049 | 0 | 103843110 | 36.7397 | -121.7687 | MONTE RD | CASTROVILLE | GJME | 2020-10-27 | ECFOH | HEAGERTY | 2020-10-22 | LMMY | 2020-10-26 | 2020-11-06 | 2020-11-06 | ACGA | 2020-11-09 | 1 |  | B | 027 | CREW
T0 | Hotshot | CC | Watsonville | 119961163 | EC | 540 |  |  |  | E |  | POHW OH PROG TER0 | 2021-04-27 |  | Connector | Temp Differential | Replace | CONN_TEMP_REPL - W. BEACH ST WATSONVILLE | OSNO ATCO | ED.76-Q200800000.STRU.POLE | Q2008 | 08319-2104, GREEN VALLEY | 12183 |  | 101793596 | 36.9062 | -121.7658 | W. BEACH ST | WATSONVILLE | GJME | 2020-10-29 | ECFOH | HEAGERTY | 2020-10-27 | LMMY | 2020-10-29 | 2020-10-27 |  |  |  | 1 |  | E | 044