## Summary_2A_and_Overview
Tree Overstrike Impact
[19 empty] | Frequency | 1.74
[19 empty] | Duration (Customer-Hours) Per Event | 0.9087
[19 empty] | Scope Per Event | 0.932
|  | 2021 Planned WMP Mitigations Analyzed Against 2020 Events and Select Four 2019 Events | [12 empty] | SCOPE | DURATION (direct) | DURATION (direct) | DURATION (direct) | DURATION (direct) | DURATION (direct) | DURATION (indirect) | DURATION (indirect) | DURATION (indirect)
| WMP Initiative | Mitigations | 2019-10-09 | 2019-10-23 | 2019-10-26 | 2019-10-29 | 2020-09-07 | 2020-09-26 | 2020-10-14 | 2020-10-21 | 2020-10-25 | 2020-12-03 | Customers Mitigated | Mitigated % | Customers Mitigated Per Event | CHOUR | CHOUR Per Event | CHOUR with 30min restoration time improvement | CHOUR Per Event with 30 min restoration time improvement | (Tree Overstrike) CHOUR Per Event w/ 30 min rest. improve | avg duration reduction (Hour / Cust) | avg duration reduction (Min/ Cust) | CMIN Per Event
| 7.3.3.8.2 | Transmission Lines - Switching | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5800 | 0 | 5800 | 0.3299% | 580 | 212628.2628 | 21262.8263 | 209728.2628 | 20972.8263 | 19058.0072 | 0.002726 | 0.16356 | 2304.6912
| 7.3.3.17.2 | Transmission Lines - Repairs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 7.3.5.3 | Transmission Lines - Vegetation | 41050 | 3133 | 13414 | 11222 | 16713 | 2362 | 0 | 0 | 0 | 0 | 87894 | 4.999% | 8789.4 | 2091959.9502 | 209195.995 | 2048012.9502 | 204801.295 | 186102.9368 | 0.04131 | 2.4786 | 34925.6091
| 7.3.3.11.1B | Temporary Substation Microgrids | 1548 | 0 | 804 | 199 | 703 | 0 | 0 | 0 | 0 | 0 | 3254 | 0.1851% | 325.4 | 0 | 0 | 76875.3524 | 7687.5352 | 6985.6633 | 0.0015294 | 0.091763 | 1293.0113
| 7.3.3.11.1C | Temporary Distribution Microgrids | 708 | 714 | 2238 | 714 | 351 | 166 | 90 | 40 | 2238 | 0 | 7259 | 0.4129% | 725.9 | 0 | 0 | 179279.5012 | 17927.9501 | 16291.1283 | 0.0034117 | 0.2047 | 2884.4403
| 7.3.3.16 | Hardening: Underground Projects | 0 | 0 | 2005 | 0 | 10964 | 0 | 0 | 0 | 0 | 0 | 12969 | 0.7376% | 1296.9 | 0 | 0 | 425818.6093 | 42581.8609 | 38694.137 | 0.0060954 | 0.36573 | 5153.3691
| 7.3.3.8.1 | Distribution Sectionalizing | 4350 | 616 | 769 | 2027 | 3426 | 157 | 651 | 557 | 7052 | 0 | 19605 | 1.115% | 1960.5 | 0 | 0 | 572063.6406 | 57206.3641 | 51983.423 | 0.0092143 | 0.55286 | 7790.2538
| 7.3.3.17.1 | Descoping Hardened OH* | 0 | 0 | 3091 | 0 | 0 | 0 | 518 | 0 | 518 | 0 | 4127 | 0.2347% | 412.7 | 0 | 0 | 89817.9332 | 8981.7933 | 8161.7556 | 0.0019397 | 0.11638 | 1639.907
|  | Total-Customers Mitigated | 47656 | 4463 | 22321 | 14162 | 32157 | 2685 | 1259 | 597 | 15608 | 0 | 140908 | 8.014% | 14090.8 | 2304588.213 | 230458.8213 | 3601596.2497 | 360159.625 | 327277.0512 | 0.066227 | 3.9736 | 55991.2818
|  | Mitigated % | 36.95% | 2.679% | 3.962% | 6.339% | 18.64% | 4.116% | 2.383% | 1.935% | 4.411% | 0% | 8.014%
|  | Customers Affected - T&D | 128970 | 166610 | 563355 | 223423 | 172476 | 65240 | 52835 | 30858 | 353825 | 617 | 1758209
|  | Customers Affected - Dist. Only | 34659 | 152682 | 510136 | 197713 | 125774 | 66497 | 48063 | 36940 | 305346 | 617 | 1291086
Customer Affected - Transmission add.
|  | * Pending approval from wildfire governance committee | 2934191.3602 | 2719428.063 | 9798766.6302 | 4285114.8481 | 6252002.6521 | 1450785.8563 | 1951012.8475 | 573291.3875 | 12971240.534 | 12875.35
|  | Average Outage Duration | 22.751 | 16.3221 | 17.3936 | 19.1794 | 36.2485 | 22.2377 | 36.9265 | 18.5784 | 36.66 | 20.8677 | 247.1649 | <--Copied and pasted from PSPS_Duration_Regression
2.023% | 7.3.5.3-D/T | 30min Rest Process Improvement | 22.251 | 15.8221 | 16.8936 | 18.6794 | 35.7485 | 21.7377 | 36.4265 | 18.0784 | 36.16 | 20.3677 | 242.1649 |  |  | Average | 30 min Improvement
[15 empty] | Mitigated CHR | 3672050.2497 | 3601596.2497
|  |  | 2019-10-09: *2019 used backcast, adjusted with 2020 weighted average restoration time. Backcast projects full weather event time, but actual event times vary per customer. |  |  | Total CHR | 42948709.5289 | 42069605.0289
[15 empty] | Mitigated Duration % | 8.55% | 10.43%
Section 2a. Table 8.2.5.5 - Estimated Impact of 2021 Planned WMP Mitigations
| WMP Initiative | Mitigations | 2019-10-09: Customers Mitigated; 2019-10-23: Mitigated %; 2019-10-26: Customers Mitigated Per Event; 2019-10-29: Customer Hours; 2020-09-07: Customer Hours Per Event
| 7.3.3.8.2 | Transmission Lines - Switching | 2019-10-09: 5800; 2019-10-23: 0.3299%; 2019-10-26: 580; 2019-10-29: 209728.2628; 2020-09-07: 20972.8263
| 7.3.3.17.2 | Transmission Lines - Repairs | 2019-10-09: 0; 2019-10-23: 0%; 2019-10-26: 0; 2019-10-29: 0; 2020-09-07: 0
| 7.3.5.3 | Transmission Lines - Vegetation | 2019-10-09: 87894; 2019-10-23: 4.999%; 2019-10-26: 8789.4; 2019-10-29: 2048012.9502; 2020-09-07: 204801.295
| 7.3.3.11.1B | Temporary Substation Microgrids | 2019-10-09: 3254; 2019-10-23: 0.1851%; 2019-10-26: 325.4; 2019-10-29: 76875.3524; 2020-09-07: 7687.5352
| 7.3.3.11.1C | Temporary Distribution Microgrids | 2019-10-09: 7259; 2019-10-23: 0.4129%; 2019-10-26: 725.9; 2019-10-29: 179279.5012; 2020-09-07: 17927.9501
| 7.3.3.16 | Hardening: Underground Projects | 2019-10-09: 12969; 2019-10-23: 0.7376%; 2019-10-26: 1296.9; 2019-10-29: 425818.6093; 2020-09-07: 42581.8609
| 7.3.3.8.1 | Distribution Sectionalizing | 2019-10-09: 19605; 2019-10-23: 1.115%; 2019-10-26: 1960.5; 2019-10-29: 572063.6406; 2020-09-07: 57206.3641
| 7.3.3.17.1 | Descoping Hardened OH | 2019-10-09: 4127; 2019-10-23: 0.2347%; 2019-10-26: 412.7; 2019-10-29: 89817.9332; 2020-09-07: 8981.7933
| Total-Customers Mitigated |  | 2019-10-09: 140908; 2019-10-23: 8.014%; 2019-10-26: 14090.8; 2019-10-29: 3601596.2497; 2020-09-07: 360159.625
Section 2b. Table 8.2.5.6 - Estimated Impact of 2021 Planned WMP Mitigations with Tree Overstrike Inclusion
| WMP Initiative | Mitigations | 2019-10-09: Customers Mitigated; 2019-10-23: Mitigated %; 2019-10-26: Customers Mitigated Per Event; 2019-10-29: Customer Hours; 2020-09-07: Customer Hours Per Event
| 7.3.3.8.2 | Transmission Lines - Switching | 2019-10-09: 9405.744; 2019-10-23: 0.3299%; 2019-10-26: 540.56; 2019-10-29: 331609.326; 2020-09-07: 19058.0072
| 7.3.3.17.2 | Transmission Lines - Repairs | 2019-10-09: 0; 2019-10-23: 0%; 2019-10-26: 0; 2019-10-29: 0; 2020-09-07: 0
| 7.3.5.3 | Transmission Lines - Vegetation | 2019-10-09: 142535.9419; 2019-10-23: 4.999%; 2019-10-26: 8191.7208; 2019-10-29: 3238191.1001; 2020-09-07: 186102.9368
| 7.3.3.11.1B | Temporary Substation Microgrids | 2019-10-09: 5276.9467; 2019-10-23: 0.1851%; 2019-10-26: 303.2728; 2019-10-29: 121550.5409; 2020-09-07: 6985.6633
| 7.3.3.11.1C | Temporary Distribution Microgrids | 2019-10-09: 11771.7751; 2019-10-23: 0.4129%; 2019-10-26: 676.5388; 2019-10-29: 283465.632; 2020-09-07: 16291.1283
| 7.3.3.16 | Hardening: Underground Projects | 2019-10-09: 21031.5679; 2019-10-23: 0.7376%; 2019-10-26: 1208.7108; 2019-10-29: 673277.9842; 2020-09-07: 38694.137
| 7.3.3.8.1 | Distribution Sectionalizing | 2019-10-09: 31793.0364; 2019-10-23: 1.115%; 2019-10-26: 1827.186; 2019-10-29: 904511.5606; 2020-09-07: 51983.423
| 7.3.3.17.1 | Descoping Hardened OH | 2019-10-09: 6692.6734; 2019-10-23: 0.2347%; 2019-10-26: 384.6364; 2019-10-29: 142014.5472; 2020-09-07: 8161.7556
| Total-Customers Mitigated |  | 2019-10-09: 228507.6854; 2019-10-23: 8.014%; 2019-10-26: 13132.6256; 2019-10-29: 5694620.691; 2020-09-07: 327277.0512
Meteorological Guidance
| 7.3.2.1.1 | POMMS
| 7.3.2.1.2 | LFM and DFM
| 7.3.2.1.3 | Weather Stations
| 7.3.2.4 | Advanced Fire Modeling
| 7.3.2.6 | SOPP
*Programs associated with meteorology but not project future benefits in 2021

## Summary_2A_and_Overview_redline
Tree Overstrike Impact
[19 empty] | Frequency | 1.74
[19 empty] | Duration (Customer-Hours) Per Event | 0.9087
[19 empty] | Scope Per Event | 0.932
|  | 2021 Planned WMP Mitigations Portfolio Analyzed Against 2020 Events and Select Four 2019 Events | [12 empty] | SCOPE | DURATION (direct) | DURATION (direct) | DURATION (direct) | DURATION (direct) | DURATION (direct) | DURATION (indirect) | DURATION (indirect) | DURATION (indirect)
| WMP Initiative | Mitigations | 2019-10-09 | 2019-10-23 | 2019-10-26 | 2019-10-29 | 2020-09-07 | 2020-09-26 | 2020-10-14 | 2020-10-21 | 2020-10-25 | 2020-12-03 | Customers Mitigated | Mitigated % | Customers Mitigated Per Event | CMIN CHOUR | CMIN CHOUR Per Event | CHOUR with 30min restoration time improvement | CHOUR Per Event with 30 min restoration time improvement | (Tree Overstrike) CHOUR Per Event w/ 30 min rest. improve | avg duration reduction (Hour / Cust) | avg duration reduction (Min/ Cust) | CMIN Per Event
| 7.3.3.8.2 | Transmission Lines - Switching | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5800 | 0 | 5800 | 0.3299% | 580 | 212628.2628 | 21262.8263 | 209728.2628 | 20972.8263 | 19058.0072 | 0.002726 | 0.16356 | 2304.6912
| 7.3.3.17.2 | Transmission Lines - Repairs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 7.3.5.3 | Transmission Lines - Vegetation | 41050 | 3133 | 13414 | 11222 | 16713 | 2362 | 0 | 0 | 0 | 0 | 87894 | 4.999% | 8789.4 | 2091959.9502 | 209195.995 | 2048012.9502 | 204801.295 | 186102.9368 | 0.04131 | 2.4786 | 34925.6091
| 7.3.3.11.21B | Temporary Substation Temp Gens Microgrids | 1548 | 0 | 804 | 199 | 703 | 0 | 0 | 0 | 0 | 0 | 3254 | 0.1851% | 325.4 | 78502.3524 | 7850.2352 | 76875.3524 | 7687.5352 | 6985.6633 | 0.0015294 | 0.091763 | 1293.0113
| 7.3.3.11.1C | Mid-Feeder Temporary Distribution Microgrids | 708 | 714 | 2238 | 714 | 351 | 166 | 90 | 40 | 2238 | 0 | 7259 | 0.4129% | 725.9 | 182909.0012 | 18290.9001 | 179279.5012 | 17927.9501 | 16291.1283 | 0.0034117 | 0.2047 | 2884.4403
| 7.3.3.16 | Hardening: Underground Projects | 0 | 0 | 2005 | 0 | 10964 | 0 | 0 | 0 | 0 | 0 | 12969 | 0.7376% | 1296.9 | 432303.1093 | 43230.3109 | 425818.6093 | 42581.8609 | 38694.137 | 0.0060954 | 0.36573 | 5153.3691
| 7.3.3.8.1 | Distribution Switches Sectionalizing | 4350 | 616 | 769 | 2027 | 3426 | 157 | 651 | 557 | 7052 | 0 | 19605 | 1.115% | 1960.5 | 581866.1406 | 58186.6141 | 572063.6406 | 57206.3641 | 51983.423 | 0.0092143 | 0.55286 | 7790.2538
| 7.3.3.17.1 | Descoping Hardened OH* | 0 | 0 | 3091 | 0 | 0 | 0 | 518 | 0 | 518 | 0 | 4127 | 0.2347% | 412.7 | 91881.4332 | 9188.1433 | 89817.9332 | 8981.7933 | 8161.7556 | 0.0019397 | 0.11638 | 1639.907
|  | Total-Customers Mitigated | 47656 | 4463 | 22321 | 14162 | 32157 | 2685 | 1259 | 597 | 15608 | 0 | 140908 | 8.014% | 14090.8 | 3672050.2497 | 367205.025 | 3601596.2497 | 360159.625 | 327277.0512 | 0.066227 | 3.9736 | 55991.2818
|  | Mitigated % | 36.95% | 2.679% | 3.962% | 6.339% | 18.64% | 4.116% | 2.383% | 1.935% | 4.411% | 0% | 8.014%
|  | Customers Affected - T&D | 128970 | 166610 | 563355 | 223423 | 172476 | 65240 | 52835 | 30858 | 353825 | 617 | 1758209
|  | Customers Affected - Dist. Only | 34659 | 152682 | 510136 | 197713 | 125774 | 66497 | 48063 | 36940 | 305346 | 617 | 1291086
Customer Affected - Transmission add.
|  | *Pending approval from wildfire governance committee Programs ongoing approval | 2934191.3602 | 2719428.063 | 9798766.6302 | 4285114.8481 | 6252002.6521 | 1450785.8563 | 1951012.8475 | 573291.3875 | 12971240.534 | 12875.35
|  | Average Outage Duration | 22.751 | 16.3221 | 17.3936 | 19.1794 | 36.2485 | 22.2377 | 36.9265 | 18.5784 | 36.66 | 20.8677 | 247.1649 | <--Copied and pasted from PSPS_Duration_Regression
2.023% | 7.3.5.3-D/T | 30min Rest Process Improvement | 22.251 | 15.8221 | 16.8936 | 18.6794 | 35.7485 | 21.7377 | 36.4265 | 18.0784 | 36.16 | 20.3677 | 242.1649 |  |  | Average | 30 min Improvement
[15 empty] | Mitigated CHR | 3672050.2497 | 3601596.2497
|  |  | 2019-10-09: *2019 used backcast, adjusted with 2020 weighted average restoration time. Backcast projects full weather event time, but actual event times vary per customer. |  |  | Total CHR | 42948709.5289 | 42069605.0289
[15 empty] | Mitigated Duration % | 8.55% | 10.43%
Section 2a. Table 8.2.5.5 - Estimated Impact of 2021 Planned WMP Mitigations
| WMP Initiative | Mitigations | 2019-10-09: Customers Mitigated; 2019-10-23: Mitigated %; 2019-10-26: Customers Mitigated Per Event; 2019-10-29: Customer Hours; 2020-09-07: Customer Hours Per Event
| 7.3.3.8.2 | Transmission Lines - Switching | 2019-10-09: 5800; 2019-10-23: 0.3299%; 2019-10-26: 580; 2019-10-29: 209728.2628; 2020-09-07: 20972.8263
| 7.3.3.17.2 | Transmission Lines - Repairs | 2019-10-09: 0; 2019-10-23: 0%; 2019-10-26: 0; 2019-10-29: 0; 2020-09-07: 0
| 7.3.5.3 | Transmission Lines - Vegetation | 2019-10-09: 87894; 2019-10-23: 4.999%; 2019-10-26: 8789.4; 2019-10-29: 2048012.9502; 2020-09-07: 204801.295
| 7.3.3.11.1B | Temporary Substation Microgrids | 2019-10-09: 3254; 2019-10-23: 0.1851%; 2019-10-26: 325.4; 2019-10-29: 76875.3524; 2020-09-07: 7687.5352
| 7.3.3.11.1C | Temporary Distribution Microgrids | 2019-10-09: 7259; 2019-10-23: 0.4129%; 2019-10-26: 725.9; 2019-10-29: 179279.5012; 2020-09-07: 17927.9501
| 7.3.3.16 | Hardening: Underground Projects | 2019-10-09: 12969; 2019-10-23: 0.7376%; 2019-10-26: 1296.9; 2019-10-29: 425818.6093; 2020-09-07: 42581.8609
| 7.3.3.8.1 | Distribution Sectionalizing | 2019-10-09: 19605; 2019-10-23: 1.115%; 2019-10-26: 1960.5; 2019-10-29: 572063.6406; 2020-09-07: 57206.3641
| 7.3.3.17.1 | Descoping Hardened OH | 2019-10-09: 4127; 2019-10-23: 0.2347%; 2019-10-26: 412.7; 2019-10-29: 89817.9332; 2020-09-07: 8981.7933
| Total-Customers Mitigated |  | 2019-10-09: 140908; 2019-10-23: 8.014%; 2019-10-26: 14090.8; 2019-10-29: 3601596.2497; 2020-09-07: 360159.625
Section 2b. Table 8.2.5.6 - Estimated Impact of 2021 Planned WMP Mitigations with Tree Overstrike Inclusion
| WMP Initiative | Mitigations | 2019-10-09: Customers Mitigated; 2019-10-23: Mitigated %; 2019-10-26: Customers Mitigated Per Event; 2019-10-29: Customer Hours; 2020-09-07: Customer Hours Per Event
| 7.3.3.8.2 | Transmission Lines - Switching | 2019-10-09: 9405.744; 2019-10-23: 0.3299%; 2019-10-26: 540.56; 2019-10-29: 331609.326; 2020-09-07: 19058.0072
| 7.3.3.17.2 | Transmission Lines - Repairs | 2019-10-09: 0; 2019-10-23: 0%; 2019-10-26: 0; 2019-10-29: 0; 2020-09-07: 0
| 7.3.5.3 | Transmission Lines - Vegetation | 2019-10-09: 142535.9419; 2019-10-23: 4.999%; 2019-10-26: 8191.7208; 2019-10-29: 3238191.1001; 2020-09-07: 186102.9368
| 7.3.3.11.1B | Temporary Substation Microgrids | 2019-10-09: 5276.9467; 2019-10-23: 0.1851%; 2019-10-26: 303.2728; 2019-10-29: 121550.5409; 2020-09-07: 6985.6633
| 7.3.3.11.1C | Temporary Distribution Microgrids | 2019-10-09: 11771.7751; 2019-10-23: 0.4129%; 2019-10-26: 676.5388; 2019-10-29: 283465.632; 2020-09-07: 16291.1283
| 7.3.3.16 | Hardening: Underground Projects | 2019-10-09: 21031.5679; 2019-10-23: 0.7376%; 2019-10-26: 1208.7108; 2019-10-29: 673277.9842; 2020-09-07: 38694.137
| 7.3.3.8.1 | Distribution Sectionalizing | 2019-10-09: 31793.0364; 2019-10-23: 1.115%; 2019-10-26: 1827.186; 2019-10-29: 904511.5606; 2020-09-07: 51983.423
| 7.3.3.17.1 | Descoping Hardened OH | 2019-10-09: 6692.6734; 2019-10-23: 0.2347%; 2019-10-26: 384.6364; 2019-10-29: 142014.5472; 2020-09-07: 8161.7556
| Total-Customers Mitigated |  | 2019-10-09: 228507.6854; 2019-10-23: 8.014%; 2019-10-26: 13132.6256; 2019-10-29: 5694620.691; 2020-09-07: 327277.0512
Meteorological Guidance
| 7.3.2.1.1 | POMMS
| 7.3.2.1.2 | LFM and DFM
| 7.3.2.1.3 | Weather Stations
| 7.3.2.4 | Advanced Fire Modeling
| 7.3.2.6 | SOPP
*Programs associated with meteorology but not project future benefits in 2021

## Summary 2B_3
Baseline Scoping Criteria |  |  |  | With Tree Overstrike Criteria* |  |  |  | Summary Calculations
Version | Event_Id | Customers_Impacted | average_outage_duration** | Version | Event_Id | Customers_Impacted | average_outage_duration** | Property | Baseline Events | With Tree Overstrike | Percent Increase Due to Tree Overstrike
baseli | baseline_event_10 | 62414 | 14.0406 | 70th_r | 70th_r_event_31 | 124788 | 18.2287 | Frequency (Number of Events) | 27 | 47 | 74.07%
baseli | baseline_event_20 | 20059 | 18.2873 | 70th_r | 70th_r_event_0 | 328603 | 23.8914 | Scope (Average Number of Customers Per Event) | 89216.2222 | 83161.8511 | -6.786%
baseli | baseline_event_2 | 185333 | 21.5893 | 70th_r | 70th_r_event_21 | 58721 | 15.4289 | Duration (Average Outage Duration Per Event, in hours) | 17.3532 | 16.9354 | -2.408%
baseli | baseline_event_17 | 26109 | 15.1871 | 70th_r | 70th_r_event_34 | 29663 | 16.9024
baseli | baseline_event_13 | 59225 | 16.2912 | 70th_r | 70th_r_event_29 | 31462 | 17.4954 | * As referenced in Section 8.2.6, the estimated increase in customer impacts from Priority 1 and Priority 2 tags over the Tree Overstrike Potential alone for 2019 and 2020 PSPS events is less than 1% and assumes no trees associated with Priority 1 or Priority 2 tags are mitigated prior to an event. Given that PG&E will work to mitigate Priority 1 and Priority 2 tags in advance of PSPS events, and the estimated quantitative impact of such tags is minimal, we have not included the estimated the quantitative impacts of Priority 1 and Priority 2 tags in this analysis. However, we refer to the current (May 2021 – August 2021) PSPS protocols as the 2020 PSPS Protocols Plus Tree Overstrike Potential and Priority Tags when discussing quantitative targets for naming consistency throughout the Revision Notice.
baseli | baseline_event_18 | 35597 | 15.3606 | 70th_r | 70th_r_event_6 | 191619 | 24.2466
baseli | baseline_event_4 | 146244 | 23.558 | 70th_r | 70th_r_event_11 | 78269 | 19.7587
baseli | baseline_event_12 | 57466 | 15.8832 | 70th_r | 70th_r_event_45 | 21821 | 12.9231
baseli | baseline_event_24 | 95879 | 16.7957 | 70th_r | 70th_r_event_28 | 38600 | 13.3017
baseli | baseline_event_15 | 69299 | 19.073 | 70th_r | 70th_r_event_1 | 260263 | 21.1239
baseli | baseline_event_9 | 81488 | 21.2131 | 70th_r | 70th_r_event_35 | 34427 | 14.5152 | ** This is calculated as the sum of weather duration, pre-weather de-energization switching time, and post-weather restoration and patrol time.
baseli | baseline_event_14 | 104521 | 15.795 | 70th_r | 70th_r_event_22 | 34119 | 16.488
baseli | baseline_event_23 | 12619 | 15.7876 | 70th_r | 70th_r_event_7 | 172420 | 20.7579
baseli | baseline_event_1 | 237457 | 20.4 | 70th_r | 70th_r_event_26 | 60728 | 14.3511
baseli | baseline_event_5 | 132285 | 17.92 | 70th_r | 70th_r_event_46 | 28980 | 12.539
baseli | baseline_event_21 | 27221 | 14.3489 | 70th_r | 70th_r_event_10 | 89715 | 17.8987
baseli | baseline_event_3 | 146048 | 17.0043 | 70th_r | 70th_r_event_36 | 16469 | 15.9202
baseli | baseline_event_16 | 54213 | 15.1897 | 70th_r | 70th_r_event_33 | 20510 | 13.4775
baseli | baseline_event_6 | 153487 | 21.9883 | 70th_r | 70th_r_event_41 | 54877 | 11.1043
baseli | baseline_event_25 | 20736 | 16.334 | 70th_r | 70th_r_event_4 | 187487 | 23.5561
baseli | baseline_event_7 | 136224 | 20.45 | 70th_r | 70th_r_event_39 | 53806 | 12.9631
baseli | baseline_event_26 | 31368 | 13.7459 | 70th_r | 70th_r_event_37 | 61779 | 13.4958
baseli | baseline_event_11 | 51857 | 15.9355 | 70th_r | 70th_r_event_20 | 47944 | 13.5094
baseli | baseline_event_22 | 31341 | 12.4632 | 70th_r | 70th_r_event_43 | 53907 | 11.9947
baseli | baseline_event_8 | 107648 | 16.9889 | 70th_r | 70th_r_event_24 | 58488 | 14.0961
baseli | baseline_event_0 | 304823 | 22.3729 | 70th_r | 70th_r_event_42 | 41918 | 15.0504
baseli | baseline_event_19 | 17877 | 14.5328 | 70th_r | 70th_r_event_40 | 29699 | 14.5924
|  |  |  | 70th_r | 70th_r_event_32 | 47853 | 17.0455
|  |  |  | 70th_r | 70th_r_event_19 | 80729 | 18.6367
|  |  |  | 70th_r | 70th_r_event_27 | 54777 | 13.9971
|  |  |  | 70th_r | 70th_r_event_5 | 166100 | 25.6155
|  |  |  | 70th_r | 70th_r_event_18 | 41892 | 14.3722
|  |  |  | 70th_r | 70th_r_event_8 | 126950 | 18.6577
|  |  |  | 70th_r | 70th_r_event_44 | 30794 | 14.3956
|  |  |  | 70th_r | 70th_r_event_16 | 39223 | 19.3968
|  |  |  | 70th_r | 70th_r_event_14 | 56321 | 15.9886
|  |  |  | 70th_r | 70th_r_event_13 | 77606 | 18.1774
|  |  |  | 70th_r | 70th_r_event_23 | 53142 | 14.2736
|  |  |  | 70th_r | 70th_r_event_9 | 112637 | 24.9202
|  |  |  | 70th_r | 70th_r_event_12 | 103434 | 17.197
|  |  |  | 70th_r | 70th_r_event_3 | 169244 | 18.519
|  |  |  | 70th_r | 70th_r_event_15 | 117727 | 15.9573
|  |  |  | 70th_r | 70th_r_event_17 | 77626 | 21.7236
|  |  |  | 70th_r | 70th_r_event_30 | 63301 | 14.8424
|  |  |  | 70th_r | 70th_r_event_38 | 19656 | 13.9797
|  |  |  | 70th_r | 70th_r_event_2 | 214824 | 23.8941
|  |  |  | 70th_r | 70th_r_event_25 | 43689 | 14.7618

## Summary_2B_Chart
2020 Mitigations | Customers |  | 2021 Mitigations | Customers
10/26 PSPS (Customers in Scope) | 967754 |  | 10/26/19 Impacted Customers | 538054
Meteorological Guidance | -150000 |  | 2021 TLines - Vegetation | -12811.56
Transmission Line Scoping & Exclusions | -136200 |  | 2021 Temp Substation Microgrids | -767.8913
Transmission Switching | 0 |  | 2021 Temp Distribution Microgrids | -2137.4885
Distribution Segmentation | -21000 |  | 2021 Hardening: UG Projects | -1914.9529
Humboldt Bay Generating Station | -65800 |  | 2021 Distribution Sectionalizing | -734.4632
Resilience Zones (Mid-Feeder Microgrids) | -3900 |  | 2021 Descoping Hardened OH* | -2952.1792
Substation with Temporary Generation | -52800 |  | 2021 Total Mitigation | 516735.4649
Revised 10/26 (Customers Scope) | 538054
|  |  | Tree Overstrike and Priority Tags on 10/26/2019 event | 8%
|  |  | With 2021 Mitigations | 7.683%
Category | 10/26/19 Weather Event Case Study
(1) Actual Weather Event Impacted Customers based on 2019 PSPS Protocols | 967754
(2) Projected Weather Event Impacted Customers based on 2020 PSPS Protocols | 538054 | 44.4%
(3) Projected Weather Event Impacted Customers based on 2020 PSPS Protocols w/ 2021 Planned WMP Mitigations | 516735.4649 | 3.962%
(4) Projected Weather Event Impacted Customers based on 2020 PSPS Protocols w/ 2021 Planned WMP Mitigations w/ Tree Overstrike Inclusion and Priority Tags | 579392.8372 | 7.683%

## Reference
Notes 2A:
This Summary_2A_and_Overview charts assess incremental benefits from the 2021 WMP Planned mitigations.
For the customer counts, we have not included generators and other transmission customers.
Existing mitigation impacts have been accounted for, as best as possible, when reviewing the incremental benefits of the 2021 WMP Planned mitigations.
Customer counts for the 2019 PSPS events are based on simulated events using 2020 criteria which might lead to a small over estimate in the all affected customers.
This summary represents latest analysis and is subject to change based on variability in mitigation plans and further identified mitigations in 2021.
Notes 2B:
Category | Assumptions | Explanation
Event Scope | When comparing the customers impacted with and without tree overstrike, only customers located in High Fire Threat Districts (HFTD) were included in the comparison. | Due to limitations in the 10-year lookback analysis, the distribution circuits in scope due to overstrike trees were counted on a whole-circuit basis. To allow for a fair comparison, distribution circuits in scope in baseline events (without overstrike trees) were also added to scope on a whole-circuit basis. To further the accuracy of the comparison, only the customers located in HFTD were included when comparing the events scoped with and without the inclusion of overstrike trees.
Event Scope | When comparing the customers impacted with and without tree overstrike, only distribution impacts were included. Transmission line impacts were excluded for both types of events. | Due to timing and nature of the request, only distribution impacts were analyzed for this comparative 10-year lookback analysis. For the 27 PSPS events which would have occurred both with and without overstrike trees, the inclusion of overstrike trees resulted in a larger distribution scope for those events. This also results in a greater chance for overlap between transmission and distribution impacts for the events scoped with overstrike trees - for these events, the net new customers added by transmission impacts was either the same or smaller for events scoped with overstrike trees. The 20 additional events added by overstrike trees did not experience weather conditions severe enough to trigger PSPS without that additional criteria, so those events were unlikely to include transmission PSPS impacts.
General Information | The comparative lookback analysis uses 10 years of data (2010-2019), and does not include 2020 simulated or actual event impacts. | 2020 PSPS event actual impacts were not calculated on a whole-circuit basis, included transmission impacts, and also included customer mitigations (microgrids, distribution back-tie switching, etc.). This made 2020 PSPS event actual impacts unsuitable for inclusion in this comparative lookback analysis, due to the scoping limitations applied to simulated events between 2010-2019.
General Information | This analysis included all 27 simulated events from 2010 to 2019 with baseline scoping criteria, and 47 events in the same time period with the inclusion of tree overstrike criteria. | This fully accounts for the increase in event frequency due to the inclusion of overstrike trees. The 20 additional events added by the overstrike trees criteria included relatively smaller/weaker weather events (which would not have otherwise triggered a PSPS event), the 20 additional events also had lower-than-average customer impact (scope) and duration (in hours). Thus, the inclusion of overstrike trees decreased the average per-event scope (in customers) and duration (in hours). In the previous Overstrike Workshop Follow up Response, PG&E quantified the impacts of Additional PSPS Criteria on average annual event count, average event duration, average event size, max event size, net new customers, and average annual instances of back-to-back events at a per-county level. Those results showed average event size increasing due to the inclusion of Additional PSPS Criteria because they were based on a comparison of the top 27 events with and without Additional PSPS Criteria, excluding the smaller 20 events added due to that additional criteria. Due to the difference in comparison methodology, those results do not conflict with the results shown in this analysis.
Event Duration | Event Duration is calculated by adding a 9.7 hour restoration time and 1 hour pre-weather de-energization switching time (total 10.7 hours) to the weather duration for each customer. This restoration time is constant for all events. | The same restoration time and switching time are assumed for both events scoped with baseline criteria, and for events scoped with the addition of overstrike trees. Based on actual PSPS events, switching and restoration times may be longer for larger event scopes. PG&E applied the average restoration and switching times experienced in 2020 to all customer impacts.