## Cover
PACIFIC GAS AND ELECTRIC COMPANY
2020 WILDFIRE MITIGATION PLAN
UPDATED - FEBRUARY 28, 2020
ATTACHMENT 1
ALL TABLES REQUIRED BY THE WMP GUIDELINES

## Table 1
Table 1-1: Recent performance on progress metrics, last 5 years - Distribution
# | Progress metric name | Annual performance |  |  |  |  | Unit(s) | Comments
|  | 2015 | 2016 | 2017 | 2018 | 2019 |  | Comments
1 | Grid condition findings from inspection – Distribution | 0.43455 | 0.58068 | 0.59118 | 0.57725 | 6.9105 | Number of Level 1, 2, and 3 findings per mile of circuit in HFTD, and per total miles of circuit for each of the following inspection types: | No Comments
|  | 0.00011806 | 0.00023613 | 0.041991 | 0.0095238 | 0.014522 | Number of level 1 findings (A tags) per mile of circuit in HFTD (Zone 1, Tier 2 & Tier 3 combined)
|  | 0.013066 | 0.009327 | 0.013656 | 0.022117 | 0.17595 | Number of level 2 findings (B tags) per mile of circuit in HFTD (Zone 1, Tier 2 & Tier 3 combined)
|  | 0.42137 | 0.57111 | 0.53554 | 0.54561 | 6.7201 | Number of level 3 findings (E+F tags) per mile of circuit in HFTD (Zone 1, Tier 2 & Tier 3 combined)
|  | 0.00098386 | 0.0015348 | 0.058284 | 0.23499 | 0.035931 | Number of level 1 findings (A tags) per mile of total circuit
|  | 0.06281 | 0.053483 | 0.070327 | 0.085006 | 0.31421 | Number of level 2 findings (B tags) per mile of total circuit
|  | 1.3953 | 1.7043 | 1.4511 | 1.383 | 7.9763 | Number of level 3 findings (E+F tags) per mile of total circuit
2 | Vegetation clearance findings from inspections | 2362 | 2792 | 3217 | 4815 | 37807 | Trees identified as being currently, or at risk in the near future, of being out of compliance. | PG&E does not track the precise data requested; the closest available estimate has been provided. (See comment below tables)
|  | 1545000 | 1545000 | 1545000 | 1545000 | 1545000 | Total # of Overhead Distribution Primary Spans in the system
|  | 0.2% | 0.2% | 0.2% | 0.3% | 2.4% | Estimated Percentage of electric distribution spans with non-compliant clearance
3 | Extent of grid modularization | N/A | N/A | N/A | N/A | 1.767 | HFTD All Devices/Mile | "Sectionalizing devices" defined as Overhead Switches, Fuses, Reclosers, Sectionalizers, TripSavers, FuseSavers. "Circuit miles? Defined as all overhead primary lines and excludes underground primary lines. Calculated data is defined as Overhead Devices per Overhead Mile.
|  | N/A | N/A | N/A | N/A | 0.064 | HFTD SCADA Devices/Mile
|  | N/A | N/A | N/A | N/A | 3.231 | Non-HFTD All Devices/Mile
|  | N/A | N/A | N/A | N/A | 0.126 | Non-HFTD SCADA Devices/Mile
4 | 4 Data collection and reporting |  |  |  |  | 60.2% | Percent of data requested in SDR and WMP collected in initial submission | The 2019 percent collected is for the data provided in the WMP Tables 1-31 (submitted on 2/7/2020) and does not include the SDR. Data considered to be N/A or TBD for any reason, for example not currently available or not feasible, is included/was not removed from the calculation.
Item 2 Comments (1-1 Distribution) – PG&E does not track the precise data requested as PG&E’s vegetation management data is generally tracked by tree. Therefore the closest available data has been provided with an estimated translation to the “Percentage of right-of-way with noncompliant clearance” data that was requested. PG&E vegetation management pre-inspectors identify a tree that is currently violating minimum clearance distances, or may violate minimum clearance in the near future, with a special designation of being a “Hazard Notification” (HN). Not all HNs represent actively non-compliant trees, as in many cases the tree is currently compliant but may be at risk of violating minimum clearances before the normal tree work cycle can be completed. Nonetheless, HNs are the best estimate PG&E has for the number of trees that were identified as being inside or near the minimum clearance requirements and have been provided above as the “Trees identified as being currently, or at risk in the near future, of being out of compliance” data.
(1) This estimate for the number of electric overhead spans has been determined by assuming an average span length (distance between poles) of 275 feet. Therefore the ~80,560 miles of overhead distribution circuit miles (425,356,800 feet) divided by 275 feet per span results in 1,546,752 total spans, or ~1,545,000 for the purposes of this estimate.
Table 1-2: Recent performance on progress metrics, last 5 years - Transmission
# | Progress metric name | Annual performance |  |  |  |  | Unit(s) | Comments
|  | 2015 | 2016 | 2017 | 2018 | 2019
2 | Grid condition findings from inspection – Transmission | 0.52326 | 0.68742 | 0.41991 | 0.92688 | 10.6386 | Number of Level 1, 2, and 3 findings per mile of circuit in HFTD, and per total miles of circuit for each of the following inspection types: | No Comments
|  | 0.0181 | 0.0057919 | 0.0097738 | 0.0036199 | 0.037466 | Number of level 1 findings (A tags) per mile of circuit in HFTD (Zone 1, Tier 2 & Tier 3 combined)
|  | 0.037828 | 0.021357 | 0.027873 | 0.030226 | 0.87348 | Number of level 2 findings (B tags) per mile of circuit in HFTD (Zone 1, Tier 2 & Tier 3 combined)
|  | 0.46733 | 0.66027 | 0.38226 | 0.89303 | 9.7276 | Number of level 3 findings (E+F tags) per mile of circuit in HFTD (Zone 1, Tier 2 & Tier 3 combined)
|  | 0.038069 | 0.011862 | 0.014014 | 0.0061793 | 0.030731 | Number of level 1 findings (A tags) per mile of total circuit
|  | 0.059697 | 0.05771 | 0.061683 | 0.061021 | 0.41606 | Number of level 2 findings (B tags) per mile of total circuit
|  | 0.56535 | 0.54361 | 0.43614 | 0.71106 | 4.0112 | Number of level 3 findings (E+F tags) per mile of total circuit

## Table 2
Table 2: Recent performance on outcome metrics, last 5 years
Metric type | # | Outcome metric name | Annual performance |  |  |  |  | Unit(s) | Comments
|  |  | 2015 | 2016 | 2017 | 2018 | 2019
1. Near misses | 1.a. | Number of all events (such as unplanned outages, faults, conventional blown fuses, etc.) that could result in ignition, by type according to utility-provided list (total) - add a new row for each ignition type and number rows in adjacent column to the left (column "#") 1.a.i, 1.a.ii … | 38250 | 37079 | 50711 | 34066 | 46105 | Number per year
| 1.b. | Number of all events (such as unplanned outages, faults, conventional blown fuses, etc.) that could result in ignition, by type according to utility-provided list (normalized) - add a new row for each ignition type and number rows in adjacent column to the left (column "#") 1.b.i, 1.b.ii ... | 0.6042 | 0.4128 | 0.1076 | 0.0652 | 0.128 | Number per RFW circuit mile day per year
| 1.c. | Number of wires down (total) | 3853 | 4355 | 7288 | 3628 | 6327 | Number of wires down per year
| 1.d. | Number of wires down (normalized) | 0.06087 | 0.04848 | 0.01546 | 0.00694 | 0.01756 | Number per RFW circuit mile day per year
2. Utility inspection findings Distribution | 2.a. | Number of Level 1 findings that could increase the probability of ignition discovered per circuit mile inspected | EC 3 | EC 6 | EC 1007 | EC 172 | EC 339 | Average number of Level 1 findings that could increase the probability of ignition discovered by all inspections per circuit mile per year
| 2.b. | Number of Level 2 findings that could increase the probability of ignition discovered per circuit mile inspected | EC 6513 | EC 10395 | EC 9104 | EC 10578 | EC 173229 | Average number of Level 2 findings that could increase the probability of ignition discovered by all inspections per circuit mile per year
| 2.c. | Number of Level 3 findings that could increase the probability of ignition discovered per circuit mile inspected | EC 4526 | EC 4354 | EC 4851 | EC 3848 | EC 1999 | Average number of Level 3 findings that could increase the probability of ignition discovered by all inspections per circuit mile per year
2. Utility inspection findings Transmission | 2.a. | Number of Level 1 findings that could increase the probability of ignition discovered per circuit mile inspected | LC 0 | LC 3 | LC 46 | LC 25 | LC 140 | Average number of Level 1 findings that could increase the probability of ignition discovered by all inspections per circuit mile per year
| 2.b. | Number of Level 2 findings that could increase the probability of ignition discovered per circuit mile inspected | LC 12 | LC 281 | LC 787 | LC 2580 | LC 32177 | Average number of Level 2 findings that could increase the probability of ignition discovered by all inspections per circuit mile per year
| 2.c. | Number of Level 3 findings that could increase the probability of ignition discovered per circuit mile inspected | LC 6 | LC 20 | LC 68 | LC 491 | LC 343 | Average number of Level 3 findings that could increase the probability of ignition discovered by all inspections per circuit mile per year
3. Customer hours of PSPS and other outages | 3.a. | Customer hours of planned outages including PSPS (total) | 1400185 | 1390308 | 1513383 | 4015315 | 101222207 | Total customer hours of planned outages per year
| 3.b. | Customer hours of planned outages including PSPS (normalized) | 22.12 | 15.48 | 3.21 | 7.68 | 280.95 | Total customer hours of planned outages per RFW circuit mile day per year
| 3.c. | Customer hours of unplanned outages, not including PSPS (total) | 11961889 | 9745978 | 32897043 | 24597247 | 28981976 | Total customer hours of unplanned outages per year
| 3.d. | Customer hours of unplanned outages, not including PSPS (normalized) | 188.96 | 108.49 | 69.79 | 47.04 | 80.44 | Total customer hours of unplanned outages per RFW circuit mile day per year
| 3.e. | Increase in System Average Interruption Duration Index (SAIDI) | -2.1 | -25.2 | 252.4 | -64.9 | 1088.3 | Change in minutes compared to the previous year
4. Utility ignited wildfire fatalities | 4.a. | Fatalities due to utility-ignited wildfire (total) | 2 | 0 | 22 | 85 | 0 | Number of fatalities per year
| 4.b. | Fatalities due to utility-ignited wildfire (normalized) | 3.2e-05 | 0 | 4.7e-05 | 0.000163 | 0 | Number of fatalities per RFW circuit mile day per year
5. Accidental deaths resulting from utility wildfire mitigation initiatives | 5.a. | Deaths due to utility wildfire mitigation activities (total) | – | – | – | 0 | 1 | Number of fatalities per year
6. OSHA-reportable injuries from utility wildfire mitigation initiatives | 6.a. | OSHA-reportable injuries due to utility wildfire mitigation activities (total) | – | – | – | 0 | 28 | Number of OSHA-reportable injuries per year
| 6.b. | OSHA-reportable injuries due to utility wildfire mitigation activities (normalized) | – | – | – | 0 | 0.894 | Number of OSHA-reportable injuries per year per 1000 line miles of grid
7. Value of assets destroyed by utility-ignited wildfire, listed by asset type | 7.a. | Value of assets destroyed by utility-ignited wildfire (total) | $895.5M | $880k | $25.5B | $36k | $39k | Dollars of damage or destruction per year
| 7.b. | Value of assets destroyed by utility-ignited wildfire (normalized) | 14146 | 9.79 | $54.01k | 0.69 | 0.11 | Dollars of damage or destruction per RFW circuit mile day per year
8. Structures damaged or destroyed by utility-ignited wildfire | 8.a. | Number of structures destroyed by utility-ignited wildfire (total) | 965 | 0 | 2299 | 18805 | 374 | Number of structures destroyed per year
| 8.b. | Number of structures destroyed by utility-ignited wildfire (normalized) | 0.015244 | 0 | 0.004877 | 0.035966 | 0.0010381 | Number of structures destroyed per RFW circuit mile day per year
9. Acreage burned by utility-ignited wildfire | 9.a. | Acreage burned by utility-ignited wildfire (total) | 1690 | 1102 | 170455 | 167162 | 79950 | Acres burned per year
| 9.b. | Acreage burned by utility-ignited wildfire (normalized) | 0.026697 | 0.012267 | 0.36161 | 0.31971 | 0.22191 | Acres burned per RFW circuit mile day per year
10. Number of utility wildfire ignitions | 10.a. | Number of ignitions (total) according to existing ignition data reporting requirement | 12 | 9 | 35 | 20 | 21 | Number per year
| 10.b. | Number of ignitions (normalized) | 0.0001896 | 0.0001002 | 7.43e-05 | 3.83e-05 | 5.83e-05 | Number per RFW circuit mile day per year
| 10.c. | Number of ignitions in HFTD (subtotal) | 4 | 6 | 18 | 20 | 5 | Number in HFTD per year
| 10.c.i. | Number of ignitions in HFTD Zone 1 | 0 | 0 | 0 | 13 | 0 | Number in HFTD Zone 1 per year
| 10.c.ii. | Number of ignitions in HFTD Tier 2 | 2 | 5 | 14 | 6 | 5 | Number in HFTD Tier 2 per year
| 10.c.iii. | Number of ignitions in HFTD Tier 3 | 2 | 1 | 4 | 1 | 0 | Number in HFTD Tier 3 per year
| 10.d. | Number of ignitions in HFTD (subtotal, normalized) | 6.32e-05 | 6.68e-05 | 3.82e-05 | 3.83e-05 | 1.39e-05 | Number in HFTD per RFW circuit mile day per year
| 10.d.i. | Number of ignitions in HFTD Zone 1 (normalized) | 0 | 0 | 0 | 2.49e-05 | 0 | Number in HFTD Zone 1 per RFW circuit mile day per year
| 10.d.ii. | Number of ignitions in HFTD Tier 2 (normalized) | 3.16e-05 | 5.57e-05 | 2.97e-05 | 1.15e-05 | 1.39e-05 | Number in HFTD Tier 2 per RFW circuit mile day per year
| 10.d.iii. | Number of ignitions in HFTD Tier 3 (normalized) | 3.16e-05 | 1.11e-05 | 8.5e-06 | 1.9e-06 | 0 | Number in HFTD Tier 3 per RFW circuit mile day per year
| 10.e. | Number of ignitions in non-HFTD (subtotal) | 8 | 3 | 17 | 0 | 16 | Number in non-HFTD per year
| 10.f. | Number of ignitions in non-HFTD (normalized) | 0.0001264 | 3.34e-05 | 3.61e-05 | 0 | 4.44e-05 | Number in non-HFTD per RFW circuit mile day per year
11. Critical infrastructure impacted | 11.a. | Critical infrastructure impacted by PSPS | 0 | 0 | 0 | 23257 | 577060 | Number of critical infrastructure (in accordance with D.19-05-042) locations impacted per hour multiplied by hours offline per year
| 11.b. | Critical infrastructure impacted by PSPS (normalized) | 0 | 0 | 0 | < 0.01 | 1.6 | Number of critical infrastructure (in accordance with D.19-05-042) locations impacted per hour multiplied by hours offline per RFW circuit mile day per year

## Table 3
Table 3: List and description of additional metrics, last 5 years
Metric | Performance |  |  |  |  | Units | Underlying assumptions | Third-party validation
| 2015 | 2016 | 2017 | 2018 | 2019
Metric 1A - Number of Equipment Failure Caused Outages within the HFTD areas on RFW Days | 14 | 13 | 199 | 109 | 71 | Number of sustained and momentary outage events | See comments below. | See Note 1
Metric 1B - Total of Number of Equipment Failure Caused Outages within the HFTD areas on RFW Days (normalized) | 0.00028 | 0.00018 | 0.00052 | 0.00025 | 0.00024 | Sustained and momentary outage events per RFW Day-Mile / year | See comments below. | See Note 1
Metric 2A - Number of Vegetation Caused Outages within the HFTD areas on RFW Days | 22 | 4 | 187 | 79 | 53 | Number of sustained and momentary outage events | See comments below. | See Note 1
Metric 2B - Number of Vegetation Caused Outages within the HFTD areas on RFW Days (normalized) | 0.00044 | 6e-05 | 0.00049 | 0.00018 | 0.00018 | Sustained and momentary outage events per RFW Day-Mile / year | See comments below. | See Note 1
Metric 3A - Number of Other/Animal Caused Outages within the HFTD areas on RFW Days | 69 | 19 | 715 | 702 | 106 | Number of sustained and momentary outage events | See comments below. | See Note 1
Metric 3BA - Number of Other/Animal Caused Outages within the HFTD areas on RFW Days (normalized) | 0.00139 | 0.00027 | 0.00187 | 0.00164 | 0.00036 | Sustained and momentary outage events per RFW Day-Mile / year | See comments below. | See Note 1
Metric 4 – Number of non-exempt fuse devices in Tier 2 and 3 HFTD that operate due to faults | 2425 | 2233 | 3785 | 2194 | 3965 | Number of sustained outages | See comments below. | See Note 1
Metric 5A - Number of T&D Wires Down Events within the HFTD areas that occur on RFW Days | 11 | 1 | 190 | 61 | 33 | Number of T&D Wire Down Events in HFTD on RFW Days | See comments below. | See Note 1
Metric 5A.1 - Number of Wires Down Events within the HFTD areas that occur on RFW Days - D | 11 | 1 | 186 | 59 | 31 | Number of T&D Wire Down Events in HFTD on RFW Days | See comments below. | See Note 1
Metric 5A.2 - Number of Wires Down Events within the HFTD areas that occur on RFW Days - T | 0 | 0 | 4 | 2 | 2 | Number of T&D Wire Down Events in HFTD on RFW Days | See comments below. | See Note 1
Metric 5B - Number of T&D Wires Down Events within the HFTD areas that occur on RFW Days (normalized) | 0.000174 | 1.1e-05 | 0.000403 | 0.000117 | 9.2e-05 | T&D Wire Down Events in HFTD areas per RFW Day-Mile / year | See comments below. | See Note 1
Note: Add more rows as needed.

## Table 4
Table 4: List and description of program targets, last 5 years
Program target | 2019 performance | Units | Underlying assumptions | Third-party validation
Complete WSIP enhanced inspection of all Transmission structures (49,715) | 49,715 (100.0%) | structures | Aerial inspections (drone or helicopter) and either ground or climbing inspection of transmission towers and poles. | Inspections are documented in Pronto Forms.
Complete all high priority corrective actions (A and B tags) identified during Transmission inspections (5,839) | 5,215 (89.3%) | tags | (1) Only high priority tags identified from WSIP enhanced inspections by 5/31 (2) Corrective actions are assumed complete when closed in SAP, meaning work was completed in the field and proper documentation has been verified and indicated as such in SAP (3) some of the “open” tags are on de-energized lines where there is no risk present and these tags will be repaired or resolved before the line would be returned to service. | Completion report generated from the SAP system
Complete WSIP enhanced inspection of all Distribution poles in the HFTD areas (694,250) | 694,250 (100.0%) | poles | Perform enhanced ground inspections of all Tier 2 and Tier 3 HFTD poles, and some additional “buffer zone” poles | Inspections are documented using Pronto enhanced inspection forms
Complete all high priority corrective actions (A and B tags) identified during Distribution inspections (5,046) | 4,881 (96.7%) | tags | (1) Only high priority tags identified from WSIP enhanced inspections by 5/31 (2) Corrective actions are assumed complete when closed in SAP, meaning work was completed in the field and proper documentation has been verified and indicated as such in SAP | Completion report generated from the SAP system.
Complete WSIP enhanced inspection of all substations (222) | 222 (100.0%) | substations | Perform enhanced ground inspections of all Tier 2 and Tier 3 HFTD stations by May 1, 2019 | Inspections are documented using Pronto enhanced inspection forms
Complete all high priority corrective actions (A and B tags) identified during Substation inspections. (746) | 745 (100.0%)3 | tags | Complete priority A and priority B corrective notifications (tags) created by April 30, 2019. | Completion report generated from the SAP system.
System hardening in HFTD areas (150 miles) | 171 (114.1%) | miles | 1) Convert overhead circuit to underground where feasible 2) Retire/remove overhead assets where customers can be served by other means (distributed generation, micro-grid, etc.) | PG&E’s Internal Audit reviewed and validated work completion results.
Perform enhanced vegetation management work in HFTD areas (2,450 circuit miles) | 2,498 (102.0%) | miles | Reduce wildfire through (1) overhang clearing 4ft vertical from conductor to sky for particular trees, (2) 12 ft radial clearing around the conductor, and (3) hazard tree mitigation. | PG&E’s Internal Audit reviewed and validated work completion results.
Complete CEMA inspections (45,300) | 36,800 (81.0%) | inspections | CEMA inspections encompass First and Second Patrol inspections to identify dead tree abatement work in response to the tree mortality emergency. | Data tracked and downloaded from the Vegetation Management PMD – Project Management Database
Remove/work all dead or dying trees (“CEMA trees”) identified by October 1 of the current year (48,374) | 48,374 (100.0%) | trees | Excludes trees where tree work is delayed by third party delays, including environmental permitting requirements, owner refusals, and agency approval or review. | Data tracked and downloaded from the Vegetation Management Database (VMD)
SCADA enable all remaining line reclosers in Tier 2 and Tier 3 HFTD areas (287) | 287 (100.0%) | line reclosers | Install Supervisory Control and Data Acquisition (SCADA) functionality on all line reclosers which currently lack SCADA functionality and are operated manually. | CWSP Recloser Database
Operationalize resilience zone (1) | 1 (100.0%) | resilience zone | (1) Installation of sectionalizing devices to enable isolation of the intended area from the rest of the distribution grid during PSPS (2) Installation of a pre-installed interconnection hub to enable the rapid connection of mobile generation during PSPS (3) Completion of any necessary hardening treatment(s) to enable safe energization of the intended area during PSPS weather conditions | Declaration document of Operational Readiness of the pilot resiliency zone with multiple functional leader’s signoff.
Operate heavy-lift helicopters to aid in fire suppression and restoration efforts (4) | 4 (100.0%) | helicopters | Operate 4 heavy-lift helicopters to respond to 100% of the agency (e.g., CAL-Fire) requests for PG&E to operate under agency’s control to support in the 2019 fire season. | US Department of Transportation FAA Operating Certificate authorizing the operation of 4 heavy-lift helicopters.
Operationalize and install high-definition cameras (71) | 133 (187.3%) | cameras | New installations of HD cameras that are used to identify, confirm and track wildfires. | The data from the operationalized PG&E HD Cameras is available at: http://www.alertwildfire.org
Install weather stations (400) | 426 (106.5%) | weather stations | New physical installation of weather stations on a pole, tower or other asset in HFTD areas. | The data from the PG&E Weather Stations is available at: https://mesowest.utah.edu/cgi-bin/droman/stn_mnet.cgi?mnet=227
Note: Add more rows as needed.
3The one remaining B tag is an approved exception under the standard exception process as that repair is being bundled with additional notifications that need to be completed at the same substation and a single clearance has been scheduled to limit the impact on our system and customers

## Table 5
Table 5: Accidental deaths due to utility wildfire mitigation initiatives, last 5 years
Activity | Victim | [14 empty] | Total
| Full-time employee |  |  |  |  | Contractor |  |  |  |  | Member of public
Year | 2015 | 2016 | 2017 | 2018 | 2019 | 2015 | 2016 | 2017 | 2018 | 2019 | 2015 | 2016 | 2017 | 2018 | 2019
Wildfire Safety Inspection Program (WSIP) - Distribution | – | – | – | 0 | 0 | – | – | – | 0 | 0 | – | – | – | 0 | 0 | 0
Wildfire Safety Inspection Program (WSIP) - Transmission | – | – | – | 0 | 0 | – | – | – | 0 | 1 | – | – | – | 0 | 0 | 1
Vegetation management/fuel reduction | – | – | – | 0 | 0 | – | – | – | 0 | 0 | – | – | – | 0 | 0 | 0
System Hardening | – | – | – | 0 | 0 | – | – | – | 0 | 0 | – | – | – | 0 | 0 | 0
PSPS | – | – | – | 0 | 0 | – | – | – | 0 | 0 | – | – | – | 0 | 0 | 0
Total | – | – | – | 0 | 0 | – | – | – |  | 1 | – | – | – | 0 | 0
Note: Add more rows as needed.
Notes for Table 5:
1. Data for “Member of public” was derived from review of PG&E’s “Riskmaster” database, which tracks third party claims.
2. PG&E’s Community Wildfire Safety Program, under which PG&E tracks its wildfire mitigation activities, was developed in 2018, with the above activities implemented in late 2018. Therefore, the “Year 2018” data above represents data from late 2018.

## Table 6
Table 6: OSHA-reportable injuries due to utility wildfire mitigation initiatives, last 5 years
Activity | Victim | [14 empty] | Total
| Full-time employee |  |  |  |  | Contractor1 |  |  |  |  | Member of public
Year | 2015 | 2016 | 2017 | 2018 | 2019 | 2015 | 2016 | 2017 | 20183 | 2019 | 2015 | 2016 | 2017 | 20183 | 2019
Inspection-Distribution | – | – | – | 0 | 0 | – | – | – | 0 | 13 | – | – | – | 0 | 0 | 13
Inspection-Transmission | – | – | – | 0 | 0 | – | – | – | 0 | 12 | – | – | – | 0 | 0 | 12
Enhanced Vegetation management/fuel reduction | – | – | – | 0 | 0 | – | – | – | N/A1 | 25 | – | – | – | 0 | 0 | 25
System Hardening | – | – | – | 0 | 0 | – | – | – | 0 | 3 | – | – | – | 0 | 0 | 3
PSPS | – | – | – | 0 | 0 | – | – | – | 0 | 0 | – | – | – | 0 | 0 | 0
Total | – | – | – | 0 | 0 | – | – | – | N/A | 53 | – | – | – | 0 | 0
Note: Add more rows as needed.
Notes for Table 6:
1. PG&E does not generally and centrally track OSHA reportable incidents for contractors. Contractors are responsible for complying with OSHA reportable notification requirements. The data in Table 6 reflects all OSHA recordables, including any reportable incidents, that PG&E tracks for internal purposes.
2. Data for “Member of public” was derived from review of PG&E’s “Riskmaster” database, which tracks third party claims.
3.PG&E’s Community Wildfire Safety Program, under which PG&E tracks its wildfire mitigation activities, was developed in 2018, with the above activities implemented in late 2018. Therefore, the “Year 2018” data above represents data from late 2018.

## Table 7
Table 7: Methodology for potential impact of ignitions
List of all data inputs used in impact simulation | Sources of data inputs | Data selection and treatment methodologies | Assumptions, including SME input | Equation(s), functions, or other algorithms used to obtain output | Output type(s), e.g., wind speed model | Comments
PG&E Ignitions 2015-2019 CALFIRE Incidents Fire weather warning data | PG&E CALFIRE National Weather Service | Model uses the S-MAP aligned bowtie framework. See details in Section 4.2 for treatment of data for the left and right side of the bowtie. | See details in Section 4.2 | See Section 4.2 for details about Multi Attribute Value Function (MAVF) to combine all potential consequences of a risk event in a single value | Risk Score per Tranche (See Section 4.2 for modeled Consequences and Outcomes) | Inputs utilized in Wildfire Risk S-MAP conforming bowtie
Surface Fuels | LANDFIRE Remap 2016 (LF 2.0.0) | Data was extracted for these layers using the PG&E domain boundary with a buffer of 20 miles. | Fuel Models updated consistent with CPUC HFTD Map modification approach. “Sapsis, D., Brown, T., Low, C., Moritz, M., Saah, D., and Shaby,B.,“Mapping Environmental Influences on Utility Fire Threat. A Report to the California Public Utilities Commission Pursuant to R.08 – 11-005 AND R.15-05-006,” Final Report, 16 February 2016.” | CalFire supported in 2016. Systematic errors identified in LANDFIRE led to use of alternative statewide vegetation data (CALVEG 2015) as a fuel system overlay onto LANDFIRE fuels for determination of mismatched fuel typing. | Modified LANDFIRE Fuels dataset | Details provided in Reax source report
Canopy Fuels | LANDFIRE Remap 2016 (LF 2.0.0) | Data was extracted for these layers using the PG&E domain boundary with a buffer of 20 miles. | See details in “Surface Fuels” above | CalFire supported in 2016. Systematic errors identified in LANDFIRE led to use of alternative statewide vegetation data (CALVEG 2015) as a fuel system overlay onto LANDFIRE fuels for determination of mismatched fuel typing | Modified LANDFIRE Fuels dataset | Details provided in Reax source report
Terrain | USGS Geospatial Data Abstraction Library (GDAL) | USGS Geospatial Data Abstraction Library (GDAL) command line utilities were used to calculate slope, aspect, and terrain ruggedness rasters at 1/3 arcsecond resolution. | N/A | N/A | N/A | Approach utilized by Reax
Climatology | Numerical Weather Prediction (NWP) | NWP model Weather Research and Forecasting (WRF) was used to generate high-resolution wind and weather fields from ~200 historical fire weather days. | ~200 historical fire weather days identified are acceptable proxy for fire spread modeling | N/A -Output is list of dates for each 32 km by 32 km NARR pixel in California where the most severe fire weather conditions occurred since 1979 | List of dates to derive weather conditions for Monte Carlo simulations | Details provided in Reax source report
Fosberg Fire Weather Index (FFWI) | Weather fields from ~200 historical fire weather days | Fire weather index created to measure the potential influence of weather on a wildfire based on model output of temperature, wind and relative humidity. | ~200 historical fire weather days identified are acceptable proxy for fire spread modeling | FFWI = n √ (1+U2) | N/A | Details provided in Reax source report
Modified Fosberg Fire Weather Index (MFFWI) | Weather fields from ~200 historical fire weather days | MFFWI is used to identify wind events that occur simultaneously with low relative humidities and high temperatures | ~200 historical fire weather days identified are acceptable proxy for fire spread modeling | MFFWI=FFWI x P ign/100 | 204 days corresponding to highest MFFWI in NARR dataset across California | Details provided in Reax source report
Buildings | Microsoft Building Data Source and 2010 US Census data for California were in GIS (shapefile) format | Housing density (structures/mi2) was calculated for each of 710,145 census blocks in California by dividing the housing count for each census block by its area. | Census data is acceptable proxy for structure quantification | N/A | Housing density a raster having the same projection and resolution (30 m) as the underlying fuels inputs. | 2010 Census tract data was utilized by Reax
Population | LandScan 2016 and 2010 US Census data for California were in GIS (shapefile) format | Population density (people/mi2) density was calculated for each of 710,145 census blocks in California by dividing the population for each census block by its area. | Census data is acceptable proxy for quantification of population impacts | N/A | Population density a raster having the same projection and resolution (30 m) as the underlying fuels inputs. | 2010 Census tract data was utilized by Reax
PG&E Assets | EDGIS and ET GIS | N/A | N/A | N/A | N/A
Fire Escape Probability | Reax Engineering “Wildland Fire Risk Model for Establishing Fire Threat Zones: Methodology and Results” | Modeling assumed ignitions in 100 meter buffered area surrounding overhead electric transmission and distribution facilities within Fire Index Areas. | The ignition routines function by igniting a user-specified fraction (e.g., 50%) of the 30 m pixels contained within the rasterized ignition mask | Pe ∝ Vf X (+f(Pr) X f(Ds) X f(T)) | Five model outputs by percentile. Probability: Relative probability of fire escaping initial attack efforts Consequence homes: Impacted number of homes Consequence timber: Impacted acres of timber Risk homes: Overall risk to homes (probability times homes consequence) Risk timber: Overall risk to timber (probability times timber consequence) | Pe - Probability of a fire escaping initial containment efforts Vf - Fire volume (acre-ft) after 6 hours of spread from Monte Carlo simulation Calibration constant f (x) Dimensionless function normalized between 0 and 1 Pr - Road density (mi/mi2) Ds - Distance to closest fire station (mi) T - Topographical slope or ruggedness f(Ds) =min(ds/d*s,1) f(Pr) =max(1-Pr/P*r,0) f(T)=max(T-T*/90o,0)
Note: Add more rows as needed.

## Table 10
Table 10: Weather patterns, last 5 years
Weather measurement | 2015 | 2016 | 2017 | 2018 | 2019 | 5-year historical averagea,b | Unit(s)
Red Flag Warning daysd | 63304 | 89832 | 471375 | 522855 | 360281 | 301529 | RFW circuit mile days per year
Days rated at the top 30% of proprietary fire potential index or similar fire risk index measuree | 757738 | 1753176 | 2336959 | 1553760 | 2329476 | 1746222 | Circuit mile days where proprietary measure rated above top 30% threshold1 per year
95th percentile wind conditionsa | 1033719 | 1324577 | 1790954 | 1026773 | TBDa | 1,294,006c | Circuit mile days with wind gusts over 95th percentile historical (meaning the prior 10 years, 2005-2014) conditions per year
99th percentile wind conditionsa | 162809 | 179614 | 480997 | 131966 | TBDa | 238,847c | Circuit mile days with wind gusts over 99th percentile historical (meaning the prior 10 years, 2005-2014) conditions per year
Offshore (e.g., Diablo, Mono, Santa Ana) wind conditionsa | 14830 | 2867 | 96643 | 106652 | TBDa | 55,248c | Circuit mile days that experience offshore (e.g., Diablo, Mono, Santa Ana) wind conditions (offshore wind events characterized as PG&E FPI >0.14 [filter for dry conditions], Wind Direction (N to ESE): 350°—112.5°, Sustained Wind Speeds ≥ 20 mph, Relative Humidity ≤ 25%, ≥3 consecutive hour duration, ≥0.5% areal coverage of conditions over model domain)
Notes for Table 10: A. Analysis is based on PG&E’s 30-year weather and fuels climatology at 3 km spatial and hourly temporal resolution from 1989 – 2018. Data for 2019 in a similar format will not be available until late Q2 2020. B. 5-year historical average is based on PG&E’s 30-year weather and fuels climatology at 3 km spatial and hourly temporal resolution from 1989 – 2018 and has been computed from 2014-2018. C. Average based on 2015 – 2018 data. D. Based on forecast data from the National Weather Service for HFTD areas as explained in the introduction to Section 2.2. E. Based on PG&E FPI forecasts of R4 (very high) fire danger or greater _______________ 1 Threshold here defined as top 30% of FPI or equivalent scale (e.g., “Extreme” on SCE’s FPI; “extreme”, 15 or greater, on SDG&E’s FPI; and 4 or above on PG&E’s FPI)

## Table 11
Table 11-1: Key recent drivers of ignition probability, last 5 years - Distribution
Incident type by ignition probability driver |  | Near misses tracked (y/n)? | Number of incidents per year | [5 empty] | Average percentage probability of ignition per incident | [5 empty] | Number of ignitions per year from this driver
|  |  | 2015 | 2016 | 2017 | 2018 | 2019 | Average | 2015 | 2016 | 2017 | 2018 | 2019 | Average | 2015 | 2016 | 2017 | 2018 | 2019 | Average
Contact from object - Distribution | All types of object contact | Y | 9185 | 10029 | 13693 | 9171 | 13434 | 11102.4 | 2.46% | 1.86% | 1.86% | 2.84% | 1.88% | 2.13% | 226 | 187 | 255 | 260 | 253 | 236.2
| Animal contact | Y | 2346 | 2242 | 2197 | 2447 | 2072 | 2260.8 | 1.66% | 1.47% | 2.09% | 2.21% | 3.19% | 2.11% | 39 | 33 | 46 | 54 | 66 | 47.6
| Balloon contact | Y | 473 | 526 | 526 | 647 | 464 | 527.2 | 4.23% | 2.47% | 1.9% | 2.47% | 3.02% | 2.77% | 20 | 13 | 10 | 16 | 14 | 14.6
| Veg. contact | Y | 3734 | 4432 | 8277 | 3285 | 8167 | 5579 | 2.65% | 2.1% | 1.57% | 3.56% | 1.44% | 2% | 99 | 93 | 130 | 117 | 118 | 111.4
| Vehicle contact | Y | 1793 | 2041 | 1917 | 1915 | 1835 | 1900.2 | 2.62% | 1.67% | 2.76% | 2.35% | 2.02% | 2.27% | 47 | 34 | 53 | 45 | 37 | 43.2
| 3rd party Contact Other | Y | 839 | 788 | 776 | 877 | 896 | 835.2 | 2.5% | 1.78% | 2.06% | 3.19% | 2.01% | 2.32% | 21 | 14 | 16 | 28 | 18 | 19.4
All types of equipment / facility failure - Distribution | All types | Y | 11099 | 11506 | 14700 | 10164 | 13031 | 12100 | 1.49% | 1.23% | 1.46% | 1.28% | 1.07% | 1.31% | 165 | 141 | 214 | 130 | 140 | 158
| Capacitor bank failure | Y | 56 | 65 | 83 | 55 | 70 | 65.8 | 17.86% | 16.92% | 12.05% | 18.18% | 10% | 14.59% | 10 | 11 | 10 | 10 | 7 | 9.6
| Conductor failure—all | Y | 2409 | 2661 | 3827 | 2395 | 3382 | 2934.8 | 3.57% | 2.82% | 2.69% | 3.22% | 2.25% | 2.84% | 86 | 75 | 103 | 77 | 76 | 83.4
| Conductor failure— wires down | Y | 1134 | 1241 | 1996 | 1182 | 1593 | 1429.2 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Fuse failure—all | Y | 372 | 352 | 479 | 305 | 345 | 370.6 | 1.88% | 1.14% | 1.88% | 3.28% | 0.58% | 1.73% | 7 | 4 | 9 | 10 | 2 | 6.4
| Fuse failure—conven-tional blown fuse | Y | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Lightning arrestor failure | Y | 144 | 145 | 139 | 135 | 130 | 138.6 | 4.17% | 1.38% | 4.32% | 0.74% | 3.08% | 2.74% | 6 | 2 | 6 | 1 | 4 | 3.8
| Switch failure | Y | 136 | 156 | 178 | 187 | 189 | 169.2 | 2.21% | 0.64% | 1.69% | 0% | 2.12% | 1.3% | 3 | 1 | 3 | 0 | 4 | 2.2
| Trans-former failure | Y | 4213 | 3947 | 4977 | 3136 | 3962 | 4047 | 0.36% | 0.25% | 0.42% | 0.32% | 0.53% | 0.38% | 15 | 10 | 21 | 10 | 21 | 15.4
| Pole | Y | 498 | 628 | 1111 | 669 | 1162 | 813.6 | 1.2% | 0.8% | 1.17% | 0.6% | 0.34% | 0.79% | 6 | 5 | 13 | 4 | 4 | 6.4
| Insulator and bushing | Y | 249 | 295 | 384 | 273 | 374 | 315 | 2.41% | 1.02% | 2.08% | 1.83% | 1.07% | 1.65% | 6 | 3 | 8 | 5 | 4 | 5.2
| Crossarm | Y | 572 | 717 | 777 | 769 | 1001 | 767.2 | 0.52% | 0.56% | 1.42% | 0.52% | 0.2% | 0.63% | 3 | 4 | 11 | 4 | 2 | 4.8
| Voltage regulator/ Booster | Y | 59 | 62 | 60 | 52 | 59 | 58.4 | 1.69% | 1.61% | 5% | 3.85% | 5.08% | 3.42% | 1 | 1 | 3 | 2 | 3 | 2
| Recloser | Y | 54 | 57 | 92 | 69 | 106 | 75.6 | 0% | 5.26% | 3.26% | 0% | 0% | 1.59% | 0 | 3 | 3 | 0 | 0 | 1.2
| Anchor/Guy | Y | 36 | 41 | 47 | 47 | 58 | 45.8 | 2.78% | 2.44% | 2.13% | 0% | 0% | 1.31% | 1 | 1 | 1 | 0 | 0 | 0.6
| Sectiona lizer | Y | 4 | 3 | 2 | 4 | 3 | 3.2 | 0% | 33.33% | 0% | 0% | 0% | 6.25% | 0 | 1 | 0 | 0 | 0 | 0.2
| Other Equipment | Y | 2297 | 2377 | 2544 | 2068 | 2190 | 2295.2 | 0.91% | 0.84% | 0.9% | 0.34% | 0.59% | 0.73% | 21 | 20 | 23 | 7 | 13 | 16.8
Wire-to-wire contact / contamination |  | Y | 14595 | 13424 | 18889 | 12002 | 16357 | 15053.4 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Other |  | Y | 2193 | 1285 | 2160 | 1785 | 1746 | 1833.8 | 1.46% | 1.4% | 0.6% | 1.18% | 2.23% | 1.34% | 32 | 18 | 13 | 21 | 39 | 24.6
Note: Add additional rows as needed.
Table 11-2: Key recent drivers of ignition probability, last 5 years - Transmission
Incident type by ignition probability driver |  | Near misses tracked (y/n)? | Number of incidents per year | [5 empty] | Average percentage probability of ignition per incident | [5 empty] | Number of ignitions per year from this driver
|  |  | 2015 | 2016 | 2017 | 2018 | 2019 | Average | 2015 | 2016 | 2017 | 2018 | 2019 | Average | 2015 | 2016 | 2017 | 2018 | 2019 | Average
Contact from object - Transmission | All types of object contact | Y | 155 | 136 | 232 | 138 | 150 | 162.2 | 3.87% | 8.82% | 4.31% | 7.97% | 8.67% | 6.41% | 6 | 12 | 10 | 11 | 13 | 10.4
| Animal | Y | 41 | 43 | 43 | 49 | 32 | 41.6 | 14.63% | 20.93% | 11.63% | 10.2% | 18.75% | 14.9% | 6 | 9 | 5 | 5 | 6 | 6.2
| Vegetation | Y | 50 | 41 | 122 | 26 | 64 | 60.6 | 0% | 0% | 0% | 0% | 1.56% | 0.33% | 0 | 0 | 0 | 0 | 1 | 0.2
| Mylar balloon | Y | 9 | 5 | 12 | 14 | 9 | 9.8 | 0% | 20% | 8.33% | 0% | 0% | 4.08% | 0 | 1 | 1 | 0 | 0 | 0.4
| Car pole | Y | 27 | 29 | 38 | 37 | 25 | 31.2 | 0% | 3.45% | 2.63% | 8.11% | 16% | 5.77% | 0 | 1 | 1 | 3 | 4 | 1.8
| 3rd Party (foreign object /aircraft/ vandalism) | Y | 28 | 18 | 17 | 12 | 20 | 19 | 0% | 5.56% | 17.65% | 25% | 10% | 9.47% | 0 | 1 | 3 | 3 | 2 | 1.8
All types of equipment / facility failure - Transmission | All types of Equipment Failure | Y | 97 | 122 | 145 | 123 | 132 | 123.8 | 3.09% | 3.28% | 5.52% | 4.07% | 6.06% | 4.52% | 3 | 4 | 8 | 5 | 8 | 5.6
| Arrestor | Y | 0 | 1 | 1 | 0 | 0 | 0.4 | N/A | 0% | 0% | N/A | N/A | 0% | 0 | 0 | 0 | 0 | 0 | 0
| Insulator or Bushing | Y | 32 | 48 | 54 | 56 | 33 | 44.6 | 3.13% | 0% | 3.7% | 1.79% | 9.09% | 3.14% | 1 | 0 | 2 | 1 | 3 | 1.4
| Circuit breaker | Y | 6 | 3 | 4 | 7 | 8 | 5.6 | 0% | 0% | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0
| Conductor | Y | 7 | 19 | 16 | 12 | 35 | 17.8 | 14.29% | 15.79% | 25% | 8.33% | 2.86% | 11.24% | 1 | 3 | 4 | 1 | 1 | 2
| Connector/ hardware | Y | 11 | 21 | 19 | 10 | 13 | 14.8 | 0% | 0% | 0% | 0% | 7.69% | 1.35% | 0 | 0 | 0 | 0 | 1 | 0.2
| Other station | Y | 21 | 17 | 18 | 14 | 20 | 18 | 0% | 0% | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0
| Structure line | Y | 7 | 7 | 27 | 20 | 18 | 15.8 | 0% | 0% | 3.7% | 5% | 0% | 2.53% | 0 | 0 | 1 | 1 | 0 | 0.4
| Switch (line+station) | Y | 13 | 4 | 6 | 4 | 2 | 5.8 | 0% | 0% | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0
| Transformer | Y | 0 | 2 | 0 | 0 | 5 | 1.4 | N/A | 0% | N/A | N/A | 20% | 28.57% | 1 | 0 | 0 | 0 | 1 | 0.4
| Other Equipment | N/A | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | 0 | 1 | 1 | 2 | 2 | 1.2
Wire-to-wire contact / contamination | All types of contamination | Y | 14 | 18 | 20 | 36 | 11 | 19.8 | 0% | 0% | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0
Disaster | All Types of Disaster (all but 2 Fire) | Y | 37 | 22 | 66 | 35 | 13 | 34.6 | 0% | 0% | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0
Other | All types of Other (e.g., customer or IPP caused) | Y | 17 | 5 | 11 | 19 | 24 | 15.2 | 23.53% | 0% | 54.55% | 42.11% | 25% | 31.58% | 4 | 0 | 6 | 8 | 6 | 4.8
Unknown | Patrol Found No Cause, No Damage | Y | 125 | 139 | 156 | 160 | 138 | 143.6 | 0% | 0% | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0
Weather | All types of Weather | Y | 278 | 84 | 202 | 38 | 204 | 161.2 | 0% | 0% | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0
| Lightning | Y | 226 | 58 | 72 | 30 | 109 | 99 | 0% | 0% | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0
| Rain | Y | 5 | 12 | 47 | 0 | 23 | 17.4 | 0% | 0% | 0% | N/A | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0
| Snow/ Ice | Y | 7 | 1 | 38 | 8 | 61 | 23 | 0% | 0% | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0
| Wind | Y | 40 | 13 | 45 | 0 | 11 | 21.8 | 0% | 0% | 0% | N/A | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0
Work Procedure Error (WPE) | All types of WPE | Y | 20 | 16 | 18 | 26 | 21 | 20.2 | 0% | 0% | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0

## Table 12
Table 12: Recent use of PSPS, last 5 years
PSPS characteristic | 2015 | 2016 | 2017 | 2018 | 2019 | Unit(s)
Frequency of PSPS events (total) | N/A | N/A | N/A | 1 | 9 | Number of instances where utility operating protocol requires de-energization of a circuit or portion thereof to reduce ignition probability, per year
Frequency of PSPS events (normalized) | N/A | N/A | N/A | 1.9e-06 | 2.5e-05 | Number of instances where utility operating protocol requires de-energization of a circuit or portion thereof in order to reduce ignition probability, per RFW circuit mile day per year
Scope of PSPS events (total) | N/A | N/A | N/A | 41 | 16506 | Circuit-events, measured in number of events multiplied by number of circuits de-energized per year
Scope of PSPS events (normalized) | N/A | N/A | N/A | 7.8e-05 | 0.046 | Circuit-events, measured in number of events multiplied by number of circuits targeted for de-energization per RFW circuit mile day per year
Duration of PSPS events (total) | N/A | N/A | N/A | 1517371 | 98617112 | Customer hours per year
Duration of PSPS events (normalized) | N/A | N/A | N/A | 3 | 274 | Customer hours per RFW circuit mile day per year
RFW circuit mile day per year | 63304 | 89832 | 471375 | 522855 | 360281 | Aligns with CPUC WSD provided definition: “Sum of miles of utility grid subject to Red Flag Warning each day, with day being defined as a 24 hour period.
Note: Add additional rows as needed.

## Table 13
Table 13: Current baseline state of service territory and utility equipment
Land use | Characteristic tracked | In non-HFTD | In HFTD Zone 1 | In HFTD Tier 2 | In HFTD Tier 3
In urban areas | Circuit miles | 15604 | 9 | 996 | 395
| Circuit miles in WUI | 4195 | 8 | 721 | 340
| Number of critical facilities | 17009 | 7 | 442 | 204
| Number of critical facilities in WUI | 4213 | 5 | 402 | 172
| Number of customers | 3966386 | 2172 | 76068 | 29274
| Number of customers in WUI | 1165448 | 1943 | 66452 | 27165
| Number of customers belonging to access and functional needs populations | 120605 | 45 | 2084 | 727
| Number of customers belonging to access and functional needs populations in WUI | 38384 | 39 | 1895 | 688
| Circuit miles of overhead transmission lines | 2048.2859 | 0.26 | 207.52 | 53.21
| Circuit miles of overhead transmission lines in WUI | 64.2395 | 0.13 | 82.14 | 36.26
| Circuit miles of overhead distribution lines | 13555.6129 | 9.04 | 788.97 | 341.44
| Circuit miles of overhead distribution lines in WUI | 4130.3742 | 7.86 | 638.39 | 303.76
| Number of substations | 314 | 0 | 18 | 0
| Number of substations in WUI | 94 | 0 | 14 | 0
In rural areas | Circuit miles | 45119 | 87 | 17020 | 7229
| Circuit miles in WUI | 7962 | 57 | 9479 | 4671
| Number of critical facilities | 10134 | 42 | 1857 | 1009
| Number of critical facilities in WUI | 2532 | 29 | 1153 | 690
| Number of customers | 1051321 | 3877 | 249888 | 130048
| Number of customers in WUI | 483462 | 3493 | 116821 | 210802
| Number of customers belonging to access and functional needs populations | 37116 | 158 | 11161 | 5530
| Number of customers belonging to access and functional needs populations in WUI | 18815 | 149 | 10055 | 5217
| Circuit miles of overhead transmission lines | 8865.8974 | 12.88 | 2871.55 | 1071.02
| Circuit miles of overhead transmission lines in WUI | 914.6182 | 6.27 | 814.51 | 285.71
| Circuit miles of overhead distribution lines | 36253.0641 | 74.01 | 14148.89 | 6157.93
| Circuit miles of overhead distribution lines in WUI | 7047.4321 | 50.99 | 8664.03 | 4385.5
| Number of substations | 289 | 0 | 35 | 7
| Number of substations in WUI | 67 | 0 | 27 | 18
In highly rural areas | Circuit miles | 7302 | 39 | 4539 | 825
| Circuit miles in WUI | 563 | 9 | 1035 | 331
| Number of critical facilities | 649 | 8 | 326 | 104
| Number of critical facilities in WUI | 108 | 4 | 144 | 60
| Number of customers | 39611 | 1303 | 33739 | 9840
| Number of customers in WUI | 14576 | 1068 | 22200 | 7919
| Number of customers belonging to access and functional needs populations | 878 | 7 | 1098 | 231
| Number of customers belonging to access and functional needs populations in WUI | 475 | 4 | 813 | 188
| Circuit miles of overhead transmission lines | 1703.7873 | 11.96 | 1144.35 | 169.27
| Circuit miles of overhead transmission lines in WUI | 49.8895 | 0.03 | 102.06 | 30.79
| Circuit miles of overhead distribution lines | 5597.9794 | 26.96 | 3394.71 | 655.73
| Circuit miles of overhead distribution lines in WUI | 513.1181 | 9.33 | 933.07 | 300.23
| Number of substations | 51 | 0 | 22 | 6
| Number of substations in WUI | 3 | 0 | 7 | 3
Notes for Table 13: 1. The WUI data were downloaded from an Esri feature service created by SILVIS Labs of University of Wisconsin. Metadata for the layer are available here. 2. The population density layer was derived by ‘dissolving’ US Census Tract population density data by the criteria defined by the CPUC: • Urban: Greater than or Equal to 1000 persons per square mile • Rural: Less than 1000 persons per square mile but Greater that 7 persons per square mile • Highly rural: Less than or equal to 7 persons per square mile. 3. Circuit miles = Circuit miles of overhead transmission lines + Circuit miles of overhead distribution lines 4. Circuit miles in WUI = Circuit miles of overhead transmission lines in WUI + Circuit miles of overhead distribution lines in WUI 5. Critical facility data was sourced using customer billing data by intersecting the result with both the population density layer as well as the WUI layer. 6. Existing ETGIS and EDGIS data (overhead lines, substations) were intersected with the population density layer and the WUI layer, respectively.

## Table 14
Table 14: Summary data on weather station count
Weather station count type | Current count | Unit(s)
Number of weather stations (total) | 630 | Total number located in service territory and operated by utility
Number of weather stations (normalized) | 0.0063 | Total number located in service territory and operated by utility, divided by total number of circuit miles in utility service territory
Number of weather stations in non-HFTD (total) | 75 | Total number located in non-HFTD service territory and operated by utility
Number of weather stations in non-HFTD (normalized) | 0.0011 | Total number located in non-HFTD service territory and operated by utility, divided by total number of circuit miles in non-HFTD service territory
Number of weather stations in HFTD Zone 1 (total) | 0 | Total number located in HFTD Zone 1 service territory and operated by utility
Number of weather stations in HFTD Zone 1 (normalized) | N/A | Total number located in HFTD Zone 1 service territory and operated by utility, divided by total number of circuit miles in HFTD Zone 1 service territory
Number of weather stations in HFTD Tier 2 (total) | 372 | Total number located in HFTD Tier 2 service territory and operated by utility
Number of weather stations in HFTD Tier 2 (normalized) | 0.0165 | Total number located in HFTD Tier 2 service territory and operated by utility, divided by total number of circuit miles in HFTD Tier 2 service territory
Number of weather stations in HFTD Tier 3 (total) | 183 | Total number located in HFTD Tier 3 service territory and operated by utility
Number of weather stations in HFTD Tier 3 (normalized) | 0.0217 | Total number located in HFTD Tier 3 service territory and operated by utility, divided by total number of circuit miles in HFTD Tier 3 service territory
Notes for Table 14: 1. PG&E currently employs one mobile weather station which is not reflected in the above table.

## Table 15
Table 15: Summary data on fault indicator count
Fault indicator count type | Distribution Current Count | Transmission Current count | Unit(s)
Number of fault indicators (total) | 19651 | 63 | Total number located in service territory and operated by utility
Number of fault indicators (normalized) | 0.2438 | 0.0035 | Total number located in service territory and operated by utility, divided by total number of circuit miles in utility service territory
Number of fault indicators in non-HFTD (total) | 15293 | 28 | Total number located in non-HFTD service territory and operated by utility
Number of fault indicators in non-HFTD (normalized) | 0.2781 | 0.0035 | Total number located in non-HFTD service territory and operated by utility, divided by total number of circuit miles in non-HFTD service territory
Number of fault indicators in HFTD Zone 1 (total) | 46 | 0 | Total number located in HFTD Zone 1 service territory and operated by utility
Number of fault indicators in HFTD Zone 1 (normalized) | 0.4182 | 0 | Total number located in HFTD Zone 1 service territory and operated by utility, divided by total number of circuit miles in HFTD Zone 1 service territory
Number of fault indicators in HFTD Tier 2 (total) | 2978 | 28 | Total number located in HFTD Tier 2 service territory and operated by utility
Number of fault indicators in HFTD Tier 2 (normalized) | 0.1624 | 0.0064 | Total number located in HFTD Tier 2 service territory and operated by utility, divided by total number of circuit miles in HFTD Tier 2 service territory
Number of fault indicators in HFTD Tier 3 (total) | 1334 | 7 | Total number located in HFTD Tier 3 service territory and operated by utility
Number of fault indicators in HFTD Tier 3 (normalized) | 0.1864 | 0.0053 | Total number located in HFTD Tier 3 service territory and operated by utility, divided by total number of circuit miles in HFTD Tier 3 service territory

## Table 16
Table 16: Location of planned utility equipment additions or removal by end of 3-year plan term
Land use | Characteristic tracked | Changes by end-2022
|  | In non-HFTD | In HFTD Zone 1 | In HFTD Tier 2 | In HFTD Tier 3
In urban areas | Circuit miles of overhead transmission lines | 0 | 0 | 0 | 0
| Circuit miles of overhead distribution lines | -9.27 | 0 | -0.76 | -0.15
| Circuit miles of overhead transmission lines in WUI | 0 | 0 | 0 | 0
| Circuit miles of overhead distribution lines in WUI | -0.78 | 0 | -0.45 | -0.11
| Number of substations | 0 | 0 | 0 | 0
| Number of substations in WUI | 0 | 0 | 0 | 0
| Number of weather stations | N/A | N/A | N/A | N/A
| Number of weather stations in WUI | N/A | N/A | N/A | N/A
In rural areas | Circuit miles of overhead transmission lines | -0.47 | 0 | -2.09 | -1.48
| Circuit miles of overhead distribution lines | -77.1 | -0.19 | -13.18 | -5.15
| Circuit miles of overhead transmission lines in WUI |  |  | -0.38 | -0.21
| Circuit miles of overhead distribution lines in WUI | -9.06 | -0.19 | -8.76 | -4.5
| Number of substations | 0 | 0 | 0 | 0
| Number of substations in WUI | 0 | 0 | 0 | 0
| Number of weather stations | N/A | N/A | N/A | N/A
| Number of weather stations in WUI | N/A | N/A | N/A | N/A
In highly rural areas | Circuit miles of overhead transmission lines | 0 | 0 | 0 | 0
| Circuit miles of overhead distribution lines | -12.69 | 0 | -4.17 | -0.47
| Circuit miles of overhead transmission lines in WUI | 0 | 0 | 0 | 0
| Circuit miles of overhead distribution lines in WUI | -0.95 | 0 | -1.7 | -0.14
| Number of substations | -1 | 0 | 0 | 0
| Number of substations in WUI | 0 | 0 | 0 | 0
| Number of weather stations | N/A | N/A | N/A | N/A
| Number of weather stations in WUI | N/A | N/A | N/A | N/A
Transmission lines refer to all lines at or above 65kV, and distribution lines refer to all lines below 65kV.

## Table 17
Table 17: Location of planned utility infrastructure upgrades
Land use | Characteristic tracked | In non-HFTD |  |  | In HFTD Zone 1 |  |  | In HFTD Tier 2 |  |  | In HFTD Tier 3
|  | 2020 | 2021 | 2022 | 2020 | 2021 | 2022 | 2020 | 2021 | 2022 | 2020 | 2021 | 2022
Total circuit miles planned for hardening each year, all types and locations |  | 0 | TBD | TBD | 0 | TBD | TBD | 3.6 | TBD | TBD | 179.5 | TBD | TBD
Total number of substations planned for hardening each year, all locations |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
In urban areas | Circuit miles planned for grid hardening of overhead transmission lines | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Circuit miles of overhead transmission lines in WUI to harden | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Circuit miles of overhead distribution lines to harden | 0 | TBD | TBD | 0 | TBD | TBD | 2.2 | TBD | TBD | 3.8 | TBD | TBD
| Circuit miles of overhead distribution lines in WUI to harden | 0 | TBD | TBD | 0 | TBD | TBD | 2.2 | TBD | TBD | 3.8 | TBD | TBD
| Circuit miles of overhead transmission lines in WUI to harden | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Number of substations to harden | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Number of substations in WUI to harden | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
In rural areas | Circuit miles of overhead transmission lines to harden | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Circuit miles of overhead transmission lines in WUI to harden | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Circuit miles of overhead distribution lines to harden | 0 | TBD | TBD | 0 | TBD | TBD | 1.4 | TBD | TBD | 175.7 | TBD | TBD
| Circuit miles of overhead distribution lines in WUI to harden | 0 | TBD | TBD | 0 | TBD | TBD | 1.4 | TBD | TBD | 174.5 | TBD | TBD
| Circuit miles of overhead transmission lines in WUI to harden | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Number of substations to harden | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Number of substations in WUI to harden | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
In highly rural areas | Circuit miles of overhead transmission lines to harden | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Circuit miles of overhead transmission lines in WUI to harden | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Circuit miles of overhead distribution lines to harden | 0 | TBD | TBD | 0 | TBD | TBD | 0 | TBD | TBD | 0 | TBD | TBD
| Circuit miles of overhead distribution lines in WUI to harden | 0 | TBD | TBD | 0 | TBD | TBD | 0 | TBD | TBD | 0 | TBD | TBD
| Circuit miles of overhead transmission lines in WUI to harden | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Number of substations to harden | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Number of substations in WUI to harden | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Transmission lines refer to all lines at or above 65kV, and distribution lines refer to all lines below 65kV.

## Table 18
Table 18-1: Key drivers of ignition probability - Distribution
Ignition probability drivers |  | Number of incidents per year (according to 5-year historical average) | Average likelihood of ignition per incident | Ignitions from this driver (according to 5-year historical average)
|  |  |  | Total | In non-HFTD | In HFTD Zone 1 | In HFTD Tier 2 | In HFTD Tier 3
Contact from object - Distribution | All types of object contact | 11102.4 | 2.13% | 236.2 | 146 | 0.4 | 61.8 | 28
| Animal contact | 2260.8 | 2.11% | 47.6 | 37.8 | 0 | 8 | 1.8
| Balloon contact | 527.2 | 2.77% | 14.6 | 12.8 | 0 | 1.8 | 0
| Vegetation contact | 5579 | 2% | 111.4 | 50.6 | 0.4 | 39 | 21.4
| Vehicle contact | 1900.2 | 2.27% | 43.2 | 31.4 | 0 | 9.8 | 2
| Contact from Object - Other | 835.2 | 2.32% | 19.4 | 13.4 | 0 | 3.2 | 2.8
All types of equipment / facility failure - Distribution | All types | 12100 | 1.31% | 158 | 125 | 0.4 | 24.6 | 8
| Capacitor bank failure | 65.8 | 14.59% | 9.6 | 8.2 | 0 | 0.8 | 0.6
| Conductor failure— all | 2934.8 | 2.84% | 83.4 | 64.8 | 0.2 | 13.6 | 4.8
| Conductor failure— wires down | 1429.2 | N/A | N/A | N/A | N/A | N/A | N/A
| Fuse failure—all | 370.6 | 1.73% | 6.4 | 4.8 | 0 | 1.4 | 0.2
| Fuse failure—conventional blown fuse | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Lightning arrestor failure | 138.6 | 2.74% | 3.8 | 3.6 | 0 | 0.2 | 0
| Switch failure | 169.2 | 1.3% | 2.2 | 1.8 | 0 | 0.4 | 0
| Transformer failure | 4047 | 0.38% | 15.4 | 12.6 | 0.2 | 2.2 | 0.4
| Pole | 813.6 | 0.79% | 6.4 | 5.4 | 0 | 0.8 | 0.2
| Insulator and bushing | 315 | 1.65% | 5.2 | 4.4 | 0 | 0.6 | 0.2
| Crossarm | 767.2 | 0.63% | 4.8 | 3.6 | 0 | 0.8 | 0.4
| Voltage regulator/ Booster | 58.4 | 3.42% | 2 | 1.4 | 0 | 0.6 | 0
| Recloser | 75.6 | 1.59% | 1.2 | 1.2 | 0 | 0 | 0
| Anchor/Guy | 45.8 | 1.31% | 0.6 | 0.4 | 0 | 0.2 | 0
| Sectionalizer | 3.2 | 6.25% | 0.2 | 0.2 | 0 | 0 | 0
| Other Equipment | 2295.2 | 0.73% | 16.8 | 12.6 | 0 | 3 | 1.2
Wire-to-wire contact / contamination |  | 15053.4 | N/A | N/A | N/A | N/A | N/A | N/A
Other |  | 1833.8 | 1.34% | 24.6 | 19.2 | 0 | 3.4 | 2
Table 18-2: Key drivers of ignition probability - Transmission
Ignition probability drivers |  | Number of incidents per year (according to 5-year historical average) | Average likelihood of ignition per incident | Ignitions from this driver (according to 5-year historical average)
|  |  |  | Total | In non-HFTD | In HFTD Zone 1 | In HFTD Tier 2 | In HFTD Tier 3
Contact from object - Transmission | All types of object contact | 162.2 | 6.41% | 10.4 | 5.4 | 0 | 3.6 | 1.4
| Animal | 41.6 | 14.9% | 6.2 | 2.8 | 0 | 2.8 | 0.6
| Vegetation | 60.6 | 0.33% | 0.2 | 0 | 0 | 0.2 | 0
| Mylar balloon | 9.8 | 4.08% | 0.4 | 0.2 | 0 | 0 | 0.2
| Car pole | 31.2 | 5.77% | 1.8 | 1.8 | 0 | 0 | 0
| 3rd Party (foreign object /aircraft/ vandalism) | 19 | 9.47% | 1.8 | 0.6 | 0 | 0.6 | 0.6
Equipment / Facility Failure - Transmission | All types of Equipment Failure | 123.8 | 4.52% | 5.6 | 2.8 | 0 | 2.2 | 0.6
| Arrestor | 0.4 | 0% | 0 | 0 | 0 | 0 | 0
| Insulator or Bushing | 44.6 | 3.14% | 1.4 | 0.8 | 0 | 0.6 | 0
| Circuit breaker | 5.6 | 0% | 0 | 0 | 0 | 0 | 0
| Conductor | 17.8 | 11.24% | 2 | 0.8 | 0 | 1.2 | 0
| Connector/ hardware | 14.8 | 1.35% | 0.2 | 0.2 | 0 | 0 | 0
| Other station | 18 | 0% | 0 | 0 | 0 | 0 | 0
| Structure line | 15.8 | 2.53% | 0.4 | 0.4 | 0 | 0 | 0
| Switch (line+station) | 5.8 | 0% | 0 | 0 | 0 | 0 | 0
| Transformer | 1.4 | 28.57% | 0.4 | 0.2 | 0 | 0.2 | 0
| Other Eqipment | 0 | N/A | 1.2 | 0.4 | 0 | 0.2 | 0.6
Contamination | All types of contamination | 19.8 | 0% | 0 | 0 | 0 | 0 | 0
Disaster | All Types of Disaster (all but 2 Fire) | 34.6 | 0% | 0 | 0 | 0 | 0 | 0
Other | All types of Other (e.g., customer or IPP caused) | 15.2 | 31.58% | 4.8 | 3.8 | 0 | 0.8 | 0.2
Unknown | Patrol Found No Cause, No Damage | 143.6 | 0% | 0 | 0 | 0 | 0 | 0
Weather | All types of Weather | 161.2 | 0% | 0 | 0 | 0 | 0 | 0
| Lightning | 99 | 0% | 0 | 0 | 0 | 0 | 0
| Rain | 17.4 | 0% | 0 | 0 | 0 | 0 | 0
| Snow/ Ice | 23 | 0% | 0 | 0 | 0 | 0 | 0
| Wind | 21.8 | 0% | 0 | 0 | 0 | 0 | 0
Work Procedure Error (WPE) | All types of WPE | 20.2 | 0% | 0 | 0 | 0 | 0 | 0

## Table 19
Table 19: Macro trends impacting ignition probability and/or wildfire consequence
Rank | Macro trends impacting utility ignited ignition probability and estimated wildfire consequence by year 10 | Comments
1 | Change in ignition probability and estimated wildfire consequence due to climate change | Several key climate change trends are influencing variable periods of extreme wildfire risks in Northern California. These trends significantly increase wildfire ignition risks around utility networks. Warmer winters are causing increases in rainfall rather snow, resulting in a decrease to the snowpack. This reduces available water resources earlier in summer months, stressing vegetation and increasing available fuels. Compounding the shift from snow to rain are extended dry periods following summer months deeper into fall and early winter. Northeast winds are more common in fall and winter months in Northern California and if not accompanied by rainfall or other atmospheric moisture wildfire risks continue to increase despite the presence of lower temperatures. Ignitions that occur under these conditions can result in large conflagrating wildfires that can further promote risk associated with Northern California’s abundant fuel and extreme terrain resulting in fires that develop their own devastating weather. Reference OEHHA: https://oehha.ca.gov/epic/changes-climate/precipitation “Extremely dry and extremely wet years have become more common in California. On average, the state receives 75 percent of its annual precipitation from November through March, with 50 percent occurring from December through February. As the winter months have become warmer in recent years, more precipitation has been falling as rain instead of snow over the watersheds that provide most of the state’s water supplies.” “The last decade also includes the driest consecutive four-year period, from 2012 to 2015.” “Warming temperatures, declining snowpack, and earlier spring snowmelt runoff can create stresses on vegetation” Reference National Geographic : https://www.nationalgeographic.com/science/2019/10/climate-change-california-power-outage/
3 | Change in ignition probability and estimated wildfire consequence due to relevant invasive species, such as bark beetles | Invasive species create landscape level concerns that have significant potential to impact areas within utility right-of-ways (ROW). Effects can extend well beyond the ROW making effective mitigation challenging for utilities without more holistic engagement and support from surrounding stakeholders. Of concern to utilities are both invasive plant species and insect species. Invasive insect species, such as bark beetles, can exacerbate forest health concerns and result in hazardous tree conditions that require repetitious monitoring and mitigation by utilities. Native species can impose the same impacts and challenges. Invasive plant species in California tend to thrive in disturbed environments, often displacing native species. There is evidence that these invasions can change and intensify fire regimes. Landscape disturbance can be presented following fires, as well as during ROW maintenance and enhancements. Regardless of disturbance origin utilities are continually compelled to perform additional monitoring and mitigation to identify and control detrimental impacts associated with invasive species. References Emergency Proclamation – Office of Governor https://www.ca.gov/archive/gov39/2015/10/30/news19180/index.html PNAS- Invasive grasses increase fire occurrence and frequency across US ecoregions “Fire-prone invasive grasses create novel ecosystem threats by increasing fine-fuel loads and continuity, which can alter fire regimes.” “the existence of an invasive grass-fire cycle is well known, evidence of altered fire regimes is typically based on local scale studies or expert knowledge.” “As concern about US wildfires grows, accounting for fire-promoting invasive grasses will be imperative for effectively managing ecosystems.” CalFire – https://www.readyforwildfire.org/forest-health/bark-beetle-information/about-bark-beetles/
2 | Change in ignition probability and estimated wildfire consequence due to other drivers of change in fuel density and moisture | PG&E’s service territory has experienced noteworthy changes in both fuel density and moisture over the last several decades. These trends significantly increase wildfire ignition risks around utility networks. Fuel density is increasing while available moisture in critical wildfire risk periods is decreasing. This has been accompanied by increases in large tree mortality and overall changes in forest structure. Contributing factors cover a wide range of influences, including but not limited to; climate change, land use patterns, fire suppression and variable forest management practices. Forests are becoming denser with decreased presence of large trees and significant tree mortality over the last decade. Lands that are left unmanaged are subject to increases in accumulated dead and downed fuels that can be annually influenced by surrounding finer, flashier fuels following periods of sufficient rain or snowfall. Reference PNAS: https://www.pnas.org/content/112/5/1458 Reference California Energy Commission: https://www.energy.ca.gov/sites/default/files/2019-07/Projections_CCCA4-CEC-2018-014.pdf
5 | Population changes (including Access and Functional Needs population) that could be impacted by utility ignition | Population in California and PG&E’s territory continue to show projections for growth in decades to come. A fair amount of this growth continues in lands previously undeveloped and bordering fire prone wildland areas. Many utility customers have left the urban environment in favor of more fire prone areas for reasons beyond the associated risk. Current estimates suggest that at least 25% of California’s residents already have residence in areas subject to significant wildfire risk. With projection of upward population trends continuing, it is likely that Wildland Urban Interface (WUI) and/or the CPUC HFTD areas will not be exceptions to increases. The available space and desire to live in safer urban areas in the PG&E territory are realistic factors that must be considered in reaching these conclusions. Variable portions of these increases will include customer with supplemental access and other functional needs. Utilities will need to engage in programs and education campaigns that inform and prepare all customers to mitigate consequence of these eminent risks. References LCAU - https://lcau.mit.edu/project/cataloguing-interface-wildfire-and-urban-development-california PPIC - https://www.ppic.org/content/pubs/report/R_116HJ3R.pdf CNBC - Warming climate, population sprawl threaten California’s future with more destructive wildfires - https://www.cnbc.com/2019/11/09/why-californias-wildfires-are-going-to-get-worse.html
6 | Population changes in HFTD that could be impacted by utility ignition | See response item ranked “5”. Given the overall area of the HFTD as a percentage of PG&E’s service territory, it is likely that population growth in the HFTD areas will not be an exception to anticipated trends.
7 | Population changes in WUI that could be impacted by utility ignition | See response item ranked “5”. Given the overall area of the WUI as a percentage of PG&E’s service territory, it is likely that population growth in WUI will not be an exception to anticipated trends. The HFTD map was informed by WUI data and tremendous overlap between the two categories exists within PG&E service territory.
4 | Utility infrastructure location in HFTD vs non-HFTD | Location of utility infrastructure in the HFTD areas needs to be considered as a risk mitigating factor by utilities. Siting decisions associated with infrastructure placement should complement other resiliency and hardening programs continually over the decades to come. Position of infrastructure and imposed risk can vary tremendously in the HFTD areas based on a multitude of terrain, aspect and exposure factors which are in many cases also realistic limitations. For these reasons the location of infrastructure in the HFTD areas will realize more significant changes in the HFTD areas compared to Non-HFTD areas.
8 | Utility infrastructure location in urban vs rural vs highly rural areas | See response to item ranked “4”. There is high correlation between the HFTD areas and rural communities. There is similar correlation between urban areas and non-HFTD areas.

## Table 20
Table 20: Anticipated characteristics of PSPS use over next 10 years
Rank order 1-9 | PSPS characteristic | Significantly increase; increase; no change; decrease; significantly decrease | Comments
1 | Duration of PSPS events in customer hours (normalized by fire weather, e.g., Red Flag Warning line mile days) | Significant Decrease | Directionally, there is the most opportunity to reduce customer hours per fire weather event through microgrids, segmentation, restoration time, and more granular weather forecasting in the short term, and system hardening and enhanced vegetation management in the long term. The absolute number and duration of customers impacted during this timeframe is unknown and dependent of numerous external factors*.
2 | Scope of PSPS events in circuit-events, measured in number of events multiplied by number of circuits targeted for de-energization (normalized by fire weather, e.g., Red Flag Warning line mile days) | Significant Decrease | Proportionally, this is the next largest change, based on the reasons described above (1). While a significant reduction is expected, there still may be many circuits impacted, but much smaller portions of each circuit. The absolute number and duration of customers impacted during this timeframe is unknown and dependent of numerous external factors*.
3 | Number of customers affected by PSPS events (normalized by fire weather, e.g., Red Flag Warning line mile days) | Significant Decrease | There should be a significant reduction in the number of customers impacted per fire weather event for the reasons described above (1) and (2), and due to the potential for “drop and pick-up” nature of micro-grids and resiliency zones, those customers will still be impacted, but for only a short duration during switching operations. The absolute number and duration of customers impacted during this timeframe is unknown and dependent of numerous external factors*.
4 | Frequency of PSPS events in number of instances where utility operating protocol requires de-energization of a circuit or portion thereof to reduce ignition probability (normalized by fire weather, e.g., Red Flag Warning line mile days) | Potential decrease | A potential relative decrease in the frequency of events compared to all fire weather days or red flag warnings could occur as PSPS may not be required for marginal weather events based on reasons described above (1) and (2). However, changes in how red flag warnings are issued by the NWS may impact this evaluation as red flag warnings are not totally objective at this time. The absolute number and duration of customers impacted during this timeframe is unknown and dependent of numerous external factors*.
5 | Duration of PSPS events in customer hours (total) | Potential Decrease | While an absolute decrease is expected in customer hours for the reasons described above (1), long term climate models point to higher probability of more frequent fire weather conditions. The absolute number and duration of customers impacted during this timeframe is unknown and dependent of numerous external factors*.
6 | Scope of PSPS events in circuit-events, measured in number of events multiplied by number of circuits targeted for de-energization (total) | Potential Decrease | While an absolute decrease is expected in circuit events for the reasons described above (2), long term climate models point to higher probability of more frequent fire weather conditions. The absolute number and duration of customers impacted during this timeframe is unknown and dependent of numerous external factors*.
7 | Number of customers affected by PSPS events (total) | Potential Decrease | While an absolute decrease is expected in the number of customers affected for the reasons described above (3), long term climate models point to a higher probability of more frequent fire weather conditions. The absolute number and duration of customers impacted during this timeframe is unknown and dependent of numerous external factors*.
8 | Frequency of PSPS events in number of instances where utility operating protocol requires de-energization of a circuit or portion thereof to reduce ignition probability (total) | Possible Increase | Given that long term climate models point to a higher probability of more frequent fire weather conditions, it is expected that the absolute number of PSPS events may increase, while impacting fewer customers based on reasons described above (1) and (2). The absolute number and duration of customers impacted during this timeframe is unknown and dependent of numerous external factors*.
9 | Other | N/A | N/A
Notes for Table 20: 1. *External factors include but are not limited: urban expansion in the wildland urban interface, fuels treatment programs performed by state and federal agencies, changes in bark-beetle tree damage and tree mortality (e.g., sudden oak death), fuel loading, general population changes, changes in regulatory requirements, climate change, droughts, frequency and duration of dry wind events.

## Table 21
Table 21: Risk assessment and mapping
Initiative activity | Year | Total per-initiative spend ($1000's) | Subtotal A: Capital expenditure ($1000's) | Subtotal B: Operating expenses ($1000's) | Line miles to be treated | Spend ($1000's)/ treated line mile | Ignition probability drivers targeted | Risk reduction | Risk-spend efficiency | Other risk drivers addressed | Existing/ new | Existing: What proceeding has reviewed program | If new: Memorandum account | In / exceeding compliance with regulations | Cite associated rule | Comments
1. A summarized risk map showing the overall ignition probability and estimated wildfire consequence along electric lines and equipment | 2019 plan | N/A - Risk Analysis activities generally performed by internal electric operations staff with costs not tracked separately
2019 actual
2020
2021
2022
2020-2022 plan total
2. Climate-driven risk map and modelling based on various relevant weather scenarios | 2019 plan | N/A - Climate driven risk mapping is an aspect of weather and fire modeling, captured in Table 22, Initiative 4-1, Forecast of a fire risk index, fire potential index, or similar
2019 actual
2020
2021
2022
2020-2022 plan total
3. Ignition probability mapping showing the probability of ignition along the electric lines and equipment | 2019 plan | N/A - Circuit based ignition probabilities and risk analysis activities generally performed by internal electric operations staff with costs not tracked separately
2019 actual
2020
2021
2022
2020-2022 plan total
4. Initiative mapping and estimation of wildfire and PSPS risk-reduction impact | 2019 plan | N/A - Risk Analysis activities generally performed by internal electric operations staff with costs not tracked separately
2019 actual
2020
2021
2022
2020-2022 plan total
5. Match drop simulations showing the potential wildfire consequence of ignitions that occur along the electric lines and equipment | 2019 plan | N/A - 5.3.1.5 is an aspect of weather and fire modeling, captured in Table 22, Initiative 4-1, Forecast of a fire risk index, fire potential index, or similar
2019 actual
2020
2021
2022
2020-2022 plan total
6. Weather-driven risk map and modelling based on various relevant weather scenarios | 2019 plan | N/A - Weather driven risk mapping is an aspect of weather and fire modeling, captured in Table 22, 4-1, Forecast of a fire risk index, fire potential index, or similar
2019 actual
2020
2021
2022
2020-2022 plan total

## Table 22
Table 22: Situational awareness and forecasting
Initiative activity | Year | Total per-initiative spend ($1000's) | Subtotal A: Capital expenditure ($1000's) | Subtotal B: Operating expenses ($1000's) | Line miles to be treated | Spend ($1000's)/ treated line mile | Ignition probability drivers targeted | Risk reduction | Risk-spend efficiency | Other risk drivers addressed | Existing/ new | Existing: What proceeding has reviewed program | If new: Memorandum account | In / exceeding compliance with regulations | Cite associated rule | Comments
1-1. Advanced weather monitoring and weather stations , Weather Station | 2019 plan | 8517.573 | 8208 | 309.573 | 9632.9231 | 0.88421 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2019 WMP | FRMMA / WMPMA | N/A | N/A | Assumption is that 1,300 weather stations will cover all of T2 and T3. Annual "miles treated" is calculated as # of weather stations/ 1,300 * total T2 and T3 circuit miles. Note that 200 weather stations were installed in 2018 as well. (WMP)
| 2019 actual | 7539.3547 | 6933.6763 | 605.6783 | 10259 | 0.7349 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2019 WMP | FRMMA / WMPMA | N/A | N/A
| 2020 | 8636.8609 | 8077.8609 | 559 | 9632.9231 | 0.8966 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2020 GRC | N/A | N/A | N/A
| 2021 | 6294.4512 | 5717.5632 | 576.888 | 6598.5523 | 0.95391 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2020 GRC | N/A | N/A | N/A
| 2022 | 595.3484 | 0 | 595.3484 | 0 | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2020 GRC | N/A | N/A | N/A
| 2020-2022 plan total | 15526.6604 | 13795.424 | 1731.2364 | 16231.4754 | 0.95658 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A | N/A | N/A | N/A | N/A
1-2. Advanced weather monitoring and weather stations , Cameras | 2019 plan | 4643.598 | 0 | 4643.598 | 1722 | 2.6966 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2019 WMP | FRMMA / WMPMA | N/A | N/A | Assumption is that 591 cameras for the entire program will cover all of T2 and T3. Therefore annual "miles treated" is calculated as # of cameras/591 * total T2 and T3 circuit miles. Note that a 9 cameras were installed in 2018, as well. (WMP)
| 2019 actual | 2063.3694 | 0 | 2063.3694 | 7045 | 0.29288 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2019 WMP | FRMMA / WMPMA | N/A | N/A
| 2020 | 3508.8 | 0 | 3508.8 | 10594.5854 | 0.33119 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2020 GRC | N/A | N/A | N/A
| 2021 | 3621 | 0 | 3621 | 10594.5854 | 0.34178 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2020 GRC | N/A | N/A | N/A
| 2022 | 1083.7126 | 0 | 1083.7126 | 3072.4298 | 0.35272 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2020 GRC | N/A | N/A | N/A
| 2020-2022 plan total | 8213.5126 | 0 | 8213.5126 | 24261.6007 | 0.33854 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A | N/A | N/A | N/A | N/A
1-3. Advanced weather monitoring and weather stations , Satellite Fire Detection | 2019 plan | 361.17 | 0 | 361.17 | 25597 | 0.01411 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2019 WMP | FRMMA / WMPMA | N/A | N/A | Program applies to all of T3 and T2 in Distribution. (WMP)
| 2019 actual | 0 | 0 | 0 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2019 WMP | FRMMA / WMPMA | N/A | N/A
| 2020 | 341.592 | 0 | 341.592 | 25597 | 0.013345 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2020 GRC | N/A | N/A | N/A
| 2021 | 352.515 | 0 | 352.515 | 25597 | 0.013772 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2020 GRC | N/A | N/A | N/A
| 2022 | 363.8021 | 0 | 363.8021 | 25597 | 0.014213 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2020 GRC | N/A | N/A | N/A
| 2020-2022 plan total | 1057.9091 | 0 | 1057.9091 | 25597 | 0.041329 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A | N/A | N/A | N/A | N/A
2-1. Continuous monitoring sensors , Enhanced Wires Down | 2019 plan | 2258.382 | 2052 | 206.382 | 25597 | 0.088228 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2019 WMP | FRMMA / WMPMA | N/A | N/A | Program applies to all of T3 and T2 in Distribution. (WMP)
| 2019 actual | 390.7149 | 390.5367 | 0.17818 | 25597 | 0.015264 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2019 WMP | FRMMA / WMPMA | N/A | N/A
| 2020 | 929.58 | 716.8 | 212.78 | 25597 | 0.036316 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2020 GRC | N/A | N/A | N/A
| 2021 | 212.78 | 0 | 212.78 | 0 | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2020 GRC | N/A | N/A | N/A
| 2022 | 212.78 | 0 | 212.78 | 0 | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2020 GRC | N/A | N/A | N/A
| 2020-2022 plan total | 1355.14 | 716.8 | 638.34 | 25597 | 0.052941 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A | N/A | N/A | N/A | N/A
2-2. Continuous monitoring sensors , EPIC - DFA and EFD | 2019 plan | 4706.2154 | 0 | 4706.2154 | 838 | 5.616 | N/A - Exploratory Project | N/A - Exploratory Project | N/A - Exploratory Project | N/A - Exploratory Project | Existing | EPIC | N/A | N/A | N/A | Program applies to all of T3 and T2 in Distribution. (WMP and Routine Distribution)
| 2019 actual | 2474.8189 | 0 | 2474.8189 | 838 | 2.9532 | N/A - Exploratory Project | N/A - Exploratory Project | N/A - Exploratory Project | N/A - Exploratory Project | Existing | EPIC | N/A | N/A | N/A
| 2020 | 4166.467 | 0 | 4166.467 | 30 | 138.8822 | N/A - Exploratory Project | N/A - Exploratory Project | N/A - Exploratory Project | N/A - Exploratory Project | Existing | EPIC | N/A | N/A | N/A
| 2021 | 3800 | 0 | 3800 | 0 | N/A | N/A - Exploratory Project | N/A - Exploratory Project | N/A - Exploratory Project | N/A - Exploratory Project | Existing | EPIC | N/A | N/A | N/A
| 2022 | 4600 | 0 | 4600 | 0 | N/A | N/A - Exploratory Project | N/A - Exploratory Project | N/A - Exploratory Project | N/A - Exploratory Project | Existing | EPIC | N/A | N/A | N/A
| 2020-2022 plan total | 12566.467 | 0 | 12566.467 | 30 | 418.8822 | N/A - Exploratory Project | N/A - Exploratory Project | N/A - Exploratory Project | N/A - Exploratory Project | N/A | N/A | N/A | N/A | N/A
2-3. Continuous monitoring sensors , Line Sensor Devices | 2019 plan | 0 | 0 | 0 | 0 | 0 | N/A - Exploratory Project | N/A - Exploratory Project | N/A - Exploratory Project | N/A - Exploratory Project | Existing | 2017 GRC | N/A | N/A | N/A | Cost per line mile treated uses the higher end of the WMP unit ranges provided. (WMP)
| 2019 actual | 2763.8898 | 2763.8898 | 0 | 852 | 3.2444 | N/A - Exploratory Project | N/A - Exploratory Project | N/A - Exploratory Project | N/A - Exploratory Project | Existing | 2017 GRC | N/A | N/A | N/A
| 2020 | 3918.6715 | 3918.6715 | 0 | 1,000-3,000 | 1.3062 | N/A - Exploratory Project | N/A - Exploratory Project | N/A - Exploratory Project | N/A - Exploratory Project | New | N/A | FRMMA | N/A | N/A
| 2021 | 6600.6927 | 6600.6927 | 0 | 1,000-5,000 | 1.3201 | N/A - Exploratory Project | N/A - Exploratory Project | N/A - Exploratory Project | N/A - Exploratory Project | New | N/A | FRMMA | N/A | N/A
| 2022 | 7379.6284 | 7379.6284 | 0 | 1,000-4,000 | 1.8449 | N/A - Exploratory Project | N/A - Exploratory Project | N/A - Exploratory Project | N/A - Exploratory Project | New | N/A | FRMMA | N/A | N/A
| 2020-2022 plan total | 17898.9926 | 17898.9926 | 0 | 3,000-12,000 | 1.4916 | N/A - Exploratory Project | N/A - Exploratory Project | N/A - Exploratory Project | N/A - Exploratory Project | N/A | N/A | N/A | N/A | N/A
2-4. Continuous monitoring sensors , Arc Fault Signature Library | 2019 plan | 0 | 0 | 0 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | N/A | FRMMA | N/A | N/A | 2020 costs 100% reimbursable as part of joint research project with national laboratories (WMP)
| 2019 actual | 0 | 0 | 0 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | N/A | FRMMA | N/A | N/A
| 2020 | 0 | 0 | 0 | 201 | 0 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | N/A | FRMMA | N/A | N/A
| 2021 | 0 | 0 | 0 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | N/A | FRMMA | N/A | N/A
| 2022 | 0 | 0 | 0 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | N/A | FRMMA | N/A | N/A
| 2020-2022 plan total | 0 | 0 | 0 | 201 | 0 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A | N/A | N/A | N/A | N/A
2-5. Continuous monitoring sensors , Transmission SEL T400L Relays | 2019 plan | 1910 | 1910 | 0 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | Transmission Owner | N/A | N/A | N/A | (WMP)
| 2019 actual | 1200 | 1200 | 0 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | Transmission Owner | N/A | N/A | N/A
| 2020 | 700 | 700 | 0 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | Transmission Owner | N/A | N/A | N/A
| 2021 | 0 | 0 | 0 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A | N/A | N/A | N/A | N/A
| 2022 | 0 | 0 | 0 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A | N/A | N/A | N/A | N/A
| 2020-2022 plan total | 700 | 700 | 0 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A | N/A | N/A | N/A | N/A
2-6. Continuous monitoring sensors , Sensor IQ | 2019 plan | 0 | 0 | 0 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | N/A | FRMMA | N/A | N/A | Assumption is that this program provides value to the whole distribution system in HFTD (WMP)
| 2019 actual | 52.7134 | 29.212 | 23.5013 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | N/A | FRMMA | N/A | N/A
| 2020 | 1819.2733 | 0 | 1819.2733 | 25597 | 0.071074 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | N/A | FRMMA | N/A | N/A
| 2021 | 86.5851 | 0 | 86.5851 | 0 | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | N/A | FRMMA | N/A | N/A
| 2022 | 95.6883 | 0 | 95.6883 | 0 | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | N/A | FRMMA | N/A | N/A
| 2020-2022 plan total | 2001.5466 | 0 | 2001.5466 | 25597 | 0.071074 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A | N/A | N/A | N/A | N/A
3. Fault indicators for detecting faults on electric lines and equipment | 2019 plan | See Table 22, 2-6, Sensor IQ
2019 actual
2020
2021
2022
2020-2022 plan total
4. Forecast of a fire risk index, fire potential index, or similar | 2019 plan | 1635.582 | 0 | 1635.582 | 25597 | 0.063897 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2019 WMP | FRMMA / WMPMA | N/A | N/A | Program applies to all of T3 and T2 in Distribution. Assumption is this program treats all miles. (WMP)
| 2019 actual | 4530.0666 | 396.4541 | 4133.6125 | 25597 | 0.17698 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2019 WMP | FRMMA / WMPMA | N/A | N/A
| 2020 | 5122.848 | 0 | 5122.848 | 25597 | 0.20013 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2020 GRC | N/A | N/A | N/A
| 2021 | 5286.66 | 0 | 5286.66 | 25597 | 0.20653 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2020 GRC | N/A | N/A | N/A
| 2022 | 5455.9324 | 0 | 5455.9324 | 25597 | 0.21315 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2020 GRC | N/A | N/A | N/A
| 2020-2022 plan total | 15865.4404 | 0 | 15865.4404 | 25597 | 0.61982 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A | N/A | N/A | N/A | N/A
5. Personnel monitoring areas of electric lines and equipment in elevated fire risk conditions | 2019 plan | This function is performed by PG&E’s Safety and Infrastructure Protection Teams (SIPT). The costs and other details associated with the SIPT are provided in Table 26, 2. Crew-accompanying ignition prevention and suppression resources and services
2019 actual
2020
2021
2022
2020-2022 plan total
6. Weather forecasting and estimating impacts on electric lines and equipment , SOPP | 2019 plan | 180.584 | 0 | 180.584 | 25597 | 0.0070549 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2019 WMP | FRMMA / WMPMA | N/A | N/A | Program applies to all of T3 and T2 in Distribution. Assumption is this program treats all miles. (WMP)
| 2019 actual | 0 | 0 | 0 | 25597 | 0 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2019 WMP | FRMMA / WMPMA | N/A | N/A
| 2020 | 1974.216 | 0 | 1974.216 | 25597 | 0.077127 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2020 GRC | N/A | N/A | N/A
| 2021 | 2037.345 | 0 | 2037.345 | 25597 | 0.079593 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2020 GRC | N/A | N/A | N/A
| 2022 | 2102.5783 | 0 | 2102.5783 | 25597 | 0.082142 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2020 GRC | N/A | N/A | N/A
| 2020-2022 plan total | 6114.1393 | 0 | 6114.1393 | 25597 | 0.23886 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A | N/A | N/A | N/A | N/A
7-1. Other , WSOC | 2019 plan | 14878.9019 | 718.2 | 14160.7019 | 25597 | 0.58128 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2019 WMP | FRMMA / WMPMA | Exceeds | N/A | (WMP)
| 2019 actual | 7799.1706 | 2120.9695 | 5678.2011 | 25597 | 0.30469 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2019 WMP | FRMMA / WMPMA | Exceeds | N/A
| 2020 | 16741.9712 | 51.2 | 16690.7712 | 25597 | 0.65406 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2020 GRC | N/A | Exceeds | N/A
| 2021 | 20257.5028 | 52.38 | 20205.1228 | 25597 | 0.7914 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2020 GRC | N/A | Exceeds | N/A
| 2022 | 21358.0429 | 53.685 | 21304.3579 | 25597 | 0.8344 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2020 GRC | N/A | Exceeds | N/A
| 2020-2022 plan total | 58357.517 | 157.265 | 58200.252 | 25597 | 2.2799 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A | N/A | N/A | Exceeds | N/A
7-2. Other , Meteorology Operations Center | 2019 plan | 0 | 0 | 0 | N/A | 0 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A | N/A | N/A | N/A | N/A | (WMP)
| 2019 actual | 0 | 0 | 0 | N/A | 0 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A | N/A | N/A | N/A | N/A
| 2020 | 398.1394 | 398.1394 | 0 | N/A | 0 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | N/A | FRMMA | N/A | N/A
| 2021 | 0 | 0 | 0 | N/A | 0 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | N/A | N/A | N/A | N/A
| 2022 | 0 | 0 | 0 | N/A | 0 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | N/A | N/A | N/A | N/A
| 2020-2022 plan total | 398.1394 | 398.1394 | 0 | N/A | 0 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A | N/A | N/A | N/A | N/A

## Table 23
Table 23: Grid design and system hardening
Initiative activity | Year | Total per-initiative spend ($1000's) | Subtotal A: Capital expenditure ($1000's) | Subtotal B: Operating expenses ($1000's) | Line miles to be treated | Spend ($1000's)/ treated line mile | Ignition probability drivers targeted | Risk reduction | Risk-spend efficiency | Other risk drivers addressed | Existing/ new | Existing: What proceeding has reviewed program | If new: Memorandum account | In / exceeding compliance with regulations | Cite associated rule | Comments
1. Capacitor maintenance and replacement program | 2019 plan | 15929.9731 | 14975.3087 | 954.6644 | 25597 | 0.62234 | All types of equipment - facility failure: Capacitor Bank Failure | N/A - Control | N/A - Control | N/A - Control | Existing | 2017 GRC | N/A | In Compliance | GO 95 | Capacitor banks in the distribution system, both overhead and pad-mounted, are tested and inspected annually; costs for capacitor maintenance and replacement are not tracked separately but are included in PG&E’s routine overhead maintenance program. As such, costs in the table show PG&E’s non-enhanced maintenance in Tier 2 and Tier 3 HFTS areas for all overhead equipment (Routine Distribution and Emergency)
| 2019 actual | 14175.0163 | 13153.0738 | 1021.9426 | 25597 | 0.55378 | All types of equipment - facility failure: Capacitor Bank Failure | N/A - Control | N/A - Control | N/A - Control | Existing | 2017 GRC | N/A | In Compliance | GO 95
| 2020 | 16742.2674 | 15412.0661 | 1330.2013 | 25597 | 0.65407 | All types of equipment - facility failure: Capacitor Bank Failure | N/A - Control | N/A - Control | N/A - Control | Existing | 2020 GRC | N/A | In Compliance | GO 95
| 2021 | 17160.8991 | 15797.3677 | 1363.5313 | 25597 | 0.67043 | All types of equipment - facility failure: Capacitor Bank Failure | N/A - Control | N/A - Control | N/A - Control | Existing | 2020 GRC | N/A | In Compliance | GO 95
| 2022 | 17589.9715 | 16192.3019 | 1397.6696 | 25597 | 0.68719 | All types of equipment - facility failure: Capacitor Bank Failure | N/A - Control | N/A - Control | N/A - Control | Existing | 2020 GRC | N/A | In Compliance | GO 95
| 2020-2022 plan total | 51493.138 | 47401.7357 | 4091.4022 | 25597 | 2.0117 | All types of equipment - facility failure: Capacitor Bank Failure | N/A - Control | N/A - Control | N/A - Control | N/A | N/A | N/A | N/A | N/A
2-1. Circuit breaker maintenance and installation to de-energize lines upon detecting a fault - Non Enhanced, Distribution Substation | 2019 plan | 6987.6413 | 5943.5025 | 1044.1388 | N/A | N/A | All types of equipment - facility failure: Circuit Breaker | N/A - Control | N/A - Control | N/A - Control | Existing | 2017 GRC | N/A | In Compliance | GO 174 | Line Miles = N/A as substation assets are not associated with circuit miles (Routine Distribution)
| 2019 actual | 4748.6515 | 3977.8736 | 770.7779 | N/A | N/A | All types of equipment - facility failure: Circuit Breaker | N/A - Control | N/A - Control | N/A - Control | Existing | 2017 GRC | N/A | In Compliance | GO 174
| 2020 | 4055.1912 | 2941.7484 | 1113.4428 | N/A | N/A | All types of equipment - facility failure: Circuit Breaker | N/A - Control | N/A - Control | N/A - Control | Existing | 2020 GRC | N/A | In Compliance | GO 174
| 2021 | 4156.571 | 3015.2921 | 1141.2789 | N/A | N/A | All types of equipment - facility failure: Circuit Breaker | N/A - Control | N/A - Control | N/A - Control | Existing | 2020 GRC | N/A | In Compliance | GO 174
| 2022 | 4260.4853 | 3090.6744 | 1169.8109 | N/A | N/A | All types of equipment - facility failure: Circuit Breaker | N/A - Control | N/A - Control | N/A - Control | Existing | 2020 GRC | N/A | In Compliance | GO 174
| 2020-2022 plan total | 12472.2474 | 9047.7148 | 3424.5326 | N/A | N/A | All types of equipment - facility failure: Circuit Breaker | N/A - Control | N/A - Control | N/A - Control | N/A | N/A | N/A | N/A | N/A
2-2. Circuit breaker maintenance and installation to de-energize lines upon detecting a fault - Non Enhanced, Transmission Substation | 2019 plan | 22469.0333 | 22469.0333 | 0 | N/A | N/A | All types of equipment - facility failure: Circuit Breaker | N/A - Control | N/A - Control | N/A - Control | Existing | Transmission Owner | N/A | N/A | N/A | Line Miles = N/A as substation assets are not associated with circuit miles (Routine Transmission)
| 2019 actual | 16335.2016 | 16335.2016 | 0 | N/A | N/A | All types of equipment - facility failure: Circuit Breaker | N/A - Control | N/A - Control | N/A - Control | Existing | Transmission Owner | N/A | N/A | N/A
| 2020 | 25850.3662 | 25850.3662 | 0 | N/A | N/A | All types of equipment - facility failure: Circuit Breaker | N/A - Control | N/A - Control | N/A - Control | Existing | Transmission Owner | N/A | N/A | N/A
| 2021 | 26496.6254 | 26496.6254 | 0 | N/A | N/A | All types of equipment - facility failure: Circuit Breaker | N/A - Control | N/A - Control | N/A - Control | Existing | Transmission Owner | N/A | N/A | N/A
| 2022 | 27159.041 | 27159.041 | 0 | N/A | N/A | All types of equipment - facility failure: Circuit Breaker | N/A - Control | N/A - Control | N/A - Control | Existing | Transmission Owner | N/A | N/A | N/A
| 2020-2022 plan total | 79506.0327 | 79506.0327 | 0 | N/A | N/A | All types of equipment - facility failure: Circuit Breaker | N/A - Control | N/A - Control | N/A - Control | N/A | N/A | N/A | N/A | N/A
2-3. Circuit breaker maintenance and installation to de-energize lines upon detecting a fault - Enhanced, Distribution Substation | 2019 plan | 0 | 0 | 0 | N/A | N/A | All types of equipment - facility failure: Circuit Breaker | N/A - Control | N/A - Control | N/A - Control | New | 2019 WMP | FRMMA/WMPMA | Exceeds | GO 174 | Line Miles = N/A as substation assets are not associated with circuit miles (WMP and Emergency)
| 2019 actual | 14666.5297 | 9476.6161 | 5189.9136 | N/A | N/A | All types of equipment - facility failure: Circuit Breaker | N/A - Control | N/A - Control | N/A - Control | New | 2019 WMP | FRMMA/WMPMA | Exceeds | GO 174
| 2020 | 3570.7895 | 3314.95 | 255.8395 | N/A | N/A | All types of equipment - facility failure: Circuit Breaker | N/A - Control | N/A - Control | N/A - Control | New | N/A | FRMMA | Exceeds | GO 174
| 2021 | 3660.0555 | 3397.82 | 262.2355 | N/A | N/A | All types of equipment - facility failure: Circuit Breaker | N/A - Control | N/A - Control | N/A - Control | New | N/A | FRMMA | Exceeds | GO 174
| 2022 | 3751.5614 | 3482.77 | 268.7914 | N/A | N/A | All types of equipment - facility failure: Circuit Breaker | N/A - Control | N/A - Control | N/A - Control | New | N/A | FRMMA | Exceeds | GO 174
| 2020-2022 plan total | 10982.4063 | 10195.54 | 786.8663 | N/A | N/A | All types of equipment - facility failure: Circuit Breaker | N/A - Control | N/A - Control | N/A - Control | N/A | N/A | N/A | N/A | N/A
2-4. Circuit breaker maintenance and installation to de-energize lines upon detecting a fault - Enhanced, Transmission Substation | 2019 plan | 0 | 0 | 0 | N/A | N/A | All types of equipment - facility failure: Circuit Breaker | N/A - Enhanced Control | N/A - Enhanced Control | N/A - Enhanced Control | New | Transmission Owner | N/A | N/A | N/A | Line Miles = N/A as substation assets are not associated with circuit miles (WMP and Emergency)
| 2019 actual | 4048.0529 | 1234.7655 | 2813.2874 | N/A | N/A | All types of equipment - facility failure: Circuit Breaker | N/A - Enhanced Control | N/A - Enhanced Control | N/A - Enhanced Control | New | Transmission Owner | N/A | N/A | N/A
| 2020 | 718.8525 | 524 | 194.8525 | N/A | N/A | All types of equipment - facility failure: Circuit Breaker | N/A - Enhanced Control | N/A - Enhanced Control | N/A - Enhanced Control | New | Transmission Owner | N/A | N/A | N/A
| 2021 | 736.9238 | 537.2 | 199.7238 | N/A | N/A | All types of equipment - facility failure: Circuit Breaker | N/A - Enhanced Control | N/A - Enhanced Control | N/A - Enhanced Control | New | Transmission Owner | N/A | N/A | N/A
| 2022 | 755.3169 | 550.6 | 204.7169 | N/A | N/A | All types of equipment - facility failure: Circuit Breaker | N/A - Enhanced Control | N/A - Enhanced Control | N/A - Enhanced Control | New | Transmission Owner | N/A | N/A | N/A
| 2020-2022 plan total | 2211.0931 | 1611.8 | 599.2931 | N/A | N/A | All types of equipment - facility failure: Circuit Breaker | N/A - Enhanced Control | N/A - Enhanced Control | N/A - Enhanced Control | N/A | N/A | N/A | N/A | N/A
3. Covered conductor installation | 2019 plan | See Table 23, 17-1. Updates to grid topology to minimize risk of ignition in HFTDs - System Hardening, Distribution
2019 actual
2020
2021
2022
2020-2022 plan total
4. Covered conductor maintenance | 2019 plan | See Table 23, 1-1, Capacitor maintenance and replacement program
2019 actual
2020
2021
2022
2020-2022 plan total
5. Crossarm maintenance, repair, and replacement | 2019 plan | Crossarm maintenance and repair is not a specific program. Crossarm maintenance and repairs are conducted in conjunction with transmission and distribution maintenance, patrols, inspections, and system hardening
2019 actual
2020
2021
2022
2020-2022 plan total
6. Distribution pole replacement and reinforcement, including with composite poles | 2019 plan | 255234 | 253721 | 1513 | 2559.7 | 99.7125 | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Voltage Regulator failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from object: Vehicle contact, Veg. contact, Animal contact, Balloon contact, 3rd party Contact other | N/A - Enhanced Control | N/A - Enhanced Control | N/A - Enhanced Control | Existing | 2017 GRC | N/A | Exceeds | GO 95 | Based on 10 year cycle (Routine Distribution)
| 2019 actual | 108544 | 107348 | 1196 | 2559.7 | 42.405 | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Voltage Regulator failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from object: Vehicle contact, Veg. contact, Animal contact, Balloon contact, 3rd party Contact other | N/A - Enhanced Control | N/A - Enhanced Control | N/A - Enhanced Control | Existing | 2017 GRC | N/A | Exceeds | GO 95
| 2020 | 212477 | 210914 | 1563 | 2559.7 | 83.0086 | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Voltage Regulator failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from object: Vehicle contact, Veg. contact, Animal contact, Balloon contact, 3rd party Contact other | N/A - Enhanced Control | N/A - Enhanced Control | N/A - Enhanced Control | Existing | 2020 GRC | N/A | Exceeds | GO 95
| 2021 | 217789 | 216187 | 1602 | 2559.7 | 85.0838 | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Voltage Regulator failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from object: Vehicle contact, Veg. contact, Animal contact, Balloon contact, 3rd party Contact other | N/A - Enhanced Control | N/A - Enhanced Control | N/A - Enhanced Control | Existing | 2020 GRC | N/A | Exceeds | GO 95
| 2022 | 223234 | 221592 | 1642 | 2559.7 | 87.211 | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Voltage Regulator failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from object: Vehicle contact, Veg. contact, Animal contact, Balloon contact, 3rd party Contact other | N/A - Enhanced Control | N/A - Enhanced Control | N/A - Enhanced Control | Existing | 2020 GRC | N/A | Exceeds | GO 95
| 2020-2022 plan total | 653500 | 648693 | 4807 | 7679.1 | 85.1011 | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Voltage Regulator failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from object: Vehicle contact, Veg. contact, Animal contact, Balloon contact, 3rd party Contact other | N/A - Enhanced Control | N/A - Enhanced Control | N/A - Enhanced Control | N/A | N/A | N/A | N/A | N/A
7. Expulsion fuse replacement | 2019 plan | 0 | 4318.9816 | 0 | 3656.7143 | 1.1811 | Contact from Object: Vehicle contact, Veg. contact, Animal contact, Balloon contact, 3rd party Contact other | See table 23, 17-1. Updates to grid topology to minimize risk of ignition in HFTDs - System Hardening , Distribution |  | N/A - Unable to identify drivers other than already identified | New | 2019 WMP | FRMMA / WMPMA | Exceeds | GO 95 | 7 year program (WMP)
| 2019 actual | 9130.3359 | 9130.3359 | 0 | 3656.7143 | 2.4969 | Contact from Object: Vehicle contact, Veg. contact, Animal contact, Balloon contact, 3rd party Contact other |  |  | N/A - Unable to identify drivers other than already identified | New | 2019 WMP | FRMMA / WMPMA | Exceeds | GO 95
| 2020 | 5423.125 | 5423.125 | 0 | 3656.7143 | 1.4831 | Contact from Object: Vehicle contact, Veg. contact, Animal contact, Balloon contact, 3rd party Contact other |  |  | N/A - Unable to identify drivers other than already identified | New | 2020 GRC | N/A | Exceeds | GO 95
| 2021 | 5558.7031 | 5558.7031 | 0 | 3656.7143 | 1.5201 | Contact from Object: Vehicle contact, Veg. contact, Animal contact, Balloon contact, 3rd party Contact other |  |  | N/A - Unable to identify drivers other than already identified | New | 2020 GRC | N/A | Exceeds | GO 95
| 2022 | 5697.6707 | 5697.6707 | 0 | 3656.7143 | 1.5581 | Contact from Object: Vehicle contact, Veg. contact, Animal contact, Balloon contact, 3rd party Contact other |  |  | N/A - Unable to identify drivers other than already identified | New | 2020 GRC | N/A | Exceeds | GO 95
| 2020-2022 plan total | 16679.4988 | 16679.4988 | 0 | 10970.1429 | 1.5204 | Contact from Object: Vehicle contact, Veg. contact, Animal contact, Balloon contact, 3rd party Contact other |  |  | N/A - Unable to identify drivers other than already identified | N/A | N/A | N/A | N/A | N/A
8-1. Grid topology improvements to mitigate or reduce PSPS events - PSPS Granular Sectionalizing, Distribution | 2019 plan | 4176.3943 | 4176.3943 | 0 | 5585.6393 | 0.7477 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2019 WMP | FRMMA / WMPMA | Exceeds | GO 95 | (WMP)
| 2019 actual | 49802.7468 | 49802.7468 | 0 | 1892.6546 | 26.3137 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2019 WMP | FRMMA / WMPMA | Exceeds | GO 95
| 2020 | 83390 | 83390 | 0 | 17010.8106 | 4.9022 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2020 GRC | N/A | Exceeds | GO 95
| 2021 | 14709.2266 | 14709.2266 | 0 | 3000.55 | 4.9022 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2020 GRC | N/A | Exceeds | GO 95
| 2022 | 0 | 0 | 0 | 0 | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A | 2020 GRC | N/A | Exceeds | GO 95
| 2020-2022 plan total | 98099.2266 | 98099.2266 | 0 | 20011.3607 | 4.9022 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A | N/A | N/A | N/A | N/A
8-2. Grid topology improvements to mitigate or reduce PSPS events - Transmission Sectionalizing, Substation | 2019 plan | 59725.5964 | 59725.5964 | 0 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | Transmission Owner | N/A | N/A | N/A | 54 SCADA switches were installed in T2 and T3 in 2019. However focus of the program was on reliability improvement. Focus for 2020 on mitigating PSPS impacts. Circuit miles treated is to be determined based on actual locations of switches installed. (WMP)
| 2019 actual | 42212.1697 | 42212.1697 | 0 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | Transmission Owner | N/A | N/A | N/A
| 2020 | 37183.6692 | 37183.6692 | 0 | TBD | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | Transmission Owner | N/A | N/A | N/A
| 2021 | 0 | 0 | 0 | TBD | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | Transmission Owner | N/A | N/A | N/A
| 2022 | 0 | 0 | 0 | TBD | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | Transmission Owner | N/A | N/A | N/A
| 2020-2022 plan total | 37183.6692 | 37183.6692 | 0 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A | N/A | N/A | N/A | N/A
8-3. Grid topology improvements to mitigate or reduce PSPS events - Microgrids / Resilience Zones, Distribution | 2019 plan | 10489.9629 | 10489.9629 | 0 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2019 WMP | FRMMA / WMPMA | Exceeds | GO 95 | Zones determined based on customers and other criteria rather than miles treated. Microgrid activities for PSPS mitigation are subject to the ongoing Track 1 of the Microgrid and Resilience Strategies Rulemaking (R.19-09-009) and other regulatory approval processes. The targeted units and spend associated with Microgrids for PSPS mitigation in this 2020 WMP are provided for informational purposes only and are subject to change, see additional detail on regulatory approvals and overlap discussed in the footnote in section 5.3.3.8 (WMP)
| 2019 actual | 3319.9938 | 3319.9938 | 0 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2019 WMP | FRMMA / WMPMA | Exceeds | GO 95
| 2020 | 11178 | 11178 | 0 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2020 GRC | N/A | Exceeds | GO 95
| 2021 | 12882.8716 | 12882.8716 | 0 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2020 GRC | N/A | Exceeds | GO 95
| 2022 | 15481.2 | 15481.2 | 0 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2020 GRC | N/A | Exceeds | GO 95
| 2020-2022 plan total | 39542.0716 | 39542.0716 | 0 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A | N/A | N/A | N/A | N/A
8-4. Grid topology improvements to mitigate or reduce PSPS events -Substation (PSPS), Distribution | 2019 plan | 0 | 0 | 0 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A | N/A | FRMMA | Exceeds | GO 95 | (WMP)
| 2019 actual | 0 | 0 | 0 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A | N/A | FRMMA | Exceeds | GO 95
| 2020 | 145769.2332 | 99000.0025 | 46769.2308 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | N/A | FRMMA | Exceeds | GO 95
| 2021 | 0 | 0 | 0 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | N/A | FRMMA | Exceeds | GO 95
| 2022 | 0 | 0 | 0 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | N/A | FRMMA | Exceeds | GO 95
| 2020-2022 plan total | 145769.2332 | 99000.0025 | 46769.2308 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A | N/A | N/A | N/A | N/A
8-5. Grid topology improvements to mitigate or reduce PSPS events - Remote Grid, Distribution | 2019 plan | 0 | 0 | 0 | N/A | N/A | N/A - Exploratory Project | N/A - Exploratory Project | N/A - Exploratory Project | N/A - Exploratory Project | New | N/A | FRMMA | Exceeds | GO 95 | (WMP)
| 2019 actual | 30.5914 | 0 | 30.5914 | N/A | N/A | N/A - Exploratory Project | N/A - Exploratory Project | N/A - Exploratory Project | N/A - Exploratory Project | New | N/A | FRMMA | Exceeds | GO 95
| 2020 | 943.3636 | 0 | 943.3636 | N/A | N/A | N/A - Exploratory Project | N/A - Exploratory Project | N/A - Exploratory Project | N/A - Exploratory Project | New | N/A | FRMMA | Exceeds | GO 95
| 2021 | 973.5293 | 0 | 973.5293 | N/A | N/A | N/A - Exploratory Project | N/A - Exploratory Project | N/A - Exploratory Project | N/A - Exploratory Project | New | N/A | FRMMA | Exceeds | GO 95
| 2022 | 1004.7005 | 0 | 1004.7005 | N/A | N/A | N/A - Exploratory Project | N/A - Exploratory Project | N/A - Exploratory Project | N/A - Exploratory Project | New | N/A | FRMMA | Exceeds | GO 95
| 2020-2022 plan total | 2921.5934 | 0 | 2921.5934 | N/A | N/A | N/A - Exploratory Project | N/A - Exploratory Project | N/A - Exploratory Project | N/A - Exploratory Project | N/A | N/A | N/A | N/A | N/A
8-6. Grid topology improvements to mitigate or reduce PSPS events - PSPS Control Only, Distribution and Transmission | 2019 plan | 12096.9036 | 12096.9036 | 0 | N/A | N/A | N/A - Control | N/A - Control | N/A - Control | N/A - Control | Existing | 2017 GRC, Transmission Owner | N/A | N/A | N/A | Line Miles = N/A as this activity supports PSPS and not a specific volume of line miles (Routine Distribution and Transmission)
| 2019 actual | 6361.7954 | 6361.7954 | 0 | N/A | N/A | N/A - Control | N/A - Control | N/A - Control | N/A - Control | Existing | 2017 GRC, Transmission Owner | N/A | N/A | N/A
| 2020 | 9945.5368 | 9945.5368 | 0 | N/A | N/A | N/A - Control | N/A - Control | N/A - Control | N/A - Control | Existing | 2020 GRC, Transmission Owner | N/A | N/A | N/A
| 2021 | 10194.1752 | 10194.1752 | 0 | N/A | N/A | N/A - Control | N/A - Control | N/A - Control | N/A - Control | Existing | 2020 GRC, Transmission Owner | N/A | N/A | N/A
| 2022 | 10449.0296 | 10449.0296 | 0 | N/A | N/A | N/A - Control | N/A - Control | N/A - Control | N/A - Control | Existing | 2020 GRC, Transmission Owner | N/A | N/A | N/A
| 2020-2022 plan total | 30588.7415 | 30588.7415 | 0 | N/A | N/A | N/A - Control | N/A - Control | N/A - Control | N/A - Control | N/A | N/A | N/A | N/A | N/A
9-1. Installation of system automation equipment - Expanded Automation, Distribution | 2019 plan | 15377.4724 | 15297.4724 | 80 | 20283 | 0.6782 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2019 WMP | FRMMA / WMPMA | Exceeds | GO 95 | Whole system will be complete in 2020, started in 2018 (WMP)
| 2019 actual | 7247.5145 | 7046.3614 | 201.1531 | 9968 | 0.036502 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2019 WMP | FRMMA / WMPMA | Exceeds | GO 95
| 2020 | 3906.9207 | 3780 | 126.9207 | 8162 | 0.15263 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2020 GRC | N/A | Exceeds | GO 95
| 2021 | 130.4231 | 0 | 130.4231 | 0 | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2020 GRC | N/A | Exceeds | GO 95
| 2022 | 133.9256 | 0 | 133.9256 | 0 | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2020 GRC | N/A | Exceeds | GO 95
| 2020-2022 plan total | 4171.2694 | 3780 | 391.2694 | 8162 | 0.16296 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A | N/A | N/A | N/A | N/A
9-2. Installation of system automation equipment - Fuse Saver, Distribution | 2019 plan | 1766.2201 | 1766.2201 | 0 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2019 WMP | FRMMA / WMPMA | Exceeds | GO 95 | Line miles is not an applicable metric (WMP)
| 2019 actual | 0 | 0 | 0 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2019 WMP | FRMMA / WMPMA | Exceeds | GO 95
| 2020 | 3486.665 | 3486.665 | 0 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2020 GRC | N/A | Exceeds | GO 95
| 2021 | 3990.7577 | 3990.7577 | 0 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2020 GRC | N/A | Exceeds | GO 95
| 2022 | 4030.544 | 4030.544 | 0 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2020 GRC | N/A | Exceeds | GO 95
| 2020-2022 plan total | 11507.9667 | 11507.9667 | 0 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A | N/A | N/A | N/A | N/A
9-3. Installation of system automation equipment - Installation of system automation equipment, Distribution and Distribution Substation | 2019 plan | 8276.9004 | 8276.9004 | 0 | N/A | N/A | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Voltage Regulator failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from object: Vehicle contact, Veg. contact, Animal contact, Balloon contact, 3rd party Contact other | N/A - Control | N/A - Control | N/A - Control | Existing | 2017 GRC | N/A | Exceeds | GO 95 | Line Miles = N/A as substation assets are not associated with circuit miles Other costs forecast in this section are for lifecycle replacements for distribution line automation (WMP and Routine Distribution)
| 2019 actual | 7608.9843 | 7608.9843 | 0 | N/A | N/A | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Voltage Regulator failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from object: Vehicle contact, Veg. contact, Animal contact, Balloon contact, 3rd party Contact other | N/A - Control | N/A - Control | N/A - Control | Existing | 2017 GRC | N/A | Exceeds | GO 95
| 2020 | 4087.2123 | 4087.2123 | 0 | N/A | N/A | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Voltage Regulator failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from object: Vehicle contact, Veg. contact, Animal contact, Balloon contact, 3rd party Contact other | N/A - Control | N/A - Control | N/A - Control | Existing | 2020 GRC | N/A | Exceeds | GO 95
| 2021 | 4189.3926 | 4189.3926 | 0 | N/A | N/A | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Voltage Regulator failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from object: Vehicle contact, Veg. contact, Animal contact, Balloon contact, 3rd party Contact other | N/A - Control | N/A - Control | N/A - Control | Existing | 2020 GRC | N/A | Exceeds | GO 95
| 2022 | 4294.1275 | 4294.1275 | 0 | N/A | N/A | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Voltage Regulator failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from object: Vehicle contact, Veg. contact, Animal contact, Balloon contact, 3rd party Contact other | N/A - Control | N/A - Control | N/A - Control | Existing | 2020 GRC | N/A | Exceeds | GO 95
| 2020-2022 plan total | 12570.7324 | 12570.7324 | 0 | N/A | N/A | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Voltage Regulator failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from object: Vehicle contact, Veg. contact, Animal contact, Balloon contact, 3rd party Contact other | N/A - Control | N/A - Control | N/A - Control | N/A | N/A | N/A | N/A | N/A
10. Maintenance, repair, and replacement of connectors, including hotline clamps | 2019 plan | There are no specific programs associated with connector replacement in distribution. All replacements are incorporated into Distribution System Hardening (discussed in Section 5.3.3.17) and distribution maintenance. For PG&E’s transmission lines, maintenance of connectors is generally performed as part of the overhead inspection program with repairs and/or replacement done as determined necessary during these inspections. Further details can be found in Section 5.3.4.
2019 actual
2020
2021
2022
2020-2022 plan total
11. Mitigation of impact on customers and other residents affected during PSPS event | 2019 plan | See Table 23, 8. Grid topology improvements to mitigate or reduce PSPS events
2019 actual
2020
2021
2022
2020-2022 plan total
12-1. Other corrective action - Distribution Substation | 2019 plan | 138.7704 | 138.7704 | 0 | N/A | N/A | Contact with object- Animal Contact, Contact from Object - Other | N/A - Control | N/A - Control | N/A - Control | Existing | 2017 GRC | N/A | N/A | N/A | Line Miles = N/A as substation assets are not associated with circuit miles (Routine Distribution)
| 2019 actual | 224.1976 | 224.1976 | 0 | N/A | N/A | Contact with object- Animal Contact, Contact from Object - Other | N/A - Control | N/A - Control | N/A - Control | Existing | 2017 GRC | N/A | N/A | N/A
| 2020 | 492.7234 | 492.7234 | 0 | N/A | N/A | Contact with object- Animal Contact, Contact from Object - Other | N/A - Control | N/A - Control | N/A - Control | Existing | 2020 GRC | N/A | N/A | N/A
| 2021 | 505.0415 | 505.0415 | 0 | N/A | N/A | Contact with object- Animal Contact, Contact from Object - Other | N/A - Control | N/A - Control | N/A - Control | Existing | 2020 GRC | N/A | N/A | N/A
| 2022 | 517.6676 | 517.6676 | 0 | N/A | N/A | Contact with object- Animal Contact, Contact from Object - Other | N/A - Control | N/A - Control | N/A - Control | Existing | 2020 GRC | N/A | N/A | N/A
| 2020-2022 plan total | 1515.4325 | 1515.4325 | 0 | N/A | N/A | Contact with object- Animal Contact, Contact from Object - Other | N/A - Control | N/A - Control | N/A - Control | N/A | N/A | N/A | N/A | N/A
12-2. Other corrective action - Transmission Substation | 2019 plan | 8292.2654 | 8292.2654 | 0 | N/A | N/A | Contact with object- Animal Contact, Contact from Object - Other | N/A - Control | N/A - Control | N/A - Control | Existing | Transmission Owner | N/A | N/A | N/A | Line Miles = N/A as substation assets are not associated with circuit miles (Routine Transmission)
| 2019 actual | 7114.2722 | 7114.2722 | 0 | N/A | N/A | Contact with object- Animal Contact, Contact from Object - Other | N/A - Control | N/A - Control | N/A - Control | Existing | Transmission Owner | N/A | N/A | N/A
| 2020 | 10629.578 | 10629.578 | 0 | N/A | N/A | Contact with object- Animal Contact, Contact from Object - Other | N/A - Control | N/A - Control | N/A - Control | Existing | Transmission Owner | N/A | N/A | N/A
| 2021 | 10895.3174 | 10895.3174 | 0 | N/A | N/A | Contact with object- Animal Contact, Contact from Object - Other | N/A - Control | N/A - Control | N/A - Control | Existing | Transmission Owner | N/A | N/A | N/A
| 2022 | 11167.7003 | 11167.7003 | 0 | N/A | N/A | Contact with object- Animal Contact, Contact from Object - Other | N/A - Control | N/A - Control | N/A - Control | Existing | Transmission Owner | N/A | N/A | N/A
| 2020-2022 plan total | 32692.5957 | 32692.5957 | 0 | N/A | N/A | Contact with object- Animal Contact, Contact from Object - Other | N/A - Control | N/A - Control | N/A - Control | N/A | N/A | N/A | N/A | N/A
12-3. Other corrective action - Non Enhanced Maintenance, Transmission | 2019 plan | 11297.4288 | 193270.2443 | 32282.844 | 5710 | 39.5014 | All types of equipment - facility failure: Crossarm failure | N/A - Control | N/A - Control | N/A - Control | Existing | Transmission Owner | N/A | In Compliance | GO95, GO165, FERC TPL Standards | (Routine Transmission)
| 2019 actual | 154893.5322 | 148742.5241 | 6151.0081 | 5710 | 27.1267 | All types of equipment - facility failure: Crossarm failure | N/A - Control | N/A - Control | N/A - Control | Existing | Transmission Owner | N/A | In Compliance | GO95, GO165, FERC TPL Standards
| 2020 | 169393.8491 | 158096.4203 | 11297.4288 | 2768.6667 | 61.1825 | All types of equipment - facility failure: Crossarm failure | N/A - Control | N/A - Control | N/A - Control | Existing | Transmission Owner | N/A | In Compliance | GO95, GO165, FERC TPL Standards
| 2021 | 173628.6953 | 162048.8308 | 11579.8645 | 2768.6667 | 62.712 | All types of equipment - facility failure: Crossarm failure | N/A - Control | N/A - Control | N/A - Control | Existing | Transmission Owner | N/A | In Compliance | GO95, GO165, FERC TPL Standards
| 2022 | 177969.4127 | 166100.0516 | 11869.3611 | 2768.6667 | 64.2798 | All types of equipment - facility failure: Crossarm failure | N/A - Control | N/A - Control | N/A - Control | Existing | Transmission Owner | N/A | In Compliance | GO95, GO165, FERC TPL Standards
| 2020-2022 plan total | 520991.9571 | 486245.3026 | 34746.6544 | 5710 | 91.242 | All types of equipment - facility failure: Crossarm failure | N/A - Control | N/A - Control | N/A - Control | N/A | N/A | N/A | N/A | N/A
12-4. Other corrective action - Distribution | 2019 plan | 322130.4067 | 244279 | 77851.4067 | 25597 | 12.5847 | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Voltage Regulator failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from object: Vehicle contact, Veg. contact, Animal contact, Balloon contact, 3rd party Contact other | N/A - Enhanced Control | N/A - Enhanced Control | N/A - Enhanced Control | Existing/New | 2017 GRC, 2019 WMP | FRMMA/ WMPMA | Exceeds | GO 95 | Assume that these remediations are tags / notifications resulting from inspections based on the new inspection cycle of 100% T3 and 33% T2 going forward. For 2019 assumes 100% of Tiers 2&3 based on WSIP (WMP and Emergency)
| 2019 actual | 167440.5055 | 122576.7584 | 44863.7471 | 25597 | 6.5414 | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Voltage Regulator failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from object: Vehicle contact, Veg. contact, Animal contact, Balloon contact, 3rd party Contact other | N/A - Enhanced Control | N/A - Enhanced Control | N/A - Enhanced Control | Existing/New | 2017 GRC, 2019 WMP | FRMMA/ WMPMA | Exceeds | GO 95
| 2020 | 199749.3394 | 173375.2776 | 26374.0618 | 13265.6667 | 15.0576 | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Voltage Regulator failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from object: Vehicle contact, Veg. contact, Animal contact, Balloon contact, 3rd party Contact other | N/A - Enhanced Control | N/A - Enhanced Control | N/A - Enhanced Control | Existing/New | N/A | FRMMA/ WMPMA | Exceeds | GO 95
| 2021 | 204742.9229 | 177709.5095 | 27033.4134 | 13265.6667 | 15.434 | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Voltage Regulator failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from object: Vehicle contact, Veg. contact, Animal contact, Balloon contact, 3rd party Contact other | N/A - Enhanced Control | N/A - Enhanced Control | N/A - Enhanced Control | Existing/New | N/A | FRMMA/ WMPMA | Exceeds | GO 95
| 2022 | 209861.1709 | 182151.9223 | 27709.2487 | 13265.6667 | 15.8199 | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Voltage Regulator failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from object: Vehicle contact, Veg. contact, Animal contact, Balloon contact, 3rd party Contact other | N/A - Enhanced Control | N/A - Enhanced Control | N/A - Enhanced Control | Existing/New | N/A | FRMMA/ WMPMA | Exceeds | GO 95
| 2020-2022 plan total | 981209.1917 | 900092.4678 | 81116.7238 | 25597 | 38.333 | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Voltage Regulator failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from object: Vehicle contact, Veg. contact, Animal contact, Balloon contact, 3rd party Contact other | N/A - Enhanced Control | N/A - Enhanced Control | N/A - Enhanced Control | N/A | N/A | N/A | N/A | N/A
13. Pole loading infrastructure hardening and replacement program based on pole loading assessment program | 2019 plan | 0 | 0 | 0 | 0 | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | N/A | FRMMA | Exceeds | GO 95 | Whole distribution system, Wind Loading Project (WMP)
| 2019 actual | 3872.3103 | 3644.2305 | 228.0798 | 25597 | 0.15128 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | N/A | FRMMA | Exceeds | GO 95
| 2020 | 3405.0597 | 2575.5392 | 829.5205 | 25597 | 0.13303 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | N/A | FRMMA | Exceeds | GO 95
| 2021 | 149.1 | 0 | 149.1 | 0 | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | N/A | FRMMA | Exceeds | GO 95
| 2022 | 153.874 | 0 | 153.874 | 0 | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | N/A | FRMMA | Exceeds | GO 95
| 2020-2022 plan total | 3708.0337 | 2575.5392 | 1132.4945 | 25597 | 0.14486 | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A | N/A | N/A | N/A | N/A
14. Transformers maintenance and replacement | 2019 plan | See Table 23, 6-1. Distribution pole replacement and reinforcement, including with composite poles
2019 actual
2020
2021
2022
2020-2022 plan total
15. Transmission tower maintenance and replacement | 2019 plan | 443970.0927 | 333000.0005 | 110970.0921 | 5710 | 77.7531 | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Voltage Regulator failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other | N/A - Enhanced Control | N/A - Enhanced Control | N/A - Enhanced Control | New | Transmission Owner | N/A | Exceeds | GO95, GO165 | Inspected 100% of HFTD in 2019 during WSIP; for 2020 and beyond, 100% T3 and 33% T2 based on new inspection cycle (WMP)
| 2019 actual | 750405.1175 | 254710.4605 | 495694.657 | 5710 | 131.4195 | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Voltage Regulator failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other | N/A - Enhanced Control | N/A - Enhanced Control | N/A - Enhanced Control | New | Transmission Owner | N/A | Exceeds | GO95, GO165
| 2020 | 297284.7385 | 230681.758 | 66602.9805 | 2768.6667 | 107.3747 | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Voltage Regulator failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other | N/A - Enhanced Control | N/A - Enhanced Control | N/A - Enhanced Control | New | Transmission Owner | N/A | Exceeds | GO95, GO165
| 2021 | 304716.857 | 236448.802 | 68268.055 | 2768.6667 | 110.0591 | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Voltage Regulator failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other | N/A - Enhanced Control | N/A - Enhanced Control | N/A - Enhanced Control | New | Transmission Owner | N/A | Exceeds | GO95, GO165
| 2022 | 312334.7784 | 242360.022 | 69974.7564 | 2768.6667 | 112.8105 | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Voltage Regulator failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other | N/A - Enhanced Control | N/A - Enhanced Control | N/A - Enhanced Control | New | Transmission Owner | N/A | Exceeds | GO95, GO165
| 2020-2022 plan total | 914336.374 | 709490.5821 | 204845.7919 | 5710 | 160.129 | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Voltage Regulator failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other | N/A - Enhanced Control | N/A - Enhanced Control | N/A - Enhanced Control | N/A | N/A | N/A | N/A | N/A
16. Undergrounding of electric lines and/or equipment | 2019 plan | See Table 23, 17-1. Updates to grid topology to minimize risk of ignition in HFTDs - System Hardening , Distribution
2019 actual
2020
2021
2022
2020-2022 plan total
17-1. Updates to grid topology to minimize risk of ignition in HFTDs - System Hardening, Distribution | 2019 plan | 228763.5072 | 228763.5072 | 0 | 171 | 1337.7983 | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Lightning Arrestor, Pole failure, Transformer failure, Switch failure, Guy - Span wire failure, Sectionalizer failure, Recloser failure Contact from Object: Vehicle contact, Veg. contact, Animal contact, Balloon contact, 3rd party Contact other | 810.5 | 3.54 | All types of equipment - facility failure: Insulator failure, Equipment failure - Other | New | 2019 WMP | FRMMA / WMPMA | Exceeds | GO 95 | (WMP)
| 2019 actual | 287429.2652 | 287429.2652 | 0 | 150 | 1916.1951 | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Lightning Arrestor, Pole failure, Transformer failure, Switch failure, Guy - Span wire failure, Sectionalizer failure, Recloser failure Contact from Object: Vehicle contact, Veg. contact, Animal contact, Balloon contact, 3rd party Contact other | 927.33 | 3.23 | All types of equipment - facility failure: Insulator failure, Equipment failure - Other | New | 2019 WMP | FRMMA / WMPMA | Exceeds | GO 95
| 2020 | 366724.6389 | 366724.6389 | 0 | 241 | 1521.679 | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Lightning Arrestor, Pole failure, Transformer failure, Switch failure, Guy - Span wire failure, Sectionalizer failure, Recloser failure Contact from Object: Vehicle contact, Veg. contact, Animal contact, Balloon contact, 3rd party Contact other | 1309.97 | 3.83 | All types of equipment - facility failure: Insulator failure, Equipment failure - Other | New | 2020 GRC | N/A | Exceeds | GO 95
| 2021 | 565640 | 565640 | 0 | 377 | 1500.3714 | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Lightning Arrestor, Pole failure, Transformer failure, Switch failure, Guy - Span wire failure, Sectionalizer failure, Recloser failure Contact from Object: Vehicle contact, Veg. contact, Animal contact, Balloon contact, 3rd party Contact other | 2053.02 | 4.16 | All types of equipment - facility failure: Insulator failure, Equipment failure - Other | New | 2020 GRC | N/A | Exceeds | GO 95
| 2022 | 698360 | 698360 | 0 | 442 | 1580 | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Lightning Arrestor, Pole failure, Transformer failure, Switch failure, Guy - Span wire failure, Sectionalizer failure, Recloser failure Contact from Object: Vehicle contact, Veg. contact, Animal contact, Balloon contact, 3rd party Contact other | 2427.95 | 4.27 | All types of equipment - facility failure: Insulator failure, Equipment failure - Other | New | 2020 GRC | N/A | Exceeds | GO 95
| 2020-2022 plan total | 1630724.6389 | 1630724.6389 | 0 | 1060 | 1538.4195 | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Lightning Arrestor, Pole failure, Transformer failure, Switch failure, Guy - Span wire failure, Sectionalizer failure, Recloser failure Contact from Object: Vehicle contact, Veg. contact, Animal contact, Balloon contact, 3rd party Contact other | 5790.95 | 4.12 | All types of equipment - facility failure: Insulator failure, Equipment failure - Other | N/A | N/A | N/A | N/A | N/A
17-2. Updates to grid topology to minimize risk of ignition in HFTDs - Surge Arrestor, Distribution | 2019 plan | 71610.2449 | 71610.2449 | 0 | N/A | N/A | All types of equipment - facility failure: Lightning Arrestor | 63.45 | 0.89 | N/A - All drivers are represented in the 'drivers targeted' | New | 2019 WMP | FRMMA / WMPMA | Exceeds | GO 95
| 2019 actual | 21767.3506 | 21767.3506 | 0 | N/A | N/A | All types of equipment - facility failure: Lightning Arrestor | 15.25 | 0.7 | N/A - All drivers are represented in the 'drivers targeted' | New | 2019 WMP | FRMMA / WMPMA | Exceeds | GO 95
| 2020 | 62448.245 | 62448.245 | 0 | N/A | N/A | All types of equipment - facility failure: Lightning Arrestor | 46.69 | 0.8 | N/A - All drivers are represented in the 'drivers targeted' | New | 2020 GRC | N/A | Exceeds | GO 95
| 2021 | 53289.837 | 53289.837 | 0 | N/A | N/A | All types of equipment - facility failure: Lightning Arrestor | 40.05 | 0.86 | N/A - All drivers are represented in the 'drivers targeted' | New | 2020 GRC | N/A | Exceeds | GO 95
| 2022 | 0 | 0 | 0 | N/A | N/A | All types of equipment - facility failure: Lightning Arrestor | 0 | 0 | N/A - All drivers are represented in the 'drivers targeted' | New | 2020 GRC | N/A | Exceeds | GO 95
| 2020-2022 plan total | 115738.082 | 115738.082 | 0 | N/A | N/A | All types of equipment - facility failure: Lightning Arrestor | 86.74 | 0.83 | N/A - All drivers are represented in the 'drivers targeted' | N/A | N/A | N/A | N/A | N/A
17-3. Updates to grid topology to minimize risk of ignition in HFTDs - EPIC - Rapid Earth Current Fault Limiter, Distribution | 2019 plan | 7002.997 | 0 | 7002.997 | N/A | N/A | N/A - Exploratory Project | N/A - Exploratory Project | N/A - Exploratory Project | N/A - Exploratory Project | Existing | EPIC | N/A | N/A | N/A | Line miles is not an applicable metric (WMP)
| 2019 actual | 1835.4004 | 0 | 1835.4004 | N/A | N/A | N/A - Exploratory Project | N/A - Exploratory Project | N/A - Exploratory Project | N/A - Exploratory Project | Existing | EPIC | N/A | N/A | N/A
| 2020 | 5022.99 | 0 | 5022.99 | N/A | N/A | N/A - Exploratory Project | N/A - Exploratory Project | N/A - Exploratory Project | N/A - Exploratory Project | Existing | EPIC | N/A | N/A | N/A
| 2021 | 9461.7 | 9461.7 | 0 | N/A | N/A | N/A - Exploratory Project | N/A - Exploratory Project | N/A - Exploratory Project | N/A - Exploratory Project | Existing | EPIC | N/A | N/A | N/A
| 2022 | 9711 | 9711 | 0 | N/A | N/A | N/A - Exploratory Project | N/A - Exploratory Project | N/A - Exploratory Project | N/A - Exploratory Project | Existing | EPIC | N/A | N/A | N/A
| 2020-2022 plan total | 24195.69 | 19172.7 | 5022.99 | N/A | N/A | N/A - Exploratory Project | N/A - Exploratory Project | N/A - Exploratory Project | N/A - Exploratory Project | N/A | N/A | N/A | N/A | N/A
18 Other/not listed, Building and Sourcing Services- Transmission and Distribution | 2019 plan | 0 | 0 | 0 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | N/A | FRMMA / WMPMA | N/A | N/A | These costs support Grid Design and System Hardening but may also support other WMP initiatives (WMP)
| 2019 actual | 6900 | 6500 | 400 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | Transmission Owner | FRMMA / WMPMA | N/A | N/A
| 2020 | 13023.1618 | 10270 | 2753.1618 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | Transmission Owner | FRMMA | N/A | N/A
| 2021 | 10846.9881 | 5279 | 5567.9881 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | Transmission Owner | FRMMA | N/A | N/A
| 2022 | 11171.0233 | 5432 | 5739.0233 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | Transmission Owner | FRMMA | N/A | N/A
| 2020-2022 plan total | 35041.1733 | 20981 | 14060.1733 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A | N/A | N/A | N/A | N/A

## Table 24
Table 24: Asset management and inspections
Initiative activity | Year | Total per-initiative spend ($1000's) | Subtotal A: Capital expenditure ($1000's) | Subtotal B: Operating expenses ($1000's) | Line miles to be treated | Spend ($1000's)/ treated line mile | Ignition probability drivers targeted | Risk reduction | Risk-spend efficiency | Other risk drivers addressed | Existing/ new | Existing: What proceeding has reviewed program | If new: Memorandum account | In / exceeding compliance with regulations | Cite associated rule | Comments
1. Detailed inspections of distribution electric lines and equipment | 2019 plan | 99969 | 0 | 99969 | 25597 | 3.9055 | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Voltage Regulator failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from object: Veg.contact | N/A - Control | N/A - Control | N/A - Control | Existing / New | 2017 GRC, 2019 WMP | FRMMA / WMPMA (partial) | Exceeds | GO 165 | 100% for 2019 based on WSIP and 100% T3 and 33% T2 based on new inspection cycle (WMP and Routine Distribution)
| 2019 actual | 152415 | 0 | 152415 | 25597 | 5.9544 | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Voltage Regulator failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from object: Veg.contact | N/A - Control | N/A - Control | N/A - Control | Existing / New | 2017 GRC, 2019 WMP | FRMMA / WMPMA (partial) | Exceeds | GO 165
| 2020 | 88717.4077 | 0 | 88717.4077 | 13265.6667 | 6.6877 | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Voltage Regulator failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from object: Veg.contact | N/A - Control | N/A - Control | N/A - Control | Existing / New | 2020 GRC (partial) | FRMMA (partial) | Exceeds | GO 165
| 2021 | 90935.3429 | 0 | 90935.3429 | 13265.6667 | 6.8549 | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Voltage Regulator failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from object: Veg.contact | N/A - Control | N/A - Control | N/A - Control | Existing / New | 2020 GRC (partial) | FRMMA (partial) | Exceeds | GO 165
| 2022 | 93208.7265 | 0 | 93208.7265 | 13265.6667 | 7.0263 | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Voltage Regulator failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from object: Veg.contact | N/A - Control | N/A - Control | N/A - Control | Existing / New | 2020 GRC (partial) | FRMMA (partial) | Exceeds | GO 165
| 2020-2022 plan total | 272861.4771 | 0 | 272861.4771 | 25597 | 10.6599 | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Voltage Regulator failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from object: Veg.contact | N/A - Control | N/A - Control | N/A - Control | N/A | N/A | N/A | N/A | N/A
2. Detailed inspections of transmission electric lines and equipment | 2019 plan | 55663 | 0 | 55663 | 5710 | 9.7483 | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Voltage Regulator failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from object: Veg.contact | N/A - Control | N/A - Control | N/A - Control | Existing / New | Transmission Owner | N/A | In Compliance | GO95, GO165 | 100% for 2019 based on WSIP and 100% T3 and 33% T2 based on new inspection cycle (WMP and Routine Transmission)
| 2019 actual | 54834 | 0 | 54833 | 5710 | 9.6032 | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Voltage Regulator failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from object: Veg.contact | N/A - Control | N/A - Control | N/A - Control | Existing / New | Transmission Owner | N/A | In Compliance | GO95, GO165
| 2020 | 55383.415 | 0 | 55383.415 | 2768.6667 | 20.0036 | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Voltage Regulator failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from object: Veg.contact | N/A - Control | N/A - Control | N/A - Control | Existing / New | Transmission Owner | N/A | In Compliance | GO95, GO165
| 2021 | 56768.0003 | 0 | 56768.0003 | 2768.6667 | 20.5037 | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Voltage Regulator failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from object: Veg.contact | N/A - Control | N/A - Control | N/A - Control | Existing / New | Transmission Owner | N/A | In Compliance | GO95, GO165
| 2022 | 58187.2003 | 0 | 58187.2003 | 2768.6667 | 21.0163 | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Voltage Regulator failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from object: Veg.contact | N/A - Control | N/A - Control | N/A - Control | Existing / New | Transmission Owner | N/A | In Compliance | GO95, GO165
| 2020-2022 plan total | 170338.6156 | 0 | 170338.6156 | 5710 | 29.8316 | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Voltage Regulator failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from object: Veg.contact | N/A - Control | N/A - Control | N/A - Control | N/A | N/A | N/A | N/A | N/A
3. Improvement of inspections | 2019 plan | See Table 24, 1. Detailed inspections of distribution electric lines and equipment
2019 actual
2020
2021
2022
2020-2022 plan total
4. Infrared inspections of distribution electric lines and equipment | 2019 plan | 722.4246 | 0 | 722.4246 | N/A | N/A | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | Existing | 2017 GRC | N/A | Exceeds | GO 165 | Line Miles are N/A as, going forward, infrared inspections will be deployed as appropriate alongside the suite of other inspection tools and techniques include enhanced visual inspections, drones or helicopters and other emerging technologies. PG&E does not have a discrete plan for how many circuit miles will be inspected using IR systems in HFTD areas. (Routine Distribution)
| 2019 actual | 609.4421 | 0 | 609.4421 | N/A | N/A | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | Existing | 2017 GRC | N/A | Exceeds | GO 165
| 2020 | 696.5408 | 0 | 696.5408 | N/A | N/A | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | Existing | 2020 GRC | N/A | Exceeds | GO 165
| 2021 | 713.9543 | 0 | 713.9543 | N/A | N/A | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | Existing | 2020 GRC | N/A | Exceeds | GO 165
| 2022 | 731.8032 | 0 | 731.8032 | N/A | N/A | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | Existing | 2020 GRC | N/A | Exceeds | GO 165
| 2020-2022 plan total | 2142.2982 | 0 | 2142.2982 | N/A | N/A | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | N/A | N/A | N/A | N/A | N/A
5. Infrared inspections of transmission electric lines and equipment | 2019 plan | 259.6476 | 0 | 259.6476 | N/A | N/A | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | Existing | Transmission Owner | N/A | In Compliance | GO95, GO165 | Line Miles are N/A as, going forward, infrared inspections will be deployed as appropriate alongside the suite of other inspection tools and techniques include enhanced visual inspections, drones or helicopters and other emerging technologies. PG&E does not have a discrete plan for how many circuit miles will be inspected using IR systems in HFTD areas. (Routine Transmission)
| 2019 actual | 139.8964 | 0 | 139.8964 | N/A | N/A | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | Existing | Transmission Owner | N/A | In Compliance | GO95, GO165
| 2020 | 236.0867 | 0 | 236.0867 | N/A | N/A | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | Existing | Transmission Owner | N/A | In Compliance | GO95, GO165
| 2021 | 241.9888 | 0 | 241.9888 | N/A | N/A | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | Existing | Transmission Owner | N/A | In Compliance | GO95, GO165
| 2022 | 248.0385 | 0 | 248.0385 | N/A | N/A | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | Existing | Transmission Owner | N/A | In Compliance | GO95, GO165
| 2020-2022 plan total | 726.114 | 0 | 726.114 | N/A | N/A | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | N/A | N/A | N/A | N/A | N/A
6. Intrusive pole inspections | 2019 plan | 3860.2445 | 0 | 3860.2445 | 2559.7 | 1.5081 | All types of equipment - facility failure: Pole failure Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | Existing | 2017 GRC | N/A | Exceeds | GO 165 & GO 95 rule 44.3 | Based on a ten year cycle (Routine Distribution)
| 2019 actual | 5410.0156 | 0 | 5410.0156 | 2559.7 | 2.1135 | All types of equipment - facility failure: Pole failure Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | Existing | 2017 GRC | N/A | Exceeds | GO 165 & GO 95 rule 44.3
| 2020 | 4629.7311 | 0 | 4629.7311 | 2559.7 | 1.8087 | All types of equipment - facility failure: Pole failure Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | Existing | 2020 GRC | N/A | Exceeds | GO 165 & GO 95 rule 44.3
| 2021 | 4745.4743 | 0 | 4745.4743 | 2559.7 | 1.8539 | All types of equipment - facility failure: Pole failure Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | Existing | 2020 GRC | N/A | Exceeds | GO 165 & GO 95 rule 44.3
| 2022 | 4864.1112 | 0 | 4864.1112 | 2559.7 | 1.9003 | All types of equipment - facility failure: Pole failure Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | Existing | 2020 GRC | N/A | Exceeds | GO 165 & GO 95 rule 44.3
| 2020-2022 plan total | 14239.3166 | 0 | 14239.3166 | 7679.1 | 1.8543 | All types of equipment - facility failure: Pole failure Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | N/A | N/A | N/A | N/A | N/A
7. LiDAR inspections of distribution electric lines and equipment | 2019 plan | See table 25, 9. Other discretionary inspection of vegetation around distribution electric lines and equipment, beyond inspections mandated by rules and regulations
2019 actual
2020
2021
2022
2020-2022 plan total
8. LiDAR inspections of transmission electric lines and equipment | 2019 plan | See table 25, 8. LiDAR inspections of vegetation around transmission electric lines and equipment
2019 actual
2020
2021
2022
2020-2022 plan total
9. Other discretionary inspection of distribution electric lines and equipment, beyond inspections mandated by rules and regulations - Distribution Substation | 2019 plan | N/A - See Table 24, 1. Detailed inspections of distribution electric lines and equipment
2019 actual
2020
2021
2022
2020-2022 plan total
10. Other discretionary inspection of transmission electric lines and equipment, beyond inspections mandated by rules and regulations - Transmission Substation | 2019 plan | N/A See Table 24, 2. Detailed inspections of transmission electric lines and equipment
2019 actual
2020
2021
2022
2020-2022 plan total
11. Patrol inspections of distribution electric lines and equipment | 2019 plan | 0 | 0 | 0 | 0 | N/A | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | Existing | 2017 GRC | N/A | In Compliance | GO 165 | Patrols completed for HFTD assets not covered by detailed overhead inspections. For 2019 actual, since all assets were detail inspected, no routine patrols were executed; For 2020-2022 plan to patrol 2/3 of Tier 2 line miles each year. (Routine Distribution)
| 2019 actual | 0 | 0 | 0 | 0 | N/A | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | Existing | 2017 GRC | N/A | In Compliance | GO 165
| 2020 | 2259 | 0 | 2259 | 12221 | 0.18485 | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | Existing | 2020 GRC | N/A | In Compliance | GO 165
| 2021 | 2315 | 0 | 2315 | 12221 | 0.18943 | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | Existing | 2020 GRC | N/A | In Compliance | GO 165
| 2022 | 2373 | 0 | 2373 | 12221 | 0.19417 | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | Existing | 2020 GRC | N/A | In Compliance | GO 165
| 2020-2022 plan total | 6947 | 0 | 6947 | 18332 | 0.37895 | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | N/A | N/A | N/A | N/A | N/A
12. Patrol inspections of transmission electric lines and equipment | 2019 plan | 0 | 0 | 0 | 0 | N/A | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | Existing | Transmission Owner | N/A | In Compliance | GO95, GO165 | The costs in this section are for transmission patrols for facilities that cannot be patrolled by air; other transmission patrols are included in Table 24, 2. Detailed inspections of transmission electric lines and equipment. For 2019 all Tier 2 and Tier 3 were inspected, no patrols were conducted. For 2020-2022 plan to patrol 2/3 of Tier 2 line miles each year. (Routine Transmission)
| 2019 actual | 0 | 0 | 0 | 0 | N/A | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | Existing | Transmission Owner | N/A | In Compliance | GO95, GO166
| 2020 | 60.55 | 0 | 60.55 | 2915 | 0.020772 | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | Existing | Transmission Owner | N/A | In Compliance | GO95, GO167
| 2021 | 62.064 | 0 | 62.064 | 2915 | 0.021291 | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | Existing | Transmission Owner | N/A | In Compliance | GO95, GO168
| 2022 | 63.616 | 0 | 63.616 | 2915 | 0.021824 | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | Existing | Transmission Owner | N/A | In Compliance | GO95, GO169
| 2020-2022 plan total | 186.23 | 0 | 186.23 | 4373 | 0.042586 | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | N/A | N/A | N/A | N/A | N/A
13. Pole loading assessment program to determine safety factor | 2019 plan | See Table 23, 6-1. Distribution pole replacement and reinforcement, including with composite poles
2019 actual
2020
2021
2022
2020-2022 plan total
14. Quality assurance / quality control of inspections | 2019 plan | See Table 24, 1. Detailed inspections of distribution electric lines and equipment and 2. Detailed inspections of transmission electric lines and equipment
2019 actual
2020
2021
2022
2020-2022 plan total
15-1 Substation inspections - Transmission Substation | 2019 plan | 0 | 0 | 0 | N/A | N/A | All types of equipment - facility failure: Conductor failure -all, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Voltage Regulator failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from Object: Vehicle contact, Veg. contact, Animal contact, Balloon contact | N/A - Control | N/A - Control | N/A - Control | New | Transmission Owner | N/A | Exceeds | GO 174, CAISO TCA (Transmission Control Agreement) | Line Miles = N/A as substation assets are not associated with circuit miles (WMP)
| 2019 actual | 13495 | 0 | 13495 | N/A | N/A | All types of equipment - facility failure: Conductor failure -all, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Voltage Regulator failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from Object: Vehicle contact, Veg. contact, Animal contact, Balloon contact | N/A - Control | N/A - Control | N/A - Control | New | Transmission Owner | N/A | Exceeds | GO 174, CAISO TCA (Transmission Control Agreement)
| 2020 | 7273.6247 | 0 | 7273.6247 | N/A | N/A | All types of equipment - facility failure: Conductor failure -all, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Voltage Regulator failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from Object: Vehicle contact, Veg. contact, Animal contact, Balloon contact | N/A - Control | N/A - Control | N/A - Control | New | Transmission Owner | N/A | Exceeds | GO 174, CAISO TCA (Transmission Control Agreement)
| 2021 | 7455.4654 | 0 | 7455.4654 | N/A | N/A | All types of equipment - facility failure: Conductor failure -all, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Voltage Regulator failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from Object: Vehicle contact, Veg. contact, Animal contact, Balloon contact | N/A - Control | N/A - Control | N/A - Control | New | Transmission Owner | N/A | Exceeds | GO 174, CAISO TCA (Transmission Control Agreement)
| 2022 | 7641.852 | 0 | 7641.852 | N/A | N/A | All types of equipment - facility failure: Conductor failure -all, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Voltage Regulator failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from Object: Vehicle contact, Veg. contact, Animal contact, Balloon contact | N/A - Control | N/A - Control | N/A - Control | New | Transmission Owner | N/A | Exceeds | GO 174, CAISO TCA (Transmission Control Agreement)
| 2020-2022 plan total | 22370.9421 | 0 | 22370.9421 | N/A | N/A | All types of equipment - facility failure: Conductor failure -all, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Voltage Regulator failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from Object: Vehicle contact, Veg. contact, Animal contact, Balloon contact | N/A - Control | N/A - Control | N/A - Control | N/A | N/A | N/A | N/A | N/A
15-2 Substation inspections - Distribution Substation | 2019 plan | 0 | 0 | 0 | N/A | N/A | All types of equipment - facility failure: Conductor failure -all, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Voltage Regulator failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from Object: Vehicle contact, Veg. contact, Animal contact, Balloon contact | N/A - Control | N/A - Control | N/A - Control | New | 2019 WMP | FRMMA / WMPMA | Exceeds | GO 174 | Line Miles = N/A as substation assets are not associated with circuit miles (WMP)
| 2019 actual | 8148 | 0 | 8148 | N/A | N/A | All types of equipment - facility failure: Conductor failure -all, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Voltage Regulator failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from Object: Vehicle contact, Veg. contact, Animal contact, Balloon contact | N/A - Control | N/A - Control | N/A - Control | New | 2019 WMP | FRMMA / WMPMA | Exceeds | GO 174
| 2020 | 2878.8513 | 0 | 2878.8513 | N/A | N/A | All types of equipment - facility failure: Conductor failure -all, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Voltage Regulator failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from Object: Vehicle contact, Veg. contact, Animal contact, Balloon contact | N/A - Control | N/A - Control | N/A - Control | New | N/A | FRMMA / WMPMA | Exceeds | GO 174
| 2021 | 2950.8225 | 0 | 2950.8225 | N/A | N/A | All types of equipment - facility failure: Conductor failure -all, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Voltage Regulator failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from Object: Vehicle contact, Veg. contact, Animal contact, Balloon contact | N/A - Control | N/A - Control | N/A - Control | New | N/A | FRMMA / WMPMA | Exceeds | GO 174
| 2022 | 3024.5931 | 0 | 3024.5931 | N/A | N/A | All types of equipment - facility failure: Conductor failure -all, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Voltage Regulator failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from Object: Vehicle contact, Veg. contact, Animal contact, Balloon contact | N/A - Control | N/A - Control | N/A - Control | New | N/A | FRMMA / WMPMA | Exceeds | GO 174
| 2020-2022 plan total | 8854.2669 | 0 | 8854.2669 | N/A | N/A | All types of equipment - facility failure: Conductor failure -all, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Voltage Regulator failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from Object: Vehicle contact, Veg. contact, Animal contact, Balloon contact | N/A - Control | N/A - Control | N/A - Control | N/A | N/A | N/A | N/A | N/A

## Table 25
Table 25: Vegetation management and inspections
Initiative activity | Year | Total per-initiative spend ($1000's) | Subtotal A: Capital expenditure ($1000's) | Subtotal B: Operating expenses ($1000's) | Line miles to be treated | Spend ($1000's)/ treated line mile | Ignition probability drivers targeted | Risk reduction | Risk-spend efficiency | Other risk drivers addressed | Existing/ new | Existing: What proceeding has reviewed program | If new: Memorandum account | In / exceeding compliance with regulations | Cite associated rule | Comments
1. Additional efforts to manage community and environmental impacts | 2019 plan | See Table 25, 2. Detailed inspections of vegetation around distribution electric lines and equipment
2019 actual
2020
2021
2022
2020-2022 plan total
2. Detailed inspections of vegetation around distribution electric lines and equipment | 2019 plan | 65886.12 | 0 | 65886.12 | 25597 | 2.574 | Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | Existing | 2017 GRC | N/A | In Compliance | GO 95 Rule 35, and PRC 4293 | Initiative captures all routine distribution vegetation management in T2/T3 areas (Routine Distribution)
| 2019 actual | 113565.5024 | 0 | 113565.5024 | 25597 | 4.4367 | Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | Existing | 2017 GRC | N/A | In Compliance | GO 95 Rule 35, and PRC 4293
| 2020 | 178168.836 | 0 | 178168.836 | 25597 | 6.9605 | Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | Existing | 2020 GRC | N/A | In Compliance | GO 95 Rule 35, and PRC 4293
| 2021 | 183514.044 | 0 | 183514.044 | 25597 | 7.1694 | Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | Existing | 2020 GRC | N/A | In Compliance | GO 95 Rule 35, and PRC 4293
| 2022 | 189019.3224 | 0 | 189019.3224 | 25597 | 7.3844 | Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | Existing | 2020 GRC | N/A | In Compliance | GO 95 Rule 35, and PRC 4293
| 2020-2022 plan total | 550702.2024 | 0 | 550702.2024 | 25597 | 21.5143 | Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | N/A | N/A | N/A | N/A | N/A
3. Detailed inspections of vegetation around transmission electric lines and equipment | 2019 plan | 15802.0606 | 0 | 15802.0606 | 5710 | 2.7674 | Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | Existing | Transmission Owner | N/A | In Compliance | GO95, PRC 4293 | Initiative captures all routine transmission vegetation management in T2/T3 areas. (Routine Transmission)
| 2019 actual | 30909.1108 | 0 | 30909.1108 | 5710 | 5.4132 | Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | Existing | Transmission Owner | N/A | In Compliance | GO95, PRC 4293
| 2020 | 40594.64 | 0 | 40594.64 | 5710 | 7.1094 | Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | Existing | Transmission Owner | N/A | In Compliance | GO95, PRC 4293
| 2021 | 40418.688 | 0 | 40418.688 | 5710 | 7.0786 | Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | Existing | Transmission Owner | N/A | In Compliance | GO95, PRC 4293
| 2022 | 40237.0804 | 0 | 40237.0804 | 5710 | 7.0468 | Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | Existing | Transmission Owner | N/A | In Compliance | GO95, PRC 4293
| 2020-2022 plan total | 121250.4084 | 0 | 121250.4084 | 5710 | 21.2347 | Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | N/A | N/A | N/A | N/A | N/A
4. Emergency response vegetation management due to red flag warning or other urgent conditions | 2019 plan | See Table 25, 2. Detailed inspections of vegetation around distribution electric lines and equipment
2019 actual
2020
2021
2022
2020-2022 plan total
5. Fuel management and reduction of “slash” from vegetation management activities | 2019 plan | 25364 | 0 | 25364 | N/A | N/A | Cost and risk information for this initiative activity is rolled up into the RSE calculation presented in Table 25, 15 Remediation of at-risk species - Enhanced Vegetation Management |  |  |  | New | 2019 WMP | FHPMA / WMPMA | Exceeds | GO 95 Rule 35, and PRC 4293 to maintain vegetation to conductor clearances and mitigate hazard trees.; also required by PRC 4292 to maintain a 10 foot fire break around poles that support non-exempt equipment. | Program mileage is TBD based on further analysis on appropriate volumes of work that can be accomplished; 2019 miles were not tracked separately from EVM (WMP)
| 2019 actual | 8960 | 0 | 8960 | N/A | N/A |  |  |  |  | New | 2019 WMP | FHPMA / WMPMA | Exceeds | GO 95 Rule 35, and PRC 4293 to maintain vegetation to conductor clearances and mitigate hazard trees.; also required by PRC 4292 to maintain a 10 foot fire break around poles that support non-exempt equipment.
| 2020 | 25000 | 0 | 25000 | TBD | TBD |  |  |  |  | New | 2020 GRC | N/A | Exceeds | GO 95 Rule 35, and PRC 4293 to maintain vegetation to conductor clearances and mitigate hazard trees.; also required by PRC 4292 to maintain a 10 foot fire break around poles that support non-exempt equipment.
| 2021 | 25625 | 0 | 25625 | TBD | TBD |  |  |  |  | New | 2020 GRC | N/A | Exceeds | GO 95 Rule 35, and PRC 4293 to maintain vegetation to conductor clearances and mitigate hazard trees.; also required by PRC 4292 to maintain a 10 foot fire break around poles that support non-exempt equipment.
| 2022 | 26266 | 0 | 26266 | TBD | TBD |  |  |  |  | New | 2020 GRC | N/A | Exceeds | GO 95 Rule 35, and PRC 4293 to maintain vegetation to conductor clearances and mitigate hazard trees.; also required by PRC 4292 to maintain a 10 foot fire break around poles that support non-exempt equipment.
| 2020-2022 plan total | 76891 | 0 | 76891 | TBD | TBD |  |  |  |  | N/A | N/A | N/A | N/A | N/A
6. Improvement of inspections | 2019 plan | See Table 25, 2. Detailed inspections of vegetation around distribution electric lines and equipment
2019 actual
2020
2021
2022
2020-2022 plan total
7-1 LiDAR inspections of vegetation around distribution electric lines and equipment, Enhanced Vegetation Management, Distribution | 2019 plan | 8015 | 0 | 8015 | TBD | TBD | Cost and risk information for this initiative activity is rolled up into the RSE calculation presented in Table 25, 15 Remediation of at-risk species - Enhanced Vegetation Management |  |  |  | New | N/A | FRMMA / WMPMA | In Compliance | GO 95 Rule 35, and PRC 4293 | 2019 mileage is in the process of being validated. 2020-2022 are to be determined (WMP)
| 2019 actual | 27047 | 0 | 27047 | TBD | TBD |  |  |  |  | New | N/A | FRMMA / WMPMA | In Compliance | GO 95 Rule 35, and PRC 4293
| 2020 | 7155 | 0 | 7155 | TBD | TBD |  |  |  |  | New | N/A | FRMMA / WMPMA | In Compliance | GO 95 Rule 35, and PRC 4293
| 2021 | 7369.65 | 0 | 7369.65 | TBD | TBD |  |  |  |  | New | N/A | FRMMA / WMPMA | In Compliance | GO 95 Rule 35, and PRC 4293
| 2022 | 7590.7395 | 0 | 7590.7395 | TBD | TBD |  |  |  |  | New | N/A | FRMMA / WMPMA | In Compliance | GO 95 Rule 35, and PRC 4293
| 2020-2022 plan total | 22115.3895 | 0 | 22115.3895 | TBD | TBD |  |  |  |  | N/A | N/A | N/A | N/A | N/A
7-2 LiDAR inspections of vegetation around distribution electric lines and equipment, Routine Vegetation Management, Distribution | 2019 plan | 9992 | 0 | 9992 | TBD | TBD | Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | Existing | 2017 GRC | N/A | In Compliance | GO 95 Rule 35, and PRC 4293 | 2019 mileage is in the process of being validated. 2020-2022 are to be determined (Routine Distribution)
| 2019 actual | 5 | 0 | 5 | TBD | TBD | Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | Existing | 2017 GRC | N/A | In Compliance | GO 95 Rule 35, and PRC 4293
| 2020 | 0 | 0 | 0 | TBD | TBD | Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | Existing | 2020 GRC | N/A | In Compliance | GO 95 Rule 35, and PRC 4293
| 2021 | 0 | 0 | 0 | TBD | TBD | Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | Existing | 2020 GRC | N/A | In Compliance | GO 95 Rule 35, and PRC 4293
| 2022 | 0 | 0 | 0 | TBD | TBD | Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | Existing | 2020 GRC | N/A | In Compliance | GO 95 Rule 35, and PRC 4293
| 2020-2022 plan total | 0 | 0 | 0 | TBD | TBD | Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | N/A | N/A | N/A | N/A | N/A
8. LiDAR inspections of vegetation around transmission electric lines and equipment | 2019 plan | 0 | 0 | 0 | TBD | TBD | Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | Existing | Transmission Owner | N/A | In Compliance | GO95, PRC 4293 | 2019 mileage is in the process of being validated. 2020-2022 are to be determined (Routine Transmission)
| 2019 actual | 7288 | 0 | 7288 | TBD | TBD | Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | Existing | Transmission Owner | N/A | In Compliance | GO95, PRC 4293
| 2020 | 17812 | 0 | 17812 | TBD | TBD | Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | Existing | Transmission Owner | N/A | In Compliance | GO95, PRC 4293
| 2021 | 18346.36 | 0 | 18346.36 | TBD | TBD | Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | Existing | Transmission Owner | N/A | In Compliance | GO95, PRC 4293
| 2022 | 18896.7508 | 0 | 18896.7508 | TBD | TBD | Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | Existing | Transmission Owner | N/A | In Compliance | GO95, PRC 4293
| 2020-2022 plan total | 55055.1108 | 0 | 55055.1108 | TBD | TBD | Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | N/A | N/A | N/A | N/A | N/A
9. Other discretionary inspection of vegetation around distribution electric lines and equipment, beyond inspections mandated by rules and regulations | 2019 plan | 71703.12 | 0 | 71703.12 | 25597 | 1.9622 | Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | Existing | CEMA | CEMA | Exceeds | GO 95 Rule 35, and PRC 4293 | Represents removal of dead and dying trees due to drought; all distribution HFTD miles inspected annually (CEMA)
| 2019 actual | 70757.9 | 0 | 70757.9 | 25597 | 2.7643 | Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | Existing | CEMA | CEMA | Exceeds | GO 95 Rule 35, and PRC 4293
| 2020 | 106509.26 | 0 | 106509.26 | 25597 | 4.161 | Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | Existing | CEMA | CEMA | Exceeds | GO 95 Rule 35, and PRC 4293
| 2021 | 109704.805 | 0 | 109704.805 | 25597 | 4.2858 | Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | Existing | CEMA | CEMA | Exceeds | GO 95 Rule 35, and PRC 4293
| 2022 | 112995.54 | 0 | 112995.54 | 25597 | 4.4144 | Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | Existing | CEMA | CEMA | Exceeds | GO 95 Rule 35, and PRC 4293
| 2020-2022 plan total | 329209.605 | 0 | 329209.605 | 25597 | 12.8613 | Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | N/A | N/A | N/A | N/A | N/A
10. Other discretionary inspection of vegetation around transmission electric lines and equipment, beyond inspections mandated by rules and regulations | 2019 plan | See Table 25, 3. Detailed inspections of vegetation around transmission electric lines and equipment
2019 actual
2020
2021
2022
2020-2022 plan total
11. Patrol inspections of vegetation around distribution electric lines and equipment | 2019 plan | See Table 25, 2. Detailed inspections of vegetation around distribution electric lines and equipment and Table 25, 9. Other discretionary inspection of vegetation around distribution electric lines and equipment, beyond inspections mandated by rules and regulations
2019 actual
2020
2021
2022
2020-2022 plan total
12. Patrol inspections of vegetation around transmission electric lines and equipment | 2019 plan | See Table 25, 3. Detailed inspections of vegetation around transmission electric lines and equipment
2019 actual
2020
2021
2022
2020-2022 plan total
13. Quality assurance / quality control of inspections (Enhanced, Routine & CEMA) | 2019 plan | 2085.026 | 0 | 2085.026 | N/A | N/A | Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | Existing | 2017 GRC | N/A | In Compliance | GO 95 Rule 35, and PRC 4293 | Quality costs reflected here include quality efforts to support multiple programs: EVM, Routine & CEMA on both transmission and distribution Miles considered N/A as this program validates work on mileage from other programs. (Routine Distribution)
| 2019 actual | 12575.26 | 0 | 12575.26 | N/A | N/A | Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | Existing | 2017 GRC | N/A | In Compliance | GO 95 Rule 35, and PRC 4293
| 2020 | 16250.0024 | 0 | 16250.0024 | N/A | N/A | Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | Existing | 2020 GRC | N/A | In Compliance | GO 95 Rule 35, and PRC 4293
| 2021 | 16737.5025 | 0 | 16737.5025 | N/A | N/A | Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | Existing | 2020 GRC | N/A | In Compliance | GO 95 Rule 35, and PRC 4293
| 2022 | 17239.6275 | 0 | 17239.6275 | N/A | N/A | Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | Existing | 2020 GRC | N/A | In Compliance | GO 95 Rule 35, and PRC 4293
| 2020-2022 plan total | 50227.1324 | 0 | 50227.1324 | N/A | N/A | Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | N/A | N/A | N/A | N/A | N/A
14. Recruiting and training of vegetation management personnel | 2019 plan | See Table 25, 13-1. Quality assurance / quality control of inspections
2019 actual
2020
2021
2022
2020-2022 plan total
15. Remediation of at-risk species - Enhanced Vegetation Management | 2019 plan | 294825.4741 | 0 | 294825.4741 | 2450 | 120.3369 | Contact from Object: Veg. contact | 279.64 | 0.85 | N/A - All drivers are represented in the 'drivers targeted' | New | 2019 WMP | FHPMA / WMPMA | Exceeds | GO 95 Rule 35, and PRC 4293 | Represents enhanced vegetation management in T2/T3 areas (WMP)
| 2019 actual | 424156.0941 | 0 | 424156.0941 | 2498 | 169.7983 | Contact from Object: Veg. contact | 301.22 | 0.68 | N/A - All drivers are represented in the 'drivers targeted' | New | 2019 WMP | FHPMA / WMPMA | Exceeds | GO 95 Rule 35, and PRC 4293
| 2020 | 449038.3956 | 0 | 449038.3956 | 1800 | 249.4658 | Contact from Object: Veg. contact | 72.34 | 0.16 | N/A - All drivers are represented in the 'drivers targeted' | New | 2020 GRC | N/A | Exceeds | GO 95 Rule 35, and PRC 4293
| 2021 | 462634.5475 | 0 | 462634.5475 | 1800 | 257.0192 | Contact from Object: Veg. contact | 65.79 | 0.15 | N/A - All drivers are represented in the 'drivers targeted' | New | 2020 GRC | N/A | Exceeds | GO 95 Rule 35, and PRC 4293
| 2022 | 476641.7089 | 0 | 476641.7089 | 1800 | 264.8009 | Contact from Object: Veg. contact | 63.7 | 0.15 | N/A - All drivers are represented in the 'drivers targeted' | New | 2020 GRC | N/A | Exceeds | GO 95 Rule 35, and PRC 4293
| 2020-2022 plan total | 1388314.652 | 0 | 1388314.652 | 5400 | 257.0953 | Contact from Object: Veg. contact | 201.83 | 0.15 | N/A - All drivers are represented in the 'drivers targeted' | N/A | N/A | N/A | N/A | N/A
16. Removal and remediation of trees with strike potential to electric lines and equipment, Transmission | 2019 plan | 18114 | 18114 | 0 | 226 | 80.1504 | Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | Existing | Transmission Owner | N/A | Meets | GO95, PRC 4293 | Represents Transmission ROW clearing; for 2019 plan the actual miles is estimated (Routine Transmission)
| 2019 actual | 5707.7572 | 5707.7572 | 0 | 141 | 40.4805 | Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | Existing | Transmission Owner | N/A | Meets | GO95, PRC 4293
| 2020 | 14683.1944 | 14683.1944 | 0 | 262 | 56.0427 | Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | Existing | Transmission Owner | N/A | Meets | GO95, PRC 4293
| 2021 | 15050.18 | 15050.18 | 0 | 367 | 41.0087 | Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | Existing | Transmission Owner | N/A | Meets | GO95, PRC 4293
| 2022 | 15426.5916 | 15426.5916 | 0 | 120 | 128.5549 | Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | Existing | Transmission Owner | N/A | Meets | GO95, PRC 4293
| 2020-2022 plan total | 45159.966 | 45159.966 | 0 | 749 | 60.2937 | Contact from Object: Veg. contact | N/A - Control | N/A - Control | N/A - Control | N/A | N/A | N/A | N/A | N/A
17-1. Substation inspections - Enhanced Substation Maintenance Vegetation, Distribution Substation | 2019 plan | 0 | 0 | 0 | N/A | N/A | Contact from Object: Veg. contact | N/A - Enhanced Control | N/A - Enhanced Control | N/A - Enhanced Control | New | 2019 WMP | FRMMA / WMPMA | Exceeds | GO 95 Rule 35/PRC 4293/NERC Standard FAC-003-3. | Line Miles = N/A as substation assets are not associated with circuit miles (WMP)
| 2019 actual | 7277.5774 | 0 | 7277.5774 | N/A | N/A | Contact from Object: Veg. contact | N/A - Enhanced Control | N/A - Enhanced Control | N/A - Enhanced Control | New | 2019 WMP | FRMMA / WMPMA | Exceeds | GO 95 Rule 35/PRC 4293/NERC Standard FAC-003-3.
| 2020 | 862.1392 | 0 | 862.1392 | N/A | N/A | Contact from Object: Veg. contact | N/A - Enhanced Control | N/A - Enhanced Control | N/A - Enhanced Control | New | N/A | FRMMA / WMPMA | Exceeds | GO 95 Rule 35/PRC 4293/NERC Standard FAC-003-3.
| 2021 | 883.6927 | 0 | 883.6927 | N/A | N/A | Contact from Object: Veg. contact | N/A - Enhanced Control | N/A - Enhanced Control | N/A - Enhanced Control | New | N/A | FRMMA / WMPMA | Exceeds | GO 95 Rule 35/PRC 4293/NERC Standard FAC-003-3.
| 2022 | 905.785 | 0 | 905.785 | N/A | N/A | Contact from Object: Veg. contact | N/A - Enhanced Control | N/A - Enhanced Control | N/A - Enhanced Control | New | N/A | FRMMA / WMPMA | Exceeds | GO 95 Rule 35/PRC 4293/NERC Standard FAC-003-3.
| 2020-2022 plan total | 2651.6169 | 0 | 2651.6169 | N/A | N/A | Contact from Object: Veg. contact | N/A - Enhanced Control | N/A - Enhanced Control | N/A - Enhanced Control | N/A | N/A | N/A | N/A | N/A
17-2. Substation inspections - Enhanced Substation Maintenance Vegetation, Transmission Substation | 2019 plan | 0 | 0 | 0 | N/A | N/A | Contact from Object: Veg. contact | N/A - Enhanced Control | N/A - Enhanced Control | N/A - Enhanced Control | New | Transmission Owner | N/A | N/A | N/A | Line Miles = N/A as substation assets are not associated with circuit miles (WMP)
| 2019 actual | 1259.3591 | 0 | 1259.3591 | N/A | N/A | Contact from Object: Veg. contact | N/A - Enhanced Control | N/A - Enhanced Control | N/A - Enhanced Control | New | Transmission Owner | N/A | N/A | N/A
| 2020 | 1026.9226 | 0 | 1026.9226 | N/A | N/A | Contact from Object: Veg. contact | N/A - Enhanced Control | N/A - Enhanced Control | N/A - Enhanced Control | New | Transmission Owner | N/A | N/A | N/A
| 2021 | 1052.5957 | 0 | 1052.5957 | N/A | N/A | Contact from Object: Veg. contact | N/A - Enhanced Control | N/A - Enhanced Control | N/A - Enhanced Control | New | Transmission Owner | N/A | N/A | N/A
| 2022 | 1078.9106 | 0 | 1078.9106 | N/A | N/A | Contact from Object: Veg. contact | N/A - Enhanced Control | N/A - Enhanced Control | N/A - Enhanced Control | New | Transmission Owner | N/A | N/A | N/A
| 2020-2022 plan total | 3158.4288 | 0 | 3158.4288 | N/A | N/A | Contact from Object: Veg. contact | N/A - Enhanced Control | N/A - Enhanced Control | N/A - Enhanced Control | N/A | N/A | N/A | N/A | N/A
18. Substation vegetation management | 2019 plan | See Table 25, 17. Substation Inspections
2019 actual
2020
2021
2022
2020-2022 plan total
19. Vegetation inventory system | 2019 plan | See Table 25, 2. Detailed inspections of vegetation around distribution electric lines and equipment
2019 actual
2020
2021
2022
2020-2022 plan total
20. Vegetation management to achieve clearances around electric lines and equipment | 2019 plan | See Table 25, 2. Detailed inspections of vegetation around distribution electric lines and equipment
2019 actual
2020
2021
2022
2020-2022 plan total

## Table 26
Table 26: Grid operations and protocols
Initiative activity | Year | Total per-initiative spend ($1000's) | Subtotal A: Capital expenditure ($1000's) | Subtotal B: Operating expenses ($1000's) | Line miles to be treated | Spend ($1000's)/ treated line mile | Ignition probability drivers targeted | Risk reduction | Risk-spend efficiency | Other risk drivers addressed | Existing/ new | Existing: What proceeding has reviewed program | If new: Memorandum account | In / exceeding compliance with regulations | Cite associated rule | Comments
1. Automatic recloser operations | 2019 plan | See Table 23, 9-1. Installation of system automation equipment - Expanded Automation , Distribution
2019 actual
2020
2021
2022
2020-2022 plan total
2. Crew-accompanying ignition prevention and suppression resources and services | 2019 plan | 12708.067 | 0 | 12708.067 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2019 WMP | FRMMA | N/A | N/A | Line miles is not an applicable metric (WMP)
| 2019 actual | 13560.6166 | 642.3526 | 12918.264 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2019 WMP | FRMMA | N/A | N/A
| 2020 | 24343.5055 | 675.84 | 23667.6655 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2020 GRC, 2019 WMP | N/A | N/A | N/A
| 2021 | 38208.8781 | 1152.36 | 37056.5181 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2020 GRC, 2019 WMP | N/A | N/A | N/A
| 2022 | 41285.8776 | 0 | 41285.8776 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2020 GRC, 2019 WMP | N/A | N/A | N/A
| 2020-2022 plan total | 103838.2612 | 1828.2 | 102010.0612 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A | N/A | N/A | N/A | N/A
3. Personnel work procedures and training in conditions of elevated fire risk | 2019 plan | 1800 | 0 | 1800 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2019 WMP | FRMMA / WMPMA | N/A | N/A | (WMP)
| 2019 actual | 1385 | 0 | 1385 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2019 WMP | FRMMA / WMPMA | N/A | N/A
| 2020 | 1235.28 | 0 | 1235.28 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2020 GRC | N/A | N/A | N/A
| 2021 | 317.85 | 0 | 317.85 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2020 GRC | N/A | N/A | N/A
| 2022 | 327.09 | 0 | 327.09 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2020 GRC | N/A | N/A | N/A
| 2020-2022 plan total | 1880.22 | 0 | 1880.22 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A | N/A | N/A | N/A | N/A
4-1 Protocols for PSPS re-energization - Distribution | 2019 plan | 7428.6997 | 0 | 7428.6997 | N/A | N/A | Cost and risk information for this initiative activity is rolled up into the RSE calculation presented in Table 26, 5-1 PSPS events and mitigation of PSPS impacts - Distribution |  |  |  | New | 2019 WMP | FRMMA / WMPMA | TBD | TBD | Line miles is not an applicable metric (WMP)
| 2019 actual | 28079.8257 | 756.8257 | 27323 | N/A | N/A |  |  |  |  | New | 2019 WMP | FRMMA / WMPMA | TBD | TBD
| 2020 | 16059 | 0 | 16059 | N/A | N/A |  |  |  |  | New | N/A | FRMMA | TBD | TBD
| 2021 | 16460 | 0 | 16460 | N/A | N/A |  |  |  |  | New | N/A | FRMMA | TBD | TBD
| 2022 | 16872 | 0 | 16872 | N/A | N/A |  |  |  |  | New | N/A | FRMMA | TBD | TBD
| 2020-2022 plan total | 49391 | 0 | 49391 | N/A | N/A |  |  |  |  | N/A | N/A | N/A | N/A | N/A
4-2 Protocols for PSPS re-energization - Transmission | 2019 plan | 0 | 0 | 0 | N/A | N/A | Cost and risk information for this initiative activity is rolled up into the RSE calculation presented in Table 26, 5-1 PSPS events and mitigation of PSPS impacts - Distribution |  |  |  | New | Transmission Owner | N/A | TBD | TBD | Line miles is not an applicable metric (WMP)
| 2019 actual | 1774.2242 | 0 | 1774.2242 | N/A | N/A |  |  |  |  | New | Transmission Owner | N/A | TBD | TBD
| 2020 | 1027 | 0 | 1027 | N/A | N/A |  |  |  |  | New | Transmission Owner | N/A | TBD | TBD
| 2021 | 1053 | 0 | 1053 | N/A | N/A |  |  |  |  | New | Transmission Owner | N/A | TBD | TBD
| 2022 | 1079 | 0 | 1079 | N/A | N/A |  |  |  |  | New | Transmission Owner | N/A | TBD | TBD
| 2020-2022 plan total | 3159 | 0 | 3159 | N/A | N/A |  |  |  |  | N/A | N/A | N/A | N/A | N/A
5-1 PSPS events and mitigation of PSPS impacts - Distribution | 2019 plan | 8226.0148 | 0 | 8226.0148 | N/A | N/A | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Voltage Regulator failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from Object: Vehicle contact, Veg. contact, Animal contact, Balloon contact, 3rd party Contact other | 693.06 | 44.27 | N/A - All drivers are represented in the 'drivers targeted' | New | 2019 WMP | FRMMA / WMPMA | TBD | TBD | Line miles is not an applicable metric (WMP)
| 2019 actual | 177972 | 0 | 177972 | N/A | N/A | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Voltage Regulator failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from Object: Vehicle contact, Veg. contact, Animal contact, Balloon contact, 3rd party Contact other | 41211.45 | 182.91 | N/A - All drivers are represented in the 'drivers targeted' | New | 2019 WMP | FRMMA / WMPMA | TBD | TBD
| 2020 | 139044.9362 | 0 | 139044.9362 | N/A | N/A | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Voltage Regulator failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from Object: Vehicle contact, Veg. contact, Animal contact, Balloon contact, 3rd party Contact other | 4254.97 | 26.7 | N/A - All drivers are represented in the 'drivers targeted' | New | 2020 GRC | N/A | TBD | TBD
| 2021 | 142521.0596 | 0 | 142521.0596 | N/A | N/A | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Voltage Regulator failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from Object: Vehicle contact, Veg. contact, Animal contact, Balloon contact, 3rd party Contact other | 4029.05 | 26.41 | N/A - All drivers are represented in the 'drivers targeted' | New | 2020 GRC | N/A | TBD | TBD
| 2022 | 146084.0861 | 0 | 146084.0861 | N/A | N/A | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Voltage Regulator failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from Object: Vehicle contact, Veg. contact, Animal contact, Balloon contact, 3rd party Contact other | 3812.96 | 26.12 | N/A - All drivers are represented in the 'drivers targeted' | New | 2020 GRC | N/A | TBD | TBD
| 2020-2022 plan total | 427650.0818 | 0 | 427650.0818 | N/A | N/A | All types of equipment - facility failure: Conductor failure -all, Crossarm failure, Guy - Span wire failure, Fuse failure, Insulator failure, Lightning Arrestor, Pole failure, Transformer failure, Voltage Regulator failure, Capacitor bank failure, Sectionalizer failure, Recloser failure, Switch failure, Equipment failure - Other Contact from Object: Vehicle contact, Veg. contact, Animal contact, Balloon contact, 3rd party Contact other | 12096.98 | 26.42 | N/A - All drivers are represented in the 'drivers targeted' | N/A | N/A | N/A | N/A | N/A
5-2 PSPS events and mitigation of PSPS impacts - Transmission Substation | 2019 plan | 0 | 0 | 0 | N/A | N/A | Cost and risk information for this initiative activity is rolled up into the RSE calculation presented in Table 26, 5-1 PSPS events and mitigation of PSPS impacts - Distribution |  |  |  | New | Transmission Owner | N/A | N/A | N/A | Line miles is not an applicable metric (WMP)
| 2019 actual | 18490 | 0 | 18490 | N/A | N/A |  |  |  |  | New | Transmission Owner | N/A | N/A | N/A
| 2020 | 14568.296 | 0 | 14568.296 | N/A | N/A |  |  |  |  | New | Transmission Owner | N/A | N/A | N/A
| 2021 | 14933 | 0 | 14933 | N/A | N/A |  |  |  |  | New | Transmission Owner | N/A | N/A | N/A
| 2022 | 15306 | 0 | 15306 | N/A | N/A |  |  |  |  | New | Transmission Owner | N/A | N/A | N/A
| 2020-2022 plan total | 44807.296 | 0 | 44807.296 | N/A | N/A |  |  |  |  | N/A | N/A | N/A | N/A | N/A
5-3 PSPS events and mitigation of PSPS impacts - Additional PSPS Mitigation Initiatives, Distribution | 2019 plan | 0 | 0 | 0 | N/A | N/A | See Table 26, 5-1 PSPS events and mitigation of PSPS impacts - distribution |  |  |  | N/A | N/A | FRMMA | N/A | N/A | Line miles is not an applicable metric (WMP)
| 2019 actual | 0 | 0 | 0 | N/A | N/A |  |  |  |  | N/A | N/A | FRMMA | N/A | N/A
| 2020 | 56745 | 8410 | 48334.644 | N/A | N/A |  |  |  |  | New | N/A | FRMMA | N/A | N/A
| 2021 | 49543 | 0 | 49543.0101 | N/A | N/A |  |  |  |  | New | N/A | FRMMA | N/A | N/A
| 2022 | 50782 | 0 | 50781.5854 | N/A | N/A |  |  |  |  | New | N/A | FRMMA | N/A | N/A
| 2020-2022 plan total | 48364.1119 | 0 | 48364.1119 | N/A | N/A |  |  |  |  | N/A | N/A | N/A | N/A | N/A
6. Stationed and on-call ignition prevention and suppression resources and services | 2019 plan | See Table 26, 2. Crew-accompanying ignition prevention and suppression resources and services
2019 actual
2020
2021
2022
2020-2022 plan total

## Table 27
Table 27: Data governance
Initiative activity | Year | Total per-initiative spend ($1000's) | Subtotal A: Capital expenditure ($1000's) | Subtotal B: Operating expenses ($1000's) | Line miles to be treated | Spend ($1000's)/ treated line mile | Ignition probability drivers targeted | Risk reduction | Risk-spend efficiency | Other risk drivers addressed | Existing/ new | Existing: What proceeding has reviewed program | If new: Memorandum account | In / exceeding compliance with regulations | Cite associated rule | Comments
1. Centralized repository for data | 2019 plan | See Table 27, 5. Other / not listed, Information Technology, Transmission and Distribution: Data governance initiatives fall primarily under PG&E IT programs. The costs and data for this section consists of distribution and transmission costs related to data management and governance for wildfire related activities. The IT costs represent a number of programs to support for example, PSPS, WSOC, and EVM
2019 actual
2020
2021
2022
2020-2022 plan total
2. Collaborative research on utility ignition and/or wildfire | 2019 plan | See Table 27, 5. Other / not listed, Information Technology, Transmission and Distribution: Data governance initiatives fall primarily under PG&E IT programs. The costs and data for this section consists of distribution and transmission costs related to data management and governance for wildfire related activities. The IT costs represent a number of programs to support for example, PSPS, WSOC, and EVM
2019 actual
2020
2021
2022
2020-2022 plan total
3. Documentation and disclosure of wildfire-related data and algorithms | 2019 plan | See Table 27, 5. Other / not listed, Information Technology, Transmission and Distribution: Data governance initiatives fall primarily under PG&E IT programs. The costs and data for this section consists of distribution and transmission costs related to data management and governance for wildfire related activities. The IT costs represent a number of programs to support for example, PSPS, WSOC, and EVM
2019 actual
2020
2021
2022
2020-2022 plan total
4. Tracking and analysis of near miss data | 2019 plan | See Table 27, 5. Other / not listed, Information Technology, Transmission and Distribution: Data governance initiatives fall primarily under PG&E IT programs. The costs and data for this section consists of distribution and transmission costs related to data management and governance for wildfire related activities. The IT costs represent a number of programs to support for example, PSPS, WSOC, and EVM
2019 actual
2020
2021
2022
2020-2022 plan total
5. Other / not listed, Information Technology, Transmission and Distribution | 2019 plan | 12748 | 10751.6552 | 1996.09 | N/A | N/A | N/A | N/A | N/A | N/A | New/Existing | 2017 GRC and Transmission Owner | N/A | N/A | N/A | Data governance are primarily managed within PG&E’s IT programs. The costs and data for this section consists of distribution and transmission costs related to data management and governance for several wildfire related activities, including PSPS, WSOC, and EVM (WMP and Routine Distribution)
| 2019 actual | 36095 | 27002 | 9093 | N/A | N/A | N/A | N/A | N/A | N/A | New/Existing | 2017 GRC and Transmission Owner | N/A | N/A | N/A
| 2020 | 88231 | 46399 | 41832 | N/A | N/A | N/A | N/A | N/A | N/A | New/Existing | 2020 GRC and Transmission Owner | N/A | N/A | N/A
| 2021 | 49623 | 43236 | 6387 | N/A | N/A | N/A | N/A | N/A | N/A | New/Existing | 2020 GRC and Transmission Owner | N/A | N/A | N/A
| 2022 | 39283.0048 | 34402 | 4881.0048 | N/A | N/A | N/A | N/A | N/A | N/A | New/Existing | 2020 GRC and Transmission Owner | N/A | N/A | N/A
| 2020-2022 plan total | 177137.0048 | 124037 | 53100.0048 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A

## Table 28
Table 28: Resource allocation methodology
Initiative activity | Year | Total per-initiative spend ($1000's) | Subtotal A: Capital expenditure ($1000's) | Subtotal B: Operating expenses ($1000's) | Line miles to be treated | Spend ($1000's)/ treated line mile | Ignition probability drivers targeted | Risk reduction | Risk-spend efficiency | Other risk drivers addressed | Existing/ new | Existing: What proceeding has reviewed program | If new: Memorandum account | In / exceeding compliance with regulations | Cite associated rule | Comments
1. Allocation methodology development and application | 2019 plan | N/A - PG&E does not specifically or separately track the costs associated with these foundational planning and risk analysis work activities. These activities are generally performed by internal electric operations staff
2019 actual
2020
2021
2022
2020-2022 plan total
2. Risk reduction scenario development and analysis | 2019 plan | N/A - PG&E does not specifically or separately track the costs associated with these foundational planning and risk analysis work activities. These activities are generally performed by internal electric operations staff
2019 actual
2020
2021
2022
2020-2022 plan total
3. Risk spend efficiency analysis | 2019 plan | N/A - PG&E does not specifically or separately track the costs associated with these foundational planning and risk analysis work activities. These activities are generally performed by internal electric operations staff
2019 actual
2020
2021
2022
2020-2022 plan total

## Table 29
Table 29: Emergency planning and preparedness
Initiative activity | Year | Total per-initiative spend ($1000's) | Subtotal A: Capital expenditure ($1000's) | Subtotal B: Operating expenses ($1000's) | Line miles to be treated | Spend ($1000's)/ treated line mile | Ignition probability drivers targeted | Risk reduction | Risk-spend efficiency | Other risk drivers addressed | Existing/ new | Existing: What proceeding has reviewed program | If new: Memorandum account | In / exceeding compliance with regulations | Cite associated rule | Comments
1. Adequate and trained workforce for service restoration | 2019 plan | See Table 26, 4-1 Protocols for PSPS re-energization - Distribution & Table 26, 4-2 Protocols for PSPS re-energization - Transmission
2019 actual
2020
2021
2022
2020-2022 plan total
2. Community outreach, public awareness, and communications efforts | 2019 plan | Community engagement costs for specific initiatives are captured in the financial numbers for those initiatives. See also Table 26, 4-1 Protocols for PSPS re-energization – Distribution & Table 26, and 4-2 Protocols for PSPS re-energization - Transmission Overarching Community Wildfire Safety Program, Community Engagement costs are incorporated into the numbers shown below, Table 30, 5. Other / not listed, WMP PMO and Table 30, 5-1 Other/not listed, emergency preparedness education campaign
2019 actual
2020
2021
2022
2020-2022 plan total
3. Customer support in emergencies | 2019 plan | 3100 | 0 | 3100 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | Existing | Emergency Consumer Protections | ECPMA | Exceed | • Gas & Electric Rules 1, 6, 11, 19.1, 19.2, and 19.3 • Electric Rules 12, 13, 15, 16, 21 | Line miles is not an applicable metric (Emergency)
| 2019 actual | 2559 | 0 | 2559 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | Existing | Emergency Consumer Protections | ECPMA | Exceed | • Gas & Electric Rules 1, 6, 11, 19.1, 19.2, and 19.3 • Electric Rules 12, 13, 15, 16, 21
| 2020 | 3100 | 0 | 3100 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | Existing | Emergency Consumer Protections | ECPMA | Exceed | • Gas & Electric Rules 1, 6, 11, 19.1, 19.2, and 19.3 • Electric Rules 12, 13, 15, 16, 21
| 2021 | 3177.5 | 0 | 3177.5 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | Existing | Emergency Consumer Protections | ECPMA | Exceed | • Gas & Electric Rules 1, 6, 11, 19.1, 19.2, and 19.3 • Electric Rules 12, 13, 15, 16, 21
| 2022 | 3256.9375 | 0 | 3256.9375 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | Existing | Emergency Consumer Protections | ECPMA | Exceed | • Gas & Electric Rules 1, 6, 11, 19.1, 19.2, and 19.3 • Electric Rules 12, 13, 15, 16, 21
| 2020-2022 plan total | 9534.4375 | 0 | 9534.4375 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A | N/A | N/A | N/A | N/A
4. Disaster and emergency preparedness plan - Distribution | 2019 plan | 9743 | 2607 | 7136 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | Existing | 2017 GRC | N/A | In Compliance | GO 166 Standards 1-13: The purpose of these standards is to insure that jurisdictional electric utilities are prepared for emergencies and disasters in order to minimize damage and inconvenience to the public which may occur as a result of electric system failures, major outages, or hazards posed by damage to electric distribution facilities. | Line miles is not an applicable metric (Routine Distribution)
| 2019 actual | 6759.997 | 715.355 | 6044.642 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | Existing | 2017 GRC | N/A | In Compliance | GO 166 Standards 1-13: The purpose of these standards is to insure that jurisdictional electric utilities are prepared for emergencies and disasters in order to minimize damage and inconvenience to the public which may occur as a result of electric system failures, major outages, or hazards posed by damage to electric distribution facilities.
| 2020 | 31662 | 5000 | 26662 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | Existing | 2020 GRC | N/A | In Compliance | GO 166 Standards 1-13: The purpose of these standards is to insure that jurisdictional electric utilities are prepared for emergencies and disasters in order to minimize damage and inconvenience to the public which may occur as a result of electric system failures, major outages, or hazards posed by damage to electric distribution facilities.
| 2021 | 32453 | 5125 | 27328 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | Existing | 2020 GRC | N/A | In Compliance | GO 166 Standards 1-13: The purpose of these standards is to insure that jurisdictional electric utilities are prepared for emergencies and disasters in order to minimize damage and inconvenience to the public which may occur as a result of electric system failures, major outages, or hazards posed by damage to electric distribution facilities.
| 2022 | 33265 | 5253 | 28012 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | Existing | 2020 GRC | N/A | In Compliance | GO 166 Standards 1-13: The purpose of these standards is to insure that jurisdictional electric utilities are prepared for emergencies and disasters in order to minimize damage and inconvenience to the public which may occur as a result of electric system failures, major outages, or hazards posed by damage to electric distribution facilities.
| 2020-2022 plan total | 97380 | 15378 | 82002 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A | N/A | N/A | N/A | N/A
5. Preparedness and planning for service restoration | 2019 plan | These activities are embedded within PG&E’s disaster and emergency preparedness planning activities and spend; therefore see Table 29, 4. Disaster and emergency preparedness plan - Distribution
2019 actual
2020
2021
2022
2020-2022 plan total
6. Protocols in place to learn from wildfire events | 2019 plan | These activities are embedded within PG&E’s disaster and emergency preparedness planning activities and spend; therefore see Table 29, 4. Disaster and emergency preparedness plan - Distribution
2019 actual
2020
2021
2022
2020-2022 plan total
7. Other / not listed, Aviation Support | 2019 plan | 14224.88 | 9000 | 5224.88 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2019 WMP | FRMMA / WMPMA | N/A | N/A | (WMP)
| 2019 actual | 10346.1493 | 3725.7933 | 6620.3561 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2019 WMP | FRMMA / WMPMA | N/A | N/A
| 2020 | 2156.1782 | 0 | 2156.1782 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2020 GRC | N/A | N/A | N/A
| 2021 | 2225.1258 | 0 | 2225.1258 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2020 GRC | N/A | N/A | N/A
| 2022 | 2296.3716 | 0 | 2296.3716 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2020 GRC | N/A | N/A | N/A
| 2020-2022 plan total | 6677.6757 | 0 | 6677.6757 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | N/A | N/A | N/A | N/A

## Table 30
Table 30: Stakeholder cooperation and community engagement
Initiative activity | Year | Total per-initiative spend ($1000's) | Subtotal A: Capital expenditure ($1000's) | Subtotal B: Operating expenses ($1000's) | Line miles to be treated | Spend ($1000's)/ treated line mile | Ignition probability drivers targeted | Risk reduction | Risk-spend efficiency | Other risk drivers addressed | Existing/ new | Existing: What proceeding has reviewed program | If new: Memorandum account | In / exceeding compliance with regulations | Cite associated rule | Comments
1. Community engagement | 2019 plan | Individual initiative costs associated with community engagement are captured in the financial numbers for those initiatives in other 5.3 tables. Section 5.3.3.6_Table 23 6-1. Distribution pole replacement and reinforcement, including with composite poles Section 5.3.3.15_Table 23 15. Transmission tower maintenance and replacement Section 5.3.4.1 Table 24 1. Detailed inspections of distribution electric lines and equipment Section 5.3.4.2 Table 24 2. Detailed inspections of transmission electric lines and equipment Section 5.3.3.17_Table 23 17-1. Updates to grid topology to minimize risk of ignition in HFTDs - System Hardening , Distribution Section 5.3.5.2_Table 25 2. Detailed inspections of vegetation around distribution electric lines and equipment Overarching Community Wildfire Safety Program, Community Engagement costs are incorporated into the numbers shown below, Table 30, 5. Other / not listed, WMP PMO
2019 actual
2020
2021
2022
2020-2022 plan total
2. Cooperation and best practice sharing with agencies outside CA | 2019 plan | PG&E doesn’t specifically track these work activities as separate costs; these activities are generally performed by internal resources as an ancillary function to their regular tasks
2019 actual
2020
2021
2022
2020-2022 plan total
3. Cooperation with suppression agencies | 2019 plan | PG&E doesn’t specifically track these work activities as separate costs; these activities are generally performed by internal resources as an ancillary function to their regular tasks
2019 actual
2020
2021
2022
2020-2022 plan total
4. Forest service and fuel reduction cooperation and joint roadmap | 2019 plan | 0 | 0 | 0 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A | N/A | N/A | N/A | N/A | The data in this section is for the USFS program described in 5.3.10.4. Other activities in Section 5.3.10.4 are not tracked as separate costs; these activities are generally performed by internal sources as an ancillary function to their regular tasks (WMP)
| 2019 actual | 0 | 0 | 0 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A | N/A | N/A | N/A | N/A
| 2020 | 2500 | 0 | 2500 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | Transmission Owner | N/A | N/A | N/A
| 2021 | 0 | 0 | 0 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | N/A | N/A | N/A | N/A
| 2022 | 0 | 0 | 0 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | N/A | N/A | N/A | N/A
| 2020-2022 plan total | 2500 | 0 | 2500 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A | N/A | N/A | N/A | N/A
5. Other / not listed, WMP PMO | 2019 plan | 8561.5112 | 541.1472 | 8020.364 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2019 WMP | FRMMA/ WMPMA | N/A | N/A | Represents the costs of the CWSP Program Management Office (PMO) which aggregates a number of other initiatives including public outreach, benchmarking, governance and other activities. (WMP)
| 2019 actual | 31275.2838 | 91.7807 | 31183.5031 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2019 WMP | FRMMA/ WMPMA | N/A | N/A
| 2020 | 18529.2 | 0 | 18529.2 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2020 GRC, 2019 WMP | FRMMA/ WMPMA | N/A | N/A
| 2021 | 19071 | 0 | 19071 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2020 GRC, 2019 WMP | FRMMA/ WMPMA | N/A | N/A
| 2022 | 19625.4 | 0 | 19625.4 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | 2020 GRC, 2019 WMP | FRMMA/ WMPMA | N/A | N/A
| 2020-2022 plan total | 57225.6 | 0 | 57225.6 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A | N/A | N/A | N/A | N/A
5-1 Other/not listed, Emergency preparedness education campaign | 2019 plan | 0 | 0 | 0 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | N/A | N/A | N/A | N/A | PSPS and emergency preparedness media campaign (WMP)
| 2019 actual | 7494 | 0 | 7494 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | N/A | FRMMA | N/A | N/A
| 2020 | 7720.5 | 0 | 7720.5 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | N/A | FRMMA | N/A | N/A
| 2021 | 8177.25 | 0 | 8177.25 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | N/A | FRMMA | N/A | N/A
| 2022 | 8177.25 | 0 | 8177.25 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | N/A | FRMMA | N/A | N/A
| 2020-2022 plan total | 24075 | 0 | 24075 | N/A | N/A | N/A - Foundational | N/A - Foundational | N/A - Foundational | N/A - Foundational | New | N/A | N/A | N/A | N/A

## Table 31
Table 31: Change in drivers of ignition probability taking into account planned initiatives, for each year of plan - Distribution
Incident type by ignition probability driver | Detailed risk driver | Are near misses tracked? | Number of incidents per year |  |  |  | Average percentage likelihood of ignition per incident |  |  | Number of ignitions per year
|  |  | 2019 (Actual) | 2020 | 2021 | 2022 | 2020 | 2021 | 2022 | 2019 (Actual) | 2020 | 2021 | 2022
Contact from object - Distribution | All types of object contact | Y | 13434 | 13094.17 | 12788.32 | 12513.05 | 1.88% | 1.88% | 1.88% | 253 | 246.6 | 240.84 | 235.66
| Animal contact | Y | 2072 | 2034.33 | 2000.42 | 1969.91 | 3.19% | 3.19% | 3.19% | 66 | 64.8 | 63.72 | 62.75
| Balloon contact | Y | 464 | 464 | 464 | 464 | 3.02% | 3.02% | 3.02% | 14 | 14 | 14 | 14
| Vegetation contact | Y | 8167 | 7807.1 | 7483.19 | 7191.67 | 1.44% | 1.44% | 1.44% | 118 | 112.8 | 108.12 | 103.91
| Vehicle contact | Y | 1835 | 1835 | 1835 | 1835 | 2.02% | 2.02% | 2.02% | 37 | 37 | 37 | 37
| Contact from Object - Other | Y | 896 | 896 | 896 | 896 | 2.01% | 2.01% | 2.01% | 18 | 18 | 18 | 18
All types of equipment / facility failure - Distribution | All types | Y | 13031 | 12835.54 | 12659.62 | 12501.29 | 1.07% | 1.07% | 1.07% | 140 | 137.9 | 136.01 | 134.31
| Capacitor bank failure | Y | 70 | 70 | 70 | 70 | 10% | 10% | 10% | 7 | 7 | 7 | 7
| Conductor failure—all | Y | 3382 | 3328.6 | 3280.54 | 3237.29 | 2.25% | 2.25% | 2.25% | 76 | 74.8 | 73.72 | 72.75
| Conductor failure—wires down | Y | 1593 | 1593 | 1593 | 1593 | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Fuse failure—all | Y | 345 | 345 | 345 | 345 | 0.58% | 0.58% | 0.58% | 2 | 2 | 2 | 2
| Fuse failure—conventional blown fuse | Y | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Lightning arrestor failure | Y | 130 | 130 | 130 | 130 | 3.08% | 3.08% | 3.08% | 4 | 4 | 4 | 4
| Switch failure | Y | 189 | 179.55 | 171.05 | 163.39 | 2.12% | 2.12% | 2.12% | 4 | 3.8 | 3.62 | 3.46
| Transformer failure | Y | 3962 | 3905.4 | 3854.46 | 3808.61 | 0.53% | 0.53% | 0.53% | 21 | 20.7 | 20.43 | 20.19
| Pole failure | Y | 1162 | 1162 | 1162 | 1162 | 0.34% | 0.34% | 0.34% | 4 | 4 | 4 | 4
| Insulator failure | Y | 374 | 355.3 | 338.47 | 323.32 | 1.07% | 1.07% | 1.07% | 4 | 3.8 | 3.62 | 3.46
| Crossarm failure | Y | 1001 | 1001 | 1001 | 1001 | 0.2% | 0.2% | 0.2% | 2 | 2 | 2 | 2
| Voltage Regulator failure | Y | 59 | 57.03 | 55.26 | 53.67 | 5.08% | 5.08% | 5.08% | 3 | 2.9 | 2.81 | 2.73
| Recloser failure | Y | 106 | 106 | 106 | 106 | 0% | 0% | 0% | 0 | 0 | 0 | 0
| Guy/Span Wire failure | Y | 58 | 58 | 58 | 58 | 0% | 0% | 0% | 0 | 0 | 0 | 0
| Sectionalizer failure | Y | 3 | 3 | 3 | 3 | 0% | 0% | 0% | 0 | 0 | 0 | 0
| Equipment failure - Other | Y | 2190 | 2173.15 | 2157.99 | 2144.35 | 0.59% | 0.59% | 0.59% | 13 | 12.9 | 12.81 | 12.73
Wire-to-wire contact / contamination |  | Y | 16357 | 16357 | 16357 | 16357 | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Other |  | Y | 1746 | 1746 | 1746 | 1746 | 2.23% | 2.23% | 2.23% | 39 | 39 | 39 | 39
Table 31: Change in drivers of ignition probability taking into account planned initiatives, for each year of plan - Transmission
Incident type by ignition probability driver | Detailed risk driver | Are near misses tracked? | Number of incidents per year |  |  |  | Average percentage likelihood of ignition per incident |  |  | Number of ignitions per year
|  |  | 2019 (Actual) | 2020 | 2021 | 2022 | 2020 | 2021 | 2022 | 2019 (Actual) | 2020 | 2021 | 2022
Contact from object - Transmission | All types of object contact | Y | 150 | 147.69 | 145.62 | 143.75 | 8.67% | 8.67% | 8.67% | 13 | 12.8 | 12.62 | 12.46
| Animal | Y | 32 | 31.47 | 30.99 | 30.55 | 18.75% | 18.75% | 18.75% | 6 | 5.9 | 5.81 | 5.73
| Vegetation | Y | 64 | 57.6 | 51.84 | 46.66 | 1.56% | 1.56% | 1.56% | 1 | 0.9 | 0.81 | 0.73
| Mylar balloon | Y | 9 | 9 | 9 | 9 | 0% | 0% | 0% | 0 | 0 | 0 | 0
| Car pole | Y | 25 | 25 | 25 | 25 | 16% | 16% | 16% | 4 | 4 | 4 | 4
| 3rd Party (foreign object /aircraft/ vandalism) | Y | 20 | 20 | 20 | 20 | 10% | 10% | 10% | 2 | 2 | 2 | 2
All types of equipment / facility failure - Transmission | All types of Equipment Failure | Y | 132 | 125.4 | 119.46 | 114.11 | 6.06% | 6.06% | 6.06% | 8 | 7.6 | 7.24 | 6.92
| Arrestor | Y | 0 | 0 | 0 | 0 | N/A | N/A | N/A | 0 | 0 | 0 | 0
| Insulator or Bushing | Y | 33 | 30.8 | 28.82 | 27.04 | 9.09% | 9.09% | 9.09% | 3 | 2.8 | 2.62 | 2.46
| Circuit breaker | Y | 8 | 8 | 8 | 8 | 0% | 0% | 0% | 0 | 0 | 0 | 0
| Conductor | Y | 35 | 35 | 35 | 35 | 2.86% | 2.86% | 2.86% | 1 | 1 | 1 | 1
| Connector/ hardware | Y | 13 | 13 | 13 | 13 | 7.69% | 7.69% | 7.69% | 1 | 1 | 1 | 1
| Other station | Y | 20 | 20 | 20 | 20 | 0% | 0% | 0% | 0 | 0 | 0 | 0
| Structure line | Y | 18 | 18 | 18 | 18 | 0% | 0% | 0% | 0 | 0 | 0 | 0
| Switch (line+station) | Y | 2 | 2 | 2 | 2 | 0% | 0% | 0% | 0 | 0 | 0 | 0
| Transformer | Y | 5 | 4.5 | 4.05 | 3.65 | 20% | 20% | 20% | 1 | 0.9 | 0.81 | 0.73
| Other Equipment | N/A | 0 | 0 | 0 | 0 | N/A | N/A | N/A | 2 | 1.9 | 1.81 | 1.73
Contamination | All types of contamination | Y | 11 | 11 | 11 | 11 | 0% | 0% | 0% | 0 | 0 | 0 | 0
Disaster | All Types of Disaster (all but 2 Fire) | Y | 13 | 13 | 13 | 13 | 0% | 0% | 0% | 0 | 0 | 0 | 0
Other | All types of Other (e.g., customer or IPP caused) | Y | 24 | 24 | 24 | 24 | 25% | 25% | 25% | 6 | 6 | 6 | 6
Unknown | Patrol Found No Cause, No Damage | Y | 138 | 138 | 138 | 138 | 0% | 0% | 0% | 0 | 0 | 0 | 0
Weather | All types of Weather | Y | 204 | 204 | 204 | 204 | 0% | 0% | 0% | 0 | 0 | 0 | 0
| Lightning | Y | 109 | 109 | 109 | 109 | 0% | 0% | 0% | 0 | 0 | 0 | 0
| Rain | Y | 23 | 23 | 23 | 23 | 0% | 0% | 0% | 0 | 0 | 0 | 0
| Snow/ Ice | Y | 61 | 61 | 61 | 61 | 0% | 0% | 0% | 0 | 0 | 0 | 0
| Wind | Y | 11 | 11 | 11 | 11 | 0% | 0% | 0% | 0 | 0 | 0 | 0
Work Procedure Error (WPE) | All types of WPE | Y | 21 | 21 | 21 | 21 | 0% | 0% | 0% | 0 | 0 | 0 | 0