## M2 ¦ SH SME Input
Pacific Gas and Electric Company
2020 RAMP Report
Failure of Electric Distribution Overhead Assets: Mitigation Effectiveness Workpaper - System Hardening SME Input
Line No. | Basic Cause | Supplemental Cause | Failed/Involved Equipment | Equipment Condition | System Hardening Effectiveness | Narrative
1 | 3rd Party |  | Anchor or Guy | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2 | 3rd Party |  | Conductor- Overhead | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3 | 3rd Party |  | Conductor- Overhead | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4 | 3rd Party |  | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
5 | 3rd Party |  | Fuse | Burned Open | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
6 | 3rd Party | Aircraft | Conductor- Overhead | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage. (Assumed Broken does not refer to conductor, this would be wire down/object),
7 | 3rd Party | Aircraft | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
8 | 3rd Party | Aircraft | Conductor- Overhead | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
9 | 3rd Party | Aircraft | Conductor- Overhead | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
10 | 3rd Party | Aircraft | Conductor- Overhead | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
11 | 3rd Party | Aircraft | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
12 | 3rd Party | Aircraft | Insulator | Broken | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
13 | 3rd Party | Aircraft | Jumper | Broken | High | Larger covered conductor to mostly eliminate cause and risk.
14 | 3rd Party | Aircraft | Pole-Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
15 | 3rd Party | Aircraft- crop dusting | Conductor- Overhead | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage. (Assumed Broken does not refer to conductor, this would be wire down/object),
16 | 3rd Party | Aircraft- crop dusting | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
17 | 3rd Party | Aircraft- crop dusting | Conductor- Overhead | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
18 | 3rd Party | Aircraft- crop dusting | Conductor- Overhead | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
19 | 3rd Party | Aircraft- crop dusting | Jumper | Burned Open | High | Larger covered conductor to mostly eliminate cause and risk.
20 | 3rd Party | Aircraft- crop dusting | Pole-Wood | Broken | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
21 | 3rd Party | Aircraft- crop dusting | Pole-Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
22 | 3rd Party | Aircraft- crop dusting | Transformer | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
23 | 3rd Party | Contact with High Voltage- 3rd party |  | Blown/failed | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
24 | 3rd Party | Contact with High Voltage- 3rd party | Conductor- Overhead | Annealed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
25 | 3rd Party | Contact with High Voltage- 3rd party | Conductor- Overhead | Arcing | All | New covered conductor will eliminate these contact type outages.
26 | 3rd Party | Contact with High Voltage- 3rd party | Conductor- Overhead | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage. (Assumed Broken does not refer to conductor, this would be wire down/object),
27 | 3rd Party | Contact with High Voltage- 3rd party | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
28 | 3rd Party | Contact with High Voltage- 3rd party | Conductor- Overhead | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
29 | 3rd Party | Contact with High Voltage- 3rd party | Conductor- Overhead | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
30 | 3rd Party | Contact with High Voltage- 3rd party | Conductor- Overhead | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
31 | 3rd Party | Contact with High Voltage- 3rd party | Conductor- Overhead | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
32 | 3rd Party | Contact with High Voltage- 3rd party | Conductor- Overhead | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
33 | 3rd Party | Contact with High Voltage- 3rd party | Conductor- Underground | Broken | None | Underground facilities = no ignition risk
34 | 3rd Party | Contact with High Voltage- 3rd party | Conductor- Underground | Burned/flashed | None | Underground facilities = no ignition risk
35 | 3rd Party | Contact with High Voltage- 3rd party | Connector or Splice (OH) | Normal | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
36 | 3rd Party | Contact with High Voltage- 3rd party | Elbow | Burned/flashed | All | Underground facilities = no ignition risk
37 | 3rd Party | Contact with High Voltage- 3rd party | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
38 | 3rd Party | Contact with High Voltage- 3rd party | Fuse | Normal | All | New covered wire would prevent wire contact
39 | 3rd Party | Contact with High Voltage- 3rd party | Other | Malfunctioning | None | Unknown equipment. Assume impact is great enough to cause outage.
40 | 3rd Party | Contact with High Voltage- 3rd party | Pole-Wood | Broken | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
41 | 3rd Party | Contact with High Voltage- 3rd party | Pole-Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
42 | 3rd Party | Contact with High Voltage- 3rd party | Pole-Wood | Normal | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
43 | 3rd Party | Contact with High Voltage- 3rd party | Pothead(Riser Termination) | Broken | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
44 | 3rd Party | Contact with High Voltage- 3rd party | Secondary | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
45 | 3rd Party | Contact with High Voltage- 3rd party | Secondary | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
46 | 3rd Party | Contact with High Voltage- 3rd party | Secondary | Burned Open | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
47 | 3rd Party | Contact with High Voltage- 3rd party | Secondary | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
48 | 3rd Party | Contact with High Voltage- 3rd party | Secondary | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
49 | 3rd Party | Contact with High Voltage- 3rd party | Service conductor | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
50 | 3rd Party | Contact with High Voltage- 3rd party | Transformer | Blown/failed | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
51 | 3rd Party | Contact with High Voltage- 3rd party | Transformer | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
52 | 3rd Party | Contact with High Voltage- 3rd party | Transformer | Normal | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
53 | 3rd Party | Contact with High Voltage- 3rd party | Transformer (UG) | Burned/flashed | All | Underground facilities = no ignition risk
54 | 3rd Party | Customer Equipment |  |  | None | No work is being completed on customer equipment.
55 | 3rd Party | Customer Equipment |  | Blown/failed | None | No work is being completed on customer equipment.
56 | 3rd Party | Customer Equipment |  | Normal | None | No work is being completed on customer equipment.
57 | 3rd Party | Customer Equipment | Anchor or Guy | Broken | None | No work is being completed on customer equipment.
58 | 3rd Party | Customer Equipment | Bus | Arcing | High | Transformers installed prior to 2014 will be replaced. Work would include covering jumpers and replacing some of the service conductor.
59 | 3rd Party | Customer Equipment | Bus | Blown/failed | High | Transformers installed prior to 2014 will be replaced. Work would include covering jumpers and replacing some of the service conductor.
60 | 3rd Party | Customer Equipment | Bus | Burned Open | None | No work is being completed on customer equipment.
61 | 3rd Party | Customer Equipment | Bus | Burned/flashed | None | No work is being completed on customer equipment.
62 | 3rd Party | Customer Equipment | Circuit Breaker | Arcing | Medium | System Hardening does not address substation equipment but coverered conductor will reduce annual breaker operations.
63 | 3rd Party | Customer Equipment | Circuit Breaker | Blown/failed | Medium | System Hardening does not address substation equipment but coverered conductor will reduce annual breaker operations.
64 | 3rd Party | Customer Equipment | Circuit Breaker | Broken | Medium | System Hardening does not address substation equipment but coverered conductor will reduce annual breaker operations.
65 | 3rd Party | Customer Equipment | Circuit Breaker | Burned/flashed | Medium | System Hardening does not address substation equipment but coverered conductor will reduce annual breaker operations.
66 | 3rd Party | Customer Equipment | Circuit Breaker | Malfunctioning | Medium | System Hardening does not address substation equipment but coverered conductor will reduce annual breaker operations.
67 | 3rd Party | Customer Equipment | Circuit Breaker | Normal | Medium | System Hardening does not address substation equipment but coverered conductor will reduce annual breaker operations.
68 | 3rd Party | Customer Equipment | Conductor- Overhead | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage.
69 | 3rd Party | Customer Equipment | Conductor- Overhead | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
70 | 3rd Party | Customer Equipment | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
71 | 3rd Party | Customer Equipment | Conductor- Overhead | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
72 | 3rd Party | Customer Equipment | Conductor- Overhead | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
73 | 3rd Party | Customer Equipment | Conductor- Overhead | Contaminated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
74 | 3rd Party | Customer Equipment | Conductor- Overhead | Deteriorated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
75 | 3rd Party | Customer Equipment | Conductor- Overhead | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
76 | 3rd Party | Customer Equipment | Conductor- Overhead | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
77 | 3rd Party | Customer Equipment | Conductor- Overhead | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
78 | 3rd Party | Customer Equipment | Conductor- Underground | Broken | All | Underground facilities = no ignition risk
79 | 3rd Party | Customer Equipment | Conductor- Underground | Burned/flashed | All | Underground facilities = no ignition risk
80 | 3rd Party | Customer Equipment | Conductor- Underground | Deteriorated | All | Underground facilities = no ignition risk
81 | 3rd Party | Customer Equipment | Conductor- Underground | Normal | All | Underground facilities = no ignition risk
82 | 3rd Party | Customer Equipment | Connector or Splice (OH) | Broken- wire on ground | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
83 | 3rd Party | Customer Equipment | Connector or Splice (OH) | Burned/flashed | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
84 | 3rd Party | Customer Equipment | Connector or Splice (OH) | Malfunctioning | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
85 | 3rd Party | Customer Equipment | Connector or Splice (OH) | Normal | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
86 | 3rd Party | Customer Equipment | Connector or Splice (UG) | Blown/failed | All | Underground facilities = no ignition risk
87 | 3rd Party | Customer Equipment | Connector or Splice (UG) | Burned/flashed | All | Underground facilities = no ignition risk
88 | 3rd Party | Customer Equipment | Connector or Splice (UG) | Normal | All | Underground facilities = no ignition risk
89 | 3rd Party | Customer Equipment | Crossarm- Wood | Broken | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
90 | 3rd Party | Customer Equipment | Customer Equipment | Arcing | None | No work is being completed on customer equipment.
91 | 3rd Party | Customer Equipment | Customer Equipment | Bent or Twisted | None | No work is being completed on customer equipment.
92 | 3rd Party | Customer Equipment | Customer Equipment | Blown/failed | None | No work is being completed on customer equipment.
93 | 3rd Party | Customer Equipment | Customer Equipment | Broken | None | No work is being completed on customer equipment.
94 | 3rd Party | Customer Equipment | Customer Equipment | Burned Open | None | No work is being completed on customer equipment.
95 | 3rd Party | Customer Equipment | Customer Equipment | Burned/flashed | None | No work is being completed on customer equipment.
96 | 3rd Party | Customer Equipment | Customer Equipment | Contaminated | None | No work is being completed on customer equipment.
97 | 3rd Party | Customer Equipment | Customer Equipment | Deteriorated | None | No work is being completed on customer equipment.
98 | 3rd Party | Customer Equipment | Customer Equipment | Malfunctioning | None | No work is being completed on customer equipment.
99 | 3rd Party | Customer Equipment | Customer Equipment | Normal | None | No work is being completed on customer equipment.
100 | 3rd Party | Customer Equipment | Customer Equipment | On Ground | None | No work is being completed on customer equipment.
101 | 3rd Party | Customer Equipment | Customer Equipment | Together | None | No work is being completed on customer equipment.
102 | 3rd Party | Customer Equipment | Cutout- fuse holder | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
103 | 3rd Party | Customer Equipment | Cutout- fuse holder | Broken | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
104 | 3rd Party | Customer Equipment | Cutout- fuse holder | Burned/flashed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
105 | 3rd Party | Customer Equipment | Cutout- fuse holder | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
106 | 3rd Party | Customer Equipment | Cutout- Fused- Distribution | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
107 | 3rd Party | Customer Equipment | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
108 | 3rd Party | Customer Equipment | Fuse | Normal | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
109 | 3rd Party | Customer Equipment | Generator | Malfunctioning | None | No work is being completed on customer equipment.
110 | 3rd Party | Customer Equipment | Generator | Normal | None | No work is being completed on customer equipment.
111 | 3rd Party | Customer Equipment | Insulator | Broken | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
112 | 3rd Party | Customer Equipment | Interrupter | Normal | All | Underground facilities = no ignition risk
113 | 3rd Party | Customer Equipment | Jumper | Broken | High | Larger covered conductor to mostly eliminate cause and risk.
114 | 3rd Party | Customer Equipment | Jumper | Burned Open | High | Larger covered conductor to mostly eliminate cause and risk.
115 | 3rd Party | Customer Equipment | Jumper | Burned/flashed | High | Larger covered conductor to mostly eliminate cause and risk.
116 | 3rd Party | Customer Equipment | Jumper | Normal | High | Larger covered conductor to mostly eliminate cause and risk.
117 | 3rd Party | Customer Equipment | Lightning Arrestor | Blown/failed | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
118 | 3rd Party | Customer Equipment | Metering Equipment | Arcing | None | System Hardening does not address Metering facilities.
119 | 3rd Party | Customer Equipment | Metering Equipment | Blown/failed | None | System Hardening does not address Metering facilities.
120 | 3rd Party | Customer Equipment | Metering Equipment | Broken | None | System Hardening does not address Metering facilities.
121 | 3rd Party | Customer Equipment | Metering Equipment | Burned/flashed | None | System Hardening does not address Metering facilities.
122 | 3rd Party | Customer Equipment | Metering Equipment | Deteriorated | None | System Hardening does not address Metering facilities.
123 | 3rd Party | Customer Equipment | Metering Equipment | Malfunctioning | None | System Hardening does not address Metering facilities.
124 | 3rd Party | Customer Equipment | Metering Equipment | Normal | None | System Hardening does not address Metering facilities.
125 | 3rd Party | Customer Equipment | Other | Arcing | None | No work is being completed on customer equipment.
126 | 3rd Party | Customer Equipment | Other | Blown/failed | None | No work is being completed on customer equipment.
127 | 3rd Party | Customer Equipment | Other | Broken | None | No work is being completed on customer equipment.
128 | 3rd Party | Customer Equipment | Other | Burned/flashed | None | No work is being completed on customer equipment.
129 | 3rd Party | Customer Equipment | Other | Contaminated | None | No work is being completed on customer equipment.
130 | 3rd Party | Customer Equipment | Other | Deteriorated | None | No work is being completed on customer equipment.
131 | 3rd Party | Customer Equipment | Other | Malfunctioning | None | No work is being completed on customer equipment.
132 | 3rd Party | Customer Equipment | Other | Normal | None | No work is being completed on customer equipment.
133 | 3rd Party | Customer Equipment | Other | Together | None | No work is being completed on customer equipment.
134 | 3rd Party | Customer Equipment | Pole-Wood | Broken | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
135 | 3rd Party | Customer Equipment | Pole-Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
136 | 3rd Party | Customer Equipment | Pole-Wood | Burned/flashed | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
137 | 3rd Party | Customer Equipment | Pole-Wood | Deteriorated | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
138 | 3rd Party | Customer Equipment | Pole-Wood | Normal | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
139 | 3rd Party | Customer Equipment | Pole-Wood | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
140 | 3rd Party | Customer Equipment | Pothead(Riser Termination) | Blown/failed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
141 | 3rd Party | Customer Equipment | PT/CCVT | Blown/failed | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
142 | 3rd Party | Customer Equipment | PT/CCVT | Broken | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
143 | 3rd Party | Customer Equipment | Recloser | Arcing | Medium | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters but coverered conductor will reduce annual number of operations/duty cycle.
144 | 3rd Party | Customer Equipment | Recloser | Blown/failed | Medium | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters but coverered conductor will reduce annual number of operations/duty cycle.
145 | 3rd Party | Customer Equipment | Recloser | Broken | Medium | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters but coverered conductor will reduce annual number of operations/duty cycle.
146 | 3rd Party | Customer Equipment | Recloser | Burned/flashed | Medium | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters but coverered conductor will reduce annual number of operations/duty cycle.
147 | 3rd Party | Customer Equipment | Recloser | Normal | Medium | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters but coverered conductor will reduce annual number of operations/duty cycle.
148 | 3rd Party | Customer Equipment | Riser | Burned/flashed | High | Risers are indirectly addressed on System Hardening - Pole changeouts, the covering of jumpers and leads, along with covering conductor should mitigate outages and risk.
149 | 3rd Party | Customer Equipment | Secondary | Arcing | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
150 | 3rd Party | Customer Equipment | Secondary | Blown/failed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
151 | 3rd Party | Customer Equipment | Secondary | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
152 | 3rd Party | Customer Equipment | Secondary | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
153 | 3rd Party | Customer Equipment | Secondary | Burned Open | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
154 | 3rd Party | Customer Equipment | Secondary | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
155 | 3rd Party | Customer Equipment | Secondary | Contaminated | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
156 | 3rd Party | Customer Equipment | Secondary | Deteriorated | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
157 | 3rd Party | Customer Equipment | Secondary | Malfunctioning | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
158 | 3rd Party | Customer Equipment | Secondary | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
159 | 3rd Party | Customer Equipment | Service conductor | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
160 | 3rd Party | Customer Equipment | Service conductor | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
161 | 3rd Party | Customer Equipment | Service conductor | Deteriorated | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
162 | 3rd Party | Customer Equipment | Service conductor | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
163 | 3rd Party | Customer Equipment | Switch | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
164 | 3rd Party | Customer Equipment | Switch | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
165 | 3rd Party | Customer Equipment | Switch (OH) | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
166 | 3rd Party | Customer Equipment | Switch (OH) | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
167 | 3rd Party | Customer Equipment | Switch (OH) | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
168 | 3rd Party | Customer Equipment | Switch (UG) | Blown/failed | All | Underground facilities = no ignition risk
169 | 3rd Party | Customer Equipment | Switch (UG) | Normal | All | Underground facilities = no ignition risk
170 | 3rd Party | Customer Equipment | Transformer | Arcing | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
171 | 3rd Party | Customer Equipment | Transformer | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
172 | 3rd Party | Customer Equipment | Transformer | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
173 | 3rd Party | Customer Equipment | Transformer | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
174 | 3rd Party | Customer Equipment | Transformer | Burned Open | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
175 | 3rd Party | Customer Equipment | Transformer | Burned/flashed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
176 | 3rd Party | Customer Equipment | Transformer | Deteriorated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
177 | 3rd Party | Customer Equipment | Transformer | Leaking | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
178 | 3rd Party | Customer Equipment | Transformer | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
179 | 3rd Party | Customer Equipment | Transformer | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
180 | 3rd Party | Customer Equipment | Transformer (OH) | Arcing | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
181 | 3rd Party | Customer Equipment | Transformer (OH) | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
182 | 3rd Party | Customer Equipment | Transformer (OH) | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
183 | 3rd Party | Customer Equipment | Transformer (OH) | Burned/flashed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
184 | 3rd Party | Customer Equipment | Transformer (OH) | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
185 | 3rd Party | Customer Equipment | Transformer (UG) | Blown/failed | All | Underground facilities = no ignition risk
186 | 3rd Party | Customer Equipment | Transformer (UG) | Broken | All | Underground facilities = no ignition risk
187 | 3rd Party | Customer Equipment | Transformer (UG) | Burned/flashed | All | Underground facilities = no ignition risk
188 | 3rd Party | Customer Equipment | Transformer (UG) | Deteriorated | All | Underground facilities = no ignition risk
189 | 3rd Party | Customer Equipment | Transformer (UG) | Normal | All | Underground facilities = no ignition risk
190 | 3rd Party | Dig in- 3rd party | Anchor or Guy | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
191 | 3rd Party | Dig in- 3rd party | Bushing | Broken | All | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks. Work will cover leads and jumpers.
192 | 3rd Party | Dig in- 3rd party | Cable Termination(live front | Broken | All | Underground facilities = no ignition risk
193 | 3rd Party | Dig in- 3rd party | Conductor- Overhead | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
194 | 3rd Party | Dig in- 3rd party | Conductor- Overhead | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
195 | 3rd Party | Dig in- 3rd party | Conductor- Overhead | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
196 | 3rd Party | Dig in- 3rd party | Conductor- Underground | Bent or Twisted | All | Underground facilities = no ignition risk
197 | 3rd Party | Dig in- 3rd party | Conductor- Underground | Blown/failed | All | Underground facilities = no ignition risk
198 | 3rd Party | Dig in- 3rd party | Conductor- Underground | Broken | All | Underground facilities = no ignition risk
199 | 3rd Party | Dig in- 3rd party | Conductor- Underground | Burned Open | All | Underground facilities = no ignition risk
200 | 3rd Party | Dig in- 3rd party | Conductor- Underground | Burned/flashed | All | Underground facilities = no ignition risk
201 | 3rd Party | Dig in- 3rd party | Conductor- Underground | Contaminated | All | Underground facilities = no ignition risk
202 | 3rd Party | Dig in- 3rd party | Conductor- Underground | Deteriorated | All | Underground facilities = no ignition risk
203 | 3rd Party | Dig in- 3rd party | Conductor- Underground | Normal | All | Underground facilities = no ignition risk
204 | 3rd Party | Dig in- 3rd party | Connector or Splice (OH) | Broken | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
205 | 3rd Party | Dig in- 3rd party | Connector or Splice (OH) | Broken- wire on ground | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
206 | 3rd Party | Dig in- 3rd party | Connector or Splice (UG) | Blown/failed | All | Underground facilities = no ignition risk
207 | 3rd Party | Dig in- 3rd party | Connector or Splice (UG) | Broken | All | Underground facilities = no ignition risk
208 | 3rd Party | Dig in- 3rd party | Crossarm- Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
209 | 3rd Party | Dig in- 3rd party | Customer Equipment | Broken | None | No work is being completed on customer equipment.
210 | 3rd Party | Dig in- 3rd party | Customer Equipment | Malfunctioning | None | No work is being completed on customer equipment.
211 | 3rd Party | Dig in- 3rd party | Cutout- fuse holder | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
212 | 3rd Party | Dig in- 3rd party | Elbow | Broken | All | Underground facilities = no ignition risk
213 | 3rd Party | Dig in- 3rd party | Elbow | Burned/flashed | All | Underground facilities = no ignition risk
214 | 3rd Party | Dig in- 3rd party | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
215 | 3rd Party | Dig in- 3rd party | Other | Bent or Twisted | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil.
216 | 3rd Party | Dig in- 3rd party | Other | Blown/failed | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil.
217 | 3rd Party | Dig in- 3rd party | Other | Broken | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil.
218 | 3rd Party | Dig in- 3rd party | Other | Leaking | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil.
219 | 3rd Party | Dig in- 3rd party | Other | Normal | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil.
220 | 3rd Party | Dig in- 3rd party | Pole-Wood | Broken | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
221 | 3rd Party | Dig in- 3rd party | Pole-Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
222 | 3rd Party | Dig in- 3rd party | Pole-Wood | Deteriorated | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
223 | 3rd Party | Dig in- 3rd party | Pole-Wood | Malfunctioning | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
224 | 3rd Party | Dig in- 3rd party | Pole-Wood | Normal | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
225 | 3rd Party | Dig in- 3rd party | Secondary | Bent or Twisted | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
226 | 3rd Party | Dig in- 3rd party | Secondary | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
227 | 3rd Party | Dig in- 3rd party | Secondary | Burned Open | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
228 | 3rd Party | Dig in- 3rd party | Secondary | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
229 | 3rd Party | Dig in- 3rd party | Secondary | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
230 | 3rd Party | Dig in- 3rd party | Service conductor | Bent or Twisted | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
231 | 3rd Party | Dig in- 3rd party | Service conductor | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
232 | 3rd Party | Dig in- 3rd party | Service conductor | Burned Open | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
233 | 3rd Party | Dig in- 3rd party | Switch | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
234 | 3rd Party | Dig in- 3rd party | Switch (UG) | Broken | All | Underground facilities = no ignition risk.
235 | 3rd Party | Dig in- 3rd party | Switch (UG) | Normal | All | Underground facilities = no ignition risk.
236 | 3rd Party | Dig in- 3rd party | Transformer | Broken | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
237 | 3rd Party | Dig in- 3rd party | Transformer | Burned Open | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
238 | 3rd Party | Dig in- 3rd party | Transformer | Burned/flashed | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
239 | 3rd Party | Dig in- 3rd party | Transformer | Leaking | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
240 | 3rd Party | Dig in- 3rd party | Transformer | Malfunctioning | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
241 | 3rd Party | Dig in- 3rd party | Transformer (OH) | Blown/failed | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
242 | 3rd Party | Dig in- 3rd party | Transformer (UG) | Blown/failed | All | Underground facilities = no ignition risk
243 | 3rd Party | Dig in- 3rd party | Transformer (UG) | Broken | All | Underground facilities = no ignition risk
244 | 3rd Party | Dig in- 3rd party | Transformer (UG) | Leaking | All | Underground facilities = no ignition risk
245 | 3rd Party | Dig in- 3rd party | Transformer (UG) | Normal | All | Underground facilities = no ignition risk
246 | 3rd Party | Fire- house or bldg. |  |  | All | 3rd party fire impacting PGE equipment. Not enough outage information or correct information in ILIS to determine effect of System Hardening
247 | 3rd Party | Fire- house or bldg. |  | Blown/failed | All | 3rd party fire impacting PGE equipment. Not enough outage information or correct information in ILIS to determine effect of System Hardening
248 | 3rd Party | Fire- house or bldg. | Circuit Breaker | Normal | None | 3rd party fire impacting PGE equipment
249 | 3rd Party | Fire- house or bldg. | Conductor- Overhead | Broken | None | 3rd party fire impacting PGE equipment
250 | 3rd Party | Fire- house or bldg. | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
251 | 3rd Party | Fire- house or bldg. | Conductor- Overhead | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
252 | 3rd Party | Fire- house or bldg. | Conductor- Overhead | Burned/flashed | None | 3rd party fire impacting PGE equipment
253 | 3rd Party | Fire- house or bldg. | Conductor- Overhead | Normal | None | 3rd party fire impacting PGE equipment
254 | 3rd Party | Fire- house or bldg. | Conductor- Overhead | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
255 | 3rd Party | Fire- house or bldg. | Conductor- Overhead | Together | None | 3rd party fire impacting PGE equipment
256 | 3rd Party | Fire- house or bldg. | Conductor- Underground | Broken | None | 3rd party fire impacting PGE equipment
257 | 3rd Party | Fire- house or bldg. | Conductor- Underground | Burned/flashed | None | 3rd party fire impacting PGE equipment
258 | 3rd Party | Fire- house or bldg. | Conductor- Underground | Normal | None | 3rd party fire impacting PGE equipment
259 | 3rd Party | Fire- house or bldg. | Connector or Splice (OH) | Burned Open | None | 3rd party fire impacting PGE equipment
260 | 3rd Party | Fire- house or bldg. | Crossarm- Wood | Broken | None | 3rd party fire impacting PGE equipment
261 | 3rd Party | Fire- house or bldg. | Crossarm- Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
262 | 3rd Party | Fire- house or bldg. | Crossarm- Wood | Burned/flashed | None | 3rd party fire impacting PGE equipment
263 | 3rd Party | Fire- house or bldg. | Customer Equipment | Arcing | None | 3rd party fire impacting PGE equipment
264 | 3rd Party | Fire- house or bldg. | Customer Equipment | Burned Open | None | 3rd party fire impacting PGE equipment
265 | 3rd Party | Fire- house or bldg. | Customer Equipment | Burned/flashed | None | 3rd party fire impacting PGE equipment
266 | 3rd Party | Fire- house or bldg. | Customer Equipment | Malfunctioning | None | 3rd party fire impacting PGE equipment
267 | 3rd Party | Fire- house or bldg. | Customer Equipment | Normal | None | 3rd party fire impacting PGE equipment
268 | 3rd Party | Fire- house or bldg. | Cutout- fuse holder | Blown/failed | None | 3rd party fire impacting PGE equipment
269 | 3rd Party | Fire- house or bldg. | Cutout- fuse holder | Broken | None | 3rd party fire impacting PGE equipment
270 | 3rd Party | Fire- house or bldg. | Cutout- fuse holder | Burned/flashed | None | 3rd party fire impacting PGE equipment
271 | 3rd Party | Fire- house or bldg. | Cutout- Fused- Distribution | Blown/failed | None | 3rd party fire impacting PGE equipment
272 | 3rd Party | Fire- house or bldg. | Fuse | Blown/failed | None | 3rd party fire impacting PGE equipment
273 | 3rd Party | Fire- house or bldg. | Fuse | Normal | None | 3rd party fire impacting PGE equipment
274 | 3rd Party | Fire- house or bldg. | Jumper | Broken | None | 3rd party fire impacting PGE equipment
275 | 3rd Party | Fire- house or bldg. | Jumper | Normal | None | 3rd party fire impacting PGE equipment
276 | 3rd Party | Fire- house or bldg. | Other | Arcing | None | 3rd party fire impacting PGE equipment
277 | 3rd Party | Fire- house or bldg. | Other | Burned/flashed | None | 3rd party fire impacting PGE equipment
278 | 3rd Party | Fire- house or bldg. | Other | Normal | None | 3rd party fire impacting PGE equipment
279 | 3rd Party | Fire- house or bldg. | Pole-Wood | Broken | None | 3rd party fire impacting PGE equipment
280 | 3rd Party | Fire- house or bldg. | Pole-Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
281 | 3rd Party | Fire- house or bldg. | Pole-Wood | Burned/flashed | None | 3rd party fire impacting PGE equipment
282 | 3rd Party | Fire- house or bldg. | Pole-Wood | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
283 | 3rd Party | Fire- house or bldg. | Pothead(Riser Termination) | Burned/flashed | None | 3rd party fire impacting PGE equipment
284 | 3rd Party | Fire- house or bldg. | Secondary | Arcing | None | 3rd party fire impacting PGE equipment
285 | 3rd Party | Fire- house or bldg. | Secondary | Broken | None | 3rd party fire impacting PGE equipment
286 | 3rd Party | Fire- house or bldg. | Secondary | Broken- wire on ground | None | 3rd party fire impacting PGE equipment
287 | 3rd Party | Fire- house or bldg. | Secondary | Burned Open | None | 3rd party fire impacting PGE equipment
288 | 3rd Party | Fire- house or bldg. | Secondary | Burned/flashed | None | 3rd party fire impacting PGE equipment
289 | 3rd Party | Fire- house or bldg. | Secondary | Normal | None | 3rd party fire impacting PGE equipment
290 | 3rd Party | Fire- house or bldg. | Secondary | On Ground | None | 3rd party fire impacting PGE equipment
291 | 3rd Party | Fire- house or bldg. | Secondary | Together | None | 3rd party fire impacting PGE equipment
292 | 3rd Party | Fire- house or bldg. | Service conductor | Arcing | None | 3rd party fire impacting PGE equipment
293 | 3rd Party | Fire- house or bldg. | Service conductor | Broken | None | 3rd party fire impacting PGE equipment
294 | 3rd Party | Fire- house or bldg. | Service conductor | Broken- wire on ground | None | 3rd party fire impacting PGE equipment
295 | 3rd Party | Fire- house or bldg. | Service conductor | Broken- wire on object | None | 3rd party fire impacting PGE equipment
296 | 3rd Party | Fire- house or bldg. | Service conductor | Burned Open | None | 3rd party fire impacting PGE equipment
297 | 3rd Party | Fire- house or bldg. | Service conductor | Burned/flashed | None | 3rd party fire impacting PGE equipment
298 | 3rd Party | Fire- house or bldg. | Service conductor | Normal | None | 3rd party fire impacting PGE equipment
299 | 3rd Party | Fire- house or bldg. | Service conductor | Together | None | 3rd party fire impacting PGE equipment
300 | 3rd Party | Fire- house or bldg. | Switch | Blown/failed | None | 3rd party fire impacting PGE equipment
301 | 3rd Party | Fire- house or bldg. | Switch (OH) | Normal | None | 3rd party fire impacting PGE equipment
302 | 3rd Party | Fire- house or bldg. | Switch (UG) | Normal | All | 3rd party fire impacting PGE equipment. Underground facilities = no ignition risk
303 | 3rd Party | Fire- house or bldg. | Transformer | Blown/failed | None | 3rd party fire impacting PGE equipment
304 | 3rd Party | Fire- house or bldg. | Transformer | Burned Open | None | 3rd party fire impacting PGE equipment
305 | 3rd Party | Fire- house or bldg. | Transformer | Burned/flashed | None | 3rd party fire impacting PGE equipment
306 | 3rd Party | Fire- house or bldg. | Transformer | Normal | None | 3rd party fire impacting PGE equipment
307 | 3rd Party | Fire- house or bldg. | Transformer (OH) | Arcing | None | 3rd party fire impacting PGE equipment
308 | 3rd Party | Fire- house or bldg. | Transformer (OH) | Blown/failed | None | 3rd party fire impacting PGE equipment
309 | 3rd Party | Fire- house or bldg. | Transformer (OH) | Broken | None | 3rd party fire impacting PGE equipment
310 | 3rd Party | Fire- house or bldg. | Transformer (OH) | Burned/flashed | None | 3rd party fire impacting PGE equipment
311 | 3rd Party | Fire- house or bldg. | Transformer (OH) | Normal | None | 3rd party fire impacting PGE equipment
312 | 3rd Party | Fire- house or bldg. | Transformer (UG) | Burned/flashed | All | 3rd party fire impacting PGE equipment. Underground facilities = no ignition risk
313 | 3rd Party | Fire- house or bldg. | Transformer (UG) | Contaminated | All | 3rd party fire impacting PGE equipment. Underground facilities = no ignition risk
314 | 3rd Party | Fire- house or bldg. | Transformer (UG) | Normal | All | 3rd party fire impacting PGE equipment. Underground facilities = no ignition risk
315 | 3rd Party | Gun Shot | Booster | Leaking | None | Covered wire will not prevent gun shot damage
316 | 3rd Party | Gun Shot | Conductor- Overhead | Annealed | None | Covered wire will not prevent gun shot damage
317 | 3rd Party | Gun Shot | Conductor- Overhead | Broken | None | Covered wire will not prevent gun shot damage
318 | 3rd Party | Gun Shot | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
319 | 3rd Party | Gun Shot | Conductor- Overhead | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
320 | 3rd Party | Gun Shot | Conductor- Overhead | Deteriorated | None | Covered wire will not prevent gun shot damage
321 | 3rd Party | Gun Shot | Conductor- Overhead | Normal | None | Covered wire will not prevent gun shot damage
322 | 3rd Party | Gun Shot | Conductor- Overhead | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
323 | 3rd Party | Gun Shot | Conductor- Overhead | Together | None | Covered wire will not prevent gun shot damage
324 | 3rd Party | Gun Shot | Conductor- Underground | Broken | None | Covered wire will not prevent gun shot damage
325 | 3rd Party | Gun Shot | Conductor- Underground | Burned/flashed | None | Covered wire will not prevent gun shot damage
326 | 3rd Party | Gun Shot | Connector or Splice (OH) | Broken- wire on ground | None | Covered wire will not prevent gun shot damage
327 | 3rd Party | Gun Shot | Crossarm- Wood | Broken | None | Covered wire will not prevent gun shot damage
328 | 3rd Party | Gun Shot | Fuse | Blown/failed | None | Covered wire will not prevent gun shot damage
329 | 3rd Party | Gun Shot | Fuse | Normal | None | Covered wire will not prevent gun shot damage
330 | 3rd Party | Gun Shot | Insulator | Blown/failed | None | Covered wire will not prevent gun shot damage
331 | 3rd Party | Gun Shot | Insulator | Broken | None | Covered wire will not prevent gun shot damage
332 | 3rd Party | Gun Shot | Insulator | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
333 | 3rd Party | Gun Shot | Jumper | Broken | None | Covered wire will not prevent gun shot damage
334 | 3rd Party | Gun Shot | Pole-Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
335 | 3rd Party | Gun Shot | Pothead(Riser Termination) | Blown/failed | None | Covered wire will not prevent gun shot damage
336 | 3rd Party | Gun Shot | Recloser | Broken | None | Covered wire will not prevent gun shot damage
337 | 3rd Party | Gun Shot | Regulator | Leaking | None | Covered wire will not prevent gun shot damage
338 | 3rd Party | Gun Shot | Secondary | Broken | None | Covered wire will not prevent gun shot damage
339 | 3rd Party | Gun Shot | Secondary | Broken- wire on ground | None | Covered wire will not prevent gun shot damage
340 | 3rd Party | Gun Shot | Secondary | On Ground | None | Covered wire will not prevent gun shot damage
341 | 3rd Party | Gun Shot | Transformer | Blown/failed | None | Covered wire will not prevent gun shot damage
342 | 3rd Party | Gun Shot | Transformer | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
343 | 3rd Party | Gun Shot | Transformer | Burned/flashed | None | Covered wire will not prevent gun shot damage
344 | 3rd Party | Gun Shot | Transformer | Deteriorated | None | Covered wire will not prevent gun shot damage
345 | 3rd Party | Gun Shot | Transformer | Leaking | None | Covered wire will not prevent gun shot damage
346 | 3rd Party | Gun Shot | Transformer (OH) | Blown/failed | None | Covered wire will not prevent gun shot damage
347 | 3rd Party | Gun Shot | Transformer (OH) | Leaking | None | Covered wire will not prevent gun shot damage
348 | 3rd Party | Kite | Circuit Breaker | Normal | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
349 | 3rd Party | Kite | Conductor- Overhead | Bent or Twisted | All | New covered conductor will eliminate these contact type outages.
350 | 3rd Party | Kite | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
351 | 3rd Party | Kite | Conductor- Overhead | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
352 | 3rd Party | Kite | Conductor- Overhead | Burned Open | All | Covered conductor will eliminate the line slap and risk associated with this outage.
353 | 3rd Party | Kite | Conductor- Overhead | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
354 | 3rd Party | Kite | Conductor- Overhead | Contaminated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
355 | 3rd Party | Kite | Conductor- Overhead | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
356 | 3rd Party | Kite | Conductor- Overhead | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
357 | 3rd Party | Kite | Conductor- Overhead | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
358 | 3rd Party | Kite | Cutout- fuse holder | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
359 | 3rd Party | Kite | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
360 | 3rd Party | Kite | Fuse | Normal | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
361 | 3rd Party | Kite | Jumper | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
362 | 3rd Party | Kite | Jumper | Burned Open | High | Larger covered conductor to mostly eliminate cause and risk.
363 | 3rd Party | Kite | Lightning Arrestor | Burned/flashed | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
364 | 3rd Party | Kite | Other | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
365 | 3rd Party | Kite | Recloser | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
366 | 3rd Party | Metallic Balloon |  | Blown/failed | None | Unknown what failed
367 | 3rd Party | Metallic Balloon |  | Normal | All | New covered conductor will eliminate these contact type outages.
368 | 3rd Party | Metallic Balloon | Bushing | Blown/failed | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks. Work will cover leads and jumpers.
369 | 3rd Party | Metallic Balloon | Bushing | Burned/flashed | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks. Work will cover leads and jumpers.
370 | 3rd Party | Metallic Balloon | Bushing | Normal | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks. Work will cover leads and jumpers.
371 | 3rd Party | Metallic Balloon | Capacitor | Blown/failed | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
372 | 3rd Party | Metallic Balloon | Capacitor | Burned/flashed | None | System Hardening would not address this outage
373 | 3rd Party | Metallic Balloon | Circuit Breaker | Normal | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
374 | 3rd Party | Metallic Balloon | Conductor- Overhead | Arcing | All | New covered conductor will eliminate these contact type outages.
375 | 3rd Party | Metallic Balloon | Conductor- Overhead | Bent or Twisted | All | New covered conductor will eliminate these contact type outages.
376 | 3rd Party | Metallic Balloon | Conductor- Overhead | Blown/failed | All | New covered conductor will eliminate these contact type outages.
377 | 3rd Party | Metallic Balloon | Conductor- Overhead | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
378 | 3rd Party | Metallic Balloon | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
379 | 3rd Party | Metallic Balloon | Conductor- Overhead | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
380 | 3rd Party | Metallic Balloon | Conductor- Overhead | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
381 | 3rd Party | Metallic Balloon | Conductor- Overhead | Contaminated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
382 | 3rd Party | Metallic Balloon | Conductor- Overhead | Deteriorated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
383 | 3rd Party | Metallic Balloon | Conductor- Overhead | Malfunctioning | All | Covered conductor will eliminate the line slap and risk associated with this outage.
384 | 3rd Party | Metallic Balloon | Conductor- Overhead | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
385 | 3rd Party | Metallic Balloon | Conductor- Overhead | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
386 | 3rd Party | Metallic Balloon | Conductor- Overhead | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
387 | 3rd Party | Metallic Balloon | Conductor- Underground | Normal | All | Underground facilities = no ignition risk
388 | 3rd Party | Metallic Balloon | Connector or Splice (OH) | Broken | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
389 | 3rd Party | Metallic Balloon | Connector or Splice (OH) | Broken- wire on ground | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
390 | 3rd Party | Metallic Balloon | Connector or Splice (OH) | Burned Open | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
391 | 3rd Party | Metallic Balloon | Connector or Splice (OH) | Normal | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
392 | 3rd Party | Metallic Balloon | Crossarm- Wood | Broken | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
393 | 3rd Party | Metallic Balloon | Crossarm- Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
394 | 3rd Party | Metallic Balloon | Crossarm- Wood | Burned/flashed | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
395 | 3rd Party | Metallic Balloon | Cutout- fuse holder | Arcing | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
396 | 3rd Party | Metallic Balloon | Cutout- fuse holder | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
397 | 3rd Party | Metallic Balloon | Cutout- fuse holder | Broken | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
398 | 3rd Party | Metallic Balloon | Cutout- fuse holder | Burned/flashed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
399 | 3rd Party | Metallic Balloon | Cutout- fuse holder | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
400 | 3rd Party | Metallic Balloon | Cutout- Fused- Distribution | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
401 | 3rd Party | Metallic Balloon | Fuse | Arcing | High | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
402 | 3rd Party | Metallic Balloon | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
403 | 3rd Party | Metallic Balloon | Fuse | Broken | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
404 | 3rd Party | Metallic Balloon | Fuse | Burned Open | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
405 | 3rd Party | Metallic Balloon | Fuse | Normal | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
406 | 3rd Party | Metallic Balloon | Insulator | Blown/failed | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
407 | 3rd Party | Metallic Balloon | Insulator | Broken | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
408 | 3rd Party | Metallic Balloon | Insulator | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
409 | 3rd Party | Metallic Balloon | Insulator | Burned/flashed | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
410 | 3rd Party | Metallic Balloon | Interrupter | Normal | All | Underground facilities = no ignition risk
411 | 3rd Party | Metallic Balloon | Jumper | Broken | High | Larger covered conductor to mostly eliminate cause and risk.
412 | 3rd Party | Metallic Balloon | Jumper | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
413 | 3rd Party | Metallic Balloon | Jumper | Burned Open | High | Larger covered conductor to mostly eliminate cause and risk.
414 | 3rd Party | Metallic Balloon | Jumper | Burned/flashed | High | Larger covered conductor to mostly eliminate cause and risk.
415 | 3rd Party | Metallic Balloon | Jumper | Normal | High | Larger covered conductor to mostly eliminate cause and risk.
416 | 3rd Party | Metallic Balloon | Lightning Arrestor | Blown/failed | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
417 | 3rd Party | Metallic Balloon | Other | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
418 | 3rd Party | Metallic Balloon | Pole-Wood | Broken | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
419 | 3rd Party | Metallic Balloon | Pole-Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
420 | 3rd Party | Metallic Balloon | Pole-Wood | Burned/flashed | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
421 | 3rd Party | Metallic Balloon | Pothead(Riser Termination) | Blown/failed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
422 | 3rd Party | Metallic Balloon | Pothead(Riser Termination) | Burned/flashed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
423 | 3rd Party | Metallic Balloon | Pothead(Riser Termination) | Normal | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
424 | 3rd Party | Metallic Balloon | Pothead/Riser Termination | Blown/failed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
425 | 3rd Party | Metallic Balloon | Recloser | Malfunctioning | Medium | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters but coverered conductor will reduce annual number of operations/duty cycle.
426 | 3rd Party | Metallic Balloon | Recloser | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
427 | 3rd Party | Metallic Balloon | Riser | Burned/flashed | High | Risers are indirectly addressed on System Hardening - Pole changeouts, the covering of jumpers and leads, along with covering conductor should mitigate outages and risk.
428 | 3rd Party | Metallic Balloon | Riser | Normal | High | Risers are indirectly addressed on System Hardening - Pole changeouts, the covering of jumpers and leads, along with covering conductor should mitigate outages and risk.
429 | 3rd Party | Metallic Balloon | Secondary | Arcing | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
430 | 3rd Party | Metallic Balloon | Secondary | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
431 | 3rd Party | Metallic Balloon | Secondary | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
432 | 3rd Party | Metallic Balloon | Secondary | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
433 | 3rd Party | Metallic Balloon | Switch (OH) | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
434 | 3rd Party | Metallic Balloon | Switch (OH) | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
435 | 3rd Party | Metallic Balloon | Switch (OH) | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
436 | 3rd Party | Metallic Balloon | Switch (OH) | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
437 | 3rd Party | Metallic Balloon | Transformer | Arcing | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
438 | 3rd Party | Metallic Balloon | Transformer | Blown/failed | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
439 | 3rd Party | Metallic Balloon | Transformer | Broken | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
440 | 3rd Party | Metallic Balloon | Transformer | Burned Open | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
441 | 3rd Party | Metallic Balloon | Transformer | Burned/flashed | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
442 | 3rd Party | Metallic Balloon | Transformer | Leaking | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
443 | 3rd Party | Metallic Balloon | Transformer | Normal | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
444 | 3rd Party | Metallic Balloon | Transformer (OH) | Arcing | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
445 | 3rd Party | Metallic Balloon | Transformer (OH) | Blown/failed | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
446 | 3rd Party | Metallic Balloon | Transformer (OH) | Broken | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
447 | 3rd Party | Metallic Balloon | Transformer (OH) | Burned/flashed | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
448 | 3rd Party | Metallic Balloon | Transformer (OH) | Contaminated | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
449 | 3rd Party | Metallic Balloon | Transformer (OH) | Leaking | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
450 | 3rd Party | Metallic Balloon | Transformer (OH) | Normal | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
451 | 3rd Party | Metallic Balloon | Transformer (UG) | Broken | All | Underground facilities = no ignition risk
452 | 3rd Party | Other | Anchor or Guy | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage.
453 | 3rd Party | Other | Anchor or Guy | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
454 | 3rd Party | Other | Anchor or Guy | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
455 | 3rd Party | Other | Bushing | Burned/flashed | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks. Work will cover leads and jumpers.
456 | 3rd Party | Other | Cable Termination(live front | Normal | All | Underground facilities = no ignition risk
457 | 3rd Party | Other | Circuit Breaker | Normal | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
458 | 3rd Party | Other | Conductor- Overhead | Annealed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
459 | 3rd Party | Other | Conductor- Overhead | Arcing | All | New covered conductor will eliminate these contact type outages.
460 | 3rd Party | Other | Conductor- Overhead | Bent or Twisted | All | New covered conductor will eliminate these contact type outages.
461 | 3rd Party | Other | Conductor- Overhead | Blown/failed | All | New covered conductor will eliminate these contact type outages.
462 | 3rd Party | Other | Conductor- Overhead | Broken | All | New covered conductor will eliminate these contact type outages.
463 | 3rd Party | Other | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
464 | 3rd Party | Other | Conductor- Overhead | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
465 | 3rd Party | Other | Conductor- Overhead | Contaminated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
466 | 3rd Party | Other | Conductor- Overhead | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
467 | 3rd Party | Other | Conductor- Overhead | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
468 | 3rd Party | Other | Conductor- Overhead | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
469 | 3rd Party | Other | Conductor- Underground | Broken | All | Underground facilities = no ignition risk
470 | 3rd Party | Other | Conductor- Underground | Burned/flashed | All | Underground facilities = no ignition risk
471 | 3rd Party | Other | Conductor- Underground | Contaminated | All | Underground facilities = no ignition risk
472 | 3rd Party | Other | Conductor- Underground | Normal | All | Underground facilities = no ignition risk
473 | 3rd Party | Other | Connector or Splice (OH) | Broken | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
474 | 3rd Party | Other | Connector or Splice (OH) | Broken- wire on ground | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
475 | 3rd Party | Other | Crossarm- Wood | Broken | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
476 | 3rd Party | Other | Crossarm- Wood | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
477 | 3rd Party | Other | Crossarm- Wood | Burned/flashed | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
478 | 3rd Party | Other | Crossarm- Wood | Normal | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
479 | 3rd Party | Other | Customer Equipment | Blown/failed | None | No work is being completed on customer equipment.
480 | 3rd Party | Other | Customer Equipment | Broken | None | No work is being completed on customer equipment.
481 | 3rd Party | Other | Customer Equipment | Burned/flashed | None | No work is being completed on customer equipment.
482 | 3rd Party | Other | Customer Equipment | Leaking | None | No work is being completed on customer equipment.
483 | 3rd Party | Other | Customer Equipment | Malfunctioning | None | No work is being completed on customer equipment.
484 | 3rd Party | Other | Customer Equipment | Normal | None | No work is being completed on customer equipment.
485 | 3rd Party | Other | Customer Equipment | On Ground | None | No work is being completed on customer equipment.
486 | 3rd Party | Other | Cutout- fuse holder | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
487 | 3rd Party | Other | Cutout- fuse holder | Broken | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
488 | 3rd Party | Other | Cutout- fuse holder | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
489 | 3rd Party | Other | Cutout- fuse holder | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
490 | 3rd Party | Other | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
491 | 3rd Party | Other | Fuse | Normal | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
492 | 3rd Party | Other | Insulator | Broken | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
493 | 3rd Party | Other | Insulator | Normal | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
494 | 3rd Party | Other | Interrupter | Normal | All | Underground facilities = no ignition risk
495 | 3rd Party | Other | Jumper | Broken | High | Larger covered conductor to mostly eliminate cause and risk.
496 | 3rd Party | Other | Jumper | Burned Open | High | Larger covered conductor to mostly eliminate cause and risk.
497 | 3rd Party | Other | Jumper | Normal | High | Larger covered conductor to mostly eliminate cause and risk.
498 | 3rd Party | Other | Metering Equipment | Blown/failed | None | No work is being completed on customer equipment.
499 | 3rd Party | Other | Metering Equipment | Normal | None | No work is being completed on customer equipment.
500 | 3rd Party | Other | Other | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
501 | 3rd Party | Other | Other | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
502 | 3rd Party | Other | Other | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
503 | 3rd Party | Other | Pole - Tower- steel | Broken- wire on ground | None | Significant external force broke the conductor and brought wire to the ground/object. Ignition risk not mitigated.
504 | 3rd Party | Other | Pole-Wood | Broken | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
505 | 3rd Party | Other | Pole-Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
506 | 3rd Party | Other | Pole-Wood | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
507 | 3rd Party | Other | Pole-Wood | Burned/flashed | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
508 | 3rd Party | Other | Pole-Wood | Contaminated | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
509 | 3rd Party | Other | Pole-Wood | Deteriorated | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
510 | 3rd Party | Other | Pole-Wood | Normal | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
511 | 3rd Party | Other | Pothead(Riser Termination) | Burned/flashed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
512 | 3rd Party | Other | Recloser | Blown/failed | Medium | System Hardening does not address Reclosers but coverered conductor will reduce annual recloser operations.
513 | 3rd Party | Other | Recloser | Broken | Medium | System Hardening does not address Reclosers but coverered conductor will reduce annual recloser operations.
514 | 3rd Party | Other | Recloser | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
515 | 3rd Party | Other | Regulator | Malfunctioning | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
516 | 3rd Party | Other | Secondary | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
517 | 3rd Party | Other | Secondary | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
518 | 3rd Party | Other | Secondary | Broken- wire on object | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
519 | 3rd Party | Other | Secondary | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
520 | 3rd Party | Other | Secondary | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
521 | 3rd Party | Other | Secondary | Together | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
522 | 3rd Party | Other | Service conductor | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
523 | 3rd Party | Other | Service conductor | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
524 | 3rd Party | Other | Service conductor | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
525 | 3rd Party | Other | Switch (OH) | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
526 | 3rd Party | Other | Switch (UG) | Broken | All | Underground facilities = no ignition risk
527 | 3rd Party | Other | Transformer | Blown/failed | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
528 | 3rd Party | Other | Transformer | Broken | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
529 | 3rd Party | Other | Transformer | Normal | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
530 | 3rd Party | Other | Transformer (OH) | Blown/failed | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
531 | 3rd Party | Other | Transformer (OH) | Burned/flashed | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
532 | 3rd Party | Other | Transformer (OH) | Contaminated | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
533 | 3rd Party | Other | Transformer (OH) | Normal | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
534 | 3rd Party | Other | Transformer (UG) | Broken | All | Underground facilities = no ignition risk
535 | 3rd Party | Other | Transformer (UG) | Contaminated | All | Underground facilities = no ignition risk
536 | 3rd Party | Other | Transformer (UG) | Normal | All | Underground facilities = no ignition risk
537 | 3rd Party | Thrown Object | Conductor- Overhead | Annealed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
538 | 3rd Party | Thrown Object | Conductor- Overhead | Broken | All | New covered conductor will eliminate these contact type outages.
539 | 3rd Party | Thrown Object | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
540 | 3rd Party | Thrown Object | Conductor- Overhead | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
541 | 3rd Party | Thrown Object | Conductor- Overhead | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
542 | 3rd Party | Thrown Object | Conductor- Overhead | Contaminated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
543 | 3rd Party | Thrown Object | Conductor- Overhead | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
544 | 3rd Party | Thrown Object | Conductor- Overhead | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
545 | 3rd Party | Thrown Object | Cutout- fuse holder | Burned/flashed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
546 | 3rd Party | Thrown Object | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
547 | 3rd Party | Thrown Object | Fuse | Broken | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
548 | 3rd Party | Thrown Object | Lightning Arrestor | Blown/failed | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
549 | 3rd Party | Thrown Object | Secondary | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
550 | 3rd Party | Thrown Object | Transformer | Arcing | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
551 | 3rd Party | Thrown Object | Transformer | Blown/failed | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
552 | 3rd Party | Thrown Object | Transformer | Broken | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
553 | 3rd Party | Thrown Object | Transformer (OH) | Normal | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
554 | 3rd Party | Tree - cutting- 3rd party | Anchor or Guy | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
555 | 3rd Party | Tree - cutting- 3rd party | Anchor or Guy | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
556 | 3rd Party | Tree - cutting- 3rd party | Anchor or Guy | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
557 | 3rd Party | Tree - cutting- 3rd party | Conductor- Overhead | Arcing | All | New covered conductor will eliminate these contact type outages.
558 | 3rd Party | Tree - cutting- 3rd party | Conductor- Overhead | Bent or Twisted | All | New covered conductor will eliminate these contact type outages.
559 | 3rd Party | Tree - cutting- 3rd party | Conductor- Overhead | Broken | All | New covered conductor will eliminate these contact type outages.
560 | 3rd Party | Tree - cutting- 3rd party | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
561 | 3rd Party | Tree - cutting- 3rd party | Conductor- Overhead | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
562 | 3rd Party | Tree - cutting- 3rd party | Conductor- Overhead | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
563 | 3rd Party | Tree - cutting- 3rd party | Conductor- Overhead | Deteriorated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
564 | 3rd Party | Tree - cutting- 3rd party | Conductor- Overhead | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
565 | 3rd Party | Tree - cutting- 3rd party | Conductor- Overhead | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
566 | 3rd Party | Tree - cutting- 3rd party | Conductor- Overhead | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
567 | 3rd Party | Tree - cutting- 3rd party | Conductor- Underground | Normal | All | Underground facilities = no ignition risk
568 | 3rd Party | Tree - cutting- 3rd party | Connector or Splice (OH) | Broken | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
569 | 3rd Party | Tree - cutting- 3rd party | Connector or Splice (OH) | Broken- wire on ground | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
570 | 3rd Party | Tree - cutting- 3rd party | Crossarm- Wood | Broken | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
571 | 3rd Party | Tree - cutting- 3rd party | Crossarm- Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
572 | 3rd Party | Tree - cutting- 3rd party | Crossarm- Wood | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
573 | 3rd Party | Tree - cutting- 3rd party | Cutout- fuse holder | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
574 | 3rd Party | Tree - cutting- 3rd party | Cutout- Fused- Distribution | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
575 | 3rd Party | Tree - cutting- 3rd party | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
576 | 3rd Party | Tree - cutting- 3rd party | Fuse | Burned Open | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
577 | 3rd Party | Tree - cutting- 3rd party | Fuse | Normal | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
578 | 3rd Party | Tree - cutting- 3rd party | Insulator | Broken | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
579 | 3rd Party | Tree - cutting- 3rd party | Jumper | Burned Open | High | Larger covered conductor to mostly eliminate cause and risk.
580 | 3rd Party | Tree - cutting- 3rd party | Metering Equipment | Malfunctioning | None | No work is being completed on customer equipment.
581 | 3rd Party | Tree - cutting- 3rd party | Pole-Wood | Broken | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
582 | 3rd Party | Tree - cutting- 3rd party | Pole-Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
583 | 3rd Party | Tree - cutting- 3rd party | Pole-Wood | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
584 | 3rd Party | Tree - cutting- 3rd party | Pothead/Riser Termination | Blown/failed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
585 | 3rd Party | Tree - cutting- 3rd party | Recloser | Malfunctioning | Medium | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters but coverered conductor will reduce annual number of operations/duty cycle.
586 | 3rd Party | Tree - cutting- 3rd party | Recloser | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
587 | 3rd Party | Tree - cutting- 3rd party | Secondary | Arcing | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
588 | 3rd Party | Tree - cutting- 3rd party | Secondary | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
589 | 3rd Party | Tree - cutting- 3rd party | Secondary | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
590 | 3rd Party | Tree - cutting- 3rd party | Secondary | Burned Open | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
591 | 3rd Party | Tree - cutting- 3rd party | Secondary | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
592 | 3rd Party | Tree - cutting- 3rd party | Secondary | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
593 | 3rd Party | Tree - cutting- 3rd party | Secondary | On Ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
594 | 3rd Party | Tree - cutting- 3rd party | Secondary | Together | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
595 | 3rd Party | Tree - cutting- 3rd party | Service conductor | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
596 | 3rd Party | Tree - cutting- 3rd party | Service conductor | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
597 | 3rd Party | Tree - cutting- 3rd party | Service conductor | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
598 | 3rd Party | Tree - cutting- 3rd party | Transformer | Blown/failed | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
599 | 3rd Party | Tree - cutting- 3rd party | Transformer | Broken | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
600 | 3rd Party | Tree - cutting- 3rd party | Transformer | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
601 | 3rd Party | Tree - cutting- 3rd party | Transformer | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
602 | 3rd Party | Tree - cutting- 3rd party | Transformer | Burned/flashed | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
603 | 3rd Party | Tree - cutting- 3rd party | Transformer | Contaminated | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
604 | 3rd Party | Tree - cutting- 3rd party | Transformer | Deteriorated | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
605 | 3rd Party | Tree - cutting- 3rd party | Transformer | Leaking | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
606 | 3rd Party | Tree - cutting- 3rd party | Transformer (OH) | Blown/failed | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
607 | 3rd Party | Tree - cutting- 3rd party | Transformer (OH) | Broken | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
608 | 3rd Party | Tree - cutting- 3rd party | Transformer (OH) | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
609 | 3rd Party | Tree - cutting- 3rd party | Transformer (OH) | Normal | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
610 | 3rd Party | Tree - cutting- 3rd party | Woodpin | Broken | All | Composite arms are being installed along with new insulators and bonding. Tracking insulators/pole fires will be limited though not 100% eliminate. Gunshot damage will still be a concern. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
611 | 3rd Party | Vandalism |  |  | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
612 | 3rd Party | Vandalism | Anchor or Guy | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
613 | 3rd Party | Vandalism | Anchor or Guy | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
614 | 3rd Party | Vandalism | Conductor- Overhead | Arcing | All | New covered conductor will eliminate these contact type outages.
615 | 3rd Party | Vandalism | Conductor- Overhead | Broken | All | New covered conductor will eliminate these contact type outages.
616 | 3rd Party | Vandalism | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
617 | 3rd Party | Vandalism | Conductor- Overhead | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
618 | 3rd Party | Vandalism | Conductor- Overhead | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
619 | 3rd Party | Vandalism | Conductor- Overhead | Deteriorated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
620 | 3rd Party | Vandalism | Conductor- Overhead | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
621 | 3rd Party | Vandalism | Conductor- Overhead | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
622 | 3rd Party | Vandalism | Conductor- Underground | Broken | All | Underground facilities = no ignition risk
623 | 3rd Party | Vandalism | Conductor- Underground | Burned/flashed | All | Underground facilities = no ignition risk
624 | 3rd Party | Vandalism | Conductor- Underground | Deteriorated | All | Underground facilities = no ignition risk
625 | 3rd Party | Vandalism | Conductor- Underground | Normal | All | Underground facilities = no ignition risk
626 | 3rd Party | Vandalism | Connector or Splice (UG) | Broken | All | Underground facilities = no ignition risk
627 | 3rd Party | Vandalism | Connector or Splice (UG) | Burned/flashed | All | Underground facilities = no ignition risk
628 | 3rd Party | Vandalism | Crossarm- Wood | Broken | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
629 | 3rd Party | Vandalism | Crossarm- Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
630 | 3rd Party | Vandalism | Crossarm- Wood | Burned/flashed | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
631 | 3rd Party | Vandalism | CT | Broken | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
632 | 3rd Party | Vandalism | Customer Equipment | Bent or Twisted | None | No work is being completed on customer equipment.
633 | 3rd Party | Vandalism | Customer Equipment | Broken | None | No work is being completed on customer equipment.
634 | 3rd Party | Vandalism | Customer Equipment | Burned/flashed | None | No work is being completed on customer equipment.
635 | 3rd Party | Vandalism | Customer Equipment | Malfunctioning | None | No work is being completed on customer equipment.
636 | 3rd Party | Vandalism | Cutout- Fused- Distribution | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
637 | 3rd Party | Vandalism | Elbow | Blown/failed | All | Underground facilities = no ignition risk
638 | 3rd Party | Vandalism | Elbow | Malfunctioning | All | Underground facilities = no ignition risk
639 | 3rd Party | Vandalism | Elbow | Normal | All | Underground facilities = no ignition risk
640 | 3rd Party | Vandalism | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
641 | 3rd Party | Vandalism | Fuse | Normal | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
642 | 3rd Party | Vandalism | Metering Equipment | Broken | None | No work is being completed on customer equipment.
643 | 3rd Party | Vandalism | Metering Equipment | Malfunctioning | None | No work is being completed on customer equipment.
644 | 3rd Party | Vandalism | Metering Equipment | Normal | None | No work is being completed on customer equipment.
645 | 3rd Party | Vandalism | Other | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
646 | 3rd Party | Vandalism | Other | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
647 | 3rd Party | Vandalism | Other | Malfunctioning | All | Covered conductor will eliminate the line slap and risk associated with this outage.
648 | 3rd Party | Vandalism | Other | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
649 | 3rd Party | Vandalism | Pole-Wood | Broken | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
650 | 3rd Party | Vandalism | Pole-Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
651 | 3rd Party | Vandalism | Pole-Wood | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
652 | 3rd Party | Vandalism | Pole-Wood | Burned/flashed | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
653 | 3rd Party | Vandalism | Pole-Wood | Deteriorated | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
654 | 3rd Party | Vandalism | Pole-Wood | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
655 | 3rd Party | Vandalism | Pothead(Riser Termination) | Burned/flashed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
656 | 3rd Party | Vandalism | Recloser | Broken | Medium | System Hardening does not address Reclosers but coverered conductor will reduce annual recloser operations.
657 | 3rd Party | Vandalism | Recloser | Malfunctioning | Medium | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters but coverered conductor will reduce annual number of operations/duty cycle.
658 | 3rd Party | Vandalism | Recloser | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
659 | 3rd Party | Vandalism | Secondary | Bent or Twisted | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
660 | 3rd Party | Vandalism | Secondary | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
661 | 3rd Party | Vandalism | Secondary | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
662 | 3rd Party | Vandalism | Secondary | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
663 | 3rd Party | Vandalism | Secondary | Malfunctioning | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
664 | 3rd Party | Vandalism | Secondary | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
665 | 3rd Party | Vandalism | Secondary | Together | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
666 | 3rd Party | Vandalism | Service conductor | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
667 | 3rd Party | Vandalism | Switch (OH) | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
668 | 3rd Party | Vandalism | Switch (UG) | Broken | All | Underground facilities = no ignition risk
669 | 3rd Party | Vandalism | Switch (UG) | Normal | All | Underground facilities = no ignition risk
670 | 3rd Party | Vandalism | Transformer | Blown/failed | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
671 | 3rd Party | Vandalism | Transformer | Broken | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
672 | 3rd Party | Vandalism | Transformer | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
673 | 3rd Party | Vandalism | Transformer | Burned/flashed | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
674 | 3rd Party | Vandalism | Transformer | Leaking | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
675 | 3rd Party | Vandalism | Transformer | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
676 | 3rd Party | Vandalism | Transformer (OH) | Blown/failed | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
677 | 3rd Party | Vandalism | Transformer (OH) | Broken | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
678 | 3rd Party | Vandalism | Transformer (OH) | Burned/flashed | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
679 | 3rd Party | Vandalism | Transformer (OH) | Normal | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
680 | 3rd Party | Vandalism | Transformer (UG) | Broken | All | Underground facilities = no ignition risk
681 | 3rd Party | Vandalism | Transformer (UG) | Burned/flashed | All | Underground facilities = no ignition risk
682 | 3rd Party | Vandalism | Transformer (UG) | Contaminated | All | Underground facilities = no ignition risk
683 | 3rd Party | Vandalism | Transformer (UG) | Deteriorated | All | Underground facilities = no ignition risk
684 | 3rd Party | Vandalism | Transformer (UG) | Normal | All | Underground facilities = no ignition risk
685 | 3rd Party | Vehicle |  | Blown/failed | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
686 | 3rd Party | Vehicle |  | Broken | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
687 | 3rd Party | Vehicle |  | Burned Open | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
688 | 3rd Party | Vehicle |  | Normal | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
689 | 3rd Party | Vehicle | Anchor or Guy | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage.
690 | 3rd Party | Vehicle | Anchor or Guy | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
691 | 3rd Party | Vehicle | Anchor or Guy | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
692 | 3rd Party | Vehicle | Anchor or Guy | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
693 | 3rd Party | Vehicle | Anchor or Guy | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
694 | 3rd Party | Vehicle | Anchor or Guy | Malfunctioning | All | Covered conductor will eliminate the line slap and risk associated with this outage.
695 | 3rd Party | Vehicle | Anchor or Guy | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
696 | 3rd Party | Vehicle | Anchor or Guy | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
697 | 3rd Party | Vehicle | Bushing | Broken | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks. Work will cover leads and jumpers.
698 | 3rd Party | Vehicle | Capacitor | Blown/failed | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
699 | 3rd Party | Vehicle | Capacitor | Broken | None | System Hardening would not address this outage
700 | 3rd Party | Vehicle | Circuit Breaker | Normal | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
701 | 3rd Party | Vehicle | Conductor- Overhead | Annealed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
702 | 3rd Party | Vehicle | Conductor- Overhead | Arcing | All | New covered conductor will eliminate these contact type outages.
703 | 3rd Party | Vehicle | Conductor- Overhead | Bent or Twisted | All | New covered conductor will eliminate these contact type outages.
704 | 3rd Party | Vehicle | Conductor- Overhead | Broken | All | New covered conductor will eliminate these contact type outages.
705 | 3rd Party | Vehicle | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
706 | 3rd Party | Vehicle | Conductor- Overhead | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
707 | 3rd Party | Vehicle | Conductor- Overhead | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
708 | 3rd Party | Vehicle | Conductor- Overhead | Contaminated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
709 | 3rd Party | Vehicle | Conductor- Overhead | Deteriorated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
710 | 3rd Party | Vehicle | Conductor- Overhead | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
711 | 3rd Party | Vehicle | Conductor- Overhead | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
712 | 3rd Party | Vehicle | Conductor- Overhead | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
713 | 3rd Party | Vehicle | Conductor- Underground | Arcing | All | Underground facilities = no ignition risk
714 | 3rd Party | Vehicle | Conductor- Underground | Broken | All | Underground facilities = no ignition risk
715 | 3rd Party | Vehicle | Conductor- Underground | Burned/flashed | All | Underground facilities = no ignition risk
716 | 3rd Party | Vehicle | Conductor- Underground | Deteriorated | All | Underground facilities = no ignition risk
717 | 3rd Party | Vehicle | Conductor- Underground | Malfunctioning | All | Underground facilities = no ignition risk
718 | 3rd Party | Vehicle | Conductor- Underground | Normal | All | Underground facilities = no ignition risk
719 | 3rd Party | Vehicle | Connector or Splice (OH) | Arcing | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
720 | 3rd Party | Vehicle | Connector or Splice (OH) | Broken | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
721 | 3rd Party | Vehicle | Connector or Splice (OH) | Broken- wire on ground | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
722 | 3rd Party | Vehicle | Connector or Splice (OH) | Broken- wire on object | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
723 | 3rd Party | Vehicle | Connector or Splice (OH) | Normal | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
724 | 3rd Party | Vehicle | Connector or Splice (UG) | Broken | All | Underground facilities = no ignition risk
725 | 3rd Party | Vehicle | Connector or Splice (UG) | Normal | All | Underground facilities = no ignition risk
726 | 3rd Party | Vehicle | Crossarm- Wood | Broken | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
727 | 3rd Party | Vehicle | Crossarm- Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
728 | 3rd Party | Vehicle | Crossarm- Wood | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
729 | 3rd Party | Vehicle | Crossarm- Wood | Normal | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
730 | 3rd Party | Vehicle | Customer Equipment | Broken | None | No work is being completed on customer equipment.
731 | 3rd Party | Vehicle | Customer Equipment | On Ground | None | No work is being completed on customer equipment.
732 | 3rd Party | Vehicle | Cutout- fuse holder | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
733 | 3rd Party | Vehicle | Cutout- fuse holder | Broken | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
734 | 3rd Party | Vehicle | Cutout- fuse holder | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
735 | 3rd Party | Vehicle | Elbow | Blown/failed | All | Underground facilities = no ignition risk
736 | 3rd Party | Vehicle | Footings- Tower or Pole | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage.
737 | 3rd Party | Vehicle | Footings- Tower or Pole | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
738 | 3rd Party | Vehicle | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
739 | 3rd Party | Vehicle | Fuse | Broken | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
740 | 3rd Party | Vehicle | Fuse | Burned Open | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
741 | 3rd Party | Vehicle | Fuse | Malfunctioning | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
742 | 3rd Party | Vehicle | Fuse | Normal | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
743 | 3rd Party | Vehicle | Insulator | Broken | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
744 | 3rd Party | Vehicle | Insulator | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
745 | 3rd Party | Vehicle | Interrupter | Broken | All | Underground facilities = no ignition risk
746 | 3rd Party | Vehicle | Interrupter | Normal | All | Underground facilities = no ignition risk
747 | 3rd Party | Vehicle | Jumper | Broken | High | Larger covered conductor to mostly eliminate cause and risk.
748 | 3rd Party | Vehicle | Jumper | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
749 | 3rd Party | Vehicle | Jumper | Burned Open | High | Larger covered conductor to mostly eliminate cause and risk.
750 | 3rd Party | Vehicle | Jumper | Burned/flashed | High | Larger covered conductor to mostly eliminate cause and risk.
751 | 3rd Party | Vehicle | Jumper | Normal | High | Larger covered conductor to mostly eliminate cause and risk.
752 | 3rd Party | Vehicle | Lightning Arrestor | Burned/flashed | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
753 | 3rd Party | Vehicle | Metering Equipment | Broken | None | No work is being completed on customer equipment.
754 | 3rd Party | Vehicle | Other | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage.
755 | 3rd Party | Vehicle | Other | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
756 | 3rd Party | Vehicle | Other | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
757 | 3rd Party | Vehicle | Other | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
758 | 3rd Party | Vehicle | Other | Contaminated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
759 | 3rd Party | Vehicle | Other | Malfunctioning | All | Covered conductor will eliminate the line slap and risk associated with this outage.
760 | 3rd Party | Vehicle | Other | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
761 | 3rd Party | Vehicle | Other | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
762 | 3rd Party | Vehicle | Other | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
763 | 3rd Party | Vehicle | Pole - Tower- steel | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
764 | 3rd Party | Vehicle | Pole - Tower- steel | Broken- wire on ground | None | Significant external force broke the conductor and brought wire to the ground/object. Ignition risk not mitigated.
765 | 3rd Party | Vehicle | Pole - Tower- steel | Malfunctioning | All | Covered conductor will eliminate the line slap and risk associated with this outage.
766 | 3rd Party | Vehicle | Pole - Tower- steel | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
767 | 3rd Party | Vehicle | Pole-Wood |  | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
768 | 3rd Party | Vehicle | Pole-Wood | Arcing | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
769 | 3rd Party | Vehicle | Pole-Wood | Broken | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
770 | 3rd Party | Vehicle | Pole-Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
771 | 3rd Party | Vehicle | Pole-Wood | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
772 | 3rd Party | Vehicle | Pole-Wood | Burned/flashed | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
773 | 3rd Party | Vehicle | Pole-Wood | Deteriorated | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
774 | 3rd Party | Vehicle | Pole-Wood | Normal | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
775 | 3rd Party | Vehicle | Pole-Wood | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
776 | 3rd Party | Vehicle | Pothead(Riser Termination) | Blown/failed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
777 | 3rd Party | Vehicle | Pothead(Riser Termination) | Broken | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
778 | 3rd Party | Vehicle | Pothead(Riser Termination) | Burned/flashed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
779 | 3rd Party | Vehicle | Pothead(Riser Termination) | Normal | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
780 | 3rd Party | Vehicle | Pothead/Riser Termination | Broken | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
781 | 3rd Party | Vehicle | Recloser | Burned/flashed | Medium | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters but coverered conductor will reduce annual number of operations/duty cycle.
782 | 3rd Party | Vehicle | Recloser | Malfunctioning | Medium | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters but coverered conductor will reduce annual number of operations/duty cycle.
783 | 3rd Party | Vehicle | Recloser | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
784 | 3rd Party | Vehicle | Regulator | Broken | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
785 | 3rd Party | Vehicle | Regulator | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
786 | 3rd Party | Vehicle | Regulator | Burned/flashed | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
787 | 3rd Party | Vehicle | Riser | Bent or Twisted | High | Risers are indirectly addressed on System Hardening - Pole changeouts, the covering of jumpers and leads, along with covering conductor should mitigate outages and risk.
788 | 3rd Party | Vehicle | Riser | Broken | High | Risers are indirectly addressed on System Hardening - Pole changeouts, the covering of jumpers and leads, along with covering conductor should mitigate outages and risk.
789 | 3rd Party | Vehicle | Secondary | Arcing | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
790 | 3rd Party | Vehicle | Secondary | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
791 | 3rd Party | Vehicle | Secondary | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
792 | 3rd Party | Vehicle | Secondary | Broken- wire on object | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
793 | 3rd Party | Vehicle | Secondary | Burned Open | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
794 | 3rd Party | Vehicle | Secondary | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
795 | 3rd Party | Vehicle | Secondary | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
796 | 3rd Party | Vehicle | Secondary | On Ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
797 | 3rd Party | Vehicle | Secondary | Together | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
798 | 3rd Party | Vehicle | Sectionalizer | Blown/failed | Medium | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters but coverered conductor will reduce annual number of operations/duty cycle.
799 | 3rd Party | Vehicle | Service conductor | Bent or Twisted | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
800 | 3rd Party | Vehicle | Service conductor | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
801 | 3rd Party | Vehicle | Service conductor | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
802 | 3rd Party | Vehicle | Service conductor | Broken- wire on object | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
803 | 3rd Party | Vehicle | Service conductor | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
804 | 3rd Party | Vehicle | Service conductor | On Ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
805 | 3rd Party | Vehicle | Splice box | Broken | All | Underground facilities = no ignition risk
806 | 3rd Party | Vehicle | Switch | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
807 | 3rd Party | Vehicle | Switch | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
808 | 3rd Party | Vehicle | Switch (OH) | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
809 | 3rd Party | Vehicle | Switch (OH) | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
810 | 3rd Party | Vehicle | Switch (OH) | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
811 | 3rd Party | Vehicle | Switch (UG) | Broken | All | Underground facilities = no ignition risk
812 | 3rd Party | Vehicle | Switch (UG) | Burned/flashed | All | Underground facilities = no ignition risk
813 | 3rd Party | Vehicle | Switch (UG) | Normal | All | Underground facilities = no ignition risk
814 | 3rd Party | Vehicle | Transformer |  | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil.
815 | 3rd Party | Vehicle | Transformer | Arcing | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
816 | 3rd Party | Vehicle | Transformer | Bent or Twisted | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
817 | 3rd Party | Vehicle | Transformer | Blown/failed | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
818 | 3rd Party | Vehicle | Transformer | Broken | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
819 | 3rd Party | Vehicle | Transformer | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
820 | 3rd Party | Vehicle | Transformer | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
821 | 3rd Party | Vehicle | Transformer | Burned/flashed | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
822 | 3rd Party | Vehicle | Transformer | Deteriorated | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
823 | 3rd Party | Vehicle | Transformer | Leaking | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
824 | 3rd Party | Vehicle | Transformer | Malfunctioning | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
825 | 3rd Party | Vehicle | Transformer | Normal | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
826 | 3rd Party | Vehicle | Transformer | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
827 | 3rd Party | Vehicle | Transformer (OH) | Blown/failed | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
828 | 3rd Party | Vehicle | Transformer (OH) | Broken | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
829 | 3rd Party | Vehicle | Transformer (OH) | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
830 | 3rd Party | Vehicle | Transformer (OH) | Leaking | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
831 | 3rd Party | Vehicle | Transformer (OH) | Normal | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
832 | 3rd Party | Vehicle | Transformer (OH) | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
833 | 3rd Party | Vehicle | Transformer (UG) | Blown/failed | All | Underground facilities = no ignition risk
834 | 3rd Party | Vehicle | Transformer (UG) | Broken | All | Underground facilities = no ignition risk
835 | 3rd Party | Vehicle | Transformer (UG) | Broken- wire on ground | All | Underground facilities = no ignition risk
836 | 3rd Party | Vehicle | Transformer (UG) | Burned/flashed | All | Underground facilities = no ignition risk
837 | 3rd Party | Vehicle | Transformer (UG) | Deteriorated | All | Underground facilities = no ignition risk
838 | 3rd Party | Vehicle | Transformer (UG) | Leaking | All | Underground facilities = no ignition risk
839 | 3rd Party | Vehicle | Transformer (UG) | Normal | All | Underground facilities = no ignition risk
840 | 3rd Party | Vehicle | Transformer (UG) | On Ground | All | Underground facilities = no ignition risk
841 | 3rd Party | Vehicle | Woodpin | Broken | All | Composite arms are being installed along with new insulators and bonding. Tracking insulators/pole fires will be limited though not 100% eliminate. Gunshot damage will still be a concern. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
842 | 3rd Party | Vehicle | Woodpin | Broken- wire on object | None | Significant external force broke the conductor and brought wire to the ground/object. Ignition risk not mitigated.
843 | 3rd Party | Vehicle | Woodpin | Deteriorated | All | Composite arms are being installed along with new insulators and bonding. Tracking insulators/pole fires will be limited though not 100% eliminate. Gunshot damage will still be a concern. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
844 | Animal | Bird found |  |  | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
845 | Animal | Bird found |  | Blown/failed | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
846 | Animal | Bird found |  | Broken | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
847 | Animal | Bird found |  | Burned Open | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
848 | Animal | Bird found |  | Normal | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
849 | Animal | Bird found | Booster | Blown/failed | All | Circuit Hardening replaces boosters with voltage regulators. Work will cover leads and jumpers.
850 | Animal | Bird found | Booster | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
851 | Animal | Bird found | Booster | Burned/flashed | All | Circuit Hardening replaces boosters with voltage regulators. Leads covered.
852 | Animal | Bird found | Booster | Normal | All | Circuit Hardening replaces boosters with voltage regulators. Leads covered.
853 | Animal | Bird found | Bus | Normal | High | Transformers installed prior to 2014 will be replaced. Work would include covering jumpers and replacing some of the service conductor.
854 | Animal | Bird found | Bushing | Blown/failed | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks. Work will cover leads and jumpers.
855 | Animal | Bird found | Bushing | Burned/flashed | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks. Work will cover leads and jumpers.
856 | Animal | Bird found | Bushing | Normal | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks. Work will cover leads and jumpers.
857 | Animal | Bird found | Capacitor | Blown/failed | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
858 | Animal | Bird found | Capacitor | Burned/flashed | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
859 | Animal | Bird found | Capacitor | Normal | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
860 | Animal | Bird found | Circuit Breaker | Blown/failed | Medium | System Hardening does not address substation equipment but coverered conductor will reduce annual breaker operations.
861 | Animal | Bird found | Circuit Breaker | Normal | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
862 | Animal | Bird found | Conductor- Overhead | Arcing | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
863 | Animal | Bird found | Conductor- Overhead | Bent or Twisted | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
864 | Animal | Bird found | Conductor- Overhead | Broken | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
865 | Animal | Bird found | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
866 | Animal | Bird found | Conductor- Overhead | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
867 | Animal | Bird found | Conductor- Overhead | Burned/flashed | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
868 | Animal | Bird found | Conductor- Overhead | Contaminated | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
869 | Animal | Bird found | Conductor- Overhead | Deteriorated | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
870 | Animal | Bird found | Conductor- Overhead | Malfunctioning | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
871 | Animal | Bird found | Conductor- Overhead | Normal | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
872 | Animal | Bird found | Conductor- Overhead | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
873 | Animal | Bird found | Conductor- Overhead | Together | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
874 | Animal | Bird found | Conductor- Underground | Burned/flashed | All | Underground facilities = no ignition risk
875 | Animal | Bird found | Conductor- Underground | Normal | All | Underground facilities = no ignition risk
876 | Animal | Bird found | Connector or Splice (OH) | Arcing | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
877 | Animal | Bird found | Connector or Splice (OH) | Broken | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
878 | Animal | Bird found | Connector or Splice (OH) | Broken- wire on ground | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
879 | Animal | Bird found | Connector or Splice (OH) | Broken- wire on object | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
880 | Animal | Bird found | Connector or Splice (OH) | Burned Open | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
881 | Animal | Bird found | Connector or Splice (OH) | Burned/flashed | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
882 | Animal | Bird found | Connector or Splice (OH) | Normal | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
883 | Animal | Bird found | Crossarm- Steel | Normal | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
884 | Animal | Bird found | Crossarm- Wood | Broken | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
885 | Animal | Bird found | Crossarm- Wood | Burned/flashed | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
886 | Animal | Bird found | Crossarm- Wood | Normal | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
887 | Animal | Bird found | Customer Equipment | Blown/failed | None | No work is being completed on customer equipment.
888 | Animal | Bird found | Customer Equipment | Burned/flashed | None | No work is being completed on customer equipment.
889 | Animal | Bird found | Customer Equipment | Normal | None | No work is being completed on customer equipment.
890 | Animal | Bird found | Cutout- fuse holder | Arcing | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
891 | Animal | Bird found | Cutout- fuse holder | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
892 | Animal | Bird found | Cutout- fuse holder | Broken | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
893 | Animal | Bird found | Cutout- fuse holder | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
894 | Animal | Bird found | Cutout- fuse holder | Burned/flashed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
895 | Animal | Bird found | Cutout- fuse holder | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
896 | Animal | Bird found | Cutout- Fused- Distribution | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
897 | Animal | Bird found | Cutout- Fused- Distribution | Burned Open | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
898 | Animal | Bird found | Cutout- Fused- Distribution | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
899 | Animal | Bird found | Elbow | Blown/failed | All | Underground facilities = no ignition risk
900 | Animal | Bird found | Footings- Tower or Pole | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
901 | Animal | Bird found | Fuse | Arcing | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
902 | Animal | Bird found | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
903 | Animal | Bird found | Fuse | Broken | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
904 | Animal | Bird found | Fuse | Burned Open | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
905 | Animal | Bird found | Fuse | Normal | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
906 | Animal | Bird found | Insulator | Blown/failed | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered.
907 | Animal | Bird found | Insulator | Broken | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered.
908 | Animal | Bird found | Insulator | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
909 | Animal | Bird found | Insulator | Burned/flashed | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered.
910 | Animal | Bird found | Insulator | Normal | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered.
911 | Animal | Bird found | Interrupter | Normal | All | Underground facilities = no ignition risk
912 | Animal | Bird found | Jumper |  | High | Larger covered conductor to mostly eliminate cause and risk.
913 | Animal | Bird found | Jumper | Bent or Twisted | High | Larger covered conductor to mostly eliminate cause and risk.
914 | Animal | Bird found | Jumper | Broken | High | Larger covered conductor to mostly eliminate cause and risk.
915 | Animal | Bird found | Jumper | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
916 | Animal | Bird found | Jumper | Burned Open | High | Larger covered conductor to mostly eliminate cause and risk.
917 | Animal | Bird found | Jumper | Burned/flashed | High | Larger covered conductor to mostly eliminate cause and risk.
918 | Animal | Bird found | Jumper | Deteriorated | High | Larger covered conductor to mostly eliminate cause and risk.
919 | Animal | Bird found | Jumper | Normal | High | Larger covered conductor to mostly eliminate cause and risk.
920 | Animal | Bird found | Lightning Arrestor | Blown/failed | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
921 | Animal | Bird found | Lightning Arrestor | Burned/flashed | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
922 | Animal | Bird found | Lightning Arrestor | Normal | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
923 | Animal | Bird found | Metering Equipment | Normal | None | System Hardening does not address Metering facilities.
924 | Animal | Bird found | Other | Broken | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
925 | Animal | Bird found | Other | Burned/flashed | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
926 | Animal | Bird found | Other | Normal | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
927 | Animal | Bird found | PGs- Kearneys | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
928 | Animal | Bird found | Pole-Wood | Broken | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
929 | Animal | Bird found | Pole-Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
930 | Animal | Bird found | Pole-Wood | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
931 | Animal | Bird found | Pole-Wood | Burned/flashed | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
932 | Animal | Bird found | Pole-Wood | Deteriorated | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
933 | Animal | Bird found | Pole-Wood | Normal | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
934 | Animal | Bird found | Pothead(Riser Termination) | Arcing | Low | Pothead failure by animal/object will NOT have its risk mitigated by System Hardening
935 | Animal | Bird found | Pothead(Riser Termination) | Blown/failed | Low | Pothead failure by animal/object will NOT have its risk mitigated by System Hardening
936 | Animal | Bird found | Pothead(Riser Termination) | Broken | Low | Pothead failure by animal/object will NOT have its risk mitigated by System Hardening
937 | Animal | Bird found | Pothead(Riser Termination) | Burned/flashed | Low | Pothead failure by animal/object will NOT have its risk mitigated by System Hardening
938 | Animal | Bird found | Pothead(Riser Termination) | Normal | Low | Pothead failure by animal/object will NOT have its risk mitigated by System Hardening
939 | Animal | Bird found | Pothead/Riser Termination | Burned/flashed | Low | Pothead failure by animal/object will NOT have its risk mitigated by System Hardening
940 | Animal | Bird found | Pothead/Riser Termination | Normal | Low | Pothead failure by animal/object will NOT have its risk mitigated by System Hardening
941 | Animal | Bird found | PT/CCVT | Blown/failed | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
942 | Animal | Bird found | PT/CCVT | Burned/flashed | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
943 | Animal | Bird found | Recloser | Blown/failed | None | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters.
944 | Animal | Bird found | Recloser | Broken | None | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters.
945 | Animal | Bird found | Recloser | Burned/flashed | None | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters.
946 | Animal | Bird found | Recloser | Normal | None | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters.
947 | Animal | Bird found | Regulator | Blown/failed | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
948 | Animal | Bird found | Regulator | Broken | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
949 | Animal | Bird found | Regulator | Burned/flashed | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
950 | Animal | Bird found | Regulator | Normal | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
951 | Animal | Bird found | Riser | Normal | High | Risers are indirectly addressed on System Hardening - Pole changeouts, the covering of jumpers and leads, along with covering conductor should mitigate outages and risk.
952 | Animal | Bird found | Secondary | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
953 | Animal | Bird found | Secondary | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
954 | Animal | Bird found | Secondary | On Ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
955 | Animal | Bird found | Sectionalizer | Blown/failed | None | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters.
956 | Animal | Bird found | Stepdown | Blown/failed | All | Underground facilities = no ignition risk
957 | Animal | Bird found | Stepdown | Burned/flashed | All | Underground facilities = no ignition risk
958 | Animal | Bird found | Street Light Equipment | Blown/failed | Medium | System Hardening will not address Street Lights but will address their transformers.
959 | Animal | Bird found | Switch | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
960 | Animal | Bird found | Switch | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
961 | Animal | Bird found | Switch (OH) | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
962 | Animal | Bird found | Switch (OH) | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
963 | Animal | Bird found | Switch (OH) | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
964 | Animal | Bird found | Switch (UG) | Normal | All | Underground facilities = no ignition risk
965 | Animal | Bird found | Transformer |  | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
966 | Animal | Bird found | Transformer | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
967 | Animal | Bird found | Transformer | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
968 | Animal | Bird found | Transformer | Burned/flashed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
969 | Animal | Bird found | Transformer | Malfunctioning | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
970 | Animal | Bird found | Transformer | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
971 | Animal | Bird found | Transformer | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
972 | Animal | Bird found | Transformer (OH) |  | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
973 | Animal | Bird found | Transformer (OH) | Arcing | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
974 | Animal | Bird found | Transformer (OH) | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
975 | Animal | Bird found | Transformer (OH) | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
976 | Animal | Bird found | Transformer (OH) | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
977 | Animal | Bird found | Transformer (OH) | Burned/flashed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
978 | Animal | Bird found | Transformer (OH) | Contaminated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
979 | Animal | Bird found | Transformer (OH) | Deteriorated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
980 | Animal | Bird found | Transformer (OH) | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
981 | Animal | Bird found | Transformer (UG) | Blown/failed | All | UG Facilities = no ignition risk
982 | Animal | Bird found | Transformer (UG) | Broken | All | UG Facilities = no ignition risk
983 | Animal | Bird found | Transformer (UG) | Normal | All | UG Facilities = no ignition risk
984 | Animal | Bird found | Woodpin | Broken | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered.
985 | Animal | Bird found | Woodpin | Normal | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered.
986 | Animal | Other |  |  | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
987 | Animal | Other |  | Blown/failed | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
988 | Animal | Other |  | Broken | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
989 | Animal | Other |  | Burned Open | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
990 | Animal | Other | Anchor or Guy | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage.
991 | Animal | Other | Anchor or Guy | Normal | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
992 | Animal | Other | Booster | Burned/flashed | All | Circuit Hardening replaces boosters with voltage regulators. Leads covered.
993 | Animal | Other | Booster | Contaminated | All | Circuit Hardening replaces boosters with voltage regulators. Leads covered.
994 | Animal | Other | Bus | Normal | High | Transformers installed prior to 2014 will be replaced. Work would include covering jumpers and replacing some of the service conductor.
995 | Animal | Other | Bushing | Blown/failed | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks. Work will cover leads and jumpers.
996 | Animal | Other | Bushing | Broken | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks. Work will cover leads and jumpers.
997 | Animal | Other | Bushing | Burned/flashed | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks. Work will cover leads and jumpers.
998 | Animal | Other | Bushing | Normal | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks. Work will cover leads and jumpers.
999 | Animal | Other | Cable Termination(live front | Normal | All | Underground facilities = no ignition risk
1000 | Animal | Other | Capacitor | Blown/failed | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
1001 | Animal | Other | Capacitor | Burned/flashed | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
1002 | Animal | Other | Capacitor | Normal | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
1003 | Animal | Other | Circuit Breaker | Normal | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1004 | Animal | Other | Conductor- Overhead | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1005 | Animal | Other | Conductor- Overhead | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1006 | Animal | Other | Conductor- Overhead | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1007 | Animal | Other | Conductor- Overhead | Broken | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1008 | Animal | Other | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1009 | Animal | Other | Conductor- Overhead | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1010 | Animal | Other | Conductor- Overhead | Burned/flashed | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1011 | Animal | Other | Conductor- Overhead | Contaminated | All | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1012 | Animal | Other | Conductor- Overhead | Deteriorated | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1013 | Animal | Other | Conductor- Overhead | Normal | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1014 | Animal | Other | Conductor- Overhead | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1015 | Animal | Other | Conductor- Overhead | Together | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1016 | Animal | Other | Conductor- Underground | Broken | All | Underground facilities = no ignition risk
1017 | Animal | Other | Conductor- Underground | Burned/flashed | All | Underground facilities = no ignition risk
1018 | Animal | Other | Conductor- Underground | Deteriorated | All | Underground facilities = no ignition risk
1019 | Animal | Other | Conductor- Underground | Normal | All | Underground facilities = no ignition risk
1020 | Animal | Other | Connector or Splice (OH) | Broken- wire on ground | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
1021 | Animal | Other | Connector or Splice (OH) | Burned Open | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
1022 | Animal | Other | Connector or Splice (OH) | Contaminated | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
1023 | Animal | Other | Connector or Splice (OH) | Normal | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
1024 | Animal | Other | Connector or Splice (UG) | Burned/flashed | All | Underground facilities = no ignition risk
1025 | Animal | Other | Crossarm- Steel | Normal | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1026 | Animal | Other | Crossarm- Wood | Broken | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1027 | Animal | Other | Crossarm- Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1028 | Animal | Other | Crossarm- Wood | Burned/flashed | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1029 | Animal | Other | Crossarm- Wood | Contaminated | All | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1030 | Animal | Other | Crossarm- Wood | Normal | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1031 | Animal | Other | Customer Equipment | Burned/flashed | None | No work is being completed on customer equipment.
1032 | Animal | Other | Customer Equipment | Normal | None | No work is being completed on customer equipment.
1033 | Animal | Other | Cutout- fuse holder | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
1034 | Animal | Other | Cutout- fuse holder | Broken | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
1035 | Animal | Other | Cutout- fuse holder | Burned/flashed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
1036 | Animal | Other | Cutout- fuse holder | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
1037 | Animal | Other | Cutout- Fused- Distribution | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
1038 | Animal | Other | Cutout- Fused- Distribution | Burned/flashed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
1039 | Animal | Other | Elbow | Blown/failed | All | Underground facilities = no ignition risk
1040 | Animal | Other | Fuse | Arcing | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
1041 | Animal | Other | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
1042 | Animal | Other | Fuse | Broken | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
1043 | Animal | Other | Fuse | Burned Open | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
1044 | Animal | Other | Fuse | Normal | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
1045 | Animal | Other | Insulator | Arcing | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered.
1046 | Animal | Other | Insulator | Blown/failed | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered.
1047 | Animal | Other | Insulator | Broken | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered.
1048 | Animal | Other | Insulator | Burned/flashed | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered.
1049 | Animal | Other | Insulator | Normal | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered.
1050 | Animal | Other | Jumper | Arcing | High | Larger covered conductor to mostly eliminate cause and risk.
1051 | Animal | Other | Jumper | Broken | High | Larger covered conductor to mostly eliminate cause and risk.
1052 | Animal | Other | Jumper | Burned Open | High | Larger covered conductor to mostly eliminate cause and risk.
1053 | Animal | Other | Jumper | Burned/flashed | High | Larger covered conductor to mostly eliminate cause and risk.
1054 | Animal | Other | Jumper | Contaminated | High | Larger covered conductor to mostly eliminate cause and risk.
1055 | Animal | Other | Jumper | Normal | High | Larger covered conductor to mostly eliminate cause and risk.
1056 | Animal | Other | Lightning Arrestor | Blown/failed | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
1057 | Animal | Other | Lightning Arrestor | Broken | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
1058 | Animal | Other | Lightning Arrestor | Burned/flashed | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
1059 | Animal | Other | Lightning Arrestor | Normal | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
1060 | Animal | Other | Metering Equipment | Burned/flashed | None | System Hardening does not address Metering facilities.
1061 | Animal | Other | Metering Equipment | Malfunctioning | None | System Hardening does not address Metering facilities.
1062 | Animal | Other | Metering Equipment | Normal | None | System Hardening does not address Metering facilities.
1063 | Animal | Other | Other | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
1064 | Animal | Other | Other | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1065 | Animal | Other | Other | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
1066 | Animal | Other | Other | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
1067 | Animal | Other | Pole - Tower- steel | Normal | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1068 | Animal | Other | Pole-Wood | Broken | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
1069 | Animal | Other | Pole-Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1070 | Animal | Other | Pole-Wood | Burned/flashed | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
1071 | Animal | Other | Pole-Wood | Deteriorated | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
1072 | Animal | Other | Pole-Wood | Normal | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
1073 | Animal | Other | Pole-Wood | Together | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
1074 | Animal | Other | Pothead(Riser Termination) | Blown/failed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
1075 | Animal | Other | Pothead(Riser Termination) | Burned/flashed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
1076 | Animal | Other | Pothead(Riser Termination) | Contaminated | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
1077 | Animal | Other | Pothead(Riser Termination) | Deteriorated | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
1078 | Animal | Other | Pothead(Riser Termination) | Normal | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
1079 | Animal | Other | Pothead/Riser Termination | Arcing | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
1080 | Animal | Other | Pothead/Riser Termination | Blown/failed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
1081 | Animal | Other | Pothead/Riser Termination | Normal | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
1082 | Animal | Other | PT/CCVT | Burned/flashed | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
1083 | Animal | Other | PT/CCVT | Normal | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
1084 | Animal | Other | Recloser | Blown/failed | None | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters.
1085 | Animal | Other | Recloser | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1086 | Animal | Other | Recloser | Burned/flashed | None | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters.
1087 | Animal | Other | Recloser | Malfunctioning | None | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters.
1088 | Animal | Other | Recloser | Normal | None | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters.
1089 | Animal | Other | Regulator | Arcing | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
1090 | Animal | Other | Regulator | Blown/failed | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
1091 | Animal | Other | Regulator | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1092 | Animal | Other | Regulator | Burned/flashed | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
1093 | Animal | Other | Regulator | Normal | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
1094 | Animal | Other | Riser | Normal | High | Risers are indirectly addressed on System Hardening - Pole changeouts, the covering of jumpers and leads, along with covering conductor should mitigate outages and risk.
1095 | Animal | Other | Secondary | Annealed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1096 | Animal | Other | Secondary | Arcing | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1097 | Animal | Other | Secondary | Bent or Twisted | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1098 | Animal | Other | Secondary | Blown/failed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1099 | Animal | Other | Secondary | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1100 | Animal | Other | Secondary | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1101 | Animal | Other | Secondary | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1102 | Animal | Other | Secondary | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1103 | Animal | Other | Secondary | Together | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1104 | Animal | Other | Sectionalizer | Burned/flashed | None | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters.
1105 | Animal | Other | Sectionalizer | Normal | None | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters.
1106 | Animal | Other | Stepdown | Burned/flashed | All | Underground facilities = no ignition risk
1107 | Animal | Other | Switch | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
1108 | Animal | Other | Switch | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
1109 | Animal | Other | Switch | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
1110 | Animal | Other | Switch (OH) | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
1111 | Animal | Other | Switch (OH) | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
1112 | Animal | Other | Switch (UG) | Arcing | All | Underground facilities = no ignition risk
1113 | Animal | Other | Switch (UG) | Burned/flashed | All | Underground facilities = no ignition risk
1114 | Animal | Other | Switch (UG) | Normal | All | Underground facilities = no ignition risk
1115 | Animal | Other | Transformer | Arcing | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1116 | Animal | Other | Transformer | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1117 | Animal | Other | Transformer | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1118 | Animal | Other | Transformer | Burned/flashed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1119 | Animal | Other | Transformer | Contaminated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1120 | Animal | Other | Transformer | Malfunctioning | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1121 | Animal | Other | Transformer | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1122 | Animal | Other | Transformer (OH) | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1123 | Animal | Other | Transformer (OH) | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1124 | Animal | Other | Transformer (OH) | Burned/flashed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1125 | Animal | Other | Transformer (OH) | Deteriorated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1126 | Animal | Other | Transformer (OH) | Leaking | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1127 | Animal | Other | Transformer (OH) | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1128 | Animal | Other | Transformer (UG) | Arcing | All | UG Facilities = no ignition risk
1129 | Animal | Other | Transformer (UG) | Blown/failed | All | UG Facilities = no ignition risk
1130 | Animal | Other | Transformer (UG) | Broken | All | UG Facilities = no ignition risk
1131 | Animal | Other | Transformer (UG) | Burned/flashed | All | UG Facilities = no ignition risk
1132 | Animal | Other | Transformer (UG) | Deteriorated | All | UG Facilities = no ignition risk
1133 | Animal | Other | Transformer (UG) | Normal | All | UG Facilities = no ignition risk
1134 | Animal | Other | Woodpin | Broken | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered.
1135 | Animal | Squirrel |  |  | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
1136 | Animal | Squirrel |  | Blown/failed | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
1137 | Animal | Squirrel |  | Broken | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
1138 | Animal | Squirrel |  | Burned Open | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
1139 | Animal | Squirrel |  | Normal | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
1140 | Animal | Squirrel | Bus | Normal | Medium | Transforemers installed prior to 2014 will be replaced. Work would include covering jumpers and replacing some of the service conductor.
1141 | Animal | Squirrel | Bushing | Blown/failed | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks. Work will cover leads and jumpers.
1142 | Animal | Squirrel | Bushing | Broken | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks. Work will cover leads and jumpers.
1143 | Animal | Squirrel | Bushing | Burned/flashed | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks. Work will cover leads and jumpers.
1144 | Animal | Squirrel | Bushing | Normal | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks. Work will cover leads and jumpers.
1145 | Animal | Squirrel | Capacitor | Blown/failed | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
1146 | Animal | Squirrel | Circuit Breaker | Normal | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1147 | Animal | Squirrel | Conductor- Overhead | Arcing | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1148 | Animal | Squirrel | Conductor- Overhead | Broken | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1149 | Animal | Squirrel | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1150 | Animal | Squirrel | Conductor- Overhead | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1151 | Animal | Squirrel | Conductor- Overhead | Burned/flashed | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1152 | Animal | Squirrel | Conductor- Overhead | Deteriorated | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1153 | Animal | Squirrel | Conductor- Overhead | Malfunctioning | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1154 | Animal | Squirrel | Conductor- Overhead | Normal | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1155 | Animal | Squirrel | Conductor- Overhead | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1156 | Animal | Squirrel | Conductor- Overhead | Together | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1157 | Animal | Squirrel | Conductor- Underground | Broken | All | Underground facilities = no ignition risk
1158 | Animal | Squirrel | Conductor- Underground | Burned/flashed | All | Underground facilities = no ignition risk
1159 | Animal | Squirrel | Conductor- Underground | Deteriorated | All | Underground facilities = no ignition risk
1160 | Animal | Squirrel | Conductor- Underground | Normal | All | Underground facilities = no ignition risk
1161 | Animal | Squirrel | Connector or Splice (OH) | Broken | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
1162 | Animal | Squirrel | Connector or Splice (OH) | Broken- wire on ground | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
1163 | Animal | Squirrel | Connector or Splice (OH) | Burned Open | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
1164 | Animal | Squirrel | Connector or Splice (OH) | Normal | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
1165 | Animal | Squirrel | Connector or Splice (UG) | Normal | All | Underground facilities = no ignition risk
1166 | Animal | Squirrel | Crossarm- Steel | Normal | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1167 | Animal | Squirrel | Crossarm- Wood | Broken | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1168 | Animal | Squirrel | Crossarm- Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1169 | Animal | Squirrel | Crossarm- Wood | Burned/flashed | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1170 | Animal | Squirrel | Crossarm- Wood | Normal | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1171 | Animal | Squirrel | Customer Equipment | Burned/flashed | None | No work is being completed on customer equipment.
1172 | Animal | Squirrel | Customer Equipment | Normal | None | No work is being completed on customer equipment.
1173 | Animal | Squirrel | Cutout- fuse holder | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
1174 | Animal | Squirrel | Cutout- fuse holder | Broken | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
1175 | Animal | Squirrel | Cutout- fuse holder | Burned/flashed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
1176 | Animal | Squirrel | Cutout- fuse holder | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
1177 | Animal | Squirrel | Cutout- Fused- Distribution | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
1178 | Animal | Squirrel | Cutout- Fused- Distribution | Burned/flashed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
1179 | Animal | Squirrel | Cutout- Fused- Distribution | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
1180 | Animal | Squirrel | Fuse |  | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
1181 | Animal | Squirrel | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
1182 | Animal | Squirrel | Fuse | Broken | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
1183 | Animal | Squirrel | Fuse | Burned Open | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
1184 | Animal | Squirrel | Fuse | Normal | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
1185 | Animal | Squirrel | Insulator | Arcing | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered.
1186 | Animal | Squirrel | Insulator | Blown/failed | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered.
1187 | Animal | Squirrel | Insulator | Broken | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered.
1188 | Animal | Squirrel | Insulator | Burned/flashed | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered.
1189 | Animal | Squirrel | Insulator | Normal | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered.
1190 | Animal | Squirrel | Interrupter | Normal | All | Underground facilities = no ignition risk
1191 | Animal | Squirrel | Jumper | Bent or Twisted | High | Larger covered conductor to mostly eliminate cause and risk.
1192 | Animal | Squirrel | Jumper | Broken | High | Larger covered conductor to mostly eliminate cause and risk.
1193 | Animal | Squirrel | Jumper | Burned Open | High | Larger covered conductor to mostly eliminate cause and risk.
1194 | Animal | Squirrel | Jumper | Burned/flashed | High | Larger covered conductor to mostly eliminate cause and risk.
1195 | Animal | Squirrel | Jumper | Normal | High | Larger covered conductor to mostly eliminate cause and risk.
1196 | Animal | Squirrel | Lightning Arrestor | Blown/failed | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
1197 | Animal | Squirrel | Lightning Arrestor | Broken | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
1198 | Animal | Squirrel | Lightning Arrestor | Burned/flashed | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
1199 | Animal | Squirrel | Lightning Arrestor | Normal | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
1200 | Animal | Squirrel | Other | Arcing | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1201 | Animal | Squirrel | Other | Blown/failed | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1202 | Animal | Squirrel | Other | Burned/flashed | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1203 | Animal | Squirrel | Other | Normal | High | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
1204 | Animal | Squirrel | Pole-Wood | Broken | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
1205 | Animal | Squirrel | Pole-Wood | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1206 | Animal | Squirrel | Pole-Wood | Burned/flashed | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
1207 | Animal | Squirrel | Pole-Wood | Normal | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
1208 | Animal | Squirrel | Pothead(Riser Termination) | Blown/failed | Low | Pothead failure by animal/object will NOT have its risk mitigated by System Hardening
1209 | Animal | Squirrel | Pothead(Riser Termination) | Broken | Low | Pothead failure by animal/object will NOT have its risk mitigated by System Hardening
1210 | Animal | Squirrel | Pothead(Riser Termination) | Burned/flashed | Low | Pothead failure by animal/object will NOT have its risk mitigated by System Hardening
1211 | Animal | Squirrel | Pothead(Riser Termination) | Normal | Low | Pothead failure by animal/object will NOT have its risk mitigated by System Hardening
1212 | Animal | Squirrel | Pothead/Riser Termination | Blown/failed | Low | Pothead failure by animal/object will NOT have its risk mitigated by System Hardening
1213 | Animal | Squirrel | Pothead/Riser Termination | Broken | Low | Pothead failure by animal/object will NOT have its risk mitigated by System Hardening
1214 | Animal | Squirrel | Pothead/Riser Termination | Burned/flashed | Low | Pothead failure by animal/object will NOT have its risk mitigated by System Hardening
1215 | Animal | Squirrel | Pothead/Riser Termination | Contaminated | Low | Pothead failure by animal/object will NOT have its risk mitigated by System Hardening
1216 | Animal | Squirrel | Pothead/Riser Termination | Normal | Low | Pothead failure by animal/object will NOT have its risk mitigated by System Hardening
1217 | Animal | Squirrel | Pothead/Riser Termination | Together | Low | Pothead failure by animal/object will NOT have its risk mitigated by System Hardening
1218 | Animal | Squirrel | PT/CCVT | Burned/flashed | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
1219 | Animal | Squirrel | Recloser | Blown/failed | None | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters.
1220 | Animal | Squirrel | Recloser | Broken | None | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters.
1221 | Animal | Squirrel | Recloser | Burned/flashed | None | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters.
1222 | Animal | Squirrel | Recloser | Malfunctioning | None | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters.
1223 | Animal | Squirrel | Recloser | Normal | None | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters.
1224 | Animal | Squirrel | Regulator | Blown/failed | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
1225 | Animal | Squirrel | Regulator | Burned/flashed | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
1226 | Animal | Squirrel | Riser | Normal | High | Risers are indirectly addressed on System Hardening - Pole changeouts, the covering of jumpers and leads, along with covering conductor should mitigate outages and risk.
1227 | Animal | Squirrel | Secondary |  | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1228 | Animal | Squirrel | Secondary | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1229 | Animal | Squirrel | Secondary | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1230 | Animal | Squirrel | Secondary | Broken- wire on object | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1231 | Animal | Squirrel | Secondary | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1232 | Animal | Squirrel | Secondary | Deteriorated | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1233 | Animal | Squirrel | Secondary | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1234 | Animal | Squirrel | Secondary | On Ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1235 | Animal | Squirrel | Sectionalizer | Normal | None | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters.
1236 | Animal | Squirrel | Service conductor | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1237 | Animal | Squirrel | Service conductor | Burned Open | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1238 | Animal | Squirrel | Switch | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
1239 | Animal | Squirrel | Switch | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
1240 | Animal | Squirrel | Switch (OH) | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
1241 | Animal | Squirrel | Switch (OH) | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
1242 | Animal | Squirrel | Switch (UG) | Leaking | All | Underground facilities = no ignition risk
1243 | Animal | Squirrel | Transformer |  | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1244 | Animal | Squirrel | Transformer | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1245 | Animal | Squirrel | Transformer | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1246 | Animal | Squirrel | Transformer | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1247 | Animal | Squirrel | Transformer | Burned/flashed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1248 | Animal | Squirrel | Transformer | Malfunctioning | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1249 | Animal | Squirrel | Transformer | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1250 | Animal | Squirrel | Transformer | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1251 | Animal | Squirrel | Transformer (OH) | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1252 | Animal | Squirrel | Transformer (OH) | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1253 | Animal | Squirrel | Transformer (OH) | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1254 | Animal | Squirrel | Transformer (OH) | Burned/flashed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1255 | Animal | Squirrel | Transformer (OH) | Contaminated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1256 | Animal | Squirrel | Transformer (OH) | Deteriorated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1257 | Animal | Squirrel | Transformer (OH) | Leaking | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1258 | Animal | Squirrel | Transformer (OH) | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1259 | Animal | Squirrel | Transformer (UG) | Blown/failed | All | UG Facilities = no ignition risk
1260 | Animal | Squirrel | Transformer (UG) | Normal | All | UG Facilities = no ignition risk
1261 | Company Initiated | Construction Activity/equip- company | Anchor or Guy | Deteriorated | None | Company Initiated Outage. Not outage related.
1262 | Company Initiated | Construction Activity/equip- company | Anchor or Guy | Normal | None | Company Initiated Outage. Not outage related.
1263 | Company Initiated | Construction Activity/equip- company | Cable Termination(live front | Normal | None | Company Initiated Outage. Not outage related.
1264 | Company Initiated | Construction Activity/equip- company | Capacitor | Normal | None | Company Initiated Outage. Not outage related.
1265 | Company Initiated | Construction Activity/equip- company | Circuit Breaker | Normal | None | Company Initiated Outage. Not outage related.
1266 | Company Initiated | Construction Activity/equip- company | Conductor- Overhead | Arcing | None | Company Initiated Outage. Not outage related.
1267 | Company Initiated | Construction Activity/equip- company | Conductor- Overhead | Broken | None | Company Initiated Outage. Not outage related.
1268 | Company Initiated | Construction Activity/equip- company | Conductor- Overhead | Broken- wire on ground | None | Company Initiated Outage. Not outage related.
1269 | Company Initiated | Construction Activity/equip- company | Conductor- Overhead | Burned/flashed | None | Company Initiated Outage. Not outage related.
1270 | Company Initiated | Construction Activity/equip- company | Conductor- Overhead | Deteriorated | None | Company Initiated Outage. Not outage related.
1271 | Company Initiated | Construction Activity/equip- company | Conductor- Overhead | Normal | None | Company Initiated Outage. Not outage related.
1272 | Company Initiated | Construction Activity/equip- company | Conductor- Overhead | On Ground | None | Company Initiated Outage. Not outage related.
1273 | Company Initiated | Construction Activity/equip- company | Conductor- Overhead | Together | None | Company Initiated Outage. Not outage related.
1274 | Company Initiated | Construction Activity/equip- company | Conductor- Underground | Broken | None | Company Initiated Outage. Not outage related.
1275 | Company Initiated | Construction Activity/equip- company | Conductor- Underground | Burned/flashed | None | Company Initiated Outage. Not outage related.
1276 | Company Initiated | Construction Activity/equip- company | Conductor- Underground | Deteriorated | None | Company Initiated Outage. Not outage related.
1277 | Company Initiated | Construction Activity/equip- company | Conductor- Underground | Normal | None | Company Initiated Outage. Not outage related.
1278 | Company Initiated | Construction Activity/equip- company | Connector or Splice (OH) | Broken | None | Company Initiated Outage. Not outage related.
1279 | Company Initiated | Construction Activity/equip- company | Connector or Splice (OH) | Broken- wire on ground | None | Company Initiated Outage. Not outage related.
1280 | Company Initiated | Construction Activity/equip- company | Connector or Splice (OH) | Broken- wire on object | None | Company Initiated Outage. Not outage related.
1281 | Company Initiated | Construction Activity/equip- company | Connector or Splice (OH) | Burned Open | None | Company Initiated Outage. Not outage related.
1282 | Company Initiated | Construction Activity/equip- company | Connector or Splice (OH) | Normal | None | Company Initiated Outage. Not outage related.
1283 | Company Initiated | Construction Activity/equip- company | Connector or Splice (UG) | Blown/failed | None | Company Initiated Outage. Not outage related.
1284 | Company Initiated | Construction Activity/equip- company | Connector or Splice (UG) | Broken | None | Company Initiated Outage. Not outage related.
1285 | Company Initiated | Construction Activity/equip- company | Connector or Splice (UG) | Normal | None | Company Initiated Outage. Not outage related.
1286 | Company Initiated | Construction Activity/equip- company | Crossarm- Wood | Broken | None | Company Initiated Outage. Not outage related.
1287 | Company Initiated | Construction Activity/equip- company | Crossarm- Wood | Deteriorated | None | Company Initiated Outage. Not outage related.
1288 | Company Initiated | Construction Activity/equip- company | Crossarm- Wood | Normal | None | Company Initiated Outage. Not outage related.
1289 | Company Initiated | Construction Activity/equip- company | Cutout- fuse holder | Blown/failed | None | Company Initiated Outage. Not outage related.
1290 | Company Initiated | Construction Activity/equip- company | Cutout- fuse holder | Broken | None | Company Initiated Outage. Not outage related.
1291 | Company Initiated | Construction Activity/equip- company | Cutout- fuse holder | Burned/flashed | None | Company Initiated Outage. Not outage related.
1292 | Company Initiated | Construction Activity/equip- company | Cutout- fuse holder | Normal | None | Company Initiated Outage. Not outage related.
1293 | Company Initiated | Construction Activity/equip- company | Elbow | Blown/failed | None | Company Initiated Outage. Not outage related.
1294 | Company Initiated | Construction Activity/equip- company | Elbow | Burned/flashed | None | Company Initiated Outage. Not outage related.
1295 | Company Initiated | Construction Activity/equip- company | Elbow | Deteriorated | None | Company Initiated Outage. Not outage related.
1296 | Company Initiated | Construction Activity/equip- company | Elbow | Normal | None | Company Initiated Outage. Not outage related.
1297 | Company Initiated | Construction Activity/equip- company | Footings- Tower or Pole | Normal | None | Company Initiated Outage. Not outage related.
1298 | Company Initiated | Construction Activity/equip- company | Fuse | Arcing | None | Company Initiated Outage. Not outage related.
1299 | Company Initiated | Construction Activity/equip- company | Fuse | Blown/failed | None | Company Initiated Outage. Not outage related.
1300 | Company Initiated | Construction Activity/equip- company | Fuse | Burned Open | None | Company Initiated Outage. Not outage related.
1301 | Company Initiated | Construction Activity/equip- company | Fuse | Normal | None | Company Initiated Outage. Not outage related.
1302 | Company Initiated | Construction Activity/equip- company | Generator | Malfunctioning | None | Company Initiated Outage. Not outage related.
1303 | Company Initiated | Construction Activity/equip- company | Insulator | Broken | None | Company Initiated Outage. Not outage related.
1304 | Company Initiated | Construction Activity/equip- company | Jumper | Arcing | None | Company Initiated Outage. Not outage related.
1305 | Company Initiated | Construction Activity/equip- company | Jumper | Broken | None | Company Initiated Outage. Not outage related.
1306 | Company Initiated | Construction Activity/equip- company | Jumper | Burned Open | None | Company Initiated Outage. Not outage related.
1307 | Company Initiated | Construction Activity/equip- company | Jumper | Burned/flashed | None | Company Initiated Outage. Not outage related.
1308 | Company Initiated | Construction Activity/equip- company | Jumper | Normal | None | Company Initiated Outage. Not outage related.
1309 | Company Initiated | Construction Activity/equip- company | Lightning Arrestor | Normal | None | Company Initiated Outage. Not outage related.
1310 | Company Initiated | Construction Activity/equip- company | Other | Broken | None | Company Initiated Outage. Not outage related.
1311 | Company Initiated | Construction Activity/equip- company | Other | Normal | None | Company Initiated Outage. Not outage related.
1312 | Company Initiated | Construction Activity/equip- company | Pole - Tower- steel | Normal | None | Company Initiated Outage. Not outage related.
1313 | Company Initiated | Construction Activity/equip- company | Pole-Wood | Broken | None | Company Initiated Outage. Not outage related.
1314 | Company Initiated | Construction Activity/equip- company | Pole-Wood | Broken- wire on ground | None | Company Initiated Outage. Not outage related.
1315 | Company Initiated | Construction Activity/equip- company | Pole-Wood | Burned/flashed | None | Company Initiated Outage. Not outage related.
1316 | Company Initiated | Construction Activity/equip- company | Pole-Wood | Deteriorated | None | Company Initiated Outage. Not outage related.
1317 | Company Initiated | Construction Activity/equip- company | Pole-Wood | Normal | None | Company Initiated Outage. Not outage related.
1318 | Company Initiated | Construction Activity/equip- company | Pole-Wood | On Ground | None | Company Initiated Outage. Not outage related.
1319 | Company Initiated | Construction Activity/equip- company | Pothead(Riser Termination) | Normal | None | Company Initiated Outage. Not outage related.
1320 | Company Initiated | Construction Activity/equip- company | Recloser | Malfunctioning | None | Company Initiated Outage. Not outage related.
1321 | Company Initiated | Construction Activity/equip- company | Recloser | Normal | None | Company Initiated Outage. Not outage related.
1322 | Company Initiated | Construction Activity/equip- company | Regulator | Normal | None | Company Initiated Outage. Not outage related.
1323 | Company Initiated | Construction Activity/equip- company | Relay | Malfunctioning | None | Company Initiated Outage. Not outage related.
1324 | Company Initiated | Construction Activity/equip- company | Riser | Normal | None | Company Initiated Outage. Not outage related.
1325 | Company Initiated | Construction Activity/equip- company | Secondary | Bent or Twisted | None | Company Initiated Outage. Not outage related.
1326 | Company Initiated | Construction Activity/equip- company | Secondary | Broken | None | Company Initiated Outage. Not outage related.
1327 | Company Initiated | Construction Activity/equip- company | Secondary | Deteriorated | None | Company Initiated Outage. Not outage related.
1328 | Company Initiated | Construction Activity/equip- company | Secondary | Normal | None | Company Initiated Outage. Not outage related.
1329 | Company Initiated | Construction Activity/equip- company | Secondary | Together | None | Company Initiated Outage. Not outage related.
1330 | Company Initiated | Construction Activity/equip- company | Service conductor | Broken | None | Company Initiated Outage. Not outage related.
1331 | Company Initiated | Construction Activity/equip- company | Switch | Normal | None | Company Initiated Outage. Not outage related.
1332 | Company Initiated | Construction Activity/equip- company | Switch (OH) | Broken | None | Company Initiated Outage. Not outage related.
1333 | Company Initiated | Construction Activity/equip- company | Switch (OH) | Normal | None | Company Initiated Outage. Not outage related.
1334 | Company Initiated | Construction Activity/equip- company | Switch (UG) | Blown/failed | None | Company Initiated Outage. Not outage related.
1335 | Company Initiated | Construction Activity/equip- company | Switch (UG) | Broken | None | Company Initiated Outage. Not outage related.
1336 | Company Initiated | Construction Activity/equip- company | Switch (UG) | Normal | None | Company Initiated Outage. Not outage related.
1337 | Company Initiated | Construction Activity/equip- company | Transformer | Broken | None | Company Initiated Outage. Not outage related.
1338 | Company Initiated | Construction Activity/equip- company | Transformer | Deteriorated | None | Company Initiated Outage. Not outage related.
1339 | Company Initiated | Construction Activity/equip- company | Transformer | Leaking | None | Company Initiated Outage. Not outage related.
1340 | Company Initiated | Construction Activity/equip- company | Transformer | Normal | None | Company Initiated Outage. Not outage related.
1341 | Company Initiated | Construction Activity/equip- company | Transformer (OH) | Blown/failed | None | Company Initiated Outage. Not outage related.
1342 | Company Initiated | Construction Activity/equip- company | Transformer (OH) | Broken | None | Company Initiated Outage. Not outage related.
1343 | Company Initiated | Construction Activity/equip- company | Transformer (OH) | Normal | None | Company Initiated Outage. Not outage related.
1344 | Company Initiated | Construction Activity/equip- company | Transformer (UG) | Blown/failed | None | Company Initiated Outage. Not outage related.
1345 | Company Initiated | Construction Activity/equip- company | Transformer (UG) | Broken | None | Company Initiated Outage. Not outage related.
1346 | Company Initiated | Construction Activity/equip- company | Transformer (UG) | Leaking | None | Company Initiated Outage. Not outage related.
1347 | Company Initiated | Construction Activity/equip- company | Transformer (UG) | Normal | None | Company Initiated Outage. Not outage related.
1348 | Company Initiated | Contact with High Voltage- company |  | Blown/failed | None | Company Initiated Outage. Not outage related.
1349 | Company Initiated | Contact with High Voltage- company | Conductor- Overhead | Broken- wire on ground | None | Company Initiated Outage. Not outage related.
1350 | Company Initiated | Contact with High Voltage- company | Conductor- Overhead | Burned/flashed | None | Company Initiated Outage. Not outage related.
1351 | Company Initiated | Contact with High Voltage- company | Conductor- Overhead | Normal | None | Company Initiated Outage. Not outage related.
1352 | Company Initiated | Contact with High Voltage- company | Conductor- Overhead | On Ground | None | Company Initiated Outage. Not outage related.
1353 | Company Initiated | Contact with High Voltage- company | Conductor- Overhead | Together | None | Company Initiated Outage. Not outage related.
1354 | Company Initiated | Contact with High Voltage- company | Conductor- Underground | Burned/flashed | None | Company Initiated Outage. Not outage related.
1355 | Company Initiated | Contact with High Voltage- company | Cutout- fuse holder | Normal | None | Company Initiated Outage. Not outage related.
1356 | Company Initiated | Contact with High Voltage- company | Fuse | Blown/failed | None | Company Initiated Outage. Not outage related.
1357 | Company Initiated | Contact with High Voltage- company | Fuse | Normal | None | Company Initiated Outage. Not outage related.
1358 | Company Initiated | Contact with High Voltage- company | Pothead(Riser Termination) | Burned/flashed | None | Company Initiated Outage. Not outage related.
1359 | Company Initiated | Contact with High Voltage- company | Secondary | Burned/flashed | None | Company Initiated Outage. Not outage related.
1360 | Company Initiated | Contact with High Voltage- company | Switch (UG) | Broken | None | Company Initiated Outage. Not outage related.
1361 | Company Initiated | Coordination failure |  | Normal | None | Company Initiated Outage. Not outage related.
1362 | Company Initiated | Coordination failure | Capacitor | Normal | None | Company Initiated Outage. Not outage related.
1363 | Company Initiated | Coordination failure | Circuit Breaker | Malfunctioning | None | Company Initiated Outage. Not outage related.
1364 | Company Initiated | Coordination failure | Circuit Breaker | Normal | None | Company Initiated Outage. Not outage related.
1365 | Company Initiated | Coordination failure | Conductor- Overhead | Burned/flashed | None | Company Initiated Outage. Not outage related.
1366 | Company Initiated | Coordination failure | Conductor- Overhead | Normal | None | Company Initiated Outage. Not outage related.
1367 | Company Initiated | Coordination failure | Conductor- Underground | Broken | None | Company Initiated Outage. Not outage related.
1368 | Company Initiated | Coordination failure | Crossarm- Wood | Burned/flashed | None | Company Initiated Outage. Not outage related.
1369 | Company Initiated | Coordination failure | Crossarm- Wood | Deteriorated | None | Company Initiated Outage. Not outage related.
1370 | Company Initiated | Coordination failure | Elbow | Blown/failed | None | Company Initiated Outage. Not outage related.
1371 | Company Initiated | Coordination failure | Fuse | Blown/failed | None | Company Initiated Outage. Not outage related.
1372 | Company Initiated | Coordination failure | Fuse | Normal | None | Company Initiated Outage. Not outage related.
1373 | Company Initiated | Coordination failure | Other | Malfunctioning | None | Company Initiated Outage. Not outage related.
1374 | Company Initiated | Coordination failure | Other | Normal | None | Company Initiated Outage. Not outage related.
1375 | Company Initiated | Coordination failure | Pole-Wood | Broken- wire on ground | None | Company Initiated Outage. Not outage related.
1376 | Company Initiated | Coordination failure | Pole-Wood | Deteriorated | None | Company Initiated Outage. Not outage related.
1377 | Company Initiated | Coordination failure | Recloser | Malfunctioning | None | Company Initiated Outage. Not outage related.
1378 | Company Initiated | Coordination failure | Recloser | Normal | None | Company Initiated Outage. Not outage related.
1379 | Company Initiated | Coordination failure | Relay | Malfunctioning | None | Company Initiated Outage. Not outage related.
1380 | Company Initiated | Coordination failure | SCADA | Malfunctioning | None | Company Initiated Outage. Not outage related.
1381 | Company Initiated | Coordination failure | Stepdown | Normal | None | Company Initiated Outage. Not outage related.
1382 | Company Initiated | Coordination failure | Switch (UG) | Normal | None | Company Initiated Outage. Not outage related.
1383 | Company Initiated | Coordination failure | Transformer |  | None | Company Initiated Outage. Not outage related.
1384 | Company Initiated | Coordination failure | Transformer | Normal | None | Company Initiated Outage. Not outage related.
1385 | Company Initiated | Dig in- company | Conductor- Overhead | Normal | None | Company Initiated Outage. Not outage related.
1386 | Company Initiated | Dig in- company | Conductor- Underground | Broken | None | Company Initiated Outage. Not outage related.
1387 | Company Initiated | Dig in- company | Conductor- Underground | Burned/flashed | None | Company Initiated Outage. Not outage related.
1388 | Company Initiated | Dig in- company | Secondary | Broken | None | Company Initiated Outage. Not outage related.
1389 | Company Initiated | Dig in- company | Service conductor | Broken | None | Company Initiated Outage. Not outage related.
1390 | Company Initiated | Improper Construction | Anchor or Guy | Broken | None | Company Initiated Outage. Not outage related.
1391 | Company Initiated | Improper Construction | Booster | Normal | None | Company Initiated Outage. Not outage related.
1392 | Company Initiated | Improper Construction | Cable Termination(live front | Normal | None | Company Initiated Outage. Not outage related.
1393 | Company Initiated | Improper Construction | Conductor- Overhead | Annealed | None | Company Initiated Outage. Not outage related.
1394 | Company Initiated | Improper Construction | Conductor- Overhead | Arcing | None | Company Initiated Outage. Not outage related.
1395 | Company Initiated | Improper Construction | Conductor- Overhead | Bent or Twisted | None | Company Initiated Outage. Not outage related.
1396 | Company Initiated | Improper Construction | Conductor- Overhead | Broken | None | Company Initiated Outage. Not outage related.
1397 | Company Initiated | Improper Construction | Conductor- Overhead | Broken- wire on ground | None | Company Initiated Outage. Not outage related.
1398 | Company Initiated | Improper Construction | Conductor- Overhead | Burned/flashed | None | Company Initiated Outage. Not outage related.
1399 | Company Initiated | Improper Construction | Conductor- Overhead | Deteriorated | None | Company Initiated Outage. Not outage related.
1400 | Company Initiated | Improper Construction | Conductor- Overhead | Malfunctioning | None | Company Initiated Outage. Not outage related.
1401 | Company Initiated | Improper Construction | Conductor- Overhead | Normal | None | Company Initiated Outage. Not outage related.
1402 | Company Initiated | Improper Construction | Conductor- Overhead | Together | None | Company Initiated Outage. Not outage related.
1403 | Company Initiated | Improper Construction | Conductor- Underground | Burned/flashed | None | Company Initiated Outage. Not outage related.
1404 | Company Initiated | Improper Construction | Conductor- Underground | Normal | None | Company Initiated Outage. Not outage related.
1405 | Company Initiated | Improper Construction | Connector or Splice (OH) | Broken | None | Company Initiated Outage. Not outage related.
1406 | Company Initiated | Improper Construction | Connector or Splice (OH) | Broken- wire on ground | None | Company Initiated Outage. Not outage related.
1407 | Company Initiated | Improper Construction | Connector or Splice (OH) | Normal | None | Company Initiated Outage. Not outage related.
1408 | Company Initiated | Improper Construction | Connector or Splice (UG) | Broken | None | Company Initiated Outage. Not outage related.
1409 | Company Initiated | Improper Construction | Connector or Splice (UG) | Normal | None | Company Initiated Outage. Not outage related.
1410 | Company Initiated | Improper Construction | Connector or Splice (UG) | Together | None | Company Initiated Outage. Not outage related.
1411 | Company Initiated | Improper Construction | Crossarm- Wood | Burned/flashed | None | Company Initiated Outage. Not outage related.
1412 | Company Initiated | Improper Construction | Crossarm- Wood | Contaminated | None | Company Initiated Outage. Not outage related.
1413 | Company Initiated | Improper Construction | Crossarm- Wood | Normal | None | Company Initiated Outage. Not outage related.
1414 | Company Initiated | Improper Construction | Cutout- fuse holder | Blown/failed | None | Company Initiated Outage. Not outage related.
1415 | Company Initiated | Improper Construction | Cutout- fuse holder | Broken | None | Company Initiated Outage. Not outage related.
1416 | Company Initiated | Improper Construction | Cutout- fuse holder | Burned/flashed | None | Company Initiated Outage. Not outage related.
1417 | Company Initiated | Improper Construction | Cutout- fuse holder | Normal | None | Company Initiated Outage. Not outage related.
1418 | Company Initiated | Improper Construction | Elbow | Normal | None | Company Initiated Outage. Not outage related.
1419 | Company Initiated | Improper Construction | Fuse | Arcing | None | Company Initiated Outage. Not outage related.
1420 | Company Initiated | Improper Construction | Fuse | Blown/failed | None | Company Initiated Outage. Not outage related.
1421 | Company Initiated | Improper Construction | Fuse | Normal | None | Company Initiated Outage. Not outage related.
1422 | Company Initiated | Improper Construction | Insulator | Broken- wire on ground | None | Company Initiated Outage. Not outage related.
1423 | Company Initiated | Improper Construction | Interrupter | Normal | None | Company Initiated Outage. Not outage related.
1424 | Company Initiated | Improper Construction | Jumper | Arcing | None | Company Initiated Outage. Not outage related.
1425 | Company Initiated | Improper Construction | Jumper | Normal | None | Company Initiated Outage. Not outage related.
1426 | Company Initiated | Improper Construction | Other | Malfunctioning | None | Company Initiated Outage. Not outage related.
1427 | Company Initiated | Improper Construction | Other | Normal | None | Company Initiated Outage. Not outage related.
1428 | Company Initiated | Improper Construction | Other | Together | None | Company Initiated Outage. Not outage related.
1429 | Company Initiated | Improper Construction | Pole-Wood | Normal | None | Company Initiated Outage. Not outage related.
1430 | Company Initiated | Improper Construction | Recloser | Normal | None | Company Initiated Outage. Not outage related.
1431 | Company Initiated | Improper Construction | Regulator | Burned/flashed | None | Company Initiated Outage. Not outage related.
1432 | Company Initiated | Improper Construction | Regulator | Malfunctioning | None | Company Initiated Outage. Not outage related.
1433 | Company Initiated | Improper Construction | Regulator | Normal | None | Company Initiated Outage. Not outage related.
1434 | Company Initiated | Improper Construction | Secondary | Bent or Twisted | None | Company Initiated Outage. Not outage related.
1435 | Company Initiated | Improper Construction | Secondary | Broken | None | Company Initiated Outage. Not outage related.
1436 | Company Initiated | Improper Construction | Secondary | Burned Open | None | Company Initiated Outage. Not outage related.
1437 | Company Initiated | Improper Construction | Secondary | Normal | None | Company Initiated Outage. Not outage related.
1438 | Company Initiated | Improper Construction | Secondary | Together | None | Company Initiated Outage. Not outage related.
1439 | Company Initiated | Improper Construction | Switch | Normal | None | Company Initiated Outage. Not outage related.
1440 | Company Initiated | Improper Construction | Switch (OH) | Arcing | None | Company Initiated Outage. Not outage related.
1441 | Company Initiated | Improper Construction | Switch (OH) | Blown/failed | None | Company Initiated Outage. Not outage related.
1442 | Company Initiated | Improper Construction | Switch (OH) | Normal | None | Company Initiated Outage. Not outage related.
1443 | Company Initiated | Improper Construction | Switch (UG) | Normal | None | Company Initiated Outage. Not outage related.
1444 | Company Initiated | Improper Construction | Transformer |  | None | Company Initiated Outage. Not outage related.
1445 | Company Initiated | Improper Construction | Transformer | Blown/failed | None | Company Initiated Outage. Not outage related.
1446 | Company Initiated | Improper Construction | Transformer | Normal | None | Company Initiated Outage. Not outage related.
1447 | Company Initiated | Improper Construction | Transformer (OH) | Normal | None | Company Initiated Outage. Not outage related.
1448 | Company Initiated | Improper Construction | Transformer (UG) | Blown/failed | None | Company Initiated Outage. Not outage related.
1449 | Company Initiated | Improper Construction | Transformer (UG) | Normal | None | Company Initiated Outage. Not outage related.
1450 | Company Initiated | Insulator washing | Bushing | Broken | None | Company Initiated Outage. Not outage related.
1451 | Company Initiated | Insulator washing | Circuit Breaker | Burned/flashed | None | Company Initiated Outage. Not outage related.
1452 | Company Initiated | Insulator washing | Conductor- Overhead | Burned/flashed | None | Company Initiated Outage. Not outage related.
1453 | Company Initiated | Operating error |  |  | None | Company Initiated Outage. Not outage related.
1454 | Company Initiated | Operating error | Capacitor | Blown/failed | None | Company Initiated Outage. Not outage related.
1455 | Company Initiated | Operating error | Circuit Breaker | Normal | None | Company Initiated Outage. Not outage related.
1456 | Company Initiated | Operating error | Conductor- Overhead | Broken- wire on ground | None | Company Initiated Outage. Not outage related.
1457 | Company Initiated | Operating error | Conductor- Overhead | Burned/flashed | None | Company Initiated Outage. Not outage related.
1458 | Company Initiated | Operating error | Conductor- Overhead | Normal | None | Company Initiated Outage. Not outage related.
1459 | Company Initiated | Operating error | Conductor- Underground | Broken | None | Company Initiated Outage. Not outage related.
1460 | Company Initiated | Operating error | Conductor- Underground | Normal | None | Company Initiated Outage. Not outage related.
1461 | Company Initiated | Operating error | Customer Equipment | Malfunctioning | None | Company Initiated Outage. Not outage related.
1462 | Company Initiated | Operating error | Cutout- fuse holder | Normal | None | Company Initiated Outage. Not outage related.
1463 | Company Initiated | Operating error | Elbow | Burned/flashed | None | Company Initiated Outage. Not outage related.
1464 | Company Initiated | Operating error | Fuse |  | None | Company Initiated Outage. Not outage related.
1465 | Company Initiated | Operating error | Fuse | Blown/failed | None | Company Initiated Outage. Not outage related.
1466 | Company Initiated | Operating error | Fuse | Normal | None | Company Initiated Outage. Not outage related.
1467 | Company Initiated | Operating error | Jumper | Broken | None | Company Initiated Outage. Not outage related.
1468 | Company Initiated | Operating error | Jumper | Broken- wire on ground | None | Company Initiated Outage. Not outage related.
1469 | Company Initiated | Operating error | Jumper | Normal | None | Company Initiated Outage. Not outage related.
1470 | Company Initiated | Operating error | Other | Burned/flashed | None | Company Initiated Outage. Not outage related.
1471 | Company Initiated | Operating error | Other | Normal | None | Company Initiated Outage. Not outage related.
1472 | Company Initiated | Operating error | Recloser | Blown/failed | None | Company Initiated Outage. Not outage related.
1473 | Company Initiated | Operating error | Recloser | Normal | None | Company Initiated Outage. Not outage related.
1474 | Company Initiated | Operating error | Regulator | Normal | None | Company Initiated Outage. Not outage related.
1475 | Company Initiated | Operating error | Relay | Normal | None | Company Initiated Outage. Not outage related.
1476 | Company Initiated | Operating error | SCADA | Normal | None | Company Initiated Outage. Not outage related.
1477 | Company Initiated | Operating error | Secondary | Arcing | None | Company Initiated Outage. Not outage related.
1478 | Company Initiated | Operating error | Switch |  | None | Company Initiated Outage. Not outage related.
1479 | Company Initiated | Operating error | Switch | Contaminated | None | Company Initiated Outage. Not outage related.
1480 | Company Initiated | Operating error | Switch (OH) | Burned/flashed | None | Company Initiated Outage. Not outage related.
1481 | Company Initiated | Operating error | Switch (OH) | Normal | None | Company Initiated Outage. Not outage related.
1482 | Company Initiated | Operating error | Switch (UG) | Normal | None | Company Initiated Outage. Not outage related.
1483 | Company Initiated | Operating error | Transformer (UG) |  | None | Company Initiated Outage. Not outage related.
1484 | Company Initiated | Operating error | Transformer (UG) | Burned/flashed | None | Company Initiated Outage. Not outage related.
1485 | Company Initiated | Operating error | Transformer (UG) | Normal | None | Company Initiated Outage. Not outage related.
1486 | Company Initiated | Other Circuits |  |  | None | Company Initiated Outage. Not outage related.
1487 | Company Initiated | Other Circuits | Booster | Deteriorated | None | Company Initiated Outage. Not outage related.
1488 | Company Initiated | Other Circuits | Circuit Breaker | Normal | None | Company Initiated Outage. Not outage related.
1489 | Company Initiated | Other Circuits | Conductor- Overhead | Broken | None | Company Initiated Outage. Not outage related.
1490 | Company Initiated | Other Circuits | Conductor- Overhead | Broken- wire on ground | None | Company Initiated Outage. Not outage related.
1491 | Company Initiated | Other Circuits | Conductor- Overhead | Broken- wire on object | None | Company Initiated Outage. Not outage related.
1492 | Company Initiated | Other Circuits | Conductor- Overhead | Deteriorated | None | Company Initiated Outage. Not outage related.
1493 | Company Initiated | Other Circuits | Conductor- Overhead | Normal | None | Company Initiated Outage. Not outage related.
1494 | Company Initiated | Other Circuits | Conductor- Overhead | Together | None | Company Initiated Outage. Not outage related.
1495 | Company Initiated | Other Circuits | Conductor- Underground | Broken | None | Company Initiated Outage. Not outage related.
1496 | Company Initiated | Other Circuits | Conductor- Underground | Burned/flashed | None | Company Initiated Outage. Not outage related.
1497 | Company Initiated | Other Circuits | Conductor- Underground | Normal | None | Company Initiated Outage. Not outage related.
1498 | Company Initiated | Other Circuits | Crossarm- Wood | Broken | None | Company Initiated Outage. Not outage related.
1499 | Company Initiated | Other Circuits | Cutout- fuse holder | Broken | None | Company Initiated Outage. Not outage related.
1500 | Company Initiated | Other Circuits | Footings- Tower or Pole | Bent or Twisted | None | Company Initiated Outage. Not outage related.
1501 | Company Initiated | Other Circuits | Fuse | Blown/failed | None | Company Initiated Outage. Not outage related.
1502 | Company Initiated | Other Circuits | Fuse | Deteriorated | None | Company Initiated Outage. Not outage related.
1503 | Company Initiated | Other Circuits | Fuse | Normal | None | Company Initiated Outage. Not outage related.
1504 | Company Initiated | Other Circuits | Generator | Contaminated | None | Company Initiated Outage. Not outage related.
1505 | Company Initiated | Other Circuits | Generator | Malfunctioning | None | Company Initiated Outage. Not outage related.
1506 | Company Initiated | Other Circuits | Jumper | Burned Open | None | Company Initiated Outage. Not outage related.
1507 | Company Initiated | Other Circuits | Jumper | Malfunctioning | None | Company Initiated Outage. Not outage related.
1508 | Company Initiated | Other Circuits | Jumper | Normal | None | Company Initiated Outage. Not outage related.
1509 | Company Initiated | Other Circuits | Lightning Arrestor | Blown/failed | None | Company Initiated Outage. Not outage related.
1510 | Company Initiated | Other Circuits | Other |  | None | Company Initiated Outage. Not outage related.
1511 | Company Initiated | Other Circuits | Other | Broken | None | Company Initiated Outage. Not outage related.
1512 | Company Initiated | Other Circuits | Other | Normal | None | Company Initiated Outage. Not outage related.
1513 | Company Initiated | Other Circuits | Pole-Wood | Burned/flashed | None | Company Initiated Outage. Not outage related.
1514 | Company Initiated | Other Circuits | Pole-Wood | Deteriorated | None | Company Initiated Outage. Not outage related.
1515 | Company Initiated | Other Circuits | Pole-Wood | Normal | None | Company Initiated Outage. Not outage related.
1516 | Company Initiated | Other Circuits | Recloser | Normal | None | Company Initiated Outage. Not outage related.
1517 | Company Initiated | Other Circuits | Regulator | Broken | None | Company Initiated Outage. Not outage related.
1518 | Company Initiated | Other Circuits | Regulator | Malfunctioning | None | Company Initiated Outage. Not outage related.
1519 | Company Initiated | Other Circuits | Regulator- LTC substation | Normal | None | Company Initiated Outage. Not outage related.
1520 | Company Initiated | Other Circuits | Switch (OH) | Normal | None | Company Initiated Outage. Not outage related.
1521 | Company Initiated | Other Circuits | Switch (UG) | Normal | None | Company Initiated Outage. Not outage related.
1522 | Company Initiated | Other Circuits | Transformer | Blown/failed | None | Company Initiated Outage. Not outage related.
1523 | Company Initiated | Other Circuits | Transformer | Broken | None | Company Initiated Outage. Not outage related.
1524 | Company Initiated | Other Circuits | Transformer | Deteriorated | None | Company Initiated Outage. Not outage related.
1525 | Company Initiated | Other Circuits | Transformer | Malfunctioning | None | Company Initiated Outage. Not outage related.
1526 | Company Initiated | Other Circuits | Transformer (UG) | Normal | None | Company Initiated Outage. Not outage related.
1527 | Company Initiated | Personnel- company |  |  | None | Company Initiated Outage. Not outage related.
1528 | Company Initiated | Personnel- company |  | Blown/failed | None | Company Initiated Outage. Not outage related.
1529 | Company Initiated | Personnel- company |  | Broken | None | Company Initiated Outage. Not outage related.
1530 | Company Initiated | Personnel- company |  | Normal | None | Company Initiated Outage. Not outage related.
1531 | Company Initiated | Personnel- company | Bus | Normal | None | Company Initiated Outage. Not outage related.
1532 | Company Initiated | Personnel- company | Capacitor | Normal | None | Company Initiated Outage. Not outage related.
1533 | Company Initiated | Personnel- company | Circuit Breaker | Normal | None | Company Initiated Outage. Not outage related.
1534 | Company Initiated | Personnel- company | Conductor- Overhead |  | None | Company Initiated Outage. Not outage related.
1535 | Company Initiated | Personnel- company | Conductor- Overhead | Arcing | None | Company Initiated Outage. Not outage related.
1536 | Company Initiated | Personnel- company | Conductor- Overhead | Broken | None | Company Initiated Outage. Not outage related.
1537 | Company Initiated | Personnel- company | Conductor- Overhead | Broken- wire on ground | None | Company Initiated Outage. Not outage related.
1538 | Company Initiated | Personnel- company | Conductor- Overhead | Normal | None | Company Initiated Outage. Not outage related.
1539 | Company Initiated | Personnel- company | Conductor- Overhead | Together | None | Company Initiated Outage. Not outage related.
1540 | Company Initiated | Personnel- company | Conductor- Underground | Blown/failed | None | Company Initiated Outage. Not outage related.
1541 | Company Initiated | Personnel- company | Conductor- Underground | Burned/flashed | None | Company Initiated Outage. Not outage related.
1542 | Company Initiated | Personnel- company | Conductor- Underground | Deteriorated | None | Company Initiated Outage. Not outage related.
1543 | Company Initiated | Personnel- company | Conductor- Underground | Normal | None | Company Initiated Outage. Not outage related.
1544 | Company Initiated | Personnel- company | Connector or Splice (OH) | Broken | None | Company Initiated Outage. Not outage related.
1545 | Company Initiated | Personnel- company | Connector or Splice (OH) | Normal | None | Company Initiated Outage. Not outage related.
1546 | Company Initiated | Personnel- company | Crossarm- Wood | Broken | None | Company Initiated Outage. Not outage related.
1547 | Company Initiated | Personnel- company | Cutout- fuse holder | Arcing | None | Company Initiated Outage. Not outage related.
1548 | Company Initiated | Personnel- company | Cutout- Fused- Distribution | Normal | None | Company Initiated Outage. Not outage related.
1549 | Company Initiated | Personnel- company | Elbow | Blown/failed | None | Company Initiated Outage. Not outage related.
1550 | Company Initiated | Personnel- company | Elbow | Broken | None | Company Initiated Outage. Not outage related.
1551 | Company Initiated | Personnel- company | Elbow | Burned/flashed | None | Company Initiated Outage. Not outage related.
1552 | Company Initiated | Personnel- company | Elbow | Deteriorated | None | Company Initiated Outage. Not outage related.
1553 | Company Initiated | Personnel- company | Elbow | Normal | None | Company Initiated Outage. Not outage related.
1554 | Company Initiated | Personnel- company | Fuse | Arcing | None | Company Initiated Outage. Not outage related.
1555 | Company Initiated | Personnel- company | Fuse | Blown/failed | None | Company Initiated Outage. Not outage related.
1556 | Company Initiated | Personnel- company | Fuse | Normal | None | Company Initiated Outage. Not outage related.
1557 | Company Initiated | Personnel- company | Interrupter | Malfunctioning | None | Company Initiated Outage. Not outage related.
1558 | Company Initiated | Personnel- company | Interrupter | Normal | None | Company Initiated Outage. Not outage related.
1559 | Company Initiated | Personnel- company | Jumper | Arcing | None | Company Initiated Outage. Not outage related.
1560 | Company Initiated | Personnel- company | Jumper | Burned/flashed | None | Company Initiated Outage. Not outage related.
1561 | Company Initiated | Personnel- company | Jumper | Normal | None | Company Initiated Outage. Not outage related.
1562 | Company Initiated | Personnel- company | Metering Equipment |  | None | Company Initiated Outage. Not outage related.
1563 | Company Initiated | Personnel- company | Other | Deteriorated | None | Company Initiated Outage. Not outage related.
1564 | Company Initiated | Personnel- company | Other | Malfunctioning | None | Company Initiated Outage. Not outage related.
1565 | Company Initiated | Personnel- company | Other | Normal | None | Company Initiated Outage. Not outage related.
1566 | Company Initiated | Personnel- company | Pole-Wood | Broken | None | Company Initiated Outage. Not outage related.
1567 | Company Initiated | Personnel- company | Pole-Wood | Deteriorated | None | Company Initiated Outage. Not outage related.
1568 | Company Initiated | Personnel- company | Pole-Wood | Normal | None | Company Initiated Outage. Not outage related.
1569 | Company Initiated | Personnel- company | Pothead(Riser Termination) | Normal | None | Company Initiated Outage. Not outage related.
1570 | Company Initiated | Personnel- company | Recloser | Malfunctioning | None | Company Initiated Outage. Not outage related.
1571 | Company Initiated | Personnel- company | Recloser | Normal | None | Company Initiated Outage. Not outage related.
1572 | Company Initiated | Personnel- company | Regulator | Blown/failed | None | Company Initiated Outage. Not outage related.
1573 | Company Initiated | Personnel- company | Regulator | Broken | None | Company Initiated Outage. Not outage related.
1574 | Company Initiated | Personnel- company | Relay | Normal | None | Company Initiated Outage. Not outage related.
1575 | Company Initiated | Personnel- company | SCADA | Normal | None | Company Initiated Outage. Not outage related.
1576 | Company Initiated | Personnel- company | Secondary | Broken | None | Company Initiated Outage. Not outage related.
1577 | Company Initiated | Personnel- company | Secondary | Burned Open | None | Company Initiated Outage. Not outage related.
1578 | Company Initiated | Personnel- company | Secondary | Deteriorated | None | Company Initiated Outage. Not outage related.
1579 | Company Initiated | Personnel- company | Secondary | Normal | None | Company Initiated Outage. Not outage related.
1580 | Company Initiated | Personnel- company | Secondary | Together | None | Company Initiated Outage. Not outage related.
1581 | Company Initiated | Personnel- company | Sectionalizer | Normal | None | Company Initiated Outage. Not outage related.
1582 | Company Initiated | Personnel- company | Service conductor | Together | None | Company Initiated Outage. Not outage related.
1583 | Company Initiated | Personnel- company | Switch (OH) | Blown/failed | None | Company Initiated Outage. Not outage related.
1584 | Company Initiated | Personnel- company | Switch (OH) | Normal | None | Company Initiated Outage. Not outage related.
1585 | Company Initiated | Personnel- company | Switch (UG) | Broken | None | Company Initiated Outage. Not outage related.
1586 | Company Initiated | Personnel- company | Switch (UG) | Normal | None | Company Initiated Outage. Not outage related.
1587 | Company Initiated | Personnel- company | Transformer | Malfunctioning | None | Company Initiated Outage. Not outage related.
1588 | Company Initiated | Personnel- company | Transformer (OH) | Broken | None | Company Initiated Outage. Not outage related.
1589 | Company Initiated | Personnel- company | Transformer (OH) | Contaminated | None | Company Initiated Outage. Not outage related.
1590 | Company Initiated | Personnel- company | Transformer (OH) | Leaking | None | Company Initiated Outage. Not outage related.
1591 | Company Initiated | Personnel- company | Transformer (OH) | Normal | None | Company Initiated Outage. Not outage related.
1592 | Company Initiated | Personnel- company | Transformer (UG) |  | None | Company Initiated Outage. Not outage related.
1593 | Company Initiated | Personnel- company | Transformer (UG) | Arcing | None | Company Initiated Outage. Not outage related.
1594 | Company Initiated | Personnel- company | Transformer (UG) | Blown/failed | None | Company Initiated Outage. Not outage related.
1595 | Company Initiated | Personnel- company | Transformer (UG) | Broken | None | Company Initiated Outage. Not outage related.
1596 | Company Initiated | Personnel- company | Transformer (UG) | Deteriorated | None | Company Initiated Outage. Not outage related.
1597 | Company Initiated | Personnel- company | Transformer (UG) | Leaking | None | Company Initiated Outage. Not outage related.
1598 | Company Initiated | Personnel- company | Transformer (UG) | Normal | None | Company Initiated Outage. Not outage related.
1599 | Company Initiated | Return Circuit Normal | Booster | Burned/flashed | None | Company Initiated Outage. Not outage related.
1600 | Company Initiated | Return Circuit Normal | Bushing | Normal | None | Company Initiated Outage. Not outage related.
1601 | Company Initiated | Return Circuit Normal | Cable Termination(live front | Blown/failed | None | Company Initiated Outage. Not outage related.
1602 | Company Initiated | Return Circuit Normal | Cable Termination(live front | Normal | None | Company Initiated Outage. Not outage related.
1603 | Company Initiated | Return Circuit Normal | Circuit Breaker | Burned/flashed | None | Company Initiated Outage. Not outage related.
1604 | Company Initiated | Return Circuit Normal | Circuit Breaker | Normal | None | Company Initiated Outage. Not outage related.
1605 | Company Initiated | Return Circuit Normal | Conductor- Overhead | Arcing | None | Company Initiated Outage. Not outage related.
1606 | Company Initiated | Return Circuit Normal | Conductor- Overhead | Bent or Twisted | None | Company Initiated Outage. Not outage related.
1607 | Company Initiated | Return Circuit Normal | Conductor- Overhead | Broken | None | Company Initiated Outage. Not outage related.
1608 | Company Initiated | Return Circuit Normal | Conductor- Overhead | Broken- wire on ground | None | Company Initiated Outage. Not outage related.
1609 | Company Initiated | Return Circuit Normal | Conductor- Overhead | Broken- wire on object | None | Company Initiated Outage. Not outage related.
1610 | Company Initiated | Return Circuit Normal | Conductor- Overhead | Deteriorated | None | Company Initiated Outage. Not outage related.
1611 | Company Initiated | Return Circuit Normal | Conductor- Overhead | Normal | None | Company Initiated Outage. Not outage related.
1612 | Company Initiated | Return Circuit Normal | Conductor- Overhead | Together | None | Company Initiated Outage. Not outage related.
1613 | Company Initiated | Return Circuit Normal | Conductor- Underground | Broken | None | Company Initiated Outage. Not outage related.
1614 | Company Initiated | Return Circuit Normal | Conductor- Underground | Burned/flashed | None | Company Initiated Outage. Not outage related.
1615 | Company Initiated | Return Circuit Normal | Conductor- Underground | Deteriorated | None | Company Initiated Outage. Not outage related.
1616 | Company Initiated | Return Circuit Normal | Conductor- Underground | Normal | None | Company Initiated Outage. Not outage related.
1617 | Company Initiated | Return Circuit Normal | Connector or Splice (OH) | Arcing | None | Company Initiated Outage. Not outage related.
1618 | Company Initiated | Return Circuit Normal | Connector or Splice (OH) | Broken | None | Company Initiated Outage. Not outage related.
1619 | Company Initiated | Return Circuit Normal | Connector or Splice (OH) | Normal | None | Company Initiated Outage. Not outage related.
1620 | Company Initiated | Return Circuit Normal | Connector or Splice (UG) | Blown/failed | None | Company Initiated Outage. Not outage related.
1621 | Company Initiated | Return Circuit Normal | Connector or Splice (UG) | Burned/flashed | None | Company Initiated Outage. Not outage related.
1622 | Company Initiated | Return Circuit Normal | Connector or Splice (UG) | Normal | None | Company Initiated Outage. Not outage related.
1623 | Company Initiated | Return Circuit Normal | Crossarm- Wood | Broken | None | Company Initiated Outage. Not outage related.
1624 | Company Initiated | Return Circuit Normal | Crossarm- Wood | Burned/flashed | None | Company Initiated Outage. Not outage related.
1625 | Company Initiated | Return Circuit Normal | Crossarm- Wood | Normal | None | Company Initiated Outage. Not outage related.
1626 | Company Initiated | Return Circuit Normal | Customer Equipment | Normal | None | Company Initiated Outage. Not outage related.
1627 | Company Initiated | Return Circuit Normal | Cutout- fuse holder | Arcing | None | Company Initiated Outage. Not outage related.
1628 | Company Initiated | Return Circuit Normal | Cutout- fuse holder | Blown/failed | None | Company Initiated Outage. Not outage related.
1629 | Company Initiated | Return Circuit Normal | Cutout- fuse holder | Broken | None | Company Initiated Outage. Not outage related.
1630 | Company Initiated | Return Circuit Normal | Cutout- fuse holder | Burned/flashed | None | Company Initiated Outage. Not outage related.
1631 | Company Initiated | Return Circuit Normal | Cutout- fuse holder | Normal | None | Company Initiated Outage. Not outage related.
1632 | Company Initiated | Return Circuit Normal | Elbow | Blown/failed | None | Company Initiated Outage. Not outage related.
1633 | Company Initiated | Return Circuit Normal | Elbow | Broken | None | Company Initiated Outage. Not outage related.
1634 | Company Initiated | Return Circuit Normal | Elbow | Burned/flashed | None | Company Initiated Outage. Not outage related.
1635 | Company Initiated | Return Circuit Normal | Elbow | Deteriorated | None | Company Initiated Outage. Not outage related.
1636 | Company Initiated | Return Circuit Normal | Elbow | Normal | None | Company Initiated Outage. Not outage related.
1637 | Company Initiated | Return Circuit Normal | Fuse | Blown/failed | None | Company Initiated Outage. Not outage related.
1638 | Company Initiated | Return Circuit Normal | Fuse | Normal | None | Company Initiated Outage. Not outage related.
1639 | Company Initiated | Return Circuit Normal | Generator | Normal | None | Company Initiated Outage. Not outage related.
1640 | Company Initiated | Return Circuit Normal | Insulator | Broken | None | Company Initiated Outage. Not outage related.
1641 | Company Initiated | Return Circuit Normal | Insulator | Broken- wire on object | None | Company Initiated Outage. Not outage related.
1642 | Company Initiated | Return Circuit Normal | Insulator | Burned/flashed | None | Company Initiated Outage. Not outage related.
1643 | Company Initiated | Return Circuit Normal | Insulator | Normal | None | Company Initiated Outage. Not outage related.
1644 | Company Initiated | Return Circuit Normal | Interrupter | Normal | None | Company Initiated Outage. Not outage related.
1645 | Company Initiated | Return Circuit Normal | Jumper | Broken | None | Company Initiated Outage. Not outage related.
1646 | Company Initiated | Return Circuit Normal | Jumper | Burned Open | None | Company Initiated Outage. Not outage related.
1647 | Company Initiated | Return Circuit Normal | Jumper | Normal | None | Company Initiated Outage. Not outage related.
1648 | Company Initiated | Return Circuit Normal | Lightning Arrestor | Blown/failed | None | Company Initiated Outage. Not outage related.
1649 | Company Initiated | Return Circuit Normal | Other | Blown/failed | None | Company Initiated Outage. Not outage related.
1650 | Company Initiated | Return Circuit Normal | Other | Broken | None | Company Initiated Outage. Not outage related.
1651 | Company Initiated | Return Circuit Normal | Other | Deteriorated | None | Company Initiated Outage. Not outage related.
1652 | Company Initiated | Return Circuit Normal | Other | Normal | None | Company Initiated Outage. Not outage related.
1653 | Company Initiated | Return Circuit Normal | PGs- Kearneys | Normal | None | Company Initiated Outage. Not outage related.
1654 | Company Initiated | Return Circuit Normal | Pole-Wood | Broken | None | Company Initiated Outage. Not outage related.
1655 | Company Initiated | Return Circuit Normal | Pole-Wood | Broken- wire on ground | None | Company Initiated Outage. Not outage related.
1656 | Company Initiated | Return Circuit Normal | Pole-Wood | Burned/flashed | None | Company Initiated Outage. Not outage related.
1657 | Company Initiated | Return Circuit Normal | Pole-Wood | Deteriorated | None | Company Initiated Outage. Not outage related.
1658 | Company Initiated | Return Circuit Normal | Pole-Wood | Normal | None | Company Initiated Outage. Not outage related.
1659 | Company Initiated | Return Circuit Normal | Pole-Wood | On Ground | None | Company Initiated Outage. Not outage related.
1660 | Company Initiated | Return Circuit Normal | Pothead(Riser Termination) | Blown/failed | None | Company Initiated Outage. Not outage related.
1661 | Company Initiated | Return Circuit Normal | Pothead(Riser Termination) | Broken | None | Company Initiated Outage. Not outage related.
1662 | Company Initiated | Return Circuit Normal | Pothead(Riser Termination) | Burned/flashed | None | Company Initiated Outage. Not outage related.
1663 | Company Initiated | Return Circuit Normal | Pothead(Riser Termination) | Normal | None | Company Initiated Outage. Not outage related.
1664 | Company Initiated | Return Circuit Normal | Recloser | Broken | None | Company Initiated Outage. Not outage related.
1665 | Company Initiated | Return Circuit Normal | Recloser | Burned/flashed | None | Company Initiated Outage. Not outage related.
1666 | Company Initiated | Return Circuit Normal | Recloser | Malfunctioning | None | Company Initiated Outage. Not outage related.
1667 | Company Initiated | Return Circuit Normal | Recloser | Normal | None | Company Initiated Outage. Not outage related.
1668 | Company Initiated | Return Circuit Normal | Regulator | Malfunctioning | None | Company Initiated Outage. Not outage related.
1669 | Company Initiated | Return Circuit Normal | Regulator | Normal | None | Company Initiated Outage. Not outage related.
1670 | Company Initiated | Return Circuit Normal | SCADA | Normal | None | Company Initiated Outage. Not outage related.
1671 | Company Initiated | Return Circuit Normal | Secondary | Broken | None | Company Initiated Outage. Not outage related.
1672 | Company Initiated | Return Circuit Normal | Secondary | Burned/flashed | None | Company Initiated Outage. Not outage related.
1673 | Company Initiated | Return Circuit Normal | Secondary | Normal | None | Company Initiated Outage. Not outage related.
1674 | Company Initiated | Return Circuit Normal | Sectionalizer | Normal | None | Company Initiated Outage. Not outage related.
1675 | Company Initiated | Return Circuit Normal | Stepdown | Normal | None | Company Initiated Outage. Not outage related.
1676 | Company Initiated | Return Circuit Normal | Switch (OH) | Arcing | None | Company Initiated Outage. Not outage related.
1677 | Company Initiated | Return Circuit Normal | Switch (OH) | Broken | None | Company Initiated Outage. Not outage related.
1678 | Company Initiated | Return Circuit Normal | Switch (OH) | Normal | None | Company Initiated Outage. Not outage related.
1679 | Company Initiated | Return Circuit Normal | Switch (UG) | Blown/failed | None | Company Initiated Outage. Not outage related.
1680 | Company Initiated | Return Circuit Normal | Switch (UG) | Normal | None | Company Initiated Outage. Not outage related.
1681 | Company Initiated | Return Circuit Normal | Transformer | Malfunctioning | None | Company Initiated Outage. Not outage related.
1682 | Company Initiated | Return Circuit Normal | Transformer (OH) | Blown/failed | None | Company Initiated Outage. Not outage related.
1683 | Company Initiated | Return Circuit Normal | Transformer (OH) | Broken | None | Company Initiated Outage. Not outage related.
1684 | Company Initiated | Return Circuit Normal | Transformer (OH) | Normal | None | Company Initiated Outage. Not outage related.
1685 | Company Initiated | Return Circuit Normal | Transformer (UG) | Blown/failed | None | Company Initiated Outage. Not outage related.
1686 | Company Initiated | Return Circuit Normal | Transformer (UG) | Broken | None | Company Initiated Outage. Not outage related.
1687 | Company Initiated | Return Circuit Normal | Transformer (UG) | Leaking | None | Company Initiated Outage. Not outage related.
1688 | Company Initiated | Return Circuit Normal | Transformer (UG) | Normal | None | Company Initiated Outage. Not outage related.
1689 | Company Initiated | Return Circuit Normal | Woodpin | Broken | None | Company Initiated Outage. Not outage related.
1690 | Environmental/ External | Earthquake | Conductor- Overhead | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
1691 | Environmental/ External | Earthquake | Conductor- Overhead | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1692 | Environmental/ External | Earthquake | Other | Deteriorated | Medium | System Hardening will make circuitry more robustand moderately reduce ignition risk.
1693 | Environmental/ External | Earthquake | Pole-Wood | Burned/flashed | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
1694 | Environmental/ External | Earthquake | Transformer |  | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
1695 | Environmental/ External | Fire- Forest/Grass | Anchor or Guy | Burned/flashed | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
1696 | Environmental/ External | Fire- Forest/Grass | Circuit Breaker | Normal | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
1697 | Environmental/ External | Fire- Forest/Grass | Conductor- Overhead | Annealed | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
1698 | Environmental/ External | Fire- Forest/Grass | Conductor- Overhead | Broken | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
1699 | Environmental/ External | Fire- Forest/Grass | Conductor- Overhead | Broken- wire on ground | Medium | SECONDARY IGNITION RISK - Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1700 | Environmental/ External | Fire- Forest/Grass | Conductor- Overhead | Burned/flashed | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
1701 | Environmental/ External | Fire- Forest/Grass | Conductor- Overhead | Contaminated | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
1702 | Environmental/ External | Fire- Forest/Grass | Conductor- Overhead | Deteriorated | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
1703 | Environmental/ External | Fire- Forest/Grass | Conductor- Overhead | Normal | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
1704 | Environmental/ External | Fire- Forest/Grass | Conductor- Overhead | On Ground | Medium | SECONDARY IGNITION RISK - Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1705 | Environmental/ External | Fire- Forest/Grass | Conductor- Underground | Broken | All | Underground facilities = no ignition risk
1706 | Environmental/ External | Fire- Forest/Grass | Conductor- Underground | Burned/flashed | All | Underground facilities = no ignition risk
1707 | Environmental/ External | Fire- Forest/Grass | Conductor- Underground | Normal | All | Underground facilities = no ignition risk
1708 | Environmental/ External | Fire- Forest/Grass | Connector or Splice (OH) | Broken- wire on ground | High | SECONDARY IGNITION RISK - Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
1709 | Environmental/ External | Fire- Forest/Grass | Connector or Splice (OH) | Broken- wire on object | High | SECONDARY IGNITION RISK - Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
1710 | Environmental/ External | Fire- Forest/Grass | Connector or Splice (OH) | Burned/flashed | High | SECONDARY IGNITION RISK - Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
1711 | Environmental/ External | Fire- Forest/Grass | Connector or Splice (UG) | Normal | All | Underground facilities = no ignition risk
1712 | Environmental/ External | Fire- Forest/Grass | Crossarm- Wood | Broken | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
1713 | Environmental/ External | Fire- Forest/Grass | Crossarm- Wood | Broken- wire on ground | Medium | SECONDARY IGNITION RISK - Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1714 | Environmental/ External | Fire- Forest/Grass | Crossarm- Wood | Burned/flashed | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
1715 | Environmental/ External | Fire- Forest/Grass | Customer Equipment | Broken | None | System hardening does not address customer equipment
1716 | Environmental/ External | Fire- Forest/Grass | Customer Equipment | Burned/flashed | None | System hardening does not address customer equipment
1717 | Environmental/ External | Fire- Forest/Grass | Customer Equipment | Malfunctioning | None | System hardening does not address customer equipment
1718 | Environmental/ External | Fire- Forest/Grass | Cutout- fuse holder | Broken | High | SECONDARY IGNITION RISK - Non-exempt fused cutouts are being replaced on System Hardening Projects.
1719 | Environmental/ External | Fire- Forest/Grass | Cutout- fuse holder | Normal | High | SECONDARY IGNITION RISK - Non-exempt fused cutouts are being replaced on System Hardening Projects.
1720 | Environmental/ External | Fire- Forest/Grass | Elbow | Blown/failed | All | Underground facilities = no ignition risk
1721 | Environmental/ External | Fire- Forest/Grass | Footings- Tower or Pole | Burned/flashed | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
1722 | Environmental/ External | Fire- Forest/Grass | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
1723 | Environmental/ External | Fire- Forest/Grass | Fuse | Burned Open | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
1724 | Environmental/ External | Fire- Forest/Grass | Fuse | Normal | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk..
1725 | Environmental/ External | Fire- Forest/Grass | Insulator | Burned/flashed | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
1726 | Environmental/ External | Fire- Forest/Grass | Insulator | Normal | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
1727 | Environmental/ External | Fire- Forest/Grass | Jumper | Broken | High | SECONDARY IGNITION RISK - Larger covered conductor to mostly eliminate cause and risk.
1728 | Environmental/ External | Fire- Forest/Grass | Jumper | Normal | High | SECONDARY IGNITION RISK - Larger covered conductor to mostly eliminate cause and risk.
1729 | Environmental/ External | Fire- Forest/Grass | Lightning Arrestor | Blown/failed | All | We are replacing lightning arrestors with their exempt equivalent.
1730 | Environmental/ External | Fire- Forest/Grass | Metering Equipment | Burned/flashed | None | System Hardening does not address Metering facilities.
1731 | Environmental/ External | Fire- Forest/Grass | Other | Broken- wire on ground | Medium | SECONDARY IGNITION RISK - Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1732 | Environmental/ External | Fire- Forest/Grass | Other | Burned Open | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
1733 | Environmental/ External | Fire- Forest/Grass | Other | Burned/flashed | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
1734 | Environmental/ External | Fire- Forest/Grass | Other | Normal | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
1735 | Environmental/ External | Fire- Forest/Grass | Pole - Tower- steel | Broken- wire on ground | Medium | SECONDARY IGNITION RISK - Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1736 | Environmental/ External | Fire- Forest/Grass | Pole-Wood | Broken | High | SECONDARY IGNITION RISK - We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
1737 | Environmental/ External | Fire- Forest/Grass | Pole-Wood | Broken- wire on ground | Medium | SECONDARY IGNITION RISK - Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1738 | Environmental/ External | Fire- Forest/Grass | Pole-Wood | Broken- wire on object | Medium | SECONDARY IGNITION RISK - Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1739 | Environmental/ External | Fire- Forest/Grass | Pole-Wood | Burned/flashed | Low | A limited number of Poles have been replaced with composite material. We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
1740 | Environmental/ External | Fire- Forest/Grass | Pole-Wood | Contaminated | Low | A limited number of Poles have been replaced with composite material. We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
1741 | Environmental/ External | Fire- Forest/Grass | Pole-Wood | Deteriorated | Low | A limited number of Poles have been replaced with composite material. We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
1742 | Environmental/ External | Fire- Forest/Grass | Pole-Wood | Normal | Low | A limited number of Poles have been replaced with composite material. We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
1743 | Environmental/ External | Fire- Forest/Grass | Pole-Wood | On Ground | Medium | SECONDARY IGNITION RISK - Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1744 | Environmental/ External | Fire- Forest/Grass | Pothead(Riser Termination) | Burned/flashed | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
1745 | Environmental/ External | Fire- Forest/Grass | Pothead(Riser Termination) | Deteriorated | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
1746 | Environmental/ External | Fire- Forest/Grass | Recloser | Broken | None | System Hardening will not mitigate for Environmental factors for this outage.
1747 | Environmental/ External | Fire- Forest/Grass | Recloser | Burned/flashed | None | System Hardening will not mitigate for Environmental factors for this outage.
1748 | Environmental/ External | Fire- Forest/Grass | Recloser | Normal | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
1749 | Environmental/ External | Fire- Forest/Grass | Regulator | Blown/failed | None | System Hardening will not mitigate for Environmental factors for this outage.
1750 | Environmental/ External | Fire- Forest/Grass | Regulator | Burned/flashed | None | System Hardening will not mitigate for Environmental factors for this outage.
1751 | Environmental/ External | Fire- Forest/Grass | Relay | Normal | All | Covered conductor will eliminate "smoke arcing" and risk associated with this outage.
1752 | Environmental/ External | Fire- Forest/Grass | Secondary | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1753 | Environmental/ External | Fire- Forest/Grass | Secondary | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1754 | Environmental/ External | Fire- Forest/Grass | Secondary | Burned Open | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1755 | Environmental/ External | Fire- Forest/Grass | Secondary | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1756 | Environmental/ External | Fire- Forest/Grass | Secondary | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1757 | Environmental/ External | Fire- Forest/Grass | Secondary | Together | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1758 | Environmental/ External | Fire- Forest/Grass | Service conductor | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1759 | Environmental/ External | Fire- Forest/Grass | Service conductor | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1760 | Environmental/ External | Fire- Forest/Grass | Service conductor | Burned Open | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1761 | Environmental/ External | Fire- Forest/Grass | Service conductor | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1762 | Environmental/ External | Fire- Forest/Grass | Service conductor | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1763 | Environmental/ External | Fire- Forest/Grass | Switch | Burned/flashed | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
1764 | Environmental/ External | Fire- Forest/Grass | Switch | Normal | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
1765 | Environmental/ External | Fire- Forest/Grass | Switch (OH) | Normal | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
1766 | Environmental/ External | Fire- Forest/Grass | Switch (UG) | Normal | All | Underground facilities = no ignition risk
1767 | Environmental/ External | Fire- Forest/Grass | Transformer | Blown/failed | High | SECONDARY IGNITION RISK - Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1768 | Environmental/ External | Fire- Forest/Grass | Transformer | Broken | High | SECONDARY IGNITION RISK - Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1769 | Environmental/ External | Fire- Forest/Grass | Transformer | Burned/flashed | High | SECONDARY IGNITION RISK - Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1770 | Environmental/ External | Fire- Forest/Grass | Transformer (OH) | Blown/failed | High | SECONDARY IGNITION RISK - Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1771 | Environmental/ External | Fire- Forest/Grass | Transformer (OH) | Broken | High | SECONDARY IGNITION RISK - Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1772 | Environmental/ External | Fire- Forest/Grass | Transformer (OH) | Burned/flashed | High | SECONDARY IGNITION RISK - Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1773 | Environmental/ External | Fire- Forest/Grass | Transformer (OH) | Deteriorated | High | SECONDARY IGNITION RISK - Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1774 | Environmental/ External | Fire- Forest/Grass | Transformer (OH) | Leaking | High | SECONDARY IGNITION RISK - Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1775 | Environmental/ External | Fire- Forest/Grass | Transformer (OH) | Normal | High | SECONDARY IGNITION RISK - Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1776 | Environmental/ External | Fire- Forest/Grass | Transformer (UG) | Blown/failed | All | Underground facilities = no ignition risk
1777 | Environmental/ External | Fire- Forest/Grass | Transformer (UG) | Broken | All | Underground facilities = no ignition risk
1778 | Environmental/ External | Fire- Forest/Grass | Transformer (UG) | Burned/flashed | All | Underground facilities = no ignition risk
1779 | Environmental/ External | Fire- Forest/Grass | Transformer (UG) | Normal | All | Underground facilities = no ignition risk
1780 | Environmental/ External | Flood/Erosion | Anchor or Guy | Broken | Low | Water and Moisture limit ignition risk
1781 | Environmental/ External | Flood/Erosion | Anchor or Guy | Deteriorated | Low | Water and Moisture limit ignition risk
1782 | Environmental/ External | Flood/Erosion | Conductor- Overhead | Arcing | Low | Water and Moisture limit ignition risk
1783 | Environmental/ External | Flood/Erosion | Conductor- Overhead | Bent or Twisted | Low | Water and Moisture limit ignition risk
1784 | Environmental/ External | Flood/Erosion | Conductor- Overhead | Broken | Low | Water and Moisture limit ignition risk
1785 | Environmental/ External | Flood/Erosion | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1786 | Environmental/ External | Flood/Erosion | Conductor- Overhead | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1787 | Environmental/ External | Flood/Erosion | Conductor- Overhead | Burned/flashed | Low | Water and Moisture limit ignition risk
1788 | Environmental/ External | Flood/Erosion | Conductor- Overhead | Deteriorated | Low | Water and Moisture limit ignition risk
1789 | Environmental/ External | Flood/Erosion | Conductor- Overhead | Normal | Low | Water and Moisture limit ignition risk
1790 | Environmental/ External | Flood/Erosion | Conductor- Overhead | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1791 | Environmental/ External | Flood/Erosion | Conductor- Overhead | Together | Low | Water and Moisture limit ignition risk
1792 | Environmental/ External | Flood/Erosion | Conductor- Underground | Broken | All | Underground facilities = no ignition risk
1793 | Environmental/ External | Flood/Erosion | Conductor- Underground | Contaminated | All | Underground facilities = no ignition risk
1794 | Environmental/ External | Flood/Erosion | Conductor- Underground | Normal | All | Underground facilities = no ignition risk
1795 | Environmental/ External | Flood/Erosion | Connector or Splice (UG) | Deteriorated | All | Underground facilities = no ignition risk
1796 | Environmental/ External | Flood/Erosion | Crossarm- Wood | Broken | Low | Water and Moisture limit ignition risk
1797 | Environmental/ External | Flood/Erosion | Crossarm- Wood | Deteriorated | Low | Water and Moisture limit ignition risk
1798 | Environmental/ External | Flood/Erosion | Customer Equipment | Contaminated | None | System hardening does not address customer equipment
1799 | Environmental/ External | Flood/Erosion | Customer Equipment | Normal | None | System hardening does not address customer equipment
1800 | Environmental/ External | Flood/Erosion | Cutout- fuse holder | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
1801 | Environmental/ External | Flood/Erosion | Fuse | Blown/failed | High | Moisture and Water should eliminate Ignition Risk. Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk..
1802 | Environmental/ External | Flood/Erosion | Fuse | Normal | High | Moisture and Water should eliminate Ignition Risk. Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk..
1803 | Environmental/ External | Flood/Erosion | Metering Equipment | Normal | None | System Hardening does not address Metering facilities.
1804 | Environmental/ External | Flood/Erosion | Other | Arcing | Low | Water and Moisture limit ignition risk
1805 | Environmental/ External | Flood/Erosion | Other | Deteriorated | Low | Water and Moisture limit ignition risk
1806 | Environmental/ External | Flood/Erosion | Other | Normal | Low | Water and Moisture limit ignition risk
1807 | Environmental/ External | Flood/Erosion | Pole - Tower- steel | Deteriorated | Low | Water and Moisture limit ignition risk
1808 | Environmental/ External | Flood/Erosion | Pole-Wood | Broken | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
1809 | Environmental/ External | Flood/Erosion | Pole-Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1810 | Environmental/ External | Flood/Erosion | Pole-Wood | Contaminated | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
1811 | Environmental/ External | Flood/Erosion | Pole-Wood | Deteriorated | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
1812 | Environmental/ External | Flood/Erosion | Pole-Wood | Normal | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
1813 | Environmental/ External | Flood/Erosion | Pole-Wood | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1814 | Environmental/ External | Flood/Erosion | Secondary | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1815 | Environmental/ External | Flood/Erosion | Switch | Broken | Low | Water and Moisture limit ignition risk
1816 | Environmental/ External | Flood/Erosion | Switch (OH) | Normal | Low | Water and Moisture limit ignition risk
1817 | Environmental/ External | Flood/Erosion | Switch (UG) | Burned/flashed | All | Underground facilities = no ignition risk
1818 | Environmental/ External | Flood/Erosion | Switch (UG) | Normal | All | Underground facilities = no ignition risk
1819 | Environmental/ External | Flood/Erosion | Transformer | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1820 | Environmental/ External | Flood/Erosion | Transformer | Deteriorated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1821 | Environmental/ External | Flood/Erosion | Transformer | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1822 | Environmental/ External | Flood/Erosion | Transformer (OH) | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1823 | Environmental/ External | Flood/Erosion | Transformer (OH) | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1824 | Environmental/ External | Flood/Erosion | Transformer (UG) | Broken | All | Underground facilities = no ignition risk
1825 | Environmental/ External | Flood/Erosion | Transformer (UG) | Contaminated | All | Underground facilities = no ignition risk
1826 | Environmental/ External | Flood/Erosion | Transformer (UG) | Normal | All | Underground facilities = no ignition risk
1827 | Environmental/ External | Ice or snow |  | Blown/failed | All | Ice and Snow conditions should have no ignition risk.
1828 | Environmental/ External | Ice or snow | Conductor- Overhead | Arcing | All | Ice and Snow conditions should have no ignition risk.
1829 | Environmental/ External | Ice or snow | Conductor- Overhead | Bent or Twisted | All | Ice and Snow conditions should have no ignition risk.
1830 | Environmental/ External | Ice or snow | Conductor- Overhead | Broken | All | Ice and Snow conditions should have no ignition risk.
1831 | Environmental/ External | Ice or snow | Conductor- Overhead | Broken- wire on ground | All | Ice and Snow conditions should have no ignition risk.
1832 | Environmental/ External | Ice or snow | Conductor- Overhead | Broken- wire on object | All | Ice and Snow conditions should have no ignition risk.
1833 | Environmental/ External | Ice or snow | Conductor- Overhead | Burned/flashed | All | Ice and Snow conditions should have no ignition risk.
1834 | Environmental/ External | Ice or snow | Conductor- Overhead | Normal | All | Ice and Snow conditions should have no ignition risk.
1835 | Environmental/ External | Ice or snow | Conductor- Overhead | On Ground | All | Ice and Snow conditions should have no ignition risk.
1836 | Environmental/ External | Ice or snow | Conductor- Overhead | Together | All | Ice and Snow conditions should have no ignition risk.
1837 | Environmental/ External | Ice or snow | Connector or Splice (OH) | Broken- wire on ground | All | Ice and Snow conditions should have no ignition risk.
1838 | Environmental/ External | Ice or snow | Connector or Splice (OH) | Normal | All | Ice and Snow conditions should have no ignition risk.
1839 | Environmental/ External | Ice or snow | Crossarm- Wood | Broken | All | Ice and Snow conditions should have no ignition risk.
1840 | Environmental/ External | Ice or snow | Crossarm- Wood | Broken- wire on ground | All | Ice and Snow conditions should have no ignition risk.
1841 | Environmental/ External | Ice or snow | Crossarm- Wood | Broken- wire on object | All | Ice and Snow conditions should have no ignition risk.
1842 | Environmental/ External | Ice or snow | Fuse | Blown/failed | All | Ice and Snow conditions should have no ignition risk.
1843 | Environmental/ External | Ice or snow | Fuse | Normal | All | Ice and Snow conditions should have no ignition risk.
1844 | Environmental/ External | Ice or snow | Insulator | Broken | All | Ice and Snow conditions should have no ignition risk.
1845 | Environmental/ External | Ice or snow | Insulator | Broken- wire on ground | All | Ice and Snow conditions should have no ignition risk.
1846 | Environmental/ External | Ice or snow | Insulator | Broken- wire on object | All | Ice and Snow conditions should have no ignition risk.
1847 | Environmental/ External | Ice or snow | Jumper | Broken | All | Ice and Snow conditions should have no ignition risk.
1848 | Environmental/ External | Ice or snow | Other | Annealed | All | Ice and Snow conditions should have no ignition risk.
1849 | Environmental/ External | Ice or snow | Pole-Wood | Broken | All | Ice and Snow conditions should have no ignition risk.
1850 | Environmental/ External | Ice or snow | Pole-Wood | Broken- wire on ground | All | Ice and Snow conditions should have no ignition risk.
1851 | Environmental/ External | Ice or snow | Pole-Wood | Broken- wire on object | All | Ice and Snow conditions should have no ignition risk.
1852 | Environmental/ External | Ice or snow | Recloser | Normal | All | Ice and Snow conditions should have no ignition risk.
1853 | Environmental/ External | Ice or snow | Secondary | Broken | All | Ice and Snow conditions should have no ignition risk.
1854 | Environmental/ External | Ice or snow | Secondary | Broken- wire on ground | All | Ice and Snow conditions should have no ignition risk.
1855 | Environmental/ External | Ice or snow | Secondary | Deteriorated | All | Ice and Snow conditions should have no ignition risk.
1856 | Environmental/ External | Ice or snow | Service conductor | Broken | All | Ice and Snow conditions should have no ignition risk.
1857 | Environmental/ External | Ice or snow | Service conductor | Broken- wire on ground | All | Ice and Snow conditions should have no ignition risk.
1858 | Environmental/ External | Ice or snow | Transformer | Blown/failed | All | Ice and Snow conditions should have no ignition risk.
1859 | Environmental/ External | Ice or snow | Transformer | Broken | All | Ice and Snow conditions should have no ignition risk.
1860 | Environmental/ External | Ice or snow | Transformer | Normal | All | Ice and Snow conditions should have no ignition risk.
1861 | Environmental/ External | Ice or snow | Transformer (OH) | Blown/failed | All | Ice and Snow conditions should have no ignition risk.
1862 | Environmental/ External | Ice or snow | Transformer (UG) | Broken | All | Underground facilities = no ignition risk
1863 | Environmental/ External | Lightning |  |  | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
1864 | Environmental/ External | Lightning |  | Blown/failed | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
1865 | Environmental/ External | Lightning |  | Broken | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
1866 | Environmental/ External | Lightning |  | Burned Open | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
1867 | Environmental/ External | Lightning |  | Normal | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
1868 | Environmental/ External | Lightning | Anchor or Guy | Broken | None | System Hardening will not mitigate for Environmental factors for this outage.
1869 | Environmental/ External | Lightning | Booster | Blown/failed | None | System Hardening will not mitigate for Environmental factors for this outage.
1870 | Environmental/ External | Lightning | Bushing | Blown/failed | None | System Hardening will not mitigate for Environmental factors for this outage.
1871 | Environmental/ External | Lightning | Bushing | Broken | None | System Hardening will not mitigate for Environmental factors for this outage.
1872 | Environmental/ External | Lightning | Bushing | Burned/flashed | None | System Hardening will not mitigate for Environmental factors for this outage.
1873 | Environmental/ External | Lightning | Capacitor | Blown/failed | None | System Hardening will not mitigate for Environmental factors for this outage.
1874 | Environmental/ External | Lightning | Capacitor | Burned/flashed | None | System Hardening will not mitigate for Environmental factors for this outage.
1875 | Environmental/ External | Lightning | Circuit Breaker | Malfunctioning | None | System Hardening will not mitigate for Environmental factors for this outage.
1876 | Environmental/ External | Lightning | Circuit Breaker | Normal | None | System Hardening will not mitigate for Environmental factors for this outage.
1877 | Environmental/ External | Lightning | Conductor- Overhead | Arcing | None | System Hardening will not mitigate for Environmental factors for this outage.
1878 | Environmental/ External | Lightning | Conductor- Overhead | Broken | None | System Hardening will not mitigate for Environmental factors for this outage.
1879 | Environmental/ External | Lightning | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1880 | Environmental/ External | Lightning | Conductor- Overhead | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1881 | Environmental/ External | Lightning | Conductor- Overhead | Burned Open | None | System Hardening will not mitigate for Environmental factors for this outage.
1882 | Environmental/ External | Lightning | Conductor- Overhead | Burned/flashed | None | System Hardening will not mitigate for Environmental factors for this outage.
1883 | Environmental/ External | Lightning | Conductor- Overhead | Normal | None | System Hardening will not mitigate for Environmental factors for this outage.
1884 | Environmental/ External | Lightning | Conductor- Overhead | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1885 | Environmental/ External | Lightning | Conductor- Overhead | Together | None | System Hardening will not mitigate for Environmental factors for this outage.
1886 | Environmental/ External | Lightning | Conductor- Underground | Burned/flashed | All | Underground facilities = no ignition risk
1887 | Environmental/ External | Lightning | Connector or Splice (OH) | Broken | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
1888 | Environmental/ External | Lightning | Connector or Splice (OH) | Broken- wire on ground | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
1889 | Environmental/ External | Lightning | Connector or Splice (OH) | Burned Open | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
1890 | Environmental/ External | Lightning | Connector or Splice (UG) | Blown/failed | All | Underground facilities = no ignition risk
1891 | Environmental/ External | Lightning | Connector or Splice (UG) | Burned/flashed | All | Underground facilities = no ignition risk
1892 | Environmental/ External | Lightning | Crossarm- Steel | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
1893 | Environmental/ External | Lightning | Crossarm- Wood | Broken | None | System Hardening will not mitigate for Environmental factors for this outage.
1894 | Environmental/ External | Lightning | Crossarm- Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1895 | Environmental/ External | Lightning | Crossarm- Wood | Burned/flashed | None | System Hardening will not mitigate for Environmental factors for this outage.
1896 | Environmental/ External | Lightning | Customer Equipment | Blown/failed | None | System hardening does not address customer equipment
1897 | Environmental/ External | Lightning | Customer Equipment | Burned/flashed | None | System hardening does not address customer equipment
1898 | Environmental/ External | Lightning | Cutout- fuse holder | Arcing | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
1899 | Environmental/ External | Lightning | Cutout- fuse holder | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
1900 | Environmental/ External | Lightning | Cutout- fuse holder | Broken | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
1901 | Environmental/ External | Lightning | Cutout- fuse holder | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1902 | Environmental/ External | Lightning | Cutout- fuse holder | Burned/flashed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
1903 | Environmental/ External | Lightning | Cutout- fuse holder | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
1904 | Environmental/ External | Lightning | Cutout- Fused- Distribution | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
1905 | Environmental/ External | Lightning | Elbow | Blown/failed | All | Underground facilities = no ignition risk
1906 | Environmental/ External | Lightning | Fuse | Arcing | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk..
1907 | Environmental/ External | Lightning | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk..
1908 | Environmental/ External | Lightning | Fuse | Broken | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk..
1909 | Environmental/ External | Lightning | Fuse | Burned Open | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk..
1910 | Environmental/ External | Lightning | Fuse | Burned/flashed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk..
1911 | Environmental/ External | Lightning | Fuse | Normal | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk..
1912 | Environmental/ External | Lightning | Insulator | Blown/failed | None | System Hardening will not mitigate for Environmental factors for this outage.
1913 | Environmental/ External | Lightning | Insulator | Broken | None | System Hardening will not mitigate for Environmental factors for this outage.
1914 | Environmental/ External | Lightning | Insulator | Burned/flashed | None | System Hardening will not mitigate for Environmental factors for this outage.
1915 | Environmental/ External | Lightning | Jumper | Broken | High | Larger covered conductor to mostly eliminate cause and risk.
1916 | Environmental/ External | Lightning | Jumper | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1917 | Environmental/ External | Lightning | Jumper | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1918 | Environmental/ External | Lightning | Jumper | Burned Open | High | Larger covered conductor to mostly eliminate cause and risk.
1919 | Environmental/ External | Lightning | Jumper | Burned/flashed | High | Larger covered conductor to mostly eliminate cause and risk.
1920 | Environmental/ External | Lightning | Lightning Arrestor | Arcing | All | We are replacing lightning arrestors with their exempt equivalent.
1921 | Environmental/ External | Lightning | Lightning Arrestor | Blown/failed | All | We are replacing lightning arrestors with their exempt equivalent.
1922 | Environmental/ External | Lightning | Lightning Arrestor | Broken | All | We are replacing lightning arrestors with their exempt equivalent.
1923 | Environmental/ External | Lightning | Lightning Arrestor | Burned/flashed | All | We are replacing lightning arrestors with their exempt equivalent.
1924 | Environmental/ External | Lightning | Metering Equipment | Burned/flashed | None | System Hardening does not address Metering facilities.
1925 | Environmental/ External | Lightning | Other | Bent or Twisted | None | System Hardening will not mitigate for Environmental factors for this outage.
1926 | Environmental/ External | Lightning | Other | Blown/failed | None | System Hardening will not mitigate for Environmental factors for this outage.
1927 | Environmental/ External | Lightning | Other | Broken | None | System Hardening will not mitigate for Environmental factors for this outage.
1928 | Environmental/ External | Lightning | Other | Burned/flashed | None | System Hardening will not mitigate for Environmental factors for this outage.
1929 | Environmental/ External | Lightning | Other | Malfunctioning | None | System Hardening will not mitigate for Environmental factors for this outage.
1930 | Environmental/ External | Lightning | Other | Normal | None | System Hardening will not mitigate for Environmental factors for this outage.
1931 | Environmental/ External | Lightning | PGs- Kearneys | Broken- wire on ground | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
1932 | Environmental/ External | Lightning | Pole-Wood | Broken | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
1933 | Environmental/ External | Lightning | Pole-Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1934 | Environmental/ External | Lightning | Pole-Wood | Burned/flashed | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
1935 | Environmental/ External | Lightning | Pole-Wood | Normal | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
1936 | Environmental/ External | Lightning | Pothead(Riser Termination) | Blown/failed | None | System Hardening will not mitigate for Environmental factors for this outage.
1937 | Environmental/ External | Lightning | Pothead(Riser Termination) | Burned/flashed | None | System Hardening will not mitigate for Environmental factors for this outage.
1938 | Environmental/ External | Lightning | Pothead(Riser Termination) | Normal | None | System Hardening will not mitigate for Environmental factors for this outage.
1939 | Environmental/ External | Lightning | Pothead/Riser Termination | Blown/failed | None | System Hardening will not mitigate for Environmental factors for this outage.
1940 | Environmental/ External | Lightning | Recloser | Blown/failed | None | System Hardening will not mitigate for Environmental factors for this outage.
1941 | Environmental/ External | Lightning | Recloser | Broken | None | System Hardening will not mitigate for Environmental factors for this outage.
1942 | Environmental/ External | Lightning | Recloser | Burned/flashed | None | System Hardening will not mitigate for Environmental factors for this outage.
1943 | Environmental/ External | Lightning | Recloser | Malfunctioning | None | System Hardening will not mitigate for Environmental factors for this outage.
1944 | Environmental/ External | Lightning | Recloser | Normal | None | System Hardening will not mitigate for Environmental factors for this outage.
1945 | Environmental/ External | Lightning | Regulator | Blown/failed | None | System Hardening will not mitigate for Environmental factors for this outage.
1946 | Environmental/ External | Lightning | Regulator | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1947 | Environmental/ External | Lightning | Regulator | Burned/flashed | None | System Hardening will not mitigate for Environmental factors for this outage.
1948 | Environmental/ External | Lightning | Secondary | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1949 | Environmental/ External | Lightning | Secondary | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1950 | Environmental/ External | Lightning | Secondary | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1951 | Environmental/ External | Lightning | Sectionalizer | Broken | None | System Hardening will not mitigate for Environmental factors for this outage.
1952 | Environmental/ External | Lightning | Sectionalizer | Normal | None | System Hardening will not mitigate for Environmental factors for this outage.
1953 | Environmental/ External | Lightning | Service conductor | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
1954 | Environmental/ External | Lightning | Stepdown | Blown/failed | None | System Hardening will not mitigate for Environmental factors for this outage.
1955 | Environmental/ External | Lightning | Street Light Equipment | Blown/failed | Medium | System Hardening will not address Street Lights but will address their transformers.
1956 | Environmental/ External | Lightning | Switch | Blown/failed | None | System Hardening will not mitigate for Environmental factors for this outage.
1957 | Environmental/ External | Lightning | Switch | Broken | None | System Hardening will not mitigate for Environmental factors for this outage.
1958 | Environmental/ External | Lightning | Switch (OH) | Blown/failed | None | System Hardening will not mitigate for Environmental factors for this outage.
1959 | Environmental/ External | Lightning | Switch (OH) | Burned/flashed | None | System Hardening will not mitigate for Environmental factors for this outage.
1960 | Environmental/ External | Lightning | Switch (UG) | Blown/failed | All | Underground facilities = no ignition risk
1961 | Environmental/ External | Lightning | Transformer |  | None | System Hardening will not mitigate for Environmental factors for this outage.
1962 | Environmental/ External | Lightning | Transformer | Arcing | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1963 | Environmental/ External | Lightning | Transformer | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1964 | Environmental/ External | Lightning | Transformer | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1965 | Environmental/ External | Lightning | Transformer | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1966 | Environmental/ External | Lightning | Transformer | Burned/flashed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1967 | Environmental/ External | Lightning | Transformer | Contaminated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1968 | Environmental/ External | Lightning | Transformer | Deteriorated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1969 | Environmental/ External | Lightning | Transformer | Leaking | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1970 | Environmental/ External | Lightning | Transformer | Malfunctioning | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1971 | Environmental/ External | Lightning | Transformer | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1972 | Environmental/ External | Lightning | Transformer (OH) |  | None | System Hardening will not mitigate for Environmental factors for this outage.
1973 | Environmental/ External | Lightning | Transformer (OH) | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1974 | Environmental/ External | Lightning | Transformer (OH) | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1975 | Environmental/ External | Lightning | Transformer (OH) | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1976 | Environmental/ External | Lightning | Transformer (OH) | Burned/flashed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1977 | Environmental/ External | Lightning | Transformer (OH) | Deteriorated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1978 | Environmental/ External | Lightning | Transformer (OH) | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
1979 | Environmental/ External | Lightning | Transformer (OH) | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1980 | Environmental/ External | Lightning | Transformer (UG) | Blown/failed | All | Underground facilities = no ignition risk
1981 | Environmental/ External | Lightning | Transformer (UG) | Broken | All | Underground facilities = no ignition risk
1982 | Environmental/ External | Lightning | Transformer (UG) | Burned/flashed | All | Underground facilities = no ignition risk
1983 | Environmental/ External | Lightning | Transformer (UG) | Deteriorated | All | Underground facilities = no ignition risk
1984 | Environmental/ External | Water | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
1985 | Environmental/ External | Water | Conductor- Overhead | Contaminated | Low | Assume Water Supplemental Cause is a duplicate of Floor/Erosion Supplemental Cause. Water and Moisture limit ignition risk
1986 | Environmental/ External | Water | Conductor- Overhead | Normal | Low | Assume Water Supplemental Cause is a duplicate of Floor/Erosion Supplemental Cause. Water and Moisture limit ignition risk
1987 | Environmental/ External | Water | Conductor- Overhead | Together | Low | Assume Water Supplemental Cause is a duplicate of Floor/Erosion Supplemental Cause. Water and Moisture limit ignition risk
1988 | Environmental/ External | Water | Conductor- Underground | Burned/flashed | All | Underground facilities = no ignition risk
1989 | Environmental/ External | Water | Conductor- Underground | Normal | All | Underground facilities = no ignition risk
1990 | Environmental/ External | Water | Connector or Splice (UG) | Blown/failed | All | Underground facilities = no ignition risk
1991 | Environmental/ External | Water | Crossarm- Wood | Burned/flashed | Low | Assume Water Supplemental Cause is a duplicate of Floor/Erosion Supplemental Cause. Water and Moisture limit ignition risk
1992 | Environmental/ External | Water | Customer Equipment | Normal | None | System hardening does not address customer equipment
1993 | Environmental/ External | Water | Cutout- fuse holder | Broken | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
1994 | Environmental/ External | Water | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk..
1995 | Environmental/ External | Water | Insulator | Arcing | Low | Assume Water Supplemental Cause is a duplicate of Floor/Erosion Supplemental Cause. Water and Moisture limit ignition risk
1996 | Environmental/ External | Water | Jumper | Broken | High | Larger covered conductor to mostly eliminate cause and risk.
1997 | Environmental/ External | Water | Other | Leaking | Low | Assume Water Supplemental Cause is a duplicate of Floor/Erosion Supplemental Cause. Water and Moisture limit ignition risk
1998 | Environmental/ External | Water | Pole-Wood | Broken | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
1999 | Environmental/ External | Water | Pole-Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2000 | Environmental/ External | Water | Pole-Wood | Burned/flashed | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
2001 | Environmental/ External | Water | Pole-Wood | Deteriorated | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
2002 | Environmental/ External | Water | Pole-Wood | Normal | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
2003 | Environmental/ External | Water | Pole-Wood | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2004 | Environmental/ External | Water | Secondary | Burned/flashed | Low | Assume Water Supplemental Cause is a duplicate of Floor/Erosion Supplemental Cause. Water and Moisture limit ignition risk
2005 | Environmental/ External | Water | Secondary | Normal | Low | Assume Water Supplemental Cause is a duplicate of Floor/Erosion Supplemental Cause. Water and Moisture limit ignition risk
2006 | Environmental/ External | Water | Switch (UG) | Burned/flashed | All | Underground facilities = no ignition risk
2007 | Environmental/ External | Water | Transformer | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2008 | Environmental/ External | Water | Transformer | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2009 | Environmental/ External | Water | Transformer | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2010 | Environmental/ External | Water | Transformer | Burned Open | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2011 | Environmental/ External | Water | Transformer (OH) | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2012 | Environmental/ External | Water | Transformer (UG) | Blown/failed | All | Underground facilities = no ignition risk
2013 | Environmental/ External | Water | Transformer (UG) | Contaminated | All | Underground facilities = no ignition risk
2014 | Environmental/ External | Water | Transformer (UG) | Leaking | All | Underground facilities = no ignition risk
2015 | Environmental/ External | Water | Transformer (UG) | Normal | All | Underground facilities = no ignition risk
2016 | Equipment Failure/Involved | Electrical Overload |  | Arcing | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2017 | Equipment Failure/Involved | Electrical Overload |  | Blown/failed | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2018 | Equipment Failure/Involved | Electrical Overload |  | Broken | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2019 | Equipment Failure/Involved | Electrical Overload |  | Burned Open | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2020 | Equipment Failure/Involved | Electrical Overload |  | Normal | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2021 | Equipment Failure/Involved | Electrical Overload | Anchor or Guy | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2022 | Equipment Failure/Involved | Electrical Overload | Anchor or Guy | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2023 | Equipment Failure/Involved | Electrical Overload | Booster | Broken | All | Circuit Hardening replaces boosters with voltage regulators.
2024 | Equipment Failure/Involved | Electrical Overload | Bushing |  | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2025 | Equipment Failure/Involved | Electrical Overload | Bushing | Broken | None | Significant external force broke the bushing. Ignition risk not mitigated.
2026 | Equipment Failure/Involved | Electrical Overload | Bushing | Burned/flashed | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks.
2027 | Equipment Failure/Involved | Electrical Overload | Bushing | Normal | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks.
2028 | Equipment Failure/Involved | Electrical Overload | Capacitor | Arcing | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
2029 | Equipment Failure/Involved | Electrical Overload | Capacitor | Blown/failed | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
2030 | Equipment Failure/Involved | Electrical Overload | Capacitor | Burned/flashed | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
2031 | Equipment Failure/Involved | Electrical Overload | Circuit Breaker | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2032 | Equipment Failure/Involved | Electrical Overload | Conductor- Overhead | Annealed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2033 | Equipment Failure/Involved | Electrical Overload | Conductor- Overhead | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2034 | Equipment Failure/Involved | Electrical Overload | Conductor- Overhead | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2035 | Equipment Failure/Involved | Electrical Overload | Conductor- Overhead | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2036 | Equipment Failure/Involved | Electrical Overload | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2037 | Equipment Failure/Involved | Electrical Overload | Conductor- Overhead | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2038 | Equipment Failure/Involved | Electrical Overload | Conductor- Overhead | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2039 | Equipment Failure/Involved | Electrical Overload | Conductor- Overhead | Deteriorated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2040 | Equipment Failure/Involved | Electrical Overload | Conductor- Overhead | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2041 | Equipment Failure/Involved | Electrical Overload | Conductor- Overhead | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2042 | Equipment Failure/Involved | Electrical Overload | Conductor- Underground | Blown/failed | All | Underground facilities = no ignition risk
2043 | Equipment Failure/Involved | Electrical Overload | Conductor- Underground | Broken | All | Underground facilities = no ignition risk
2044 | Equipment Failure/Involved | Electrical Overload | Conductor- Underground | Burned/flashed | All | Underground facilities = no ignition risk
2045 | Equipment Failure/Involved | Electrical Overload | Conductor- Underground | Malfunctioning | All | Underground facilities = no ignition risk
2046 | Equipment Failure/Involved | Electrical Overload | Conductor- Underground | Normal | All | Underground facilities = no ignition risk
2047 | Equipment Failure/Involved | Electrical Overload | Connector or Splice (OH) | Arcing | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2048 | Equipment Failure/Involved | Electrical Overload | Connector or Splice (OH) | Broken | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2049 | Equipment Failure/Involved | Electrical Overload | Connector or Splice (OH) | Broken- wire on ground | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2050 | Equipment Failure/Involved | Electrical Overload | Connector or Splice (OH) | Burned Open | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2051 | Equipment Failure/Involved | Electrical Overload | Connector or Splice (OH) | Burned/flashed | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2052 | Equipment Failure/Involved | Electrical Overload | Connector or Splice (OH) | Contaminated | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2053 | Equipment Failure/Involved | Electrical Overload | Connector or Splice (OH) | Deteriorated | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2054 | Equipment Failure/Involved | Electrical Overload | Connector or Splice (OH) | Normal | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2055 | Equipment Failure/Involved | Electrical Overload | Connector or Splice (OH) | On Ground | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2056 | Equipment Failure/Involved | Electrical Overload | Crossarm- Wood | Broken | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
2057 | Equipment Failure/Involved | Electrical Overload | Crossarm- Wood | Burned/flashed | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
2058 | Equipment Failure/Involved | Electrical Overload | Crossarm- Wood | Normal | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
2059 | Equipment Failure/Involved | Electrical Overload | CT | Normal | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2060 | Equipment Failure/Involved | Electrical Overload | Customer Equipment | Arcing | None | No work is being completed on customer equipment.
2061 | Equipment Failure/Involved | Electrical Overload | Customer Equipment | Burned Open | None | No work is being completed on customer equipment.
2062 | Equipment Failure/Involved | Electrical Overload | Customer Equipment | Burned/flashed | None | No work is being completed on customer equipment.
2063 | Equipment Failure/Involved | Electrical Overload | Customer Equipment | Malfunctioning | None | No work is being completed on customer equipment.
2064 | Equipment Failure/Involved | Electrical Overload | Customer Equipment | Normal | None | No work is being completed on customer equipment.
2065 | Equipment Failure/Involved | Electrical Overload | Cutout- fuse holder | Arcing | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
2066 | Equipment Failure/Involved | Electrical Overload | Cutout- fuse holder | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
2067 | Equipment Failure/Involved | Electrical Overload | Cutout- fuse holder | Broken | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
2068 | Equipment Failure/Involved | Electrical Overload | Cutout- fuse holder | Burned/flashed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
2069 | Equipment Failure/Involved | Electrical Overload | Elbow | Blown/failed | All | Underground facilities = no ignition risk
2070 | Equipment Failure/Involved | Electrical Overload | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
2071 | Equipment Failure/Involved | Electrical Overload | Fuse | Broken | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
2072 | Equipment Failure/Involved | Electrical Overload | Fuse | Burned Open | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
2073 | Equipment Failure/Involved | Electrical Overload | Fuse | Normal | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
2074 | Equipment Failure/Involved | Electrical Overload | Generator | Broken | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2075 | Equipment Failure/Involved | Electrical Overload | Generator | Normal | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2076 | Equipment Failure/Involved | Electrical Overload | Insulator | Arcing | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
2077 | Equipment Failure/Involved | Electrical Overload | Insulator | Blown/failed | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
2078 | Equipment Failure/Involved | Electrical Overload | Insulator | Broken | All | Age or significant external force broke insulator. System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
2079 | Equipment Failure/Involved | Electrical Overload | Interrupter | Malfunctioning | All | Underground facilities = no ignition risk
2080 | Equipment Failure/Involved | Electrical Overload | Interrupter | Normal | All | Underground facilities = no ignition risk
2081 | Equipment Failure/Involved | Electrical Overload | Jumper | Arcing | High | Larger covered conductor to mostly eliminate cause and risk.
2082 | Equipment Failure/Involved | Electrical Overload | Jumper | Bent or Twisted | High | Larger covered conductor to mostly eliminate cause and risk.
2083 | Equipment Failure/Involved | Electrical Overload | Jumper | Broken | High | Larger covered conductor to mostly eliminate cause and risk.
2084 | Equipment Failure/Involved | Electrical Overload | Jumper | Burned Open | High | Larger covered conductor to mostly eliminate cause and risk.
2085 | Equipment Failure/Involved | Electrical Overload | Jumper | Deteriorated | High | Larger covered conductor to mostly eliminate cause and risk.
2086 | Equipment Failure/Involved | Electrical Overload | Lightning Arrestor | Blown/failed | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
2087 | Equipment Failure/Involved | Electrical Overload | Lightning Arrestor | Broken | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
2088 | Equipment Failure/Involved | Electrical Overload | Metering Equipment | Blown/failed | None | System Hardening does not address Metering facilities.
2089 | Equipment Failure/Involved | Electrical Overload | Metering Equipment | Malfunctioning | None | System Hardening does not address Metering facilities.
2090 | Equipment Failure/Involved | Electrical Overload | Metering Equipment | Normal | None | System Hardening does not address Metering facilities.
2091 | Equipment Failure/Involved | Electrical Overload | Other | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2092 | Equipment Failure/Involved | Electrical Overload | Other | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2093 | Equipment Failure/Involved | Electrical Overload | Other | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2094 | Equipment Failure/Involved | Electrical Overload | Other | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2095 | Equipment Failure/Involved | Electrical Overload | Other | Deteriorated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2096 | Equipment Failure/Involved | Electrical Overload | Other | Malfunctioning | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2097 | Equipment Failure/Involved | Electrical Overload | Other | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2098 | Equipment Failure/Involved | Electrical Overload | Other | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2099 | Equipment Failure/Involved | Electrical Overload | PGs- Kearneys | Broken | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2100 | Equipment Failure/Involved | Electrical Overload | PGs- Kearneys | Burned Open | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2101 | Equipment Failure/Involved | Electrical Overload | Pole-Wood | Broken | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
2102 | Equipment Failure/Involved | Electrical Overload | Pole-Wood | Burned/flashed | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
2103 | Equipment Failure/Involved | Electrical Overload | Pole-Wood | Deteriorated | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
2104 | Equipment Failure/Involved | Electrical Overload | Pothead(Riser Termination) | Arcing | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
2105 | Equipment Failure/Involved | Electrical Overload | Pothead(Riser Termination) | Blown/failed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
2106 | Equipment Failure/Involved | Electrical Overload | Pothead(Riser Termination) | Broken | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
2107 | Equipment Failure/Involved | Electrical Overload | Pothead(Riser Termination) | Burned/flashed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
2108 | Equipment Failure/Involved | Electrical Overload | Recloser | Burned/flashed | Medium | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters but coverered conductor will reduce annual number of operations/duty cycle.
2109 | Equipment Failure/Involved | Electrical Overload | Recloser | Malfunctioning | Medium | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters but coverered conductor will reduce annual number of operations/duty cycle.
2110 | Equipment Failure/Involved | Electrical Overload | Recloser | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2111 | Equipment Failure/Involved | Electrical Overload | Regulator | Blown/failed | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2112 | Equipment Failure/Involved | Electrical Overload | Regulator | Malfunctioning | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2113 | Equipment Failure/Involved | Electrical Overload | Relay | Normal | None | Circuit Hardening will not affect substation equipment.
2114 | Equipment Failure/Involved | Electrical Overload | Secondary | Arcing | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2115 | Equipment Failure/Involved | Electrical Overload | Secondary | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2116 | Equipment Failure/Involved | Electrical Overload | Secondary | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2117 | Equipment Failure/Involved | Electrical Overload | Secondary | Broken- wire on object | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2118 | Equipment Failure/Involved | Electrical Overload | Secondary | Burned Open | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2119 | Equipment Failure/Involved | Electrical Overload | Secondary | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2120 | Equipment Failure/Involved | Electrical Overload | Secondary | Deteriorated | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2121 | Equipment Failure/Involved | Electrical Overload | Secondary | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2122 | Equipment Failure/Involved | Electrical Overload | Secondary | Together | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2123 | Equipment Failure/Involved | Electrical Overload | Sectionalizer | Arcing | Medium | System Hardening does not address Reclosers/Sectionalizers but coverered conductor will reduce annual recloser operations.
2124 | Equipment Failure/Involved | Electrical Overload | Service conductor | Arcing | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2125 | Equipment Failure/Involved | Electrical Overload | Service conductor | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2126 | Equipment Failure/Involved | Electrical Overload | Service conductor | Burned Open | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2127 | Equipment Failure/Involved | Electrical Overload | Service conductor | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2128 | Equipment Failure/Involved | Electrical Overload | Service conductor | Together | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2129 | Equipment Failure/Involved | Electrical Overload | Stepdown | Blown/failed | All | Underground facilities = no ignition risk
2130 | Equipment Failure/Involved | Electrical Overload | Switch | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2131 | Equipment Failure/Involved | Electrical Overload | Switch | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2132 | Equipment Failure/Involved | Electrical Overload | Switch (OH) | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2133 | Equipment Failure/Involved | Electrical Overload | Switch (OH) | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2134 | Equipment Failure/Involved | Electrical Overload | Switch (OH) | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2135 | Equipment Failure/Involved | Electrical Overload | Switch (UG) | Normal | All | Underground facilities = no ignition risk
2136 | Equipment Failure/Involved | Electrical Overload | Transformer |  | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2137 | Equipment Failure/Involved | Electrical Overload | Transformer | Annealed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2138 | Equipment Failure/Involved | Electrical Overload | Transformer | Arcing | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2139 | Equipment Failure/Involved | Electrical Overload | Transformer | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2140 | Equipment Failure/Involved | Electrical Overload | Transformer | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2141 | Equipment Failure/Involved | Electrical Overload | Transformer | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2142 | Equipment Failure/Involved | Electrical Overload | Transformer | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2143 | Equipment Failure/Involved | Electrical Overload | Transformer | Burned Open | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2144 | Equipment Failure/Involved | Electrical Overload | Transformer | Burned/flashed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2145 | Equipment Failure/Involved | Electrical Overload | Transformer | Deteriorated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2146 | Equipment Failure/Involved | Electrical Overload | Transformer | Leaking | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2147 | Equipment Failure/Involved | Electrical Overload | Transformer | Malfunctioning | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2148 | Equipment Failure/Involved | Electrical Overload | Transformer | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2149 | Equipment Failure/Involved | Electrical Overload | Transformer | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2150 | Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Arcing | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2151 | Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2152 | Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2153 | Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Burned/flashed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2154 | Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Deteriorated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2155 | Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Leaking | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2156 | Equipment Failure/Involved | Electrical Overload | Transformer (OH) | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2157 | Equipment Failure/Involved | Electrical Overload | Transformer (UG) | Blown/failed | All | UG Facilities = no ignition risk
2158 | Equipment Failure/Involved | Electrical Overload | Transformer (UG) | Broken | All | UG Facilities = no ignition risk
2159 | Equipment Failure/Involved | Electrical Overload | Transformer (UG) | Deteriorated | All | UG Facilities = no ignition risk
2160 | Equipment Failure/Involved | Electrical Overload | Transformer (UG) | Leaking | All | UG Facilities = no ignition risk
2161 | Equipment Failure/Involved | Electrical Overload | Transformer (UG) | Normal | All | UG Facilities = no ignition risk
2162 | Equipment Failure/Involved | Fire- pole | Anchor or Guy | Broken | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2163 | Equipment Failure/Involved | Fire- pole | Anchor or Guy | Deteriorated | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2164 | Equipment Failure/Involved | Fire- pole | Bushing | Broken | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2165 | Equipment Failure/Involved | Fire- pole | Bushing | Burned/flashed | High | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2166 | Equipment Failure/Involved | Fire- pole | Capacitor | Arcing | Low | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2167 | Equipment Failure/Involved | Fire- pole | Capacitor | Blown/failed | Low | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2168 | Equipment Failure/Involved | Fire- pole | Capacitor | Broken | Low | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2169 | Equipment Failure/Involved | Fire- pole | Capacitor | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2170 | Equipment Failure/Involved | Fire- pole | Capacitor | Burned/flashed | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2171 | Equipment Failure/Involved | Fire- pole | Conductor- Overhead | Arcing | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2172 | Equipment Failure/Involved | Fire- pole | Conductor- Overhead | Broken | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2173 | Equipment Failure/Involved | Fire- pole | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2174 | Equipment Failure/Involved | Fire- pole | Conductor- Overhead | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2175 | Equipment Failure/Involved | Fire- pole | Conductor- Overhead | Burned/flashed | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2176 | Equipment Failure/Involved | Fire- pole | Conductor- Overhead | Normal | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2177 | Equipment Failure/Involved | Fire- pole | Conductor- Overhead | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2178 | Equipment Failure/Involved | Fire- pole | Conductor- Overhead | Together | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2179 | Equipment Failure/Involved | Fire- pole | Conductor- Underground | Burned/flashed | All | Underground facilities = no ignition risk
2180 | Equipment Failure/Involved | Fire- pole | Connector or Splice (OH) | Broken | High | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2181 | Equipment Failure/Involved | Fire- pole | Connector or Splice (OH) | Broken- wire on ground | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2182 | Equipment Failure/Involved | Fire- pole | Connector or Splice (OH) | Burned Open | High | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2183 | Equipment Failure/Involved | Fire- pole | Connector or Splice (OH) | Burned/flashed | High | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2184 | Equipment Failure/Involved | Fire- pole | Connector or Splice (UG) | Burned/flashed | All | Underground facilities = no ignition risk
2185 | Equipment Failure/Involved | Fire- pole | Crossarm- Steel | Burned/flashed | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2186 | Equipment Failure/Involved | Fire- pole | Crossarm- Wood | Broken | High | Composite arms are being installed along with new insulators and bonding. Tracking insulators/pole fires will be limited though not 100% eliminate. Gunshot damage will still be a concern. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
2187 | Equipment Failure/Involved | Fire- pole | Crossarm- Wood | Broken- wire on ground | High | Composite arms are being installed along with new insulators and bonding. Tracking insulators/pole fires will be limited though not 100% eliminate. Gunshot damage will still be a concern. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
2188 | Equipment Failure/Involved | Fire- pole | Crossarm- Wood | Broken- wire on object | High | Composite arms are being installed along with new insulators and bonding. Tracking insulators/pole fires will be limited though not 100% eliminate. Gunshot damage will still be a concern. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
2189 | Equipment Failure/Involved | Fire- pole | Crossarm- Wood | Burned/flashed | High | Composite arms are being installed along with new insulators and bonding. Tracking insulators/pole fires will be limited though not 100% eliminate. Gunshot damage will still be a concern. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
2190 | Equipment Failure/Involved | Fire- pole | Cutout- fuse holder | Blown/failed | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2191 | Equipment Failure/Involved | Fire- pole | Cutout- fuse holder | Broken | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2192 | Equipment Failure/Involved | Fire- pole | Cutout- fuse holder | Burned/flashed | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2193 | Equipment Failure/Involved | Fire- pole | Fuse | Arcing | All | Composite arms are being installed along with new insulators and bonding. Tracking insulators/pole fires will be limited though not 100% eliminate. Gunshot damage will still be a concern. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
2194 | Equipment Failure/Involved | Fire- pole | Fuse | Blown/failed | All | Composite arms are being installed along with new insulators and bonding. Tracking insulators/pole fires will be limited though not 100% eliminate. Gunshot damage will still be a concern. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
2195 | Equipment Failure/Involved | Fire- pole | Fuse | Burned Open | All | Composite arms are being installed along with new insulators and bonding. Tracking insulators/pole fires will be limited though not 100% eliminate. Gunshot damage will still be a concern. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
2196 | Equipment Failure/Involved | Fire- pole | Fuse | Normal | All | Composite arms are being installed along with new insulators and bonding. Tracking insulators/pole fires will be limited though not 100% eliminate. Gunshot damage will still be a concern. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
2197 | Equipment Failure/Involved | Fire- pole | Insulator | Arcing | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2198 | Equipment Failure/Involved | Fire- pole | Insulator | Blown/failed | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2199 | Equipment Failure/Involved | Fire- pole | Insulator | Broken | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2200 | Equipment Failure/Involved | Fire- pole | Insulator | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2201 | Equipment Failure/Involved | Fire- pole | Insulator | Burned/flashed | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2202 | Equipment Failure/Involved | Fire- pole | Jumper | Broken | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2203 | Equipment Failure/Involved | Fire- pole | Jumper | Burned Open | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2204 | Equipment Failure/Involved | Fire- pole | Lightning Arrestor | Burned/flashed | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2205 | Equipment Failure/Involved | Fire- pole | Other | Blown/failed | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2206 | Equipment Failure/Involved | Fire- pole | Other | Broken | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2207 | Equipment Failure/Involved | Fire- pole | Other | Burned/flashed | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2208 | Equipment Failure/Involved | Fire- pole | Pole-Wood | Broken | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2209 | Equipment Failure/Involved | Fire- pole | Pole-Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2210 | Equipment Failure/Involved | Fire- pole | Pole-Wood | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2211 | Equipment Failure/Involved | Fire- pole | Pole-Wood | Burned Open | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2212 | Equipment Failure/Involved | Fire- pole | Pole-Wood | Burned/flashed | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2213 | Equipment Failure/Involved | Fire- pole | Pole-Wood | Contaminated | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2214 | Equipment Failure/Involved | Fire- pole | Pole-Wood | Deteriorated | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2215 | Equipment Failure/Involved | Fire- pole | Pole-Wood | Normal | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2216 | Equipment Failure/Involved | Fire- pole | Pole-Wood | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2217 | Equipment Failure/Involved | Fire- pole | Pothead(Riser Termination) | Blown/failed | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2218 | Equipment Failure/Involved | Fire- pole | Pothead(Riser Termination) | Burned/flashed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
2219 | Equipment Failure/Involved | Fire- pole | Pothead/Riser Termination | Blown/failed | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2220 | Equipment Failure/Involved | Fire- pole | Recloser | Arcing | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2221 | Equipment Failure/Involved | Fire- pole | Recloser | Burned/flashed | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2222 | Equipment Failure/Involved | Fire- pole | Recloser | Malfunctioning | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2223 | Equipment Failure/Involved | Fire- pole | Recloser | Normal | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2224 | Equipment Failure/Involved | Fire- pole | Regulator | Arcing | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2225 | Equipment Failure/Involved | Fire- pole | Regulator | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2226 | Equipment Failure/Involved | Fire- pole | Regulator | Burned/flashed | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2227 | Equipment Failure/Involved | Fire- pole | Riser | Burned/flashed | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2228 | Equipment Failure/Involved | Fire- pole | Secondary | Burned Open | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2229 | Equipment Failure/Involved | Fire- pole | Secondary | Burned/flashed | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2230 | Equipment Failure/Involved | Fire- pole | Secondary | Normal | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2231 | Equipment Failure/Involved | Fire- pole | Service conductor | Burned/flashed | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2232 | Equipment Failure/Involved | Fire- pole | Street Light Equipment | Arcing | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2233 | Equipment Failure/Involved | Fire- pole | Switch (OH) | Arcing | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2234 | Equipment Failure/Involved | Fire- pole | Switch (OH) | Burned/flashed | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2235 | Equipment Failure/Involved | Fire- pole | Transformer | Blown/failed | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2236 | Equipment Failure/Involved | Fire- pole | Transformer | Burned/flashed | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2237 | Equipment Failure/Involved | Fire- pole | Transformer | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2238 | Equipment Failure/Involved | Fire- pole | Transformer (OH) | Arcing | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2239 | Equipment Failure/Involved | Fire- pole | Transformer (OH) | Blown/failed | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2240 | Equipment Failure/Involved | Fire- pole | Transformer (OH) | Broken | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2241 | Equipment Failure/Involved | Fire- pole | Transformer (OH) | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2242 | Equipment Failure/Involved | Fire- pole | Transformer (OH) | Burned/flashed | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
2243 | Equipment Failure/Involved | Fire- pole | Transformer (OH) | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2244 | Equipment Failure/Involved | Fire- pole | Transformer (UG) | Broken | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2245 | Equipment Failure/Involved | Fire- pole | Woodpin | Broken | All | Composite arms are being installed along with new insulators and bonding. Tracking insulators/pole fires will be limited though not 100% eliminate. Gunshot damage will still be a concern. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
2246 | Equipment Failure/Involved | Other |  |  | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2247 | Equipment Failure/Involved | Other |  | Blown/failed | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2248 | Equipment Failure/Involved | Other |  | Broken | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2249 | Equipment Failure/Involved | Other |  | Burned Open | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2250 | Equipment Failure/Involved | Other |  | Normal | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2251 | Equipment Failure/Involved | Other | Anchor or Guy | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2252 | Equipment Failure/Involved | Other | Anchor or Guy | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2253 | Equipment Failure/Involved | Other | Anchor or Guy | Deteriorated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2254 | Equipment Failure/Involved | Other | Anchor or Guy | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2255 | Equipment Failure/Involved | Other | Booster | Burned/flashed | All | Circuit Hardening replaces boosters with voltage regulators.
2256 | Equipment Failure/Involved | Other | Booster | Malfunctioning | All | Circuit Hardening replaces boosters with voltage regulators.
2257 | Equipment Failure/Involved | Other | Bus | Broken | High | Transformers installed prior to 2014 will be replaced. Work would include covering jumpers and replacing some of the service conductor.
2258 | Equipment Failure/Involved | Other | Bus | Burned/flashed | High | Transformers installed prior to 2014 will be replaced. Work would include covering jumpers and replacing some of the service conductor.
2259 | Equipment Failure/Involved | Other | Bus | Deteriorated | High | Transformers installed prior to 2014 will be replaced. Work would include covering jumpers and replacing some of the service conductor.
2260 | Equipment Failure/Involved | Other | Bushing | Blown/failed | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks.
2261 | Equipment Failure/Involved | Other | Bushing | Broken | None | Significant external force broke the bushing. Ignition risk not mitigated.
2262 | Equipment Failure/Involved | Other | Bushing | Burned/flashed | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks.
2263 | Equipment Failure/Involved | Other | Bushing | Deteriorated | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks.
2264 | Equipment Failure/Involved | Other | Bushing | Leaking | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks.
2265 | Equipment Failure/Involved | Other | Cable Termination(live front | Burned/flashed | All | Underground facilities = no ignition risk
2266 | Equipment Failure/Involved | Other | Capacitor | Arcing | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
2267 | Equipment Failure/Involved | Other | Capacitor | Blown/failed | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
2268 | Equipment Failure/Involved | Other | Capacitor | Broken | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
2269 | Equipment Failure/Involved | Other | Capacitor | Burned/flashed | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
2270 | Equipment Failure/Involved | Other | Capacitor | Malfunctioning | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
2271 | Equipment Failure/Involved | Other | Capacitor | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2272 | Equipment Failure/Involved | Other | Conductor- Overhead | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2273 | Equipment Failure/Involved | Other | Conductor- Overhead | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2274 | Equipment Failure/Involved | Other | Conductor- Overhead | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2275 | Equipment Failure/Involved | Other | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2276 | Equipment Failure/Involved | Other | Conductor- Overhead | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2277 | Equipment Failure/Involved | Other | Conductor- Overhead | Burned Open | All | Covered conductor will likely eliminate the temporary fault condition that caused this outage.
2278 | Equipment Failure/Involved | Other | Conductor- Overhead | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2279 | Equipment Failure/Involved | Other | Conductor- Overhead | Deteriorated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2280 | Equipment Failure/Involved | Other | Conductor- Overhead | Malfunctioning | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2281 | Equipment Failure/Involved | Other | Conductor- Overhead | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2282 | Equipment Failure/Involved | Other | Conductor- Overhead | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2283 | Equipment Failure/Involved | Other | Conductor- Overhead | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2284 | Equipment Failure/Involved | Other | Conductor- Underground | Blown/failed | All | Underground facilities = no ignition risk
2285 | Equipment Failure/Involved | Other | Conductor- Underground | Broken | All | Underground facilities = no ignition risk
2286 | Equipment Failure/Involved | Other | Conductor- Underground | Broken- wire on ground | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2287 | Equipment Failure/Involved | Other | Conductor- Underground | Burned Open | All | Underground facilities = no ignition risk
2288 | Equipment Failure/Involved | Other | Conductor- Underground | Burned/flashed | All | Underground facilities = no ignition risk
2289 | Equipment Failure/Involved | Other | Conductor- Underground | Contaminated | All | Underground facilities = no ignition risk
2290 | Equipment Failure/Involved | Other | Conductor- Underground | Deteriorated | All | Underground facilities = no ignition risk
2291 | Equipment Failure/Involved | Other | Conductor- Underground | Malfunctioning | All | Underground facilities = no ignition risk
2292 | Equipment Failure/Involved | Other | Conductor- Underground | Normal | All | Underground facilities = no ignition risk
2293 | Equipment Failure/Involved | Other | Connector or Splice (OH) | Arcing | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2294 | Equipment Failure/Involved | Other | Connector or Splice (OH) | Bent or Twisted | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2295 | Equipment Failure/Involved | Other | Connector or Splice (OH) | Broken | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2296 | Equipment Failure/Involved | Other | Connector or Splice (OH) | Broken- wire on ground | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2297 | Equipment Failure/Involved | Other | Connector or Splice (OH) | Broken- wire on object | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2298 | Equipment Failure/Involved | Other | Connector or Splice (OH) | Burned Open | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2299 | Equipment Failure/Involved | Other | Connector or Splice (OH) | Burned/flashed | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2300 | Equipment Failure/Involved | Other | Connector or Splice (OH) | Contaminated | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2301 | Equipment Failure/Involved | Other | Connector or Splice (OH) | Deteriorated | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2302 | Equipment Failure/Involved | Other | Connector or Splice (OH) | Malfunctioning | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2303 | Equipment Failure/Involved | Other | Connector or Splice (OH) | On Ground | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2304 | Equipment Failure/Involved | Other | Connector or Splice (UG) | Arcing | All | Underground facilities = no ignition risk
2305 | Equipment Failure/Involved | Other | Connector or Splice (UG) | Blown/failed | All | Underground facilities = no ignition risk
2306 | Equipment Failure/Involved | Other | Connector or Splice (UG) | Broken | All | Underground facilities = no ignition risk
2307 | Equipment Failure/Involved | Other | Connector or Splice (UG) | Burned Open | All | Underground facilities = no ignition risk
2308 | Equipment Failure/Involved | Other | Connector or Splice (UG) | Burned/flashed | All | Underground facilities = no ignition risk
2309 | Equipment Failure/Involved | Other | Connector or Splice (UG) | Deteriorated | All | Underground facilities = no ignition risk
2310 | Equipment Failure/Involved | Other | Connector or Splice (UG) | Malfunctioning | All | Underground facilities = no ignition risk
2311 | Equipment Failure/Involved | Other | Connector or Splice (UG) | Normal | All | Underground facilities = no ignition risk
2312 | Equipment Failure/Involved | Other | Crossarm- Steel | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2313 | Equipment Failure/Involved | Other | Crossarm- Steel | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2314 | Equipment Failure/Involved | Other | Crossarm- Steel | Deteriorated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2315 | Equipment Failure/Involved | Other | Crossarm- Wood |  | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2316 | Equipment Failure/Involved | Other | Crossarm- Wood | Broken | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
2317 | Equipment Failure/Involved | Other | Crossarm- Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2318 | Equipment Failure/Involved | Other | Crossarm- Wood | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2319 | Equipment Failure/Involved | Other | Crossarm- Wood | Burned Open | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
2320 | Equipment Failure/Involved | Other | Crossarm- Wood | Burned/flashed | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
2321 | Equipment Failure/Involved | Other | Crossarm- Wood | Deteriorated | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
2322 | Equipment Failure/Involved | Other | Crossarm- Wood | Malfunctioning | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
2323 | Equipment Failure/Involved | Other | Customer Equipment | Arcing | None | No work is being completed on customer equipment.
2324 | Equipment Failure/Involved | Other | Customer Equipment | Blown/failed | None | No work is being completed on customer equipment.
2325 | Equipment Failure/Involved | Other | Customer Equipment | Broken | None | No work is being completed on customer equipment.
2326 | Equipment Failure/Involved | Other | Customer Equipment | Burned Open | None | No work is being completed on customer equipment.
2327 | Equipment Failure/Involved | Other | Customer Equipment | Burned/flashed | None | No work is being completed on customer equipment.
2328 | Equipment Failure/Involved | Other | Customer Equipment | Deteriorated | None | No work is being completed on customer equipment.
2329 | Equipment Failure/Involved | Other | Customer Equipment | Leaking | None | No work is being completed on customer equipment.
2330 | Equipment Failure/Involved | Other | Customer Equipment | Malfunctioning | None | No work is being completed on customer equipment.
2331 | Equipment Failure/Involved | Other | Customer Equipment | Normal | None | No work is being completed on customer equipment.
2332 | Equipment Failure/Involved | Other | Cutout- fuse holder | Arcing | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
2333 | Equipment Failure/Involved | Other | Cutout- fuse holder | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
2334 | Equipment Failure/Involved | Other | Cutout- fuse holder | Broken | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
2335 | Equipment Failure/Involved | Other | Cutout- fuse holder | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2336 | Equipment Failure/Involved | Other | Cutout- fuse holder | Burned Open | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
2337 | Equipment Failure/Involved | Other | Cutout- fuse holder | Burned/flashed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
2338 | Equipment Failure/Involved | Other | Cutout- fuse holder | Deteriorated | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
2339 | Equipment Failure/Involved | Other | Cutout- fuse holder | Malfunctioning | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
2340 | Equipment Failure/Involved | Other | Cutout- fuse holder | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
2341 | Equipment Failure/Involved | Other | Cutout- Fused- Distribution | Arcing | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
2342 | Equipment Failure/Involved | Other | Cutout- Fused- Distribution | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
2343 | Equipment Failure/Involved | Other | Cutout- Fused- Distribution | Broken | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
2344 | Equipment Failure/Involved | Other | Cutout- Fused- Distribution | Burned/flashed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
2345 | Equipment Failure/Involved | Other | Cutout- Fused- Distribution | Deteriorated | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
2346 | Equipment Failure/Involved | Other | Elbow | Arcing | All | Underground facilities = no ignition risk
2347 | Equipment Failure/Involved | Other | Elbow | Blown/failed | All | Underground facilities = no ignition risk
2348 | Equipment Failure/Involved | Other | Elbow | Broken | All | Underground facilities = no ignition risk
2349 | Equipment Failure/Involved | Other | Elbow | Burned Open | All | Underground facilities = no ignition risk
2350 | Equipment Failure/Involved | Other | Elbow | Burned/flashed | All | Underground facilities = no ignition risk
2351 | Equipment Failure/Involved | Other | Elbow | Malfunctioning | All | Underground facilities = no ignition risk
2352 | Equipment Failure/Involved | Other | Fuse | Arcing | All | Covered conductor will eliminate the line to ground connection that likely caused this outage/risk.
2353 | Equipment Failure/Involved | Other | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
2354 | Equipment Failure/Involved | Other | Fuse | Broken | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
2355 | Equipment Failure/Involved | Other | Fuse | Burned Open | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
2356 | Equipment Failure/Involved | Other | Fuse | Burned/flashed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
2357 | Equipment Failure/Involved | Other | Fuse | Deteriorated | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
2358 | Equipment Failure/Involved | Other | Fuse | Malfunctioning | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
2359 | Equipment Failure/Involved | Other | Fuse | Normal | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
2360 | Equipment Failure/Involved | Other | Insulator | Arcing | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
2361 | Equipment Failure/Involved | Other | Insulator | Blown/failed | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
2362 | Equipment Failure/Involved | Other | Insulator | Broken | All | Age or significant external force broke insulator. System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
2363 | Equipment Failure/Involved | Other | Insulator | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2364 | Equipment Failure/Involved | Other | Insulator | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2365 | Equipment Failure/Involved | Other | Insulator | Burned/flashed | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
2366 | Equipment Failure/Involved | Other | Insulator | Contaminated | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
2367 | Equipment Failure/Involved | Other | Insulator | Deteriorated | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
2368 | Equipment Failure/Involved | Other | Insulator | Leaking | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
2369 | Equipment Failure/Involved | Other | Insulator | Malfunctioning | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
2370 | Equipment Failure/Involved | Other | Interrupter | Blown/failed | All | Underground facilities = no ignition risk
2371 | Equipment Failure/Involved | Other | Interrupter | Broken | All | Underground facilities = no ignition risk
2372 | Equipment Failure/Involved | Other | Interrupter | Burned/flashed | All | Underground facilities = no ignition risk
2373 | Equipment Failure/Involved | Other | Interrupter | Malfunctioning | All | Underground facilities = no ignition risk
2374 | Equipment Failure/Involved | Other | Jumper | Arcing | High | Larger covered conductor to mostly eliminate cause and risk.
2375 | Equipment Failure/Involved | Other | Jumper | Bent or Twisted | High | Larger covered conductor to mostly eliminate cause and risk.
2376 | Equipment Failure/Involved | Other | Jumper | Blown/failed | High | Larger covered conductor to mostly eliminate cause and risk.
2377 | Equipment Failure/Involved | Other | Jumper | Broken | High | Larger covered conductor to mostly eliminate cause and risk.
2378 | Equipment Failure/Involved | Other | Jumper | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2379 | Equipment Failure/Involved | Other | Jumper | Burned Open | High | Larger covered conductor to mostly eliminate cause and risk.
2380 | Equipment Failure/Involved | Other | Jumper | Burned/flashed | High | Larger covered conductor to mostly eliminate cause and risk.
2381 | Equipment Failure/Involved | Other | Jumper | Deteriorated | High | Larger covered conductor to mostly eliminate cause and risk.
2382 | Equipment Failure/Involved | Other | Jumper | Malfunctioning | High | Larger covered conductor to mostly eliminate cause and risk.
2383 | Equipment Failure/Involved | Other | Jumper | Normal | High | Larger covered conductor to mostly eliminate cause and risk.
2384 | Equipment Failure/Involved | Other | Lightning Arrestor | Arcing | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
2385 | Equipment Failure/Involved | Other | Lightning Arrestor | Blown/failed | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
2386 | Equipment Failure/Involved | Other | Lightning Arrestor | Broken | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
2387 | Equipment Failure/Involved | Other | Lightning Arrestor | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2388 | Equipment Failure/Involved | Other | Lightning Arrestor | Burned Open | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
2389 | Equipment Failure/Involved | Other | Lightning Arrestor | Burned/flashed | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
2390 | Equipment Failure/Involved | Other | Lightning Arrestor | Deteriorated | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
2391 | Equipment Failure/Involved | Other | Lightning Arrestor | Malfunctioning | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
2392 | Equipment Failure/Involved | Other | Metering Equipment | Blown/failed | None | System Hardening does not address Metering facilities.
2393 | Equipment Failure/Involved | Other | Metering Equipment | Burned/flashed | None | System Hardening does not address Metering facilities.
2394 | Equipment Failure/Involved | Other | Metering Equipment | Malfunctioning | None | System Hardening does not address Metering facilities.
2395 | Equipment Failure/Involved | Other | Other | Annealed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2396 | Equipment Failure/Involved | Other | Other | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2397 | Equipment Failure/Involved | Other | Other | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2398 | Equipment Failure/Involved | Other | Other | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2399 | Equipment Failure/Involved | Other | Other | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2400 | Equipment Failure/Involved | Other | Other | Burned Open | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2401 | Equipment Failure/Involved | Other | Other | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2402 | Equipment Failure/Involved | Other | Other | Deteriorated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2403 | Equipment Failure/Involved | Other | Other | Leaking | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2404 | Equipment Failure/Involved | Other | Other | Malfunctioning | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2405 | Equipment Failure/Involved | Other | Other | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2406 | Equipment Failure/Involved | Other | Other | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2407 | Equipment Failure/Involved | Other | PGs- Kearneys | Broken | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2408 | Equipment Failure/Involved | Other | PGs- Kearneys | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2409 | Equipment Failure/Involved | Other | PGs- Kearneys | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2410 | Equipment Failure/Involved | Other | PGs- Kearneys | Burned/flashed | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2411 | Equipment Failure/Involved | Other | PGs- Kearneys | Deteriorated | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2412 | Equipment Failure/Involved | Other | Pole-Wood | Arcing | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
2413 | Equipment Failure/Involved | Other | Pole-Wood | Bent or Twisted | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
2414 | Equipment Failure/Involved | Other | Pole-Wood | Broken | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
2415 | Equipment Failure/Involved | Other | Pole-Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2416 | Equipment Failure/Involved | Other | Pole-Wood | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2417 | Equipment Failure/Involved | Other | Pole-Wood | Burned Open | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
2418 | Equipment Failure/Involved | Other | Pole-Wood | Burned/flashed | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
2419 | Equipment Failure/Involved | Other | Pole-Wood | Deteriorated | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
2420 | Equipment Failure/Involved | Other | Pole-Wood | Normal | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
2421 | Equipment Failure/Involved | Other | Pole-Wood | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2422 | Equipment Failure/Involved | Other | Pothead/Riser Termination | Arcing | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
2423 | Equipment Failure/Involved | Other | Pothead/Riser Termination | Blown/failed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
2424 | Equipment Failure/Involved | Other | Pothead/Riser Termination | Broken | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
2425 | Equipment Failure/Involved | Other | Pothead/Riser Termination | Burned Open | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
2426 | Equipment Failure/Involved | Other | Pothead/Riser Termination | Burned/flashed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
2427 | Equipment Failure/Involved | Other | Pothead/Riser Termination | Contaminated | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
2428 | Equipment Failure/Involved | Other | Pothead/Riser Termination | Malfunctioning | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
2429 | Equipment Failure/Involved | Other | Recloser | Burned/flashed | Medium | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters but coverered conductor will reduce annual number of operations/duty cycle.
2430 | Equipment Failure/Involved | Other | Recloser | Malfunctioning | Medium | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters but coverered conductor will reduce annual number of operations/duty cycle.
2431 | Equipment Failure/Involved | Other | Regulator | Arcing | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2432 | Equipment Failure/Involved | Other | Regulator | Blown/failed | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2433 | Equipment Failure/Involved | Other | Regulator | Burned/flashed | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2434 | Equipment Failure/Involved | Other | Regulator | Leaking | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2435 | Equipment Failure/Involved | Other | Regulator | Malfunctioning | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2436 | Equipment Failure/Involved | Other | Riser | Blown/failed | High | Risers are indirectly addressed on System Hardening - Pole changeouts, the covering of jumpers and leads, along with covering conductor should mitigate outages and risk.
2437 | Equipment Failure/Involved | Other | Riser | Malfunctioning | High | Risers are indirectly addressed on System Hardening - Pole changeouts, the covering of jumpers and leads, along with covering conductor should mitigate outages and risk.
2438 | Equipment Failure/Involved | Other | Secondary | Arcing | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2439 | Equipment Failure/Involved | Other | Secondary | Blown/failed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2440 | Equipment Failure/Involved | Other | Secondary | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2441 | Equipment Failure/Involved | Other | Secondary | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2442 | Equipment Failure/Involved | Other | Secondary | Burned Open | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2443 | Equipment Failure/Involved | Other | Secondary | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2444 | Equipment Failure/Involved | Other | Secondary | Contaminated | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2445 | Equipment Failure/Involved | Other | Secondary | Deteriorated | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2446 | Equipment Failure/Involved | Other | Secondary | Leaking | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2447 | Equipment Failure/Involved | Other | Secondary | Malfunctioning | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2448 | Equipment Failure/Involved | Other | Secondary | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2449 | Equipment Failure/Involved | Other | Secondary | On Ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2450 | Equipment Failure/Involved | Other | Secondary | Together | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2451 | Equipment Failure/Involved | Other | Service conductor | Arcing | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2452 | Equipment Failure/Involved | Other | Service conductor | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2453 | Equipment Failure/Involved | Other | Service conductor | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2454 | Equipment Failure/Involved | Other | Service conductor | Broken- wire on object | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2455 | Equipment Failure/Involved | Other | Service conductor | Burned Open | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2456 | Equipment Failure/Involved | Other | Service conductor | Deteriorated | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2457 | Equipment Failure/Involved | Other | Service conductor | Malfunctioning | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2458 | Equipment Failure/Involved | Other | Service conductor | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2459 | Equipment Failure/Involved | Other | Service conductor | Together | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2460 | Equipment Failure/Involved | Other | Splice box | Burned Open | All | Underground facilities = no ignition risk
2461 | Equipment Failure/Involved | Other | Splice box | Leaking | All | Underground facilities = no ignition risk
2462 | Equipment Failure/Involved | Other | Switch | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2463 | Equipment Failure/Involved | Other | Switch | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2464 | Equipment Failure/Involved | Other | Switch | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2465 | Equipment Failure/Involved | Other | Switch | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2466 | Equipment Failure/Involved | Other | Switch | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2467 | Equipment Failure/Involved | Other | Switch | Leaking | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2468 | Equipment Failure/Involved | Other | Switch | Malfunctioning | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2469 | Equipment Failure/Involved | Other | Switch | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2470 | Equipment Failure/Involved | Other | Transformer |  | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2471 | Equipment Failure/Involved | Other | Transformer | Arcing | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2472 | Equipment Failure/Involved | Other | Transformer | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2473 | Equipment Failure/Involved | Other | Transformer | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2474 | Equipment Failure/Involved | Other | Transformer | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2475 | Equipment Failure/Involved | Other | Transformer | Burned Open | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2476 | Equipment Failure/Involved | Other | Transformer | Burned/flashed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2477 | Equipment Failure/Involved | Other | Transformer | Contaminated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2478 | Equipment Failure/Involved | Other | Transformer | Deteriorated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2479 | Equipment Failure/Involved | Other | Transformer | Leaking | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2480 | Equipment Failure/Involved | Other | Transformer | Malfunctioning | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2481 | Equipment Failure/Involved | Other | Transformer | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2482 | Equipment Failure/Involved | Other | Transformer | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2483 | Equipment Failure/Involved | Other | Transformer (OH) | Arcing | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2484 | Equipment Failure/Involved | Other | Transformer (OH) | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2485 | Equipment Failure/Involved | Other | Transformer (OH) | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2486 | Equipment Failure/Involved | Other | Transformer (OH) | Deteriorated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2487 | Equipment Failure/Involved | Other | Transformer (OH) | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2488 | Equipment Failure/Involved | Other | Transformer (UG) | Blown/failed | All | UG Facilities = no ignition risk
2489 | Equipment Failure/Involved | Other | Transformer (UG) | Broken | All | UG Facilities = no ignition risk
2490 | Equipment Failure/Involved | Other | Woodpin | Broken | All | Composite arms are being installed along with new insulators and bonding. Tracking insulators/pole fires will be limited though not 100% eliminate. Gunshot damage will still be a concern. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
2491 | Equipment Failure/Involved | Other | Woodpin | Broken- wire on ground | None | Significant external force broke the conductor and brought wire to the ground/object. Ignition risk not mitigated.
2492 | Equipment Failure/Involved | Other | Woodpin | Deteriorated | All | Composite arms are being installed along with new insulators and bonding. Tracking insulators/pole fires will be limited though not 100% eliminate. Gunshot damage will still be a concern. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
2493 | Equipment Failure/Involved | Overhead |  |  | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2494 | Equipment Failure/Involved | Overhead |  | Arcing | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2495 | Equipment Failure/Involved | Overhead |  | Blown/failed | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2496 | Equipment Failure/Involved | Overhead |  | Broken | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2497 | Equipment Failure/Involved | Overhead |  | Burned Open | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2498 | Equipment Failure/Involved | Overhead |  | Normal | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2499 | Equipment Failure/Involved | Overhead | Anchor or Guy | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2500 | Equipment Failure/Involved | Overhead | Anchor or Guy | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2501 | Equipment Failure/Involved | Overhead | Anchor or Guy | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2502 | Equipment Failure/Involved | Overhead | Anchor or Guy | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2503 | Equipment Failure/Involved | Overhead | Anchor or Guy | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2504 | Equipment Failure/Involved | Overhead | Anchor or Guy | Contaminated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2505 | Equipment Failure/Involved | Overhead | Anchor or Guy | Deteriorated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2506 | Equipment Failure/Involved | Overhead | Anchor or Guy | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2507 | Equipment Failure/Involved | Overhead | Booster | Arcing | All | Circuit Hardening replaces boosters with voltage regulators.
2508 | Equipment Failure/Involved | Overhead | Booster | Blown/failed | All | Circuit Hardening replaces boosters with voltage regulators.
2509 | Equipment Failure/Involved | Overhead | Booster | Broken | All | Circuit Hardening replaces boosters with voltage regulators.
2510 | Equipment Failure/Involved | Overhead | Booster | Burned/flashed | All | Circuit Hardening replaces boosters with voltage regulators.
2511 | Equipment Failure/Involved | Overhead | Booster | Malfunctioning | All | Circuit Hardening replaces boosters with voltage regulators.
2512 | Equipment Failure/Involved | Overhead | Booster | Normal | All | Circuit Hardening replaces boosters with voltage regulators.
2513 | Equipment Failure/Involved | Overhead | Bus | Arcing | High | Transformers installed prior to 2014 will be replaced. Work would include covering jumpers and replacing some of the service conductor.
2514 | Equipment Failure/Involved | Overhead | Bus | Blown/failed | High | Transformers installed prior to 2014 will be replaced. Work would include covering jumpers and replacing some of the service conductor.
2515 | Equipment Failure/Involved | Overhead | Bus | Burned Open | High | Transformers installed prior to 2014 will be replaced. Work would include covering jumpers and replacing some of the service conductor.
2516 | Equipment Failure/Involved | Overhead | Bus | Burned/flashed | High | Transformers installed prior to 2014 will be replaced. Work would include covering jumpers and replacing some of the service conductor.
2517 | Equipment Failure/Involved | Overhead | Bus | Deteriorated | High | Transformers installed prior to 2014 will be replaced. Work would include covering jumpers and replacing some of the service conductor.
2518 | Equipment Failure/Involved | Overhead | Bushing | Arcing | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks.
2519 | Equipment Failure/Involved | Overhead | Bushing | Blown/failed | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks.
2520 | Equipment Failure/Involved | Overhead | Bushing | Broken | None | Significant external force broke the bushing. Ignition risk not mitigated.
2521 | Equipment Failure/Involved | Overhead | Bushing | Burned Open | None | Significant external force broke the bushing. Ignition risk not mitigated.
2522 | Equipment Failure/Involved | Overhead | Bushing | Burned/flashed | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks.
2523 | Equipment Failure/Involved | Overhead | Bushing | Contaminated | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks.
2524 | Equipment Failure/Involved | Overhead | Bushing | Deteriorated | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks.
2525 | Equipment Failure/Involved | Overhead | Bushing | Leaking | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks.
2526 | Equipment Failure/Involved | Overhead | Bushing | Normal | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks.
2527 | Equipment Failure/Involved | Overhead | Capacitor | Arcing | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
2528 | Equipment Failure/Involved | Overhead | Capacitor | Blown/failed | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
2529 | Equipment Failure/Involved | Overhead | Capacitor | Broken | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
2530 | Equipment Failure/Involved | Overhead | Capacitor | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2531 | Equipment Failure/Involved | Overhead | Capacitor | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2532 | Equipment Failure/Involved | Overhead | Capacitor | Burned/flashed | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
2533 | Equipment Failure/Involved | Overhead | Capacitor | Leaking | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
2534 | Equipment Failure/Involved | Overhead | Capacitor | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2535 | Equipment Failure/Involved | Overhead | Conductor- Overhead | Annealed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2536 | Equipment Failure/Involved | Overhead | Conductor- Overhead | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2537 | Equipment Failure/Involved | Overhead | Conductor- Overhead | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2538 | Equipment Failure/Involved | Overhead | Conductor- Overhead | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2539 | Equipment Failure/Involved | Overhead | Conductor- Overhead | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2540 | Equipment Failure/Involved | Overhead | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2541 | Equipment Failure/Involved | Overhead | Conductor- Overhead | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2542 | Equipment Failure/Involved | Overhead | Conductor- Overhead | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2543 | Equipment Failure/Involved | Overhead | Conductor- Overhead | Contaminated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2544 | Equipment Failure/Involved | Overhead | Conductor- Overhead | Deteriorated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2545 | Equipment Failure/Involved | Overhead | Conductor- Overhead | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2546 | Equipment Failure/Involved | Overhead | Conductor- Overhead | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2547 | Equipment Failure/Involved | Overhead | Conductor- Overhead | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2548 | Equipment Failure/Involved | Overhead | Conductor- Underground | Blown/failed | All | Underground facilities = no ignition risk
2549 | Equipment Failure/Involved | Overhead | Conductor- Underground | Broken | All | Underground facilities = no ignition risk
2550 | Equipment Failure/Involved | Overhead | Conductor- Underground | Burned/flashed | All | Underground facilities = no ignition risk
2551 | Equipment Failure/Involved | Overhead | Conductor- Underground | Deteriorated | All | Underground facilities = no ignition risk
2552 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) |  | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2553 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Arcing | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2554 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2555 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken- wire on ground | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2556 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Broken- wire on object | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2557 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Burned Open | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2558 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Burned/flashed | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2559 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Contaminated | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2560 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Deteriorated | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2561 | Equipment Failure/Involved | Overhead | Connector or Splice (OH) | Normal | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2562 | Equipment Failure/Involved | Overhead | Connector or Splice (UG) | Blown/failed | All | Underground facilities = no ignition risk
2563 | Equipment Failure/Involved | Overhead | Connector or Splice (UG) | Burned/flashed | All | Underground facilities = no ignition risk
2564 | Equipment Failure/Involved | Overhead | Crossarm- Steel | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2565 | Equipment Failure/Involved | Overhead | Crossarm- Steel | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2566 | Equipment Failure/Involved | Overhead | Crossarm- Steel | Deteriorated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2567 | Equipment Failure/Involved | Overhead | Crossarm- Steel | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2568 | Equipment Failure/Involved | Overhead | Crossarm- Wood |  | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2569 | Equipment Failure/Involved | Overhead | Crossarm- Wood | Blown/failed | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
2570 | Equipment Failure/Involved | Overhead | Crossarm- Wood | Broken | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
2571 | Equipment Failure/Involved | Overhead | Crossarm- Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2572 | Equipment Failure/Involved | Overhead | Crossarm- Wood | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2573 | Equipment Failure/Involved | Overhead | Crossarm- Wood | Burned/flashed | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
2574 | Equipment Failure/Involved | Overhead | Crossarm- Wood | Contaminated | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
2575 | Equipment Failure/Involved | Overhead | Crossarm- Wood | Deteriorated | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
2576 | Equipment Failure/Involved | Overhead | Crossarm- Wood | Normal | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
2577 | Equipment Failure/Involved | Overhead | CT | Blown/failed | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2578 | Equipment Failure/Involved | Overhead | CT | Deteriorated | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2579 | Equipment Failure/Involved | Overhead | Customer Equipment | Arcing | None | No work is being completed on customer equipment.
2580 | Equipment Failure/Involved | Overhead | Customer Equipment | Blown/failed | None | No work is being completed on customer equipment.
2581 | Equipment Failure/Involved | Overhead | Customer Equipment | Broken | None | No work is being completed on customer equipment.
2582 | Equipment Failure/Involved | Overhead | Customer Equipment | Burned/flashed | None | No work is being completed on customer equipment.
2583 | Equipment Failure/Involved | Overhead | Customer Equipment | Deteriorated | None | No work is being completed on customer equipment.
2584 | Equipment Failure/Involved | Overhead | Customer Equipment | Malfunctioning | None | No work is being completed on customer equipment.
2585 | Equipment Failure/Involved | Overhead | Customer Equipment | Together | None | No work is being completed on customer equipment.
2586 | Equipment Failure/Involved | Overhead | Cutout- fuse holder | Arcing | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
2587 | Equipment Failure/Involved | Overhead | Cutout- fuse holder | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
2588 | Equipment Failure/Involved | Overhead | Cutout- fuse holder | Broken | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
2589 | Equipment Failure/Involved | Overhead | Cutout- fuse holder | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2590 | Equipment Failure/Involved | Overhead | Cutout- fuse holder | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2591 | Equipment Failure/Involved | Overhead | Cutout- fuse holder | Burned/flashed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
2592 | Equipment Failure/Involved | Overhead | Cutout- fuse holder | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
2593 | Equipment Failure/Involved | Overhead | Footings- Tower or Pole | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2594 | Equipment Failure/Involved | Overhead | Footings- Tower or Pole | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2595 | Equipment Failure/Involved | Overhead | Footings- Tower or Pole | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2596 | Equipment Failure/Involved | Overhead | Fuse | Arcing | All | Covered conductor will eliminate the line to ground connection that likely caused this outage/risk.
2597 | Equipment Failure/Involved | Overhead | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
2598 | Equipment Failure/Involved | Overhead | Fuse | Broken | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
2599 | Equipment Failure/Involved | Overhead | Fuse | Burned Open | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
2600 | Equipment Failure/Involved | Overhead | Fuse | Normal | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
2601 | Equipment Failure/Involved | Overhead | Generator | Malfunctioning | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2602 | Equipment Failure/Involved | Overhead | Generator | Normal | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2603 | Equipment Failure/Involved | Overhead | Insulator | Arcing | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
2604 | Equipment Failure/Involved | Overhead | Insulator | Blown/failed | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
2605 | Equipment Failure/Involved | Overhead | Insulator | Broken | All | Age or significant external force broke insulator. System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
2606 | Equipment Failure/Involved | Overhead | Insulator | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2607 | Equipment Failure/Involved | Overhead | Insulator | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2608 | Equipment Failure/Involved | Overhead | Insulator | Burned/flashed | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
2609 | Equipment Failure/Involved | Overhead | Insulator | Normal | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
2610 | Equipment Failure/Involved | Overhead | Jumper | Arcing | High | Larger covered conductor to mostly eliminate cause and risk.
2611 | Equipment Failure/Involved | Overhead | Jumper | Bent or Twisted | High | Larger covered conductor to mostly eliminate cause and risk.
2612 | Equipment Failure/Involved | Overhead | Jumper | Broken | High | Larger covered conductor to mostly eliminate cause and risk.
2613 | Equipment Failure/Involved | Overhead | Jumper | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2614 | Equipment Failure/Involved | Overhead | Jumper | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2615 | Equipment Failure/Involved | Overhead | Jumper | Burned Open | High | Larger covered conductor to mostly eliminate cause and risk.
2616 | Equipment Failure/Involved | Overhead | Jumper | Burned/flashed | High | Larger covered conductor to mostly eliminate cause and risk.
2617 | Equipment Failure/Involved | Overhead | Jumper | Deteriorated | High | Larger covered conductor to mostly eliminate cause and risk.
2618 | Equipment Failure/Involved | Overhead | Jumper | Normal | High | Larger covered conductor to mostly eliminate cause and risk.
2619 | Equipment Failure/Involved | Overhead | Lightning Arrestor | Arcing | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
2620 | Equipment Failure/Involved | Overhead | Lightning Arrestor | Blown/failed | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
2621 | Equipment Failure/Involved | Overhead | Lightning Arrestor | Broken | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
2622 | Equipment Failure/Involved | Overhead | Lightning Arrestor | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2623 | Equipment Failure/Involved | Overhead | Lightning Arrestor | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2624 | Equipment Failure/Involved | Overhead | Lightning Arrestor | Burned/flashed | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
2625 | Equipment Failure/Involved | Overhead | Lightning Arrestor | Normal | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
2626 | Equipment Failure/Involved | Overhead | Metering Equipment |  | None | System Hardening does not address Metering facilities.
2627 | Equipment Failure/Involved | Overhead | Metering Equipment | Arcing | None | System Hardening does not address Metering facilities.
2628 | Equipment Failure/Involved | Overhead | Metering Equipment | Blown/failed | None | System Hardening does not address Metering facilities.
2629 | Equipment Failure/Involved | Overhead | Metering Equipment | Burned/flashed | None | System Hardening does not address Metering facilities.
2630 | Equipment Failure/Involved | Overhead | Metering Equipment | Deteriorated | None | System Hardening does not address Metering facilities.
2631 | Equipment Failure/Involved | Overhead | Metering Equipment | Malfunctioning | None | System Hardening does not address Metering facilities.
2632 | Equipment Failure/Involved | Overhead | Other | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2633 | Equipment Failure/Involved | Overhead | Other | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2634 | Equipment Failure/Involved | Overhead | Other | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2635 | Equipment Failure/Involved | Overhead | Other | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2636 | Equipment Failure/Involved | Overhead | Other | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2637 | Equipment Failure/Involved | Overhead | Other | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2638 | Equipment Failure/Involved | Overhead | Other | Burned Open | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2639 | Equipment Failure/Involved | Overhead | Other | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2640 | Equipment Failure/Involved | Overhead | Other | Contaminated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2641 | Equipment Failure/Involved | Overhead | Other | Deteriorated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2642 | Equipment Failure/Involved | Overhead | Other | Leaking | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2643 | Equipment Failure/Involved | Overhead | Other | Malfunctioning | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2644 | Equipment Failure/Involved | Overhead | Other | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2645 | Equipment Failure/Involved | Overhead | Other | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2646 | Equipment Failure/Involved | Overhead | PGs- Kearneys | Arcing | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2647 | Equipment Failure/Involved | Overhead | PGs- Kearneys | Broken | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2648 | Equipment Failure/Involved | Overhead | PGs- Kearneys | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2649 | Equipment Failure/Involved | Overhead | PGs- Kearneys | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2650 | Equipment Failure/Involved | Overhead | PGs- Kearneys | Burned Open | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2651 | Equipment Failure/Involved | Overhead | PGs- Kearneys | Burned/flashed | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2652 | Equipment Failure/Involved | Overhead | PGs- Kearneys | Deteriorated | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2653 | Equipment Failure/Involved | Overhead | Pole - Tower- steel | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2654 | Equipment Failure/Involved | Overhead | Pole - Tower- steel | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2655 | Equipment Failure/Involved | Overhead | Pole - Tower- steel | Broken- wire on ground | None | Significant external force broke the conductor and brought wire to the ground/object. Ignition risk not mitigated.
2656 | Equipment Failure/Involved | Overhead | Pole - Tower- steel | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2657 | Equipment Failure/Involved | Overhead | Pole - Tower- steel | Deteriorated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2658 | Equipment Failure/Involved | Overhead | Pole-Wood | Blown/failed | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
2659 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
2660 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2661 | Equipment Failure/Involved | Overhead | Pole-Wood | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2662 | Equipment Failure/Involved | Overhead | Pole-Wood | Burned/flashed | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
2663 | Equipment Failure/Involved | Overhead | Pole-Wood | Contaminated | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
2664 | Equipment Failure/Involved | Overhead | Pole-Wood | Deteriorated | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
2665 | Equipment Failure/Involved | Overhead | Pole-Wood | Normal | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
2666 | Equipment Failure/Involved | Overhead | Pole-Wood | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2667 | Equipment Failure/Involved | Overhead | Pothead(Riser Termination) | Arcing | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
2668 | Equipment Failure/Involved | Overhead | Pothead(Riser Termination) | Blown/failed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
2669 | Equipment Failure/Involved | Overhead | Pothead(Riser Termination) | Broken | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
2670 | Equipment Failure/Involved | Overhead | Pothead(Riser Termination) | Burned Open | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
2671 | Equipment Failure/Involved | Overhead | Pothead(Riser Termination) | Burned/flashed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
2672 | Equipment Failure/Involved | Overhead | Pothead(Riser Termination) | Contaminated | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
2673 | Equipment Failure/Involved | Overhead | Pothead(Riser Termination) | Deteriorated | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
2674 | Equipment Failure/Involved | Overhead | Pothead(Riser Termination) | Normal | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
2675 | Equipment Failure/Involved | Overhead | Pothead/Riser Termination |  | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
2676 | Equipment Failure/Involved | Overhead | Pothead/Riser Termination | Blown/failed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
2677 | Equipment Failure/Involved | Overhead | Pothead/Riser Termination | Burned/flashed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
2678 | Equipment Failure/Involved | Overhead | PT/CCVT | Arcing | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2679 | Equipment Failure/Involved | Overhead | PT/CCVT | Blown/failed | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2680 | Equipment Failure/Involved | Overhead | PT/CCVT | Burned Open | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2681 | Equipment Failure/Involved | Overhead | PT/CCVT | Burned/flashed | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2682 | Equipment Failure/Involved | Overhead | PT/CCVT | Contaminated | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2683 | Equipment Failure/Involved | Overhead | Recloser | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2684 | Equipment Failure/Involved | Overhead | Recloser | Blown/failed | Medium | System Hardening does not address Reclosers but coverered conductor will reduce annual recloser operations.
2685 | Equipment Failure/Involved | Overhead | Recloser | Broken | Medium | System Hardening does not address Reclosers but coverered conductor will reduce annual recloser operations.
2686 | Equipment Failure/Involved | Overhead | Recloser | Burned/flashed | Medium | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters but coverered conductor will reduce annual number of operations/duty cycle.
2687 | Equipment Failure/Involved | Overhead | Recloser | Leaking | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2688 | Equipment Failure/Involved | Overhead | Recloser | Malfunctioning | Medium | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters but coverered conductor will reduce annual number of operations/duty cycle.
2689 | Equipment Failure/Involved | Overhead | Recloser | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2690 | Equipment Failure/Involved | Overhead | Regulator | Arcing | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2691 | Equipment Failure/Involved | Overhead | Regulator | Blown/failed | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2692 | Equipment Failure/Involved | Overhead | Regulator | Broken | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2693 | Equipment Failure/Involved | Overhead | Regulator | Burned/flashed | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2694 | Equipment Failure/Involved | Overhead | Regulator | Leaking | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2695 | Equipment Failure/Involved | Overhead | Regulator | Malfunctioning | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2696 | Equipment Failure/Involved | Overhead | Regulator | Normal | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2697 | Equipment Failure/Involved | Overhead | Regulator- LTC substation | Malfunctioning | None | Circuit Hardening will not affect substation equipment.
2698 | Equipment Failure/Involved | Overhead | Relay | Malfunctioning | None | Circuit Hardening will not affect substation equipment.
2699 | Equipment Failure/Involved | Overhead | SCADA | Malfunctioning | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2700 | Equipment Failure/Involved | Overhead | Secondary |  | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2701 | Equipment Failure/Involved | Overhead | Secondary | Annealed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2702 | Equipment Failure/Involved | Overhead | Secondary | Arcing | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2703 | Equipment Failure/Involved | Overhead | Secondary | Bent or Twisted | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2704 | Equipment Failure/Involved | Overhead | Secondary | Blown/failed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2705 | Equipment Failure/Involved | Overhead | Secondary | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2706 | Equipment Failure/Involved | Overhead | Secondary | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2707 | Equipment Failure/Involved | Overhead | Secondary | Broken- wire on object | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2708 | Equipment Failure/Involved | Overhead | Secondary | Burned Open | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2709 | Equipment Failure/Involved | Overhead | Secondary | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2710 | Equipment Failure/Involved | Overhead | Secondary | Contaminated | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2711 | Equipment Failure/Involved | Overhead | Secondary | Deteriorated | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2712 | Equipment Failure/Involved | Overhead | Secondary | Malfunctioning | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2713 | Equipment Failure/Involved | Overhead | Secondary | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2714 | Equipment Failure/Involved | Overhead | Secondary | On Ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2715 | Equipment Failure/Involved | Overhead | Secondary | Together | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2716 | Equipment Failure/Involved | Overhead | Sectionalizer | Blown/failed | Medium | System Hardening does not address Reclosers/Sectionalizers but coverered conductor will reduce annual recloser operations.
2717 | Equipment Failure/Involved | Overhead | Sectionalizer | Broken | Medium | System Hardening does not address Reclosers/Sectionalizers but coverered conductor will reduce annual recloser operations.
2718 | Equipment Failure/Involved | Overhead | Sectionalizer | Burned/flashed | Medium | System Hardening does not address Reclosers/Sectionalizers but coverered conductor will reduce annual recloser operations.
2719 | Equipment Failure/Involved | Overhead | Sectionalizer | Malfunctioning | Medium | System Hardening does not address Reclosers/Sectionalizers but coverered conductor will reduce annual recloser operations.
2720 | Equipment Failure/Involved | Overhead | Sectionalizer | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2721 | Equipment Failure/Involved | Overhead | Service conductor |  | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2722 | Equipment Failure/Involved | Overhead | Service conductor | Annealed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2723 | Equipment Failure/Involved | Overhead | Service conductor | Arcing | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2724 | Equipment Failure/Involved | Overhead | Service conductor | Bent or Twisted | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2725 | Equipment Failure/Involved | Overhead | Service conductor | Blown/failed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2726 | Equipment Failure/Involved | Overhead | Service conductor | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2727 | Equipment Failure/Involved | Overhead | Service conductor | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2728 | Equipment Failure/Involved | Overhead | Service conductor | Broken- wire on object | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2729 | Equipment Failure/Involved | Overhead | Service conductor | Burned Open | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2730 | Equipment Failure/Involved | Overhead | Service conductor | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2731 | Equipment Failure/Involved | Overhead | Service conductor | Contaminated | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2732 | Equipment Failure/Involved | Overhead | Service conductor | Deteriorated | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2733 | Equipment Failure/Involved | Overhead | Service conductor | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2734 | Equipment Failure/Involved | Overhead | Service conductor | On Ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2735 | Equipment Failure/Involved | Overhead | Service conductor | Together | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2736 | Equipment Failure/Involved | Overhead | Stepdown | Arcing | All | Underground facilities = no ignition risk
2737 | Equipment Failure/Involved | Overhead | Stepdown | Blown/failed | All | Underground facilities = no ignition risk
2738 | Equipment Failure/Involved | Overhead | Stepdown | Broken | All | Underground facilities = no ignition risk
2739 | Equipment Failure/Involved | Overhead | Stepdown | Burned/flashed | All | Underground facilities = no ignition risk
2740 | Equipment Failure/Involved | Overhead | Stepdown | Deteriorated | All | Underground facilities = no ignition risk
2741 | Equipment Failure/Involved | Overhead | Stepdown | Normal | All | Underground facilities = no ignition risk
2742 | Equipment Failure/Involved | Overhead | Street Light Equipment | Arcing | Medium | System Hardening will not address Street Lights but will address their transformers.
2743 | Equipment Failure/Involved | Overhead | Street Light Equipment | Blown/failed | Medium | System Hardening will not address Street Lights but will address their transformers.
2744 | Equipment Failure/Involved | Overhead | Street Light Equipment | Broken | Medium | System Hardening will not address Street Lights but will address their transformers.
2745 | Equipment Failure/Involved | Overhead | Street Light Equipment | Burned/flashed | Medium | System Hardening will not address Street Lights but will address their transformers.
2746 | Equipment Failure/Involved | Overhead | Street Light Equipment | Malfunctioning | Medium | System Hardening will not address Street Lights but will address their transformers.
2747 | Equipment Failure/Involved | Overhead | Switch | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2748 | Equipment Failure/Involved | Overhead | Switch | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2749 | Equipment Failure/Involved | Overhead | Switch | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2750 | Equipment Failure/Involved | Overhead | Switch | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2751 | Equipment Failure/Involved | Overhead | Switch | Leaking | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2752 | Equipment Failure/Involved | Overhead | Switch | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2753 | Equipment Failure/Involved | Overhead | Switch (OH) | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2754 | Equipment Failure/Involved | Overhead | Switch (OH) | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2755 | Equipment Failure/Involved | Overhead | Switch (OH) | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2756 | Equipment Failure/Involved | Overhead | Switch (OH) | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2757 | Equipment Failure/Involved | Overhead | Switch (OH) | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2758 | Equipment Failure/Involved | Overhead | Switch (OH) | Leaking | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2759 | Equipment Failure/Involved | Overhead | Switch (OH) | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2760 | Equipment Failure/Involved | Overhead | Transformer |  | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2761 | Equipment Failure/Involved | Overhead | Transformer | Annealed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2762 | Equipment Failure/Involved | Overhead | Transformer | Arcing | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2763 | Equipment Failure/Involved | Overhead | Transformer | Bent or Twisted | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2764 | Equipment Failure/Involved | Overhead | Transformer | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2765 | Equipment Failure/Involved | Overhead | Transformer | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2766 | Equipment Failure/Involved | Overhead | Transformer | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2767 | Equipment Failure/Involved | Overhead | Transformer | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2768 | Equipment Failure/Involved | Overhead | Transformer | Burned Open | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2769 | Equipment Failure/Involved | Overhead | Transformer | Burned/flashed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2770 | Equipment Failure/Involved | Overhead | Transformer | Contaminated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2771 | Equipment Failure/Involved | Overhead | Transformer | Deteriorated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2772 | Equipment Failure/Involved | Overhead | Transformer | Leaking | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2773 | Equipment Failure/Involved | Overhead | Transformer | Malfunctioning | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2774 | Equipment Failure/Involved | Overhead | Transformer | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2775 | Equipment Failure/Involved | Overhead | Transformer | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2776 | Equipment Failure/Involved | Overhead | Transformer | Together | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2777 | Equipment Failure/Involved | Overhead | Transformer (OH) |  | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2778 | Equipment Failure/Involved | Overhead | Transformer (OH) | Arcing | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2779 | Equipment Failure/Involved | Overhead | Transformer (OH) | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2780 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2781 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2782 | Equipment Failure/Involved | Overhead | Transformer (OH) | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2783 | Equipment Failure/Involved | Overhead | Transformer (OH) | Burned/flashed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2784 | Equipment Failure/Involved | Overhead | Transformer (OH) | Contaminated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2785 | Equipment Failure/Involved | Overhead | Transformer (OH) | Deteriorated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2786 | Equipment Failure/Involved | Overhead | Transformer (OH) | Leaking | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2787 | Equipment Failure/Involved | Overhead | Transformer (OH) | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
2788 | Equipment Failure/Involved | Overhead | Transformer (OH) | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
2789 | Equipment Failure/Involved | Overhead | Transformer (UG) | Deteriorated | All | UG Facilities = no ignition risk
2790 | Equipment Failure/Involved | Overhead | Transformer (UG) | Normal | All | UG Facilities = no ignition risk
2791 | Equipment Failure/Involved | Overhead | Woodpin | Broken | All | Composite arms are being installed along with new insulators and bonding. Tracking insulators/pole fires will be limited though not 100% eliminate. Gunshot damage will still be a concern. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
2792 | Equipment Failure/Involved | Overhead | Woodpin | Broken- wire on ground | None | Significant external force broke the conductor and brought wire to the ground/object. Ignition risk not mitigated.
2793 | Equipment Failure/Involved | Overhead | Woodpin | Broken- wire on object | None | Significant external force broke the conductor and brought wire to the ground/object. Ignition risk not mitigated.
2794 | Equipment Failure/Involved | Overhead | Woodpin | Burned/flashed | All | Composite arms are being installed along with new insulators and bonding. Tracking insulators/pole fires will be limited though not 100% eliminate. Gunshot damage will still be a concern. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
2795 | Equipment Failure/Involved | Overhead | Woodpin | Contaminated | All | Composite arms are being installed along with new insulators and bonding. Tracking insulators/pole fires will be limited though not 100% eliminate. Gunshot damage will still be a concern. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
2796 | Equipment Failure/Involved | Overhead | Woodpin | Deteriorated | All | Composite arms are being installed along with new insulators and bonding. Tracking insulators/pole fires will be limited though not 100% eliminate. Gunshot damage will still be a concern. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
2797 | Equipment Failure/Involved | Overhead | Woodpin | Normal | All | Composite arms are being installed along with new insulators and bonding. Tracking insulators/pole fires will be limited though not 100% eliminate. Gunshot damage will still be a concern. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
2798 | Equipment Failure/Involved | Substation | Circuit Breaker | Blown/failed | Medium | System Hardening does not address substation equipment but coverered conductor will reduce annual breaker operations.
2799 | Equipment Failure/Involved | Substation | Circuit Breaker | Broken | Medium | System Hardening does not address substation equipment but coverered conductor will reduce annual breaker operations.
2800 | Equipment Failure/Involved | Substation | Circuit Breaker | Contaminated | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2801 | Equipment Failure/Involved | Substation | Circuit Breaker | Malfunctioning | Medium | System Hardening does not address substation equipment but coverered conductor will reduce annual breaker operations.
2802 | Equipment Failure/Involved | Substation | Circuit Breaker | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2803 | Equipment Failure/Involved | Substation | Conductor- Underground | Broken | All | Underground facilities = no ignition risk
2804 | Equipment Failure/Involved | Substation | Connector or Splice (OH) | Burned Open | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2805 | Equipment Failure/Involved | Substation | CT | Normal | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2806 | Equipment Failure/Involved | Substation | Cutout- fuse holder | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
2807 | Equipment Failure/Involved | Substation | Generator | Leaking | None | Circuit Hardening will not affect substation equipment.
2808 | Equipment Failure/Involved | Substation | Generator | Normal | None | Circuit Hardening will not affect substation equipment.
2809 | Equipment Failure/Involved | Substation | Insulator | Blown/failed | none | Circuit hardening does not address substation equipment.
2810 | Equipment Failure/Involved | Substation | Insulator | Broken | none | System Hardening does not address substation equipment..
2811 | Equipment Failure/Involved | Substation | Lightning Arrestor | Blown/failed | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
2812 | Equipment Failure/Involved | Substation | Metering Equipment | Malfunctioning | None | System Hardening does not address Metering facilities.
2813 | Equipment Failure/Involved | Substation | Other | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2814 | Equipment Failure/Involved | Substation | Other | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
2815 | Equipment Failure/Involved | Substation | Other | Burned Open | None | Circuit Hardening will not affect substation equipment.
2816 | Equipment Failure/Involved | Substation | Other | Burned/flashed | None | Circuit Hardening will not affect substation equipment.
2817 | Equipment Failure/Involved | Substation | Other | Leaking | None | Circuit Hardening will not affect substation equipment.
2818 | Equipment Failure/Involved | Substation | Other | Malfunctioning | None | Circuit Hardening will not affect substation equipment.
2819 | Equipment Failure/Involved | Substation | Other | Normal | None | Circuit Hardening will not affect substation equipment.
2820 | Equipment Failure/Involved | Substation | Pothead(Riser Termination) | Blown/failed | None | Substation equipment is not addressed with system hardening.
2821 | Equipment Failure/Involved | Substation | PT/CCVT | Blown/failed | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2822 | Equipment Failure/Involved | Substation | Recloser | Normal | All | Circuit hardening does not address substation equipment.
2823 | Equipment Failure/Involved | Substation | Relay | Malfunctioning | None | Circuit Hardening will not affect substation equipment.
2824 | Equipment Failure/Involved | Substation | Relay | Normal | None | Circuit Hardening will not affect substation equipment.
2825 | Equipment Failure/Involved | Substation | Secondary | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2826 | Equipment Failure/Involved | Substation | Secondary | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2827 | Equipment Failure/Involved | Substation | Secondary | Burned Open | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2828 | Equipment Failure/Involved | Substation | Stepdown | Blown/failed | None | System Hardening does not address substation equipment but coverered conductor will reduce annual breaker operations.
2829 | Equipment Failure/Involved | Substation | Transformer | Blown/failed | None | Circuit Hardening will not affect substation equipment.
2830 | Equipment Failure/Involved | Substation | Transformer | Broken | None | Circuit Hardening will not affect substation equipment.
2831 | Equipment Failure/Involved | Substation | Transformer | Leaking | None | Circuit Hardening will not affect substation equipment.
2832 | Equipment Failure/Involved | Underground |  |  | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2833 | Equipment Failure/Involved | Underground |  | Blown/failed | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2834 | Equipment Failure/Involved | Underground |  | Broken | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2835 | Equipment Failure/Involved | Underground | Bus | Arcing | All | UG Facilities = no ignition risk
2836 | Equipment Failure/Involved | Underground | Bus | Bent or Twisted | All | UG Facilities = no ignition risk
2837 | Equipment Failure/Involved | Underground | Bus | Blown/failed | All | UG Facilities = no ignition risk
2838 | Equipment Failure/Involved | Underground | Bus | Burned/flashed | All | UG Facilities = no ignition risk
2839 | Equipment Failure/Involved | Underground | Bus | Contaminated | All | UG Facilities = no ignition risk
2840 | Equipment Failure/Involved | Underground | Bus | Deteriorated | All | UG Facilities = no ignition risk
2841 | Equipment Failure/Involved | Underground | Bus | Normal | All | UG Facilities = no ignition risk
2842 | Equipment Failure/Involved | Underground | Bushing | Arcing | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2843 | Equipment Failure/Involved | Underground | Bushing | Blown/failed | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2844 | Equipment Failure/Involved | Underground | Bushing | Broken | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2845 | Equipment Failure/Involved | Underground | Bushing | Burned/flashed | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2846 | Equipment Failure/Involved | Underground | Bushing | Deteriorated | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2847 | Equipment Failure/Involved | Underground | Bushing | Normal | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2848 | Equipment Failure/Involved | Underground | Cable Termination(live front | Arcing | All | Underground facilities = no ignition risk
2849 | Equipment Failure/Involved | Underground | Cable Termination(live front | Blown/failed | All | Underground facilities = no ignition risk
2850 | Equipment Failure/Involved | Underground | Cable Termination(live front | Broken | All | Underground facilities = no ignition risk
2851 | Equipment Failure/Involved | Underground | Cable Termination(live front | Burned/flashed | All | Underground facilities = no ignition risk
2852 | Equipment Failure/Involved | Underground | Cable Termination(live front | Contaminated | All | Underground facilities = no ignition risk
2853 | Equipment Failure/Involved | Underground | Cable Termination(live front | Deteriorated | All | Underground facilities = no ignition risk
2854 | Equipment Failure/Involved | Underground | Cable Termination(live front | Normal | All | Underground facilities = no ignition risk
2855 | Equipment Failure/Involved | Underground | Capacitor | Blown/failed | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
2856 | Equipment Failure/Involved | Underground | Capacitor | Broken | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
2857 | Equipment Failure/Involved | Underground | Capacitor | Burned/flashed | All | Underground facilities = no ignition risk
2858 | Equipment Failure/Involved | Underground | Capacitor | Leaking | All | Underground facilities = no ignition risk
2859 | Equipment Failure/Involved | Underground | Conductor- Overhead | Burned/flashed | All | Underground facilities = no ignition risk
2860 | Equipment Failure/Involved | Underground | Conductor- Underground |  | All | Underground facilities = no ignition risk
2861 | Equipment Failure/Involved | Underground | Conductor- Underground | Blown/failed | All | Underground facilities = no ignition risk
2862 | Equipment Failure/Involved | Underground | Conductor- Underground | Broken | All | Underground facilities = no ignition risk
2863 | Equipment Failure/Involved | Underground | Conductor- Underground | Burned/flashed | All | Underground facilities = no ignition risk
2864 | Equipment Failure/Involved | Underground | Conductor- Underground | Contaminated | All | Underground facilities = no ignition risk
2865 | Equipment Failure/Involved | Underground | Conductor- Underground | Deteriorated | All | Underground facilities = no ignition risk
2866 | Equipment Failure/Involved | Underground | Conductor- Underground | Normal | All | Underground facilities = no ignition risk
2867 | Equipment Failure/Involved | Underground | Connector or Splice (OH) | Burned/flashed | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
2868 | Equipment Failure/Involved | Underground | Connector or Splice (UG) |  | All | Underground facilities = no ignition risk
2869 | Equipment Failure/Involved | Underground | Connector or Splice (UG) | Arcing | All | Underground facilities = no ignition risk
2870 | Equipment Failure/Involved | Underground | Connector or Splice (UG) | Blown/failed | All | Underground facilities = no ignition risk
2871 | Equipment Failure/Involved | Underground | Connector or Splice (UG) | Broken | All | Underground facilities = no ignition risk
2872 | Equipment Failure/Involved | Underground | Connector or Splice (UG) | Burned/flashed | All | Underground facilities = no ignition risk
2873 | Equipment Failure/Involved | Underground | Connector or Splice (UG) | Contaminated | All | Underground facilities = no ignition risk
2874 | Equipment Failure/Involved | Underground | Connector or Splice (UG) | Deteriorated | All | Underground facilities = no ignition risk
2875 | Equipment Failure/Involved | Underground | Connector or Splice (UG) | Normal | All | Underground facilities = no ignition risk
2876 | Equipment Failure/Involved | Underground | Customer Equipment | Arcing | None | No work is being completed on customer equipment.
2877 | Equipment Failure/Involved | Underground | Customer Equipment | Blown/failed | None | No work is being completed on customer equipment.
2878 | Equipment Failure/Involved | Underground | Customer Equipment | Broken | None | No work is being completed on customer equipment.
2879 | Equipment Failure/Involved | Underground | Customer Equipment | Burned Open | None | No work is being completed on customer equipment.
2880 | Equipment Failure/Involved | Underground | Customer Equipment | Burned/flashed | None | No work is being completed on customer equipment.
2881 | Equipment Failure/Involved | Underground | Customer Equipment | Deteriorated | None | No work is being completed on customer equipment.
2882 | Equipment Failure/Involved | Underground | Customer Equipment | Malfunctioning | None | No work is being completed on customer equipment.
2883 | Equipment Failure/Involved | Underground | Customer Equipment | Normal | None | No work is being completed on customer equipment.
2884 | Equipment Failure/Involved | Underground | Cutout- fuse holder | Arcing | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
2885 | Equipment Failure/Involved | Underground | Cutout- fuse holder | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
2886 | Equipment Failure/Involved | Underground | Cutout- fuse holder | Broken | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
2887 | Equipment Failure/Involved | Underground | Cutout- fuse holder | Burned/flashed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
2888 | Equipment Failure/Involved | Underground | Elbow | Blown/failed | All | Underground facilities = no ignition risk
2889 | Equipment Failure/Involved | Underground | Elbow | Broken | All | Underground facilities = no ignition risk
2890 | Equipment Failure/Involved | Underground | Elbow | Burned/flashed | All | Underground facilities = no ignition risk
2891 | Equipment Failure/Involved | Underground | Elbow | Contaminated | All | Underground facilities = no ignition risk
2892 | Equipment Failure/Involved | Underground | Elbow | Deteriorated | All | Underground facilities = no ignition risk
2893 | Equipment Failure/Involved | Underground | Elbow | Normal | All | Underground facilities = no ignition risk
2894 | Equipment Failure/Involved | Underground | Fuse | Arcing | All | Underground facilities = no ignition risk
2895 | Equipment Failure/Involved | Underground | Fuse | Blown/failed | All | Underground facilities = no ignition risk
2896 | Equipment Failure/Involved | Underground | Fuse | Broken | All | Underground facilities = no ignition risk
2897 | Equipment Failure/Involved | Underground | Fuse | Burned Open | All | Underground facilities = no ignition risk
2898 | Equipment Failure/Involved | Underground | Fuse | Normal | All | Underground facilities = no ignition risk
2899 | Equipment Failure/Involved | Underground | Generator | Broken | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2900 | Equipment Failure/Involved | Underground | Generator | Malfunctioning | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2901 | Equipment Failure/Involved | Underground | Generator | Normal | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2902 | Equipment Failure/Involved | Underground | Interrupter | Arcing | All | Underground facilities = no ignition risk
2903 | Equipment Failure/Involved | Underground | Interrupter | Blown/failed | All | Underground facilities = no ignition risk
2904 | Equipment Failure/Involved | Underground | Interrupter | Broken | All | Underground facilities = no ignition risk
2905 | Equipment Failure/Involved | Underground | Interrupter | Leaking | All | Underground facilities = no ignition risk
2906 | Equipment Failure/Involved | Underground | Interrupter | Malfunctioning | All | Underground facilities = no ignition risk
2907 | Equipment Failure/Involved | Underground | Interrupter | Normal | All | Underground facilities = no ignition risk
2908 | Equipment Failure/Involved | Underground | Metering Equipment |  | None | System Hardening does not address Metering facilities.
2909 | Equipment Failure/Involved | Underground | Metering Equipment | Arcing | None | System Hardening does not address Metering facilities.
2910 | Equipment Failure/Involved | Underground | Metering Equipment | Blown/failed | None | System Hardening does not address Metering facilities.
2911 | Equipment Failure/Involved | Underground | Metering Equipment | Broken | None | System Hardening does not address Metering facilities.
2912 | Equipment Failure/Involved | Underground | Metering Equipment | Malfunctioning | None | System Hardening does not address Metering facilities.
2913 | Equipment Failure/Involved | Underground | Other | Arcing | All | Underground facilities = no ignition risk
2914 | Equipment Failure/Involved | Underground | Other | Bent or Twisted | All | Underground facilities = no ignition risk
2915 | Equipment Failure/Involved | Underground | Other | Blown/failed | All | Underground facilities = no ignition risk
2916 | Equipment Failure/Involved | Underground | Other | Broken | All | Underground facilities = no ignition risk
2917 | Equipment Failure/Involved | Underground | Other | Burned Open | All | Underground facilities = no ignition risk
2918 | Equipment Failure/Involved | Underground | Other | Burned/flashed | All | Underground facilities = no ignition risk
2919 | Equipment Failure/Involved | Underground | Other | Contaminated | All | Underground facilities = no ignition risk
2920 | Equipment Failure/Involved | Underground | Other | Deteriorated | All | Underground facilities = no ignition risk
2921 | Equipment Failure/Involved | Underground | Other | Leaking | All | Underground facilities = no ignition risk
2922 | Equipment Failure/Involved | Underground | Other | Malfunctioning | All | Underground facilities = no ignition risk
2923 | Equipment Failure/Involved | Underground | Other | Normal | All | Underground facilities = no ignition risk
2924 | Equipment Failure/Involved | Underground | Other | Together | All | Underground facilities = no ignition risk
2925 | Equipment Failure/Involved | Underground | Pothead(Riser Termination) | Blown/failed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
2926 | Equipment Failure/Involved | Underground | Pothead(Riser Termination) | Burned/flashed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
2927 | Equipment Failure/Involved | Underground | Pothead/Riser Termination | Blown/failed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
2928 | Equipment Failure/Involved | Underground | Pothead/Riser Termination | Broken | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
2929 | Equipment Failure/Involved | Underground | Pothead/Riser Termination | Burned/flashed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
2930 | Equipment Failure/Involved | Underground | Pothead/Riser Termination | Deteriorated | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
2931 | Equipment Failure/Involved | Underground | PT/CCVT | Blown/failed | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2932 | Equipment Failure/Involved | Underground | PT/CCVT | Burned/flashed | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2933 | Equipment Failure/Involved | Underground | Recloser | Burned/flashed | None | Underground facilities = no ignition risk
2934 | Equipment Failure/Involved | Underground | Recloser | Malfunctioning | All | Underground facilities = no ignition risk
2935 | Equipment Failure/Involved | Underground | Relay | Malfunctioning | All | Underground facilities = no ignition risk
2936 | Equipment Failure/Involved | Underground | Relay | Normal | All | Underground facilities = no ignition risk
2937 | Equipment Failure/Involved | Underground | SCADA | Malfunctioning | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
2938 | Equipment Failure/Involved | Underground | Secondary |  | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2939 | Equipment Failure/Involved | Underground | Secondary | Annealed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
2940 | Equipment Failure/Involved | Underground | Secondary | Arcing | All | Underground facilities = no ignition risk
2941 | Equipment Failure/Involved | Underground | Secondary | Bent or Twisted | All | Underground facilities = no ignition risk
2942 | Equipment Failure/Involved | Underground | Secondary | Broken | All | Underground facilities = no ignition risk
2943 | Equipment Failure/Involved | Underground | Secondary | Burned Open | All | Underground facilities = no ignition risk
2944 | Equipment Failure/Involved | Underground | Secondary | Burned/flashed | All | Underground facilities = no ignition risk
2945 | Equipment Failure/Involved | Underground | Secondary | Contaminated | All | Underground facilities = no ignition risk
2946 | Equipment Failure/Involved | Underground | Secondary | Deteriorated | All | Underground facilities = no ignition risk
2947 | Equipment Failure/Involved | Underground | Secondary | Normal | All | Underground facilities = no ignition risk
2948 | Equipment Failure/Involved | Underground | Secondary | Together | All | Underground facilities = no ignition risk
2949 | Equipment Failure/Involved | Underground | Service conductor | Arcing | All | Underground facilities = no ignition risk
2950 | Equipment Failure/Involved | Underground | Service conductor | Blown/failed | All | Underground facilities = no ignition risk
2951 | Equipment Failure/Involved | Underground | Service conductor | Broken | All | Underground facilities = no ignition risk
2952 | Equipment Failure/Involved | Underground | Service conductor | Burned Open | All | Underground facilities = no ignition risk
2953 | Equipment Failure/Involved | Underground | Service conductor | Burned/flashed | All | Underground facilities = no ignition risk
2954 | Equipment Failure/Involved | Underground | Service conductor | Deteriorated | All | Underground facilities = no ignition risk
2955 | Equipment Failure/Involved | Underground | Service conductor | Normal | All | Underground facilities = no ignition risk
2956 | Equipment Failure/Involved | Underground | Stepdown | Arcing | All | Underground facilities = no ignition risk
2957 | Equipment Failure/Involved | Underground | Stepdown | Blown/failed | All | Underground facilities = no ignition risk
2958 | Equipment Failure/Involved | Underground | Stepdown | Broken | All | Underground facilities = no ignition risk
2959 | Equipment Failure/Involved | Underground | Stepdown | Normal | All | Underground facilities = no ignition risk
2960 | Equipment Failure/Involved | Underground | Switch | Arcing | All | Underground facilities = no ignition risk
2961 | Equipment Failure/Involved | Underground | Switch | Blown/failed | All | Underground facilities = no ignition risk
2962 | Equipment Failure/Involved | Underground | Switch | Broken | All | Underground facilities = no ignition risk
2963 | Equipment Failure/Involved | Underground | Switch | Burned/flashed | All | Underground facilities = no ignition risk
2964 | Equipment Failure/Involved | Underground | Switch | Leaking | All | Underground facilities = no ignition risk
2965 | Equipment Failure/Involved | Underground | Switch | Normal | All | Underground facilities = no ignition risk
2966 | Equipment Failure/Involved | Underground | Switch (UG) | Arcing | All | Underground facilities = no ignition risk
2967 | Equipment Failure/Involved | Underground | Switch (UG) | Blown/failed | All | Underground facilities = no ignition risk
2968 | Equipment Failure/Involved | Underground | Switch (UG) | Broken | All | Underground facilities = no ignition risk
2969 | Equipment Failure/Involved | Underground | Switch (UG) | Burned/flashed | All | Underground facilities = no ignition risk
2970 | Equipment Failure/Involved | Underground | Switch (UG) | Leaking | All | Underground facilities = no ignition risk
2971 | Equipment Failure/Involved | Underground | Switch (UG) | Normal | All | Underground facilities = no ignition risk
2972 | Equipment Failure/Involved | Underground | Transformer | Arcing | All | Underground facilities = no ignition risk
2973 | Equipment Failure/Involved | Underground | Transformer | Blown/failed | All | Underground facilities = no ignition risk
2974 | Equipment Failure/Involved | Underground | Transformer | Broken | All | Underground facilities = no ignition risk
2975 | Equipment Failure/Involved | Underground | Transformer | Burned Open | All | Underground facilities = no ignition risk
2976 | Equipment Failure/Involved | Underground | Transformer | Burned/flashed | All | Underground facilities = no ignition risk
2977 | Equipment Failure/Involved | Underground | Transformer | Deteriorated | All | Underground facilities = no ignition risk
2978 | Equipment Failure/Involved | Underground | Transformer | Leaking | All | Underground facilities = no ignition risk
2979 | Equipment Failure/Involved | Underground | Transformer | Malfunctioning | All | Underground facilities = no ignition risk
2980 | Equipment Failure/Involved | Underground | Transformer | Normal | All | Underground facilities = no ignition risk
2981 | Equipment Failure/Involved | Underground | Transformer (OH) | Blown/failed | All | Underground facilities = no ignition risk
2982 | Equipment Failure/Involved | Underground | Transformer (OH) | Broken | All | Underground facilities = no ignition risk
2983 | Equipment Failure/Involved | Underground | Transformer (OH) | Leaking | All | Underground facilities = no ignition risk
2984 | Equipment Failure/Involved | Underground | Transformer (UG) | Arcing | All | UG Facilities = no ignition risk
2985 | Equipment Failure/Involved | Underground | Transformer (UG) | Blown/failed | All | UG Facilities = no ignition risk
2986 | Equipment Failure/Involved | Underground | Transformer (UG) | Broken | All | UG Facilities = no ignition risk
2987 | Equipment Failure/Involved | Underground | Transformer (UG) | Broken- wire on ground | All | UG Facilities = no ignition risk
2988 | Equipment Failure/Involved | Underground | Transformer (UG) | Burned/flashed | All | UG Facilities = no ignition risk
2989 | Equipment Failure/Involved | Underground | Transformer (UG) | Contaminated | All | UG Facilities = no ignition risk
2990 | Equipment Failure/Involved | Underground | Transformer (UG) | Deteriorated | All | UG Facilities = no ignition risk
2991 | Equipment Failure/Involved | Underground | Transformer (UG) | Leaking | All | UG Facilities = no ignition risk
2992 | Equipment Failure/Involved | Underground | Transformer (UG) | Malfunctioning | All | UG Facilities = no ignition risk
2993 | Equipment Failure/Involved | Underground | Transformer (UG) | Normal | All | UG Facilities = no ignition risk
2994 | Unknown Cause |  |  |  | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2995 | Unknown Cause | Patrol - found nothing |  |  | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2996 | Unknown Cause | Patrol - found nothing |  | Blown/failed | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2997 | Unknown Cause | Patrol - found nothing |  | Broken | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2998 | Unknown Cause | Patrol - found nothing |  | Burned Open | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
2999 | Unknown Cause | Patrol - found nothing |  | Normal | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3000 | Unknown Cause | Patrol - found nothing | Circuit Breaker | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3001 | Unknown Cause | Patrol - found nothing | Conductor- Overhead | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3002 | Unknown Cause | Patrol - found nothing | Conductor- Overhead | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3003 | Unknown Cause | Patrol - found nothing | Conductor- Overhead | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3004 | Unknown Cause | Patrol - found nothing | Conductor- Overhead | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3005 | Unknown Cause | Patrol - found nothing | Conductor- Overhead | Contaminated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3006 | Unknown Cause | Patrol - found nothing | Conductor- Overhead | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3007 | Unknown Cause | Patrol - found nothing | Conductor- Overhead | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3008 | Unknown Cause | Patrol - found nothing | Conductor- Underground | Broken | All | Underground facilities = no ignition risk
3009 | Unknown Cause | Patrol - found nothing | Conductor- Underground | Burned/flashed | All | Underground facilities = no ignition risk
3010 | Unknown Cause | Patrol - found nothing | Conductor- Underground | Deteriorated | All | Underground facilities = no ignition risk
3011 | Unknown Cause | Patrol - found nothing | Connector or Splice (OH) | Broken | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3012 | Unknown Cause | Patrol - found nothing | Crossarm- Wood | Broken | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
3013 | Unknown Cause | Patrol - found nothing | Crossarm- Wood | Burned/flashed | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
3014 | Unknown Cause | Patrol - found nothing | Customer Equipment | Malfunctioning | None | No work is being completed on customer equipment.
3015 | Unknown Cause | Patrol - found nothing | Cutout- fuse holder | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3016 | Unknown Cause | Patrol - found nothing | Cutout- fuse holder | Broken | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3017 | Unknown Cause | Patrol - found nothing | Cutout- fuse holder | Burned/flashed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3018 | Unknown Cause | Patrol - found nothing | Cutout- fuse holder | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3019 | Unknown Cause | Patrol - found nothing | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3020 | Unknown Cause | Patrol - found nothing | Insulator | Broken | All | Age or significant external force broke insulator. System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
3021 | Unknown Cause | Patrol - found nothing | Interrupter |  | All | Underground facilities = no ignition risk
3022 | Unknown Cause | Patrol - found nothing | Jumper | Broken | High | Larger covered conductor to mostly eliminate cause and risk.
3023 | Unknown Cause | Patrol - found nothing | Jumper | Burned Open | High | Larger covered conductor to mostly eliminate cause and risk.
3024 | Unknown Cause | Patrol - found nothing | Lightning Arrestor | Blown/failed | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
3025 | Unknown Cause | Patrol - found nothing | Other | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3026 | Unknown Cause | Patrol - found nothing | Other | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3027 | Unknown Cause | Patrol - found nothing | Other | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3028 | Unknown Cause | Patrol - found nothing | Pole-Wood | Broken | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
3029 | Unknown Cause | Patrol - found nothing | Pole-Wood | Burned/flashed | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
3030 | Unknown Cause | Patrol - found nothing | Pole-Wood | Deteriorated | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
3031 | Unknown Cause | Patrol - found nothing | Pothead/Riser Termination | Blown/failed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
3032 | Unknown Cause | Patrol - found nothing | Recloser | Malfunctioning | Medium | System Hardening does not address Reclosers but coverered conductor will reduce annual recloser operations.
3033 | Unknown Cause | Patrol - found nothing | Recloser | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3034 | Unknown Cause | Patrol - found nothing | Secondary | Together | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3035 | Unknown Cause | Patrol - found nothing | Sectionalizer | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3036 | Unknown Cause | Patrol - found nothing | Service conductor | Burned Open | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3037 | Unknown Cause | Patrol - found nothing | Transformer |  | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3038 | Unknown Cause | Patrol - found nothing | Transformer | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3039 | Unknown Cause | Patrol - found nothing | Transformer | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3040 | Unknown Cause | Patrol - found nothing | Transformer | Burned Open | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3041 | Unknown Cause | Patrol - found nothing | Transformer | Burned/flashed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3042 | Unknown Cause | Patrol - found nothing | Transformer | Deteriorated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3043 | Unknown Cause | Patrol - found nothing | Transformer | Leaking | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3044 | Unknown Cause | Patrol - found nothing | Transformer | Malfunctioning | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3045 | Unknown Cause | Patrol - found nothing | Transformer | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3046 | Unknown Cause | Patrol - not conducted |  |  | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3047 | Unknown Cause | Patrol - not conducted |  | Blown/failed | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3048 | Unknown Cause | Patrol - not conducted |  | Broken | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3049 | Unknown Cause | Patrol - not conducted |  | Burned Open | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3050 | Unknown Cause | Patrol - not conducted |  | Normal | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3051 | Unknown Cause | Patrol - not conducted | Circuit Breaker | Malfunctioning | Medium | System Hardening does not address substation equipment but coverered conductor will reduce annual breaker operations.
3052 | Unknown Cause | Patrol - not conducted | Circuit Breaker | Normal | All | Covered conductor will likely eliminate the temporary fault condition that caused this outage.
3053 | Unknown Cause | Patrol - not conducted | Conductor- Overhead | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3054 | Unknown Cause | Patrol - not conducted | Conductor- Overhead | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3055 | Unknown Cause | Patrol - not conducted | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3056 | Unknown Cause | Patrol - not conducted | Conductor- Overhead | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3057 | Unknown Cause | Patrol - not conducted | Conductor- Overhead | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3058 | Unknown Cause | Patrol - not conducted | Conductor- Overhead | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3059 | Unknown Cause | Patrol - not conducted | Customer Equipment | Blown/failed | None | No work is being completed on customer equipment.
3060 | Unknown Cause | Patrol - not conducted | Cutout- fuse holder | Broken | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3061 | Unknown Cause | Patrol - not conducted | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3062 | Unknown Cause | Patrol - not conducted | Other | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3063 | Unknown Cause | Patrol - not conducted | Pole-Wood | Broken | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
3064 | Unknown Cause | Patrol - not conducted | Pothead/Riser Termination | Blown/failed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
3065 | Unknown Cause | Patrol - not conducted | Recloser | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3066 | Unknown Cause | Patrol - not conducted | Secondary | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3067 | Unknown Cause | Patrol - not conducted | Secondary | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3068 | Unknown Cause | Patrol - not conducted | Transformer | Arcing | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3069 | Unknown Cause | Patrol - not conducted | Transformer | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3070 | Unknown Cause | Patrol - not conducted | Transformer | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3071 | Unknown Cause | Patrol - not conducted | Transformer | Leaking | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3072 | Unknown Cause | Patrol - not conducted | Transformer | Malfunctioning | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3073 | Unknown Cause | Patrol - not conducted | Transformer | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3074 | Vegetation | Other ground vegetation |  | Blown/failed | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3075 | Vegetation | Other ground vegetation | Anchor or Guy | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3076 | Vegetation | Other ground vegetation | Conductor- Overhead | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3077 | Vegetation | Other ground vegetation | Conductor- Overhead | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3078 | Vegetation | Other ground vegetation | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3079 | Vegetation | Other ground vegetation | Conductor- Overhead | Contaminated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3080 | Vegetation | Other ground vegetation | Conductor- Overhead | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3081 | Vegetation | Other ground vegetation | Conductor- Overhead | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3082 | Vegetation | Other ground vegetation | Conductor- Underground | Burned/flashed | All | Underground facilities = no ignition risk
3083 | Vegetation | Other ground vegetation | Conductor- Underground | Normal | All | Underground facilities = no ignition risk
3084 | Vegetation | Other ground vegetation | Crossarm- Wood | Broken | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
3085 | Vegetation | Other ground vegetation | Crossarm- Wood | Contaminated | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
3086 | Vegetation | Other ground vegetation | Customer Equipment | Contaminated | None | No work is being completed on customer equipment.
3087 | Vegetation | Other ground vegetation | Cutout- fuse holder | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3088 | Vegetation | Other ground vegetation | Cutout- fuse holder | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3089 | Vegetation | Other ground vegetation | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3090 | Vegetation | Other ground vegetation | Fuse | Normal | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3091 | Vegetation | Other ground vegetation | Insulator | Arcing | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
3092 | Vegetation | Other ground vegetation | Jumper | Burned Open | High | Larger covered conductor to mostly eliminate cause and risk.
3093 | Vegetation | Other ground vegetation | Lightning Arrestor | Normal | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
3094 | Vegetation | Other ground vegetation | Other | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3095 | Vegetation | Other ground vegetation | Pole-Wood | Broken | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
3096 | Vegetation | Other ground vegetation | Pole-Wood | Burned/flashed | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
3097 | Vegetation | Other ground vegetation | Pole-Wood | Normal | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
3098 | Vegetation | Other ground vegetation | Pothead(Riser Termination) | Burned/flashed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
3099 | Vegetation | Other ground vegetation | Secondary | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3100 | Vegetation | Other ground vegetation | Secondary | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3101 | Vegetation | Other ground vegetation | Service conductor | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3102 | Vegetation | Other ground vegetation | Street Light Equipment | Blown/failed | Medium | System Hardening will not address Street Lights but will address their transformers.
3103 | Vegetation | Other ground vegetation | Transformer | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3104 | Vegetation | Other ground vegetation | Transformer | Burned/flashed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3105 | Vegetation | Other ground vegetation | Transformer | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3106 | Vegetation | Other ground vegetation | Transformer (OH) | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3107 | Vegetation | Other ground vegetation | Transformer (UG) | Blown/failed | All | UG Facilities = no ignition risk
3108 | Vegetation | Other ground vegetation | Transformer (UG) | Broken | All | UG Facilities = no ignition risk
3109 | Vegetation | Other ground vegetation | Transformer (UG) | Burned/flashed | All | UG Facilities = no ignition risk
3110 | Vegetation | Other ground vegetation | Transformer (UG) | Contaminated | All | UG Facilities = no ignition risk
3111 | Vegetation | Other ground vegetation | Transformer (UG) | Normal | All | UG Facilities = no ignition risk
3112 | Vegetation | Tree - bark fell into line |  |  | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3113 | Vegetation | Tree - bark fell into line |  | Arcing | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3114 | Vegetation | Tree - bark fell into line |  | Blown/failed | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3115 | Vegetation | Tree - bark fell into line |  | Burned Open | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3116 | Vegetation | Tree - bark fell into line | Anchor or Guy | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3117 | Vegetation | Tree - bark fell into line | Circuit Breaker | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3118 | Vegetation | Tree - bark fell into line | Conductor- Overhead | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3119 | Vegetation | Tree - bark fell into line | Conductor- Overhead | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3120 | Vegetation | Tree - bark fell into line | Conductor- Overhead | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3121 | Vegetation | Tree - bark fell into line | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3122 | Vegetation | Tree - bark fell into line | Conductor- Overhead | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3123 | Vegetation | Tree - bark fell into line | Conductor- Overhead | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3124 | Vegetation | Tree - bark fell into line | Conductor- Overhead | Contaminated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3125 | Vegetation | Tree - bark fell into line | Conductor- Overhead | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3126 | Vegetation | Tree - bark fell into line | Conductor- Overhead | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3127 | Vegetation | Tree - bark fell into line | Conductor- Overhead | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3128 | Vegetation | Tree - bark fell into line | Conductor- Underground | Normal | All | Underground facilities = no ignition risk
3129 | Vegetation | Tree - bark fell into line | Connector or Splice (OH) | Arcing | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3130 | Vegetation | Tree - bark fell into line | Connector or Splice (OH) | Broken | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3131 | Vegetation | Tree - bark fell into line | Connector or Splice (OH) | Broken- wire on ground | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3132 | Vegetation | Tree - bark fell into line | Connector or Splice (OH) | Burned Open | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3133 | Vegetation | Tree - bark fell into line | Connector or Splice (OH) | Burned/flashed | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3134 | Vegetation | Tree - bark fell into line | Connector or Splice (OH) | Normal | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3135 | Vegetation | Tree - bark fell into line | Crossarm- Wood | Broken | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
3136 | Vegetation | Tree - bark fell into line | Crossarm- Wood | Burned/flashed | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
3137 | Vegetation | Tree - bark fell into line | Cutout- fuse holder | Arcing | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3138 | Vegetation | Tree - bark fell into line | Cutout- fuse holder | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3139 | Vegetation | Tree - bark fell into line | Cutout- fuse holder | Broken | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3140 | Vegetation | Tree - bark fell into line | Cutout- fuse holder | Burned Open | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3141 | Vegetation | Tree - bark fell into line | Cutout- fuse holder | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3142 | Vegetation | Tree - bark fell into line | Cutout- Fused- Distribution | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3143 | Vegetation | Tree - bark fell into line | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3144 | Vegetation | Tree - bark fell into line | Fuse | Broken | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3145 | Vegetation | Tree - bark fell into line | Fuse | Normal | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3146 | Vegetation | Tree - bark fell into line | Insulator | Broken | All | Age or significant external force broke insulator. System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
3147 | Vegetation | Tree - bark fell into line | Insulator | Burned/flashed | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
3148 | Vegetation | Tree - bark fell into line | Jumper | Burned Open | High | Larger covered conductor to mostly eliminate cause and risk.
3149 | Vegetation | Tree - bark fell into line | Lightning Arrestor | Burned/flashed | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
3150 | Vegetation | Tree - bark fell into line | Other | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3151 | Vegetation | Tree - bark fell into line | Pole-Wood | Broken | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
3152 | Vegetation | Tree - bark fell into line | Pole-Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3153 | Vegetation | Tree - bark fell into line | Pole-Wood | Normal | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
3154 | Vegetation | Tree - bark fell into line | Pothead(Riser Termination) | Blown/failed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
3155 | Vegetation | Tree - bark fell into line | Recloser | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3156 | Vegetation | Tree - bark fell into line | Riser | Normal | High | Risers are indirectly addressed on System Hardening - Pole changeouts, the covering of jumpers and leads, along with covering conductor should mitigate outages and risk.
3157 | Vegetation | Tree - bark fell into line | Secondary | Arcing | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3158 | Vegetation | Tree - bark fell into line | Secondary | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3159 | Vegetation | Tree - bark fell into line | Secondary | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3160 | Vegetation | Tree - bark fell into line | Secondary | Broken- wire on object | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3161 | Vegetation | Tree - bark fell into line | Secondary | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3162 | Vegetation | Tree - bark fell into line | Secondary | On Ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3163 | Vegetation | Tree - bark fell into line | Secondary | Together | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3164 | Vegetation | Tree - bark fell into line | Service conductor | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3165 | Vegetation | Tree - bark fell into line | Service conductor | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3166 | Vegetation | Tree - bark fell into line | Switch (OH) | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3167 | Vegetation | Tree - bark fell into line | Transformer | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3168 | Vegetation | Tree - bark fell into line | Transformer | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3169 | Vegetation | Tree - bark fell into line | Transformer | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3170 | Vegetation | Tree - bark fell into line | Transformer | Burned Open | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3171 | Vegetation | Tree - bark fell into line | Transformer | Burned/flashed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3172 | Vegetation | Tree - bark fell into line | Transformer | Malfunctioning | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3173 | Vegetation | Tree - bark fell into line | Transformer | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3174 | Vegetation | Tree - bark fell into line | Transformer | Together | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3175 | Vegetation | Tree - bark fell into line | Transformer (OH) | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3176 | Vegetation | Tree - bark fell into line | Transformer (OH) | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3177 | Vegetation | Tree - bark fell into line | Transformer (OH) | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3178 | Vegetation | Tree - branch fell on line |  |  | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3179 | Vegetation | Tree - branch fell on line |  | Blown/failed | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3180 | Vegetation | Tree - branch fell on line |  | Broken | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3181 | Vegetation | Tree - branch fell on line |  | Burned Open | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3182 | Vegetation | Tree - branch fell on line |  | Normal | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3183 | Vegetation | Tree - branch fell on line | Anchor or Guy | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3184 | Vegetation | Tree - branch fell on line | Anchor or Guy | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3185 | Vegetation | Tree - branch fell on line | Anchor or Guy | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3186 | Vegetation | Tree - branch fell on line | Bushing | Broken | None | Significant external force broke the bushing. Ignition risk not mitigated.
3187 | Vegetation | Tree - branch fell on line | Bushing | Normal | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks.
3188 | Vegetation | Tree - branch fell on line | Capacitor | Arcing | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
3189 | Vegetation | Tree - branch fell on line | Capacitor | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3190 | Vegetation | Tree - branch fell on line | Circuit Breaker | Malfunctioning | Medium | System Hardening does not address substation equipment but coverered conductor will reduce annual breaker operations.
3191 | Vegetation | Tree - branch fell on line | Circuit Breaker | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3192 | Vegetation | Tree - branch fell on line | Conductor- Overhead | Annealed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3193 | Vegetation | Tree - branch fell on line | Conductor- Overhead | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3194 | Vegetation | Tree - branch fell on line | Conductor- Overhead | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3195 | Vegetation | Tree - branch fell on line | Conductor- Overhead | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3196 | Vegetation | Tree - branch fell on line | Conductor- Overhead | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3197 | Vegetation | Tree - branch fell on line | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3198 | Vegetation | Tree - branch fell on line | Conductor- Overhead | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3199 | Vegetation | Tree - branch fell on line | Conductor- Overhead | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3200 | Vegetation | Tree - branch fell on line | Conductor- Overhead | Contaminated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3201 | Vegetation | Tree - branch fell on line | Conductor- Overhead | Deteriorated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3202 | Vegetation | Tree - branch fell on line | Conductor- Overhead | Malfunctioning | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3203 | Vegetation | Tree - branch fell on line | Conductor- Overhead | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3204 | Vegetation | Tree - branch fell on line | Conductor- Overhead | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3205 | Vegetation | Tree - branch fell on line | Conductor- Overhead | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3206 | Vegetation | Tree - branch fell on line | Conductor- Underground |  | All | Underground facilities = no ignition risk
3207 | Vegetation | Tree - branch fell on line | Conductor- Underground | Normal | All | Underground facilities = no ignition risk
3208 | Vegetation | Tree - branch fell on line | Conductor- Underground | Together | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3209 | Vegetation | Tree - branch fell on line | Connector or Splice (OH) | Broken | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3210 | Vegetation | Tree - branch fell on line | Connector or Splice (OH) | Broken- wire on ground | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3211 | Vegetation | Tree - branch fell on line | Connector or Splice (OH) | Broken- wire on object | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3212 | Vegetation | Tree - branch fell on line | Connector or Splice (OH) | Burned Open | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3213 | Vegetation | Tree - branch fell on line | Connector or Splice (OH) | Burned/flashed | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3214 | Vegetation | Tree - branch fell on line | Connector or Splice (OH) | Normal | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3215 | Vegetation | Tree - branch fell on line | Crossarm- Wood | Broken | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
3216 | Vegetation | Tree - branch fell on line | Crossarm- Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3217 | Vegetation | Tree - branch fell on line | Crossarm- Wood | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3218 | Vegetation | Tree - branch fell on line | Crossarm- Wood | Burned/flashed | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
3219 | Vegetation | Tree - branch fell on line | Crossarm- Wood | Deteriorated | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
3220 | Vegetation | Tree - branch fell on line | Crossarm- Wood | Normal | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
3221 | Vegetation | Tree - branch fell on line | Customer Equipment | Broken | None | No work is being completed on customer equipment.
3222 | Vegetation | Tree - branch fell on line | Customer Equipment | Broken- wire on ground | None | No work is being completed on customer equipment.
3223 | Vegetation | Tree - branch fell on line | Customer Equipment | Normal | None | No work is being completed on customer equipment.
3224 | Vegetation | Tree - branch fell on line | Cutout- fuse holder | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3225 | Vegetation | Tree - branch fell on line | Cutout- fuse holder | Broken | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3226 | Vegetation | Tree - branch fell on line | Cutout- fuse holder | Burned/flashed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3227 | Vegetation | Tree - branch fell on line | Cutout- fuse holder | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3228 | Vegetation | Tree - branch fell on line | Cutout- Fused- Distribution | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3229 | Vegetation | Tree - branch fell on line | Cutout- Fused- Distribution | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3230 | Vegetation | Tree - branch fell on line | Cutout- Fused- Distribution | Burned Open | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3231 | Vegetation | Tree - branch fell on line | Cutout- Fused- Distribution | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3232 | Vegetation | Tree - branch fell on line | Elbow |  | All | Underground facilities = no ignition risk
3233 | Vegetation | Tree - branch fell on line | Fuse | Arcing | All | Covered conductor will eliminate the line to ground connection that likely caused this outage/risk.
3234 | Vegetation | Tree - branch fell on line | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3235 | Vegetation | Tree - branch fell on line | Fuse | Broken | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3236 | Vegetation | Tree - branch fell on line | Fuse | Burned Open | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3237 | Vegetation | Tree - branch fell on line | Fuse | Normal | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3238 | Vegetation | Tree - branch fell on line | Fuse | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3239 | Vegetation | Tree - branch fell on line | Insulator | Blown/failed | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
3240 | Vegetation | Tree - branch fell on line | Insulator | Broken | All | Age or significant external force broke insulator. System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
3241 | Vegetation | Tree - branch fell on line | Insulator | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3242 | Vegetation | Tree - branch fell on line | Insulator | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3243 | Vegetation | Tree - branch fell on line | Insulator | Burned/flashed | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
3244 | Vegetation | Tree - branch fell on line | Jumper |  | High | Larger covered conductor to mostly eliminate cause and risk.
3245 | Vegetation | Tree - branch fell on line | Jumper | Bent or Twisted | High | Larger covered conductor to mostly eliminate cause and risk.
3246 | Vegetation | Tree - branch fell on line | Jumper | Broken | High | Larger covered conductor to mostly eliminate cause and risk.
3247 | Vegetation | Tree - branch fell on line | Jumper | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3248 | Vegetation | Tree - branch fell on line | Jumper | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3249 | Vegetation | Tree - branch fell on line | Jumper | Burned Open | High | Larger covered conductor to mostly eliminate cause and risk.
3250 | Vegetation | Tree - branch fell on line | Jumper | Normal | High | Larger covered conductor to mostly eliminate cause and risk.
3251 | Vegetation | Tree - branch fell on line | Lightning Arrestor | Broken | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
3252 | Vegetation | Tree - branch fell on line | Lightning Arrestor | Burned/flashed | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
3253 | Vegetation | Tree - branch fell on line | Lightning Arrestor | Normal | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
3254 | Vegetation | Tree - branch fell on line | Other | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3255 | Vegetation | Tree - branch fell on line | Other | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3256 | Vegetation | Tree - branch fell on line | Other | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3257 | Vegetation | Tree - branch fell on line | Other | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3258 | Vegetation | Tree - branch fell on line | Other | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3259 | Vegetation | Tree - branch fell on line | Other | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3260 | Vegetation | Tree - branch fell on line | Other | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3261 | Vegetation | Tree - branch fell on line | Pole-Wood | Broken | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
3262 | Vegetation | Tree - branch fell on line | Pole-Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3263 | Vegetation | Tree - branch fell on line | Pole-Wood | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3264 | Vegetation | Tree - branch fell on line | Pole-Wood | Normal | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
3265 | Vegetation | Tree - branch fell on line | Pothead(Riser Termination) | Blown/failed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
3266 | Vegetation | Tree - branch fell on line | Pothead(Riser Termination) | Broken | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
3267 | Vegetation | Tree - branch fell on line | Pothead(Riser Termination) | Burned/flashed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
3268 | Vegetation | Tree - branch fell on line | Pothead(Riser Termination) | Deteriorated | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
3269 | Vegetation | Tree - branch fell on line | Pothead(Riser Termination) | Normal | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
3270 | Vegetation | Tree - branch fell on line | Pothead/Riser Termination | Normal | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
3271 | Vegetation | Tree - branch fell on line | Recloser | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3272 | Vegetation | Tree - branch fell on line | Recloser | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3273 | Vegetation | Tree - branch fell on line | Secondary | Arcing | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3274 | Vegetation | Tree - branch fell on line | Secondary | Bent or Twisted | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3275 | Vegetation | Tree - branch fell on line | Secondary | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3276 | Vegetation | Tree - branch fell on line | Secondary | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3277 | Vegetation | Tree - branch fell on line | Secondary | Broken- wire on object | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3278 | Vegetation | Tree - branch fell on line | Secondary | Burned Open | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3279 | Vegetation | Tree - branch fell on line | Secondary | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3280 | Vegetation | Tree - branch fell on line | Secondary | Contaminated | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3281 | Vegetation | Tree - branch fell on line | Secondary | Deteriorated | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3282 | Vegetation | Tree - branch fell on line | Secondary | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3283 | Vegetation | Tree - branch fell on line | Secondary | On Ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3284 | Vegetation | Tree - branch fell on line | Secondary | Together | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3285 | Vegetation | Tree - branch fell on line | Service conductor | Arcing | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3286 | Vegetation | Tree - branch fell on line | Service conductor | Bent or Twisted | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3287 | Vegetation | Tree - branch fell on line | Service conductor | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3288 | Vegetation | Tree - branch fell on line | Service conductor | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3289 | Vegetation | Tree - branch fell on line | Service conductor | Broken- wire on object | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3290 | Vegetation | Tree - branch fell on line | Service conductor | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3291 | Vegetation | Tree - branch fell on line | Service conductor | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3292 | Vegetation | Tree - branch fell on line | Service conductor | On Ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3293 | Vegetation | Tree - branch fell on line | Service conductor | Together | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3294 | Vegetation | Tree - branch fell on line | Switch | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3295 | Vegetation | Tree - branch fell on line | Switch (OH) | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3296 | Vegetation | Tree - branch fell on line | Switch (OH) | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3297 | Vegetation | Tree - branch fell on line | Switch (OH) | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3298 | Vegetation | Tree - branch fell on line | Switch (OH) | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3299 | Vegetation | Tree - branch fell on line | Switch (UG) | Normal | All | Underground facilities = no ignition risk
3300 | Vegetation | Tree - branch fell on line | Transformer |  | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3301 | Vegetation | Tree - branch fell on line | Transformer | Annealed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3302 | Vegetation | Tree - branch fell on line | Transformer | Arcing | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3303 | Vegetation | Tree - branch fell on line | Transformer | Bent or Twisted | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3304 | Vegetation | Tree - branch fell on line | Transformer | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3305 | Vegetation | Tree - branch fell on line | Transformer | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3306 | Vegetation | Tree - branch fell on line | Transformer | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3307 | Vegetation | Tree - branch fell on line | Transformer | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3308 | Vegetation | Tree - branch fell on line | Transformer | Burned Open | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3309 | Vegetation | Tree - branch fell on line | Transformer | Burned/flashed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3310 | Vegetation | Tree - branch fell on line | Transformer | Deteriorated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3311 | Vegetation | Tree - branch fell on line | Transformer | Leaking | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3312 | Vegetation | Tree - branch fell on line | Transformer | Malfunctioning | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3313 | Vegetation | Tree - branch fell on line | Transformer | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3314 | Vegetation | Tree - branch fell on line | Transformer | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3315 | Vegetation | Tree - branch fell on line | Transformer | Together | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3316 | Vegetation | Tree - branch fell on line | Transformer (OH) | Arcing | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3317 | Vegetation | Tree - branch fell on line | Transformer (OH) | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3318 | Vegetation | Tree - branch fell on line | Transformer (OH) | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3319 | Vegetation | Tree - branch fell on line | Transformer (OH) | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3320 | Vegetation | Tree - branch fell on line | Transformer (OH) | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3321 | Vegetation | Tree - branch fell on line | Transformer (OH) | Burned/flashed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3322 | Vegetation | Tree - branch fell on line | Transformer (OH) | Contaminated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3323 | Vegetation | Tree - branch fell on line | Transformer (OH) | Leaking | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3324 | Vegetation | Tree - branch fell on line | Transformer (OH) | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3325 | Vegetation | Tree - branch fell on line | Transformer (UG) | Broken | All | UG Facilities = no ignition risk
3326 | Vegetation | Tree - branch fell on line | Transformer (UG) | Leaking | All | UG Facilities = no ignition risk
3327 | Vegetation | Tree - branch fell on line | Woodpin | Broken | All | Composite arms are being installed along with new insulators and bonding. Tracking insulators/pole fires will be limited though not 100% eliminate. Gunshot damage will still be a concern. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
3328 | Vegetation | Tree - branch fell on line | Woodpin | Broken- wire on ground | None | Significant external force broke the conductor and brought wire to the ground/object. Ignition risk not mitigated.
3329 | Vegetation | Tree - cutting- 3rd party | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3330 | Vegetation | Tree - cutting- 3rd party | Secondary | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3331 | Vegetation | Tree - cutting- 3rd party | Secondary | Together | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3332 | Vegetation | Tree - cutting- PG&E contractor | Anchor or Guy | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3333 | Vegetation | Tree - cutting- PG&E contractor | Conductor- Overhead | Annealed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3334 | Vegetation | Tree - cutting- PG&E contractor | Conductor- Overhead | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3335 | Vegetation | Tree - cutting- PG&E contractor | Conductor- Overhead | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3336 | Vegetation | Tree - cutting- PG&E contractor | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3337 | Vegetation | Tree - cutting- PG&E contractor | Conductor- Overhead | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3338 | Vegetation | Tree - cutting- PG&E contractor | Conductor- Overhead | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3339 | Vegetation | Tree - cutting- PG&E contractor | Conductor- Overhead | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3340 | Vegetation | Tree - cutting- PG&E contractor | Connector or Splice (OH) | Normal | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3341 | Vegetation | Tree - cutting- PG&E contractor | Crossarm- Wood | Broken | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
3342 | Vegetation | Tree - cutting- PG&E contractor | Crossarm- Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3343 | Vegetation | Tree - cutting- PG&E contractor | Cutout- Fused- Distribution | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3344 | Vegetation | Tree - cutting- PG&E contractor | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3345 | Vegetation | Tree - cutting- PG&E contractor | Fuse | Normal | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3346 | Vegetation | Tree - cutting- PG&E contractor | Insulator | Broken | All | Age or significant external force broke insulator. System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
3347 | Vegetation | Tree - cutting- PG&E contractor | Other | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3348 | Vegetation | Tree - cutting- PG&E contractor | Pole-Wood | Broken | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
3349 | Vegetation | Tree - cutting- PG&E contractor | Pole-Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3350 | Vegetation | Tree - cutting- PG&E contractor | Secondary | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3351 | Vegetation | Tree - cutting- PG&E contractor | Secondary | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3352 | Vegetation | Tree - cutting- PG&E contractor | Secondary | Broken- wire on object | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3353 | Vegetation | Tree - cutting- PG&E contractor | Secondary | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3354 | Vegetation | Tree - cutting- PG&E contractor | Secondary | On Ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3355 | Vegetation | Tree - cutting- PG&E contractor | Service conductor | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3356 | Vegetation | Tree - cutting- PG&E contractor | Transformer | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3357 | Vegetation | Tree - cutting- PG&E contractor | Transformer | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3358 | Vegetation | Tree - cutting- PG&E contractor | Transformer | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3359 | Vegetation | Tree - cutting- PG&E contractor | Transformer (OH) | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3360 | Vegetation | Tree - cutting- PG&E contractor | Woodpin | Broken | All | Composite arms are being installed along with new insulators and bonding. Tracking insulators/pole fires will be limited though not 100% eliminate. Gunshot damage will still be a concern. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
3361 | Vegetation | Tree - fell into line |  |  | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3362 | Vegetation | Tree - fell into line |  | Blown/failed | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3363 | Vegetation | Tree - fell into line |  | Broken | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3364 | Vegetation | Tree - fell into line |  | Burned Open | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3365 | Vegetation | Tree - fell into line |  | Normal | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3366 | Vegetation | Tree - fell into line | Anchor or Guy | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3367 | Vegetation | Tree - fell into line | Anchor or Guy | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3368 | Vegetation | Tree - fell into line | Anchor or Guy | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3369 | Vegetation | Tree - fell into line | Anchor or Guy | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3370 | Vegetation | Tree - fell into line | Bushing | Broken | None | Significant external force broke the bushing. Ignition risk not mitigated.
3371 | Vegetation | Tree - fell into line | Bushing | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3372 | Vegetation | Tree - fell into line | Capacitor | Broken | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
3373 | Vegetation | Tree - fell into line | Capacitor | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3374 | Vegetation | Tree - fell into line | Capacitor | Burned/flashed | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
3375 | Vegetation | Tree - fell into line | Circuit Breaker | Malfunctioning | Medium | System Hardening does not address substation equipment but coverered conductor will reduce annual breaker operations.
3376 | Vegetation | Tree - fell into line | Circuit Breaker | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3377 | Vegetation | Tree - fell into line | Conductor- Overhead |  | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3378 | Vegetation | Tree - fell into line | Conductor- Overhead | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3379 | Vegetation | Tree - fell into line | Conductor- Overhead | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3380 | Vegetation | Tree - fell into line | Conductor- Overhead | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3381 | Vegetation | Tree - fell into line | Conductor- Overhead | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3382 | Vegetation | Tree - fell into line | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3383 | Vegetation | Tree - fell into line | Conductor- Overhead | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3384 | Vegetation | Tree - fell into line | Conductor- Overhead | Burned Open | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3385 | Vegetation | Tree - fell into line | Conductor- Overhead | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3386 | Vegetation | Tree - fell into line | Conductor- Overhead | Contaminated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3387 | Vegetation | Tree - fell into line | Conductor- Overhead | Deteriorated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3388 | Vegetation | Tree - fell into line | Conductor- Overhead | Malfunctioning | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3389 | Vegetation | Tree - fell into line | Conductor- Overhead | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3390 | Vegetation | Tree - fell into line | Conductor- Overhead | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3391 | Vegetation | Tree - fell into line | Conductor- Overhead | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3392 | Vegetation | Tree - fell into line | Conductor- Underground | Broken | All | Underground facilities = no ignition risk
3393 | Vegetation | Tree - fell into line | Conductor- Underground | Broken- wire on ground | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3394 | Vegetation | Tree - fell into line | Conductor- Underground | Normal | All | Underground facilities = no ignition risk
3395 | Vegetation | Tree - fell into line | Connector or Splice (OH) | Broken | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3396 | Vegetation | Tree - fell into line | Connector or Splice (OH) | Broken- wire on ground | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3397 | Vegetation | Tree - fell into line | Connector or Splice (OH) | Broken- wire on object | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3398 | Vegetation | Tree - fell into line | Connector or Splice (OH) | Burned/flashed | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3399 | Vegetation | Tree - fell into line | Connector or Splice (OH) | Normal | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3400 | Vegetation | Tree - fell into line | Crossarm- Steel | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3401 | Vegetation | Tree - fell into line | Crossarm- Steel | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3402 | Vegetation | Tree - fell into line | Crossarm- Wood | Broken | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
3403 | Vegetation | Tree - fell into line | Crossarm- Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3404 | Vegetation | Tree - fell into line | Crossarm- Wood | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3405 | Vegetation | Tree - fell into line | Crossarm- Wood | Burned/flashed | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
3406 | Vegetation | Tree - fell into line | Crossarm- Wood | Deteriorated | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
3407 | Vegetation | Tree - fell into line | Customer Equipment | Broken | None | No work is being completed on customer equipment.
3408 | Vegetation | Tree - fell into line | Customer Equipment | Burned/flashed | None | No work is being completed on customer equipment.
3409 | Vegetation | Tree - fell into line | Customer Equipment | Malfunctioning | None | No work is being completed on customer equipment.
3410 | Vegetation | Tree - fell into line | Customer Equipment | On Ground | None | No work is being completed on customer equipment.
3411 | Vegetation | Tree - fell into line | Cutout- fuse holder | Arcing | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3412 | Vegetation | Tree - fell into line | Cutout- fuse holder | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3413 | Vegetation | Tree - fell into line | Cutout- fuse holder | Broken | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3414 | Vegetation | Tree - fell into line | Cutout- fuse holder | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3415 | Vegetation | Tree - fell into line | Cutout- fuse holder | Burned Open | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3416 | Vegetation | Tree - fell into line | Cutout- fuse holder | Burned/flashed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3417 | Vegetation | Tree - fell into line | Cutout- fuse holder | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3418 | Vegetation | Tree - fell into line | Cutout- Fused- Distribution | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3419 | Vegetation | Tree - fell into line | Cutout- Fused- Distribution | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3420 | Vegetation | Tree - fell into line | Footings- Tower or Pole | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3421 | Vegetation | Tree - fell into line | Fuse | Arcing | All | Covered conductor will eliminate the line to ground connection that likely caused this outage/risk.
3422 | Vegetation | Tree - fell into line | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3423 | Vegetation | Tree - fell into line | Fuse | Broken | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3424 | Vegetation | Tree - fell into line | Fuse | Burned Open | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3425 | Vegetation | Tree - fell into line | Fuse | Normal | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3426 | Vegetation | Tree - fell into line | Insulator | Broken | All | Age or significant external force broke insulator. System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
3427 | Vegetation | Tree - fell into line | Insulator | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3428 | Vegetation | Tree - fell into line | Insulator | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3429 | Vegetation | Tree - fell into line | Insulator | Normal | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
3430 | Vegetation | Tree - fell into line | Jumper | Broken | High | Larger covered conductor to mostly eliminate cause and risk.
3431 | Vegetation | Tree - fell into line | Jumper | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3432 | Vegetation | Tree - fell into line | Jumper | Burned Open | High | Larger covered conductor to mostly eliminate cause and risk.
3433 | Vegetation | Tree - fell into line | Jumper | Burned/flashed | High | Larger covered conductor to mostly eliminate cause and risk.
3434 | Vegetation | Tree - fell into line | Jumper | Normal | High | Larger covered conductor to mostly eliminate cause and risk.
3435 | Vegetation | Tree - fell into line | Lightning Arrestor | Blown/failed | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
3436 | Vegetation | Tree - fell into line | Metering Equipment | Broken | None | System Hardening does not address Metering facilities.
3437 | Vegetation | Tree - fell into line | Other | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3438 | Vegetation | Tree - fell into line | Other | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3439 | Vegetation | Tree - fell into line | Other | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3440 | Vegetation | Tree - fell into line | Other | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3441 | Vegetation | Tree - fell into line | Other | Leaking | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3442 | Vegetation | Tree - fell into line | Other | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3443 | Vegetation | Tree - fell into line | Other | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3444 | Vegetation | Tree - fell into line | PGs- Kearneys | Broken | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3445 | Vegetation | Tree - fell into line | Pole - Tower- steel | Broken- wire on ground | None | Significant external force broke the conductor and brought wire to the ground/object. Ignition risk not mitigated.
3446 | Vegetation | Tree - fell into line | Pole - Tower- steel | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3447 | Vegetation | Tree - fell into line | Pole - Tower- steel | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3448 | Vegetation | Tree - fell into line | Pole-Wood | Broken | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
3449 | Vegetation | Tree - fell into line | Pole-Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3450 | Vegetation | Tree - fell into line | Pole-Wood | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3451 | Vegetation | Tree - fell into line | Pole-Wood | Burned/flashed | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
3452 | Vegetation | Tree - fell into line | Pole-Wood | Deteriorated | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
3453 | Vegetation | Tree - fell into line | Pole-Wood | Normal | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
3454 | Vegetation | Tree - fell into line | Pole-Wood | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3455 | Vegetation | Tree - fell into line | Pole-Wood | Together | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
3456 | Vegetation | Tree - fell into line | Pothead(Riser Termination) | Arcing | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
3457 | Vegetation | Tree - fell into line | Pothead(Riser Termination) | Broken | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
3458 | Vegetation | Tree - fell into line | Recloser | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3459 | Vegetation | Tree - fell into line | Recloser | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3460 | Vegetation | Tree - fell into line | Recloser | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3461 | Vegetation | Tree - fell into line | Secondary | Arcing | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3462 | Vegetation | Tree - fell into line | Secondary | Bent or Twisted | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3463 | Vegetation | Tree - fell into line | Secondary | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3464 | Vegetation | Tree - fell into line | Secondary | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3465 | Vegetation | Tree - fell into line | Secondary | Broken- wire on object | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3466 | Vegetation | Tree - fell into line | Secondary | Burned Open | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3467 | Vegetation | Tree - fell into line | Secondary | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3468 | Vegetation | Tree - fell into line | Secondary | Contaminated | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3469 | Vegetation | Tree - fell into line | Secondary | Deteriorated | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3470 | Vegetation | Tree - fell into line | Secondary | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3471 | Vegetation | Tree - fell into line | Secondary | On Ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3472 | Vegetation | Tree - fell into line | Secondary | Together | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3473 | Vegetation | Tree - fell into line | Sectionalizer | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3474 | Vegetation | Tree - fell into line | Service conductor | Bent or Twisted | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3475 | Vegetation | Tree - fell into line | Service conductor | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3476 | Vegetation | Tree - fell into line | Service conductor | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3477 | Vegetation | Tree - fell into line | Service conductor | Broken- wire on object | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3478 | Vegetation | Tree - fell into line | Service conductor | Burned Open | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3479 | Vegetation | Tree - fell into line | Service conductor | Contaminated | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3480 | Vegetation | Tree - fell into line | Service conductor | Deteriorated | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3481 | Vegetation | Tree - fell into line | Service conductor | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3482 | Vegetation | Tree - fell into line | Service conductor | On Ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3483 | Vegetation | Tree - fell into line | Service conductor | Together | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3484 | Vegetation | Tree - fell into line | Switch | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3485 | Vegetation | Tree - fell into line | Switch | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3486 | Vegetation | Tree - fell into line | Switch (OH) | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3487 | Vegetation | Tree - fell into line | Switch (OH) | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3488 | Vegetation | Tree - fell into line | Transformer |  | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3489 | Vegetation | Tree - fell into line | Transformer | Arcing | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3490 | Vegetation | Tree - fell into line | Transformer | Bent or Twisted | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3491 | Vegetation | Tree - fell into line | Transformer | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3492 | Vegetation | Tree - fell into line | Transformer | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3493 | Vegetation | Tree - fell into line | Transformer | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3494 | Vegetation | Tree - fell into line | Transformer | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3495 | Vegetation | Tree - fell into line | Transformer | Burned Open | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3496 | Vegetation | Tree - fell into line | Transformer | Burned/flashed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3497 | Vegetation | Tree - fell into line | Transformer | Contaminated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3498 | Vegetation | Tree - fell into line | Transformer | Deteriorated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3499 | Vegetation | Tree - fell into line | Transformer | Leaking | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3500 | Vegetation | Tree - fell into line | Transformer | Malfunctioning | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3501 | Vegetation | Tree - fell into line | Transformer | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3502 | Vegetation | Tree - fell into line | Transformer | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3503 | Vegetation | Tree - fell into line | Transformer | Together | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3504 | Vegetation | Tree - fell into line | Transformer (OH) | Arcing | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3505 | Vegetation | Tree - fell into line | Transformer (OH) | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3506 | Vegetation | Tree - fell into line | Transformer (OH) | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3507 | Vegetation | Tree - fell into line | Transformer (OH) | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3508 | Vegetation | Tree - fell into line | Transformer (OH) | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3509 | Vegetation | Tree - fell into line | Transformer (OH) | Burned/flashed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3510 | Vegetation | Tree - fell into line | Transformer (OH) | Contaminated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3511 | Vegetation | Tree - fell into line | Transformer (OH) | Leaking | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3512 | Vegetation | Tree - fell into line | Transformer (OH) | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3513 | Vegetation | Tree - fell into line | Transformer (OH) | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3514 | Vegetation | Tree - fell into line | Transformer (UG) | Broken | All | UG Facilities = no ignition risk
3515 | Vegetation | Tree - fell into line | Transformer (UG) | Leaking | All | UG Facilities = no ignition risk
3516 | Vegetation | Tree - fell into line | Transformer (UG) | Normal | All | UG Facilities = no ignition risk
3517 | Vegetation | Tree - fell into line | Woodpin | Broken | All | Composite arms are being installed along with new insulators and bonding. Tracking insulators/pole fires will be limited though not 100% eliminate. Gunshot damage will still be a concern. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
3518 | Vegetation | Tree - fell into line | Woodpin | Broken- wire on ground | None | Significant external force broke the conductor and brought wire to the ground/object. Ignition risk not mitigated.
3519 | Vegetation | Tree - fell into line | Woodpin | Broken- wire on object | None | Significant external force broke the conductor and brought wire to the ground/object. Ignition risk not mitigated.
3520 | Vegetation | Tree - fell into line | Woodpin | Normal | All | Composite arms are being installed along with new insulators and bonding. Tracking insulators/pole fires will be limited though not 100% eliminate. Gunshot damage will still be a concern. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
3521 | Vegetation | Tree - grew into line |  |  | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3522 | Vegetation | Tree - grew into line |  | Blown/failed | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3523 | Vegetation | Tree - grew into line |  | Normal | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3524 | Vegetation | Tree - grew into line | Anchor or Guy | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3525 | Vegetation | Tree - grew into line | Circuit Breaker | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3526 | Vegetation | Tree - grew into line | Conductor- Overhead | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3527 | Vegetation | Tree - grew into line | Conductor- Overhead | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3528 | Vegetation | Tree - grew into line | Conductor- Overhead | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3529 | Vegetation | Tree - grew into line | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3530 | Vegetation | Tree - grew into line | Conductor- Overhead | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3531 | Vegetation | Tree - grew into line | Conductor- Overhead | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3532 | Vegetation | Tree - grew into line | Conductor- Overhead | Contaminated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3533 | Vegetation | Tree - grew into line | Conductor- Overhead | Deteriorated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3534 | Vegetation | Tree - grew into line | Conductor- Overhead | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3535 | Vegetation | Tree - grew into line | Conductor- Overhead | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3536 | Vegetation | Tree - grew into line | Conductor- Overhead | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3537 | Vegetation | Tree - grew into line | Connector or Splice (OH) | Broken- wire on ground | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3538 | Vegetation | Tree - grew into line | Connector or Splice (OH) | Burned Open | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3539 | Vegetation | Tree - grew into line | Connector or Splice (OH) | Normal | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3540 | Vegetation | Tree - grew into line | Crossarm- Wood | Broken | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
3541 | Vegetation | Tree - grew into line | Crossarm- Wood | Burned/flashed | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
3542 | Vegetation | Tree - grew into line | Crossarm- Wood | Deteriorated | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
3543 | Vegetation | Tree - grew into line | Customer Equipment | Malfunctioning | None | No work is being completed on customer equipment.
3544 | Vegetation | Tree - grew into line | Cutout- fuse holder | Arcing | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3545 | Vegetation | Tree - grew into line | Cutout- fuse holder | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3546 | Vegetation | Tree - grew into line | Cutout- fuse holder | Burned/flashed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3547 | Vegetation | Tree - grew into line | Cutout- fuse holder | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3548 | Vegetation | Tree - grew into line | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3549 | Vegetation | Tree - grew into line | Fuse | Normal | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3550 | Vegetation | Tree - grew into line | Jumper | Normal | High | Larger covered conductor to mostly eliminate cause and risk.
3551 | Vegetation | Tree - grew into line | Lightning Arrestor | Blown/failed | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
3552 | Vegetation | Tree - grew into line | Pole-Wood | Broken | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
3553 | Vegetation | Tree - grew into line | Pole-Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3554 | Vegetation | Tree - grew into line | Pole-Wood | Normal | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
3555 | Vegetation | Tree - grew into line | Pothead(Riser Termination) | Blown/failed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
3556 | Vegetation | Tree - grew into line | Pothead(Riser Termination) | Normal | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
3557 | Vegetation | Tree - grew into line | Pothead/Riser Termination | Burned/flashed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
3558 | Vegetation | Tree - grew into line | Secondary | Annealed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3559 | Vegetation | Tree - grew into line | Secondary | Arcing | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3560 | Vegetation | Tree - grew into line | Secondary | Bent or Twisted | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3561 | Vegetation | Tree - grew into line | Secondary | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3562 | Vegetation | Tree - grew into line | Secondary | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3563 | Vegetation | Tree - grew into line | Secondary | Broken- wire on object | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3564 | Vegetation | Tree - grew into line | Secondary | Burned Open | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3565 | Vegetation | Tree - grew into line | Secondary | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3566 | Vegetation | Tree - grew into line | Secondary | Contaminated | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3567 | Vegetation | Tree - grew into line | Secondary | Deteriorated | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3568 | Vegetation | Tree - grew into line | Secondary | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3569 | Vegetation | Tree - grew into line | Secondary | On Ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3570 | Vegetation | Tree - grew into line | Secondary | Together | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3571 | Vegetation | Tree - grew into line | Service conductor | Arcing | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3572 | Vegetation | Tree - grew into line | Service conductor | Bent or Twisted | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3573 | Vegetation | Tree - grew into line | Service conductor | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3574 | Vegetation | Tree - grew into line | Service conductor | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3575 | Vegetation | Tree - grew into line | Service conductor | Burned Open | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3576 | Vegetation | Tree - grew into line | Service conductor | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3577 | Vegetation | Tree - grew into line | Service conductor | Deteriorated | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3578 | Vegetation | Tree - grew into line | Service conductor | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3579 | Vegetation | Tree - grew into line | Switch (OH) | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3580 | Vegetation | Tree - grew into line | Transformer |  | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3581 | Vegetation | Tree - grew into line | Transformer | Annealed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3582 | Vegetation | Tree - grew into line | Transformer | Arcing | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3583 | Vegetation | Tree - grew into line | Transformer | Bent or Twisted | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3584 | Vegetation | Tree - grew into line | Transformer | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3585 | Vegetation | Tree - grew into line | Transformer | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3586 | Vegetation | Tree - grew into line | Transformer | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3587 | Vegetation | Tree - grew into line | Transformer | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3588 | Vegetation | Tree - grew into line | Transformer | Burned/flashed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3589 | Vegetation | Tree - grew into line | Transformer | Contaminated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3590 | Vegetation | Tree - grew into line | Transformer | Deteriorated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3591 | Vegetation | Tree - grew into line | Transformer | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3592 | Vegetation | Tree - grew into line | Transformer | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3593 | Vegetation | Tree - grew into line | Transformer | Together | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3594 | Vegetation | Tree - grew into line | Transformer (OH) | Arcing | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3595 | Vegetation | Tree - grew into line | Transformer (OH) | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3596 | Vegetation | Tree - grew into line | Transformer (OH) | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3597 | Vegetation | Tree - grew into line | Transformer (OH) | Burned/flashed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3598 | Vegetation | Tree - grew into line | Transformer (OH) | Contaminated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3599 | Vegetation | Tree - grew into line | Transformer (OH) | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3600 | Vegetation | Tree - palm frond fell into line |  | Blown/failed | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3601 | Vegetation | Tree - palm frond fell into line | Bushing | Blown/failed | All | Age or significant external force broke insulator. System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
3602 | Vegetation | Tree - palm frond fell into line | Capacitor | Blown/failed | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
3603 | Vegetation | Tree - palm frond fell into line | Capacitor | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3604 | Vegetation | Tree - palm frond fell into line | Circuit Breaker | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3605 | Vegetation | Tree - palm frond fell into line | Conductor- Overhead | Annealed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3606 | Vegetation | Tree - palm frond fell into line | Conductor- Overhead | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3607 | Vegetation | Tree - palm frond fell into line | Conductor- Overhead | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3608 | Vegetation | Tree - palm frond fell into line | Conductor- Overhead | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3609 | Vegetation | Tree - palm frond fell into line | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3610 | Vegetation | Tree - palm frond fell into line | Conductor- Overhead | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3611 | Vegetation | Tree - palm frond fell into line | Conductor- Overhead | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3612 | Vegetation | Tree - palm frond fell into line | Conductor- Overhead | Contaminated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3613 | Vegetation | Tree - palm frond fell into line | Conductor- Overhead | Deteriorated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3614 | Vegetation | Tree - palm frond fell into line | Conductor- Overhead | Malfunctioning | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3615 | Vegetation | Tree - palm frond fell into line | Conductor- Overhead | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3616 | Vegetation | Tree - palm frond fell into line | Conductor- Overhead | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3617 | Vegetation | Tree - palm frond fell into line | Conductor- Overhead | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3618 | Vegetation | Tree - palm frond fell into line | Conductor- Underground | Normal | All | Underground facilities = no ignition risk
3619 | Vegetation | Tree - palm frond fell into line | Connector or Splice (OH) | Arcing | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3620 | Vegetation | Tree - palm frond fell into line | Connector or Splice (OH) | Broken- wire on ground | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3621 | Vegetation | Tree - palm frond fell into line | Connector or Splice (OH) | Normal | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3622 | Vegetation | Tree - palm frond fell into line | Crossarm- Wood | Burned/flashed | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
3623 | Vegetation | Tree - palm frond fell into line | Cutout- fuse holder | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3624 | Vegetation | Tree - palm frond fell into line | Cutout- fuse holder | Broken | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3625 | Vegetation | Tree - palm frond fell into line | Cutout- fuse holder | Burned/flashed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3626 | Vegetation | Tree - palm frond fell into line | Cutout- fuse holder | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3627 | Vegetation | Tree - palm frond fell into line | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3628 | Vegetation | Tree - palm frond fell into line | Fuse | Broken | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3629 | Vegetation | Tree - palm frond fell into line | Fuse | Normal | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3630 | Vegetation | Tree - palm frond fell into line | Insulator | Broken | All | Age or significant external force broke insulator. System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
3631 | Vegetation | Tree - palm frond fell into line | Insulator | Burned/flashed | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
3632 | Vegetation | Tree - palm frond fell into line | Insulator | Normal | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
3633 | Vegetation | Tree - palm frond fell into line | Jumper | Broken | High | Larger covered conductor to mostly eliminate cause and risk.
3634 | Vegetation | Tree - palm frond fell into line | Jumper | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3635 | Vegetation | Tree - palm frond fell into line | Jumper | Burned Open | High | Larger covered conductor to mostly eliminate cause and risk.
3636 | Vegetation | Tree - palm frond fell into line | Lightning Arrestor | Blown/failed | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
3637 | Vegetation | Tree - palm frond fell into line | Other | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3638 | Vegetation | Tree - palm frond fell into line | Other | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3639 | Vegetation | Tree - palm frond fell into line | Pole-Wood | Burned/flashed | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
3640 | Vegetation | Tree - palm frond fell into line | Pothead(Riser Termination) | Blown/failed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
3641 | Vegetation | Tree - palm frond fell into line | Pothead/Riser Termination | Broken | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
3642 | Vegetation | Tree - palm frond fell into line | Recloser | Blown/failed | Medium | System Hardening does not address Reclosers but coverered conductor will reduce annual recloser operations.
3643 | Vegetation | Tree - palm frond fell into line | Recloser | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3644 | Vegetation | Tree - palm frond fell into line | Secondary |  | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3645 | Vegetation | Tree - palm frond fell into line | Secondary | Arcing | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3646 | Vegetation | Tree - palm frond fell into line | Secondary | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3647 | Vegetation | Tree - palm frond fell into line | Secondary | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3648 | Vegetation | Tree - palm frond fell into line | Secondary | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3649 | Vegetation | Tree - palm frond fell into line | Secondary | Together | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3650 | Vegetation | Tree - palm frond fell into line | Service conductor | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3651 | Vegetation | Tree - palm frond fell into line | Service conductor | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3652 | Vegetation | Tree - palm frond fell into line | Service conductor | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3653 | Vegetation | Tree - palm frond fell into line | Switch (OH) | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3654 | Vegetation | Tree - palm frond fell into line | Transformer | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3655 | Vegetation | Tree - palm frond fell into line | Transformer | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3656 | Vegetation | Tree - palm frond fell into line | Transformer | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3657 | Vegetation | Tree - palm frond fell into line | Transformer | Burned/flashed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3658 | Vegetation | Tree - palm frond fell into line | Transformer (OH) | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3659 | Vegetation | Tree - palm frond fell into line | Transformer (OH) | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3660 | Vegetation | Tree - palm frond fell into line | Transformer (OH) | Burned/flashed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3661 | Vegetation | Tree - palm frond fell into line | Transformer (OH) | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3662 | 3rd Party | Aircraft- crop dusting | Conductor- Overhead | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3663 | 3rd Party | Aircraft- crop dusting | Insulator | Normal | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
3664 | 3rd Party | Contact with High Voltage- 3rd party | Secondary | Broken- wire on object | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3665 | 3rd Party | Contact with High Voltage- 3rd party | Cutout- fuse holder | Burned Open | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3666 | 3rd Party | Contact with High Voltage- 3rd party | Secondary | Blown/failed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3667 | 3rd Party | Contact with High Voltage- 3rd party | Connector or Splice (OH) | Broken- wire on ground | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3668 | 3rd Party | Contact with High Voltage- 3rd party | Anchor or Guy | Burned Open | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3669 | 3rd Party | Contact with High Voltage- 3rd party | Pothead/Riser Termination | Normal | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
3670 | 3rd Party | Contact with High Voltage- 3rd party | Transformer | Leaking | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
3671 | 3rd Party | Contact with High Voltage- 3rd party | Elbow | Broken | All | Underground facilities = no ignition risk
3672 | 3rd Party | Contact with High Voltage- 3rd party | Transformer | Malfunctioning | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
3673 | 3rd Party | Contact with High Voltage- 3rd party | Street Light Equipment | Burned/flashed | Medium | System Hardening will not address Street Lights but will address their transformers.
3674 | 3rd Party | Contact with High Voltage- 3rd party | Conductor- Underground | Burned Open | All | Underground facilities = no ignition risk
3675 | 3rd Party | Contact with High Voltage- 3rd party | Other | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3676 | 3rd Party | Contact with High Voltage- 3rd party | Capacitor | Burned/flashed | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
3677 | 3rd Party | Contact with High Voltage- 3rd party | Connector or Splice (OH) | Burned Open | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3678 | 3rd Party | Customer Equipment | Conductor- Underground | Malfunctioning | All | Underground facilities = no ignition risk
3679 | 3rd Party | Customer Equipment | Cutout- Fused- Distribution | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3680 | 3rd Party | Customer Equipment | Customer Equipment | Broken- wire on ground | None | No work is being completed on customer equipment.
3681 | 3rd Party | Customer Equipment | Service conductor | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3682 | 3rd Party | Customer Equipment | Conductor- Underground | Burned Open | All | Underground facilities = no ignition risk
3683 | 3rd Party | Customer Equipment | Service conductor | Burned Open | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3684 | 3rd Party | Customer Equipment |  | Broken | None | No work is being completed on customer equipment.
3685 | 3rd Party | Customer Equipment | Recloser | Malfunctioning | Medium | System Hardening does not address Reclosers/Sectionalizers/Stepdown or autoboosters but coverered conductor will reduce annual number of operations/duty cycle.
3686 | 3rd Party | Customer Equipment | Pole-Wood | Malfunctioning | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
3687 | 3rd Party | Customer Equipment | Switch | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3688 | 3rd Party | Customer Equipment | Switch | Burned Open | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3689 | 3rd Party | Customer Equipment | Metering Equipment | Burned Open | None | System Hardening does not address Metering facilities.
3690 | 3rd Party | Customer Equipment | Conductor- Overhead | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3691 | 3rd Party | Customer Equipment | Transformer | Malfunctioning | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3692 | 3rd Party | Customer Equipment | Conductor- Underground | Blown/failed | All | Underground facilities = no ignition risk
3693 | 3rd Party | Customer Equipment | Splice box | Blown/failed | All | Underground facilities = no ignition risk
3694 | 3rd Party | Customer Equipment | Fuse | Burned Open | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3695 | 3rd Party | Customer Equipment | Relay | Normal | None | No work is being completed on customer equipment.
3696 | 3rd Party | Dig in- 3rd party | Conductor- Underground | Malfunctioning | All | Underground facilities = no ignition risk
3697 | 3rd Party | Dig in- 3rd party | Secondary | Malfunctioning | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3698 | 3rd Party | Dig in- 3rd party | Conductor- Overhead | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3699 | 3rd Party | Dig in- 3rd party | Transformer | Normal | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
3700 | 3rd Party | Dig in- 3rd party | Conductor- Underground | On Ground | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3701 | 3rd Party | Dig in- 3rd party | Connector or Splice (UG) | Bent or Twisted | All | Underground facilities = no ignition risk
3702 | 3rd Party | Dig in- 3rd party |  | Blown/failed | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3703 | 3rd Party | Dig in- 3rd party | Service conductor | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3704 | 3rd Party | Fire- house or bldg. | Service conductor | On Ground | None | 3rd party fire impacting PGE equipment
3705 | 3rd Party | Fire- house or bldg. | Service conductor | Deteriorated | None | 3rd party fire impacting PGE equipment
3706 | 3rd Party | Fire- house or bldg. | Connector or Splice (OH) | Broken- wire on ground | None | 3rd party fire impacting PGE equipment
3707 | 3rd Party | Fire- house or bldg. | Transformer | Malfunctioning | None | 3rd party fire impacting PGE equipment
3708 | 3rd Party | Fire- house or bldg. | Conductor- Overhead | Burned Open | None | 3rd party fire impacting PGE equipment
3709 | 3rd Party | Fire- house or bldg. | Pole-Wood | Burned Open | None | 3rd party fire impacting PGE equipment
3710 | 3rd Party | Fire- house or bldg. | Interrupter | Normal | None | 3rd party fire impacting PGE equipment
3711 | 3rd Party | Fire- house or bldg. | Customer Equipment | On Ground | None | 3rd party fire impacting PGE equipment
3712 | 3rd Party | Gun Shot | Conductor- Overhead | Malfunctioning | None | Covered wire will not prevent gun shot damage
3713 | 3rd Party | Gun Shot | Transformer | Broken | None | Covered wire will not prevent gun shot damage
3714 | 3rd Party | Gun Shot | Secondary | Deteriorated | None | Covered wire will not prevent gun shot damage
3715 | 3rd Party | Gun Shot | Fuse | Broken | None | Covered wire will not prevent gun shot damage
3716 | 3rd Party | Gun Shot | Cutout- fuse holder | Broken | None | Covered wire will not prevent gun shot damage
3717 | 3rd Party | Gun Shot | Conductor- Overhead | Contaminated | None | Covered wire will not prevent gun shot damage
3718 | 3rd Party | Kite | Connector or Splice (OH) | Broken | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3719 | 3rd Party | Kite | Cutout- fuse holder | Burned/flashed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3720 | 3rd Party | Kite | Conductor- Overhead | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3721 | 3rd Party | Metallic Balloon | Connector or Splice (OH) | Malfunctioning | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3722 | 3rd Party | Metallic Balloon | Conductor- Overhead | Burned Open | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3723 | 3rd Party | Metallic Balloon | Cutout- Fused- Distribution | Burned Open | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3724 | 3rd Party | Metallic Balloon | Cutout- fuse holder | Burned Open | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3725 | 3rd Party | Metallic Balloon | Conductor- Underground | Broken | All | Underground facilities = no ignition risk
3726 | 3rd Party | Metallic Balloon | Cutout- Fused- Distribution | Contaminated | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3727 | 3rd Party | Metallic Balloon | Transformer | Malfunctioning | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
3728 | 3rd Party | Metallic Balloon | Switch | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3729 | 3rd Party | Metallic Balloon | Switch | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3730 | 3rd Party | Metallic Balloon | Other | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3731 | 3rd Party | Metallic Balloon | Pothead/Riser Termination | Contaminated | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
3732 | 3rd Party | Metallic Balloon | Pothead/Riser Termination | Burned/flashed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
3733 | 3rd Party | Other | Crossarm- Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3734 | 3rd Party | Other |  |  | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3735 | 3rd Party | Thrown Object | Cutout- Fused- Distribution | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3736 | 3rd Party | Thrown Object | Secondary | Arcing | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3737 | 3rd Party | Thrown Object | Secondary | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3738 | 3rd Party | Thrown Object | Connector or Splice (OH) | Normal | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3739 | 3rd Party | Thrown Object | Fuse | Normal | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3740 | 3rd Party | Thrown Object | Cutout- Fused- Distribution | Normal | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3741 | 3rd Party | Thrown Object | Conductor- Overhead | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3742 | 3rd Party | Tree - cutting- 3rd party | Other | Broken | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3743 | 3rd Party | Tree - cutting- 3rd party | Service conductor | Blown/failed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3744 | 3rd Party | Tree - cutting- 3rd party | Connector or Splice (OH) | Burned Open | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3745 | 3rd Party | Tree - cutting- 3rd party | Other | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3746 | 3rd Party | Vandalism | Insulator | Normal | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
3747 | 3rd Party | Vandalism | Service conductor | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3748 | 3rd Party | Vandalism | Conductor- Underground | Blown/failed | All | Underground facilities = no ignition risk
3749 | 3rd Party | Vandalism | Conductor- Underground | Malfunctioning | All | Underground facilities = no ignition risk
3750 | 3rd Party | Vandalism | Switch | Broken | None | System Hardening does not address ….
3751 | 3rd Party | Vandalism | Metering Equipment | Blown/failed | None | System Hardening does not address Metering facilities.
3752 | 3rd Party | Vandalism | Switch | Malfunctioning | None | System Hardening does not address ….
3753 | 3rd Party | Vandalism | Conductor- Overhead | Malfunctioning | All | New covered conductor will eliminate these contact type outages.
3754 | 3rd Party | Vandalism | Transformer | Normal | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
3755 | 3rd Party | Vandalism | Service conductor | Malfunctioning | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3756 | 3rd Party | Vandalism | Conductor- Underground | Burned Open | All | Underground facilities = no ignition risk
3757 | 3rd Party | Vandalism | Secondary | Arcing | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3758 | 3rd Party | Vehicle | Conductor- Overhead | Malfunctioning | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3759 | 3rd Party | Vehicle | Jumper | Arcing | High | Larger covered conductor to mostly eliminate cause and risk.
3760 | 3rd Party | Vehicle | Pole-Wood | Malfunctioning | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
3761 | 3rd Party | Vehicle | Switch | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3762 | 3rd Party | Vehicle | Pole-Wood | Bent or Twisted | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
3763 | 3rd Party | Vehicle | Street Light Equipment | On Ground | Medium | System Hardening will not address Street Lights but will address their transformers.
3764 | 3rd Party | Vehicle | Fuse | Bent or Twisted | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3765 | 3rd Party | Vehicle | Crossarm- Wood | Bent or Twisted | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
3766 | 3rd Party | Vehicle | Cutout- fuse holder | Burned/flashed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3767 | 3rd Party | Vehicle | Transformer | Contaminated | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
3768 | 3rd Party | Vehicle | Manhole- primary box | Broken | All | Underground facilities = no ignition risk
3769 | 3rd Party | Vehicle |  |  | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3770 | 3rd Party | Vehicle | Other | Burned/flashed | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
3771 | 3rd Party | Vehicle | Cutout- Fused- Distribution | Broken | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3772 | 3rd Party | Vehicle | Crossarm- Wood | Burned/flashed | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
3773 | 3rd Party | Vehicle | Transformer | Burned Open | High | System Hardening will replace all transformers (pre-2014) with FR3 fluid eliminating ignition risk.
3774 | 3rd Party | Vehicle | Cutout- Fused- Distribution | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3775 | 3rd Party | Vehicle | Insulator | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3776 | 3rd Party | Vehicle | Customer Equipment | Normal | None | No work is being completed on customer equipment.
3777 | 3rd Party | Vehicle | Conductor- Overhead | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3778 | 3rd Party | Vehicle | Crossarm- Wood | Deteriorated | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
3779 | 3rd Party | Vehicle | Riser | Normal | High | Risers are indirectly addressed on System Hardening - Pole changeouts, the covering of jumpers and leads, along with covering conductor should mitigate outages and risk.
3780 | 3rd Party | Vehicle | Switch | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3781 | 3rd Party | Vehicle | Street Light Equipment | Broken | Medium | System Hardening will not address Street Lights but will address their transformers.
3782 | 3rd Party | Vehicle | Customer Equipment | Bent or Twisted | None | No work is being completed on customer equipment.
3783 | 3rd Party | Vehicle | Cutout- Fused- Distribution | Normal | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3784 | 3rd Party | Vehicle | Pole-Wood | Together | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
3785 | 3rd Party | Vehicle | Insulator | Normal | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
3786 | 3rd Party | Vehicle | Street Light Equipment | Together | Medium | System Hardening will not address Street Lights but will address their transformers.
3787 | 3rd Party | Vehicle | Connector or Splice (OH) | Bent or Twisted | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3788 | Animal | Bird found | Cutout- Fused- Distribution | Burned/flashed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3789 | Animal | Bird found | Cutout- fuse holder | Burned Open | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3790 | Animal | Bird found | Transformer | Burned Open | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3791 | Animal | Bird found | Transformer | Arcing | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3792 | Animal | Bird found | Pothead/Riser Termination | Blown/failed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
3793 | Animal | Bird found | Secondary | Blown/failed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3794 | Animal | Bird found | Cutout- fuse holder | Malfunctioning | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3795 | Animal | Bird found | Switch | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3796 | Animal | Bird found | Cutout- Fused- Distribution | Contaminated | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3797 | Animal | Bird found | Conductor- Overhead | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
3798 | Animal | Bird found | Other | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3799 | Animal | Bird found | Transformer | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3800 | Animal | Bird found | Riser | Burned/flashed | High | Risers are indirectly addressed on System Hardening - Pole changeouts, the covering of jumpers and leads, along with covering conductor should mitigate outages and risk.
3801 | Animal | Bird found | Secondary | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3802 | Animal | Bird found | Fuse | Malfunctioning | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3803 | Animal | Bird found | Transformer | Leaking | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3804 | Animal | Bird found | Connector or Splice (OH) | Together | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3805 | Animal | Bird found | Conductor- Overhead | Burned Open | All | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
3806 | Animal | Bird found | PGs- Kearneys | Burned Open | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3807 | Animal | Bird found | Recloser | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3808 | Animal | Other | Pole-Wood | Contaminated | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
3809 | Animal | Other | Pothead/Riser Termination | Burned/flashed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
3810 | Animal | Other | Cutout- Fused- Distribution | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3811 | Animal | Other | Switch | Contaminated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3812 | Animal | Other | Pothead/Riser Termination | Contaminated | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
3813 | Animal | Other | Pothead/Riser Termination | Deteriorated | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
3814 | Animal | Other | Metering Equipment | Burned Open | None | System Hardening does not address Metering facilities.
3815 | Animal | Other | Jumper | Malfunctioning | High | Larger covered conductor to mostly eliminate cause and risk.
3816 | Animal | Other | Transformer | Burned Open | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3817 | Animal | Squirrel | Cutout- Fused- Distribution | Burned Open | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3818 | Animal | Squirrel | Cutout- Fused- Distribution | Broken | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3819 | Animal | Squirrel | Transformer | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3820 | Animal | Squirrel | Elbow | Burned/flashed | All | Underground facilities = no ignition risk
3821 | Animal | Squirrel | Elbow | Normal | All | Underground facilities = no ignition risk
3822 | Animal | Squirrel | Connector or Splice (OH) | Broken- wire on object | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3823 | Animal | Squirrel | Cutout- fuse holder | Burned Open | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3824 | Animal | Squirrel | Cutout- fuse holder | Together | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3825 | Animal | Squirrel | Secondary | Malfunctioning | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
3826 | Animal | Squirrel | Cutout- fuse holder | Malfunctioning | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3827 | Animal | Squirrel | Jumper | Together | High | Larger covered conductor to mostly eliminate cause and risk.
3828 | Animal | Squirrel | Conductor- Overhead | Burned Open | All | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
3829 | Animal | Squirrel | Riser | Blown/failed | High | Risers are indirectly addressed on System Hardening - Pole changeouts, the covering of jumpers and leads, along with covering conductor should mitigate outages and risk.
3830 | Animal | Squirrel | Connector or Splice (OH) | Malfunctioning | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
3831 | Animal | Squirrel | Cutout- Fused- Distribution | Malfunctioning | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
3832 | Animal | Squirrel | Other | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3833 | Animal | Squirrel | Conductor- Overhead | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage. Transformers will be replaced (older than 2014) and have their leads/jumpers covered
3834 | Animal | Squirrel | Fuse | Burned/flashed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
3835 | Animal | Squirrel | Connector or Splice (UG) | Malfunctioning | All | Underground facilities = no ignition risk
3836 | Animal | Squirrel | Pothead/Riser Termination | Malfunctioning | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
3837 | Animal | Squirrel | Insulator | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3838 | Animal | Squirrel | Switch | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3839 | Animal | Squirrel | Conductor- Underground | Burned Open | All | Underground facilities = no ignition risk
3840 | Animal | Squirrel | Footings- Tower or Pole | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
3841 | Animal | Squirrel | Cutout- Fused- Distribution | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3842 | Animal | Squirrel | Transformer | Together | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3843 | Animal | Squirrel | Transformer | Leaking | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3844 | Animal | Squirrel | Transformer | Burned Open | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3845 | Animal | Squirrel | Transformer | Arcing | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
3846 | Animal | Squirrel | Insulator | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
3847 | Company Initiated | Construction Activity/equip- company | Conductor- Overhead | Normal | None | Company Initiated Outage. Not outage related.
3848 | Company Initiated | Construction Activity/equip- company | Secondary | Deteriorated | None | Company Initiated Outage. Not outage related.
3849 | Company Initiated | Construction Activity/equip- company | Pole-Wood | Normal | None | Company Initiated Outage. Not outage related.
3850 | Company Initiated | Construction Activity/equip- company | Conductor- Overhead | Together | None | Company Initiated Outage. Not outage related.
3851 | Company Initiated | Construction Activity/equip- company | Connector or Splice (OH) | Broken | None | Company Initiated Outage. Not outage related.
3852 | Company Initiated | Construction Activity/equip- company | Other | Normal | None | Company Initiated Outage. Not outage related.
3853 | Company Initiated | Construction Activity/equip- company | Cutout- fuse holder | Normal | None | Company Initiated Outage. Not outage related.
3854 | Company Initiated | Construction Activity/equip- company | Fuse | Normal | None | Company Initiated Outage. Not outage related.
3855 | Company Initiated | Construction Activity/equip- company | Jumper | Normal | None | Company Initiated Outage. Not outage related.
3856 | Company Initiated | Construction Activity/equip- company | Transformer | Deteriorated | None | Company Initiated Outage. Not outage related.
3857 | Company Initiated | Construction Activity/equip- company | Conductor- Underground | Normal | None | Company Initiated Outage. Not outage related.
3858 | Company Initiated | Construction Activity/equip- company | Conductor- Overhead | Broken- wire on ground | None | Company Initiated Outage. Not outage related.
3859 | Company Initiated | Construction Activity/equip- company | Conductor- Underground | Burned/flashed | None | Company Initiated Outage. Not outage related.
3860 | Company Initiated | Construction Activity/equip- company | Fuse | Burned Open | None | Company Initiated Outage. Not outage related.
3861 | Company Initiated | Construction Activity/equip- company | Transformer | Normal | None | Company Initiated Outage. Not outage related.
3862 | Company Initiated | Construction Activity/equip- company | Elbow | Burned/flashed | None | Company Initiated Outage. Not outage related.
3863 | Company Initiated | Construction Activity/equip- company | Anchor or Guy | Normal | None | Company Initiated Outage. Not outage related.
3864 | Company Initiated | Construction Activity/equip- company | Transformer (UG) | Normal | None | Company Initiated Outage. Not outage related.
3865 | Company Initiated | Construction Activity/equip- company | Connector or Splice (OH) | Broken- wire on ground | None | Company Initiated Outage. Not outage related.
3866 | Company Initiated | Construction Activity/equip- company | Pole-Wood | Deteriorated | None | Company Initiated Outage. Not outage related.
3867 | Company Initiated | Construction Activity/equip- company | Fuse | Blown/failed | None | Company Initiated Outage. Not outage related.
3868 | Company Initiated | Construction Activity/equip- company | Jumper | Burned/flashed | None | Company Initiated Outage. Not outage related.
3869 | Company Initiated | Construction Activity/equip- company | Secondary | Broken- wire on ground | None | Company Initiated Outage. Not outage related.
3870 | Company Initiated | Construction Activity/equip- company | Cutout- fuse holder | Malfunctioning | None | Company Initiated Outage. Not outage related.
3871 | Company Initiated | Construction Activity/equip- company | Switch | Normal | None | Company Initiated Outage. Not outage related.
3872 | Company Initiated | Construction Activity/equip- company | Conductor- Underground | Broken | None | Company Initiated Outage. Not outage related.
3873 | Company Initiated | Construction Activity/equip- company | Elbow | Blown/failed | None | Company Initiated Outage. Not outage related.
3874 | Company Initiated | Construction Activity/equip- company | Elbow | Deteriorated | None | Company Initiated Outage. Not outage related.
3875 | Company Initiated | Construction Activity/equip- company | Crossarm- Wood | Broken | None | Company Initiated Outage. Not outage related.
3876 | Company Initiated | Construction Activity/equip- company | Transformer (UG) | Blown/failed | None | Company Initiated Outage. Not outage related.
3877 | Company Initiated | Construction Activity/equip- company | Transformer (UG) | Leaking | None | Company Initiated Outage. Not outage related.
3878 | Company Initiated | Construction Activity/equip- company | Connector or Splice (UG) | Blown/failed | None | Company Initiated Outage. Not outage related.
3879 | Company Initiated | Construction Activity/equip- company | Switch (UG) | Normal | None | Company Initiated Outage. Not outage related.
3880 | Company Initiated | Construction Activity/equip- company | Pole - Tower- steel | Normal | None | Company Initiated Outage. Not outage related.
3881 | Company Initiated | Construction Activity/equip- company | Secondary | Malfunctioning | None | Company Initiated Outage. Not outage related.
3882 | Company Initiated | Construction Activity/equip- company | Connector or Splice (UG) | Normal | None | Company Initiated Outage. Not outage related.
3883 | Company Initiated | Construction Activity/equip- company | Footings- Tower or Pole | Normal | None | Company Initiated Outage. Not outage related.
3884 | Company Initiated | Construction Activity/equip- company | Other | Malfunctioning | None | Company Initiated Outage. Not outage related.
3885 | Company Initiated | Construction Activity/equip- company | Conductor- Overhead | On Ground | None | Company Initiated Outage. Not outage related.
3886 | Company Initiated | Construction Activity/equip- company | Pole-Wood | Broken | None | Company Initiated Outage. Not outage related.
3887 | Company Initiated | Construction Activity/equip- company | Transformer (OH) | Blown/failed | None | Company Initiated Outage. Not outage related.
3888 | Company Initiated | Construction Activity/equip- company | Switch (UG) | Broken | None | Company Initiated Outage. Not outage related.
3889 | Company Initiated | Construction Activity/equip- company | Conductor- Overhead | Burned/flashed | None | Company Initiated Outage. Not outage related.
3890 | Company Initiated | Construction Activity/equip- company | Conductor- Overhead | Broken | None | Company Initiated Outage. Not outage related.
3891 | Company Initiated | Construction Activity/equip- company | Riser | Blown/failed | None | Company Initiated Outage. Not outage related.
3892 | Company Initiated | Construction Activity/equip- company | Capacitor | Malfunctioning | None | Company Initiated Outage. Not outage related.
3893 | Company Initiated | Construction Activity/equip- company | Circuit Breaker | Normal | None | Company Initiated Outage. Not outage related.
3894 | Company Initiated | Construction Activity/equip- company | Riser | Normal | None | Company Initiated Outage. Not outage related.
3895 | Company Initiated | Construction Activity/equip- company | Secondary | Together | None | Company Initiated Outage. Not outage related.
3896 | Company Initiated | Construction Activity/equip- company | Cutout- fuse holder | Burned/flashed | None | Company Initiated Outage. Not outage related.
3897 | Company Initiated | Construction Activity/equip- company | Elbow | Normal | None | Company Initiated Outage. Not outage related.
3898 | Company Initiated | Construction Activity/equip- company | Cutout- fuse holder | Broken | None | Company Initiated Outage. Not outage related.
3899 | Company Initiated | Construction Activity/equip- company | Switch (UG) | Blown/failed | None | Company Initiated Outage. Not outage related.
3900 | Company Initiated | Construction Activity/equip- company | Transformer (OH) | Normal | None | Company Initiated Outage. Not outage related.
3901 | Company Initiated | Construction Activity/equip- company | Jumper | Burned Open | None | Company Initiated Outage. Not outage related.
3902 | Company Initiated | Construction Activity/equip- company | Fuse | Arcing | None | Company Initiated Outage. Not outage related.
3903 | Company Initiated | Construction Activity/equip- company | Jumper | Broken | None | Company Initiated Outage. Not outage related.
3904 | Company Initiated | Construction Activity/equip- company | Jumper | Arcing | None | Company Initiated Outage. Not outage related.
3905 | Company Initiated | Construction Activity/equip- company | Anchor or Guy | Deteriorated | None | Company Initiated Outage. Not outage related.
3906 | Company Initiated | Construction Activity/equip- company | Lightning Arrestor | Normal | None | Company Initiated Outage. Not outage related.
3907 | Company Initiated | Construction Activity/equip- company | Connector or Splice (OH) | Normal | None | Company Initiated Outage. Not outage related.
3908 | Company Initiated | Construction Activity/equip- company | Crossarm- Wood | Deteriorated | None | Company Initiated Outage. Not outage related.
3909 | Company Initiated | Construction Activity/equip- company | Relay | Malfunctioning | None | Company Initiated Outage. Not outage related.
3910 | Company Initiated | Construction Activity/equip- company | Connector or Splice (OH) | Together | None | Company Initiated Outage. Not outage related.
3911 | Company Initiated | Construction Activity/equip- company |  |  | None | Company Initiated Outage. Not outage related.
3912 | Company Initiated | Construction Activity/equip- company | Cutout- Fused- Distribution | Blown/failed | None | Company Initiated Outage. Not outage related.
3913 | Company Initiated | Construction Activity/equip- company | Conductor- Overhead | Malfunctioning | None | Company Initiated Outage. Not outage related.
3914 | Company Initiated | Construction Activity/equip- company | Transformer | Burned/flashed | None | Company Initiated Outage. Not outage related.
3915 | Company Initiated | Construction Activity/equip- company | Recloser | Normal | None | Company Initiated Outage. Not outage related.
3916 | Company Initiated | Construction Activity/equip- company | Crossarm- Wood | Normal | None | Company Initiated Outage. Not outage related.
3917 | Company Initiated | Construction Activity/equip- company | Switch (OH) | Normal | None | Company Initiated Outage. Not outage related.
3918 | Company Initiated | Construction Activity/equip- company | Capacitor | Normal | None | Company Initiated Outage. Not outage related.
3919 | Company Initiated | Construction Activity/equip- company | Transformer | Broken | None | Company Initiated Outage. Not outage related.
3920 | Company Initiated | Construction Activity/equip- company | Transformer | Leaking | None | Company Initiated Outage. Not outage related.
3921 | Company Initiated | Construction Activity/equip- company | Transformer (UG) | Broken | None | Company Initiated Outage. Not outage related.
3922 | Company Initiated | Construction Activity/equip- company | Recloser | Malfunctioning | None | Company Initiated Outage. Not outage related.
3923 | Company Initiated | Construction Activity/equip- company | Regulator | Normal | None | Company Initiated Outage. Not outage related.
3924 | Company Initiated | Construction Activity/equip- company | Secondary | Broken | None | Company Initiated Outage. Not outage related.
3925 | Company Initiated | Construction Activity/equip- company | Cable Termination(live front | Normal | None | Company Initiated Outage. Not outage related.
3926 | Company Initiated | Construction Activity/equip- company | Secondary | Bent or Twisted | None | Company Initiated Outage. Not outage related.
3927 | Company Initiated | Construction Activity/equip- company | Insulator | Broken- wire on object | None | Company Initiated Outage. Not outage related.
3928 | Company Initiated | Construction Activity/equip- company | Pole-Wood | On Ground | None | Company Initiated Outage. Not outage related.
3929 | Company Initiated | Construction Activity/equip- company | Connector or Splice (OH) | Broken- wire on object | None | Company Initiated Outage. Not outage related.
3930 | Company Initiated | Construction Activity/equip- company | Transformer | Blown/failed | None | Company Initiated Outage. Not outage related.
3931 | Company Initiated | Construction Activity/equip- company | Other | Deteriorated | None | Company Initiated Outage. Not outage related.
3932 | Company Initiated | Construction Activity/equip- company | Conductor- Underground | Deteriorated | None | Company Initiated Outage. Not outage related.
3933 | Company Initiated | Construction Activity/equip- company | Connector or Splice (OH) | Burned Open | None | Company Initiated Outage. Not outage related.
3934 | Company Initiated | Construction Activity/equip- company | Transformer (OH) | Broken | None | Company Initiated Outage. Not outage related.
3935 | Company Initiated | Construction Activity/equip- company | Switch (OH) | Broken | None | Company Initiated Outage. Not outage related.
3936 | Company Initiated | Construction Activity/equip- company | Secondary | Normal | None | Company Initiated Outage. Not outage related.
3937 | Company Initiated | Construction Activity/equip- company | Cutout- fuse holder | Blown/failed | None | Company Initiated Outage. Not outage related.
3938 | Company Initiated | Construction Activity/equip- company |  | Malfunctioning | None | Company Initiated Outage. Not outage related.
3939 | Company Initiated | Construction Activity/equip- company | Transformer | Malfunctioning | None | Company Initiated Outage. Not outage related.
3940 | Company Initiated | Construction Activity/equip- company | Service conductor | Broken | None | Company Initiated Outage. Not outage related.
3941 | Company Initiated | Construction Activity/equip- company | Conductor- Overhead | Arcing | None | Company Initiated Outage. Not outage related.
3942 | Company Initiated | Construction Activity/equip- company | Other | Broken | None | Company Initiated Outage. Not outage related.
3943 | Company Initiated | Construction Activity/equip- company | Conductor- Overhead | Deteriorated | None | Company Initiated Outage. Not outage related.
3944 | Company Initiated | Construction Activity/equip- company | Insulator | Broken | None | Company Initiated Outage. Not outage related.
3945 | Company Initiated | Construction Activity/equip- company | Pole-Wood | Burned/flashed | None | Company Initiated Outage. Not outage related.
3946 | Company Initiated | Construction Activity/equip- company | Connector or Splice (UG) | Broken | None | Company Initiated Outage. Not outage related.
3947 | Company Initiated | Construction Activity/equip- company | Pole-Wood | Broken- wire on ground | None | Company Initiated Outage. Not outage related.
3948 | Company Initiated | Construction Activity/equip- company | Pothead(Riser Termination) | Normal | None | Company Initiated Outage. Not outage related.
3949 | Company Initiated | Construction Activity/equip- company | Generator | Malfunctioning | None | Company Initiated Outage. Not outage related.
3950 | Company Initiated | Contact with High Voltage- company | Fuse | Normal | None | Company Initiated Outage. Not outage related.
3951 | Company Initiated | Contact with High Voltage- company | Conductor- Overhead | Normal | None | Company Initiated Outage. Not outage related.
3952 | Company Initiated | Contact with High Voltage- company | Conductor- Underground | Normal | None | Company Initiated Outage. Not outage related.
3953 | Company Initiated | Contact with High Voltage- company | Conductor- Underground | Broken | None | Company Initiated Outage. Not outage related.
3954 | Company Initiated | Contact with High Voltage- company | Conductor- Underground | Burned/flashed | None | Company Initiated Outage. Not outage related.
3955 | Company Initiated | Contact with High Voltage- company | Conductor- Overhead | On Ground | None | Company Initiated Outage. Not outage related.
3956 | Company Initiated | Contact with High Voltage- company | Cutout- fuse holder | Normal | None | Company Initiated Outage. Not outage related.
3957 | Company Initiated | Contact with High Voltage- company | Conductor- Overhead | Broken- wire on ground | None | Company Initiated Outage. Not outage related.
3958 | Company Initiated | Contact with High Voltage- company | Conductor- Overhead | Burned/flashed | None | Company Initiated Outage. Not outage related.
3959 | Company Initiated | Contact with High Voltage- company | Pothead(Riser Termination) | Burned/flashed | None | Company Initiated Outage. Not outage related.
3960 | Company Initiated | Contact with High Voltage- company |  | Blown/failed | None | Company Initiated Outage. Not outage related.
3961 | Company Initiated | Contact with High Voltage- company | Transformer | Normal | None | Company Initiated Outage. Not outage related.
3962 | Company Initiated | Contact with High Voltage- company | Secondary | Burned/flashed | None | Company Initiated Outage. Not outage related.
3963 | Company Initiated | Contact with High Voltage- company | Fuse | Blown/failed | None | Company Initiated Outage. Not outage related.
3964 | Company Initiated | Contact with High Voltage- company | Conductor- Overhead | Together | None | Company Initiated Outage. Not outage related.
3965 | Company Initiated | Contact with High Voltage- company | Elbow | Normal | None | Company Initiated Outage. Not outage related.
3966 | Company Initiated | Contact with High Voltage- company | Other | Arcing | None | Company Initiated Outage. Not outage related.
3967 | Company Initiated | Contact with High Voltage- company | Secondary | Broken- wire on ground | None | Company Initiated Outage. Not outage related.
3968 | Company Initiated | Contact with High Voltage- company | Switch (UG) | Broken | None | Company Initiated Outage. Not outage related.
3969 | Company Initiated | Coordination failure | Circuit Breaker | Normal | None | Company Initiated Outage. Not outage related.
3970 | Company Initiated | Coordination failure | Fuse | Normal | None | Company Initiated Outage. Not outage related.
3971 | Company Initiated | Coordination failure | Other | Normal | None | Company Initiated Outage. Not outage related.
3972 | Company Initiated | Coordination failure | Conductor- Overhead | Normal | None | Company Initiated Outage. Not outage related.
3973 | Company Initiated | Coordination failure | Fuse | Blown/failed | None | Company Initiated Outage. Not outage related.
3974 | Company Initiated | Coordination failure | Recloser | Normal | None | Company Initiated Outage. Not outage related.
3975 | Company Initiated | Coordination failure | Transformer | Normal | None | Company Initiated Outage. Not outage related.
3976 | Company Initiated | Coordination failure | Crossarm- Wood | Deteriorated | None | Company Initiated Outage. Not outage related.
3977 | Company Initiated | Coordination failure | Conductor- Underground | Broken | None | Company Initiated Outage. Not outage related.
3978 | Company Initiated | Coordination failure | Relay | Malfunctioning | None | Company Initiated Outage. Not outage related.
3979 | Company Initiated | Coordination failure | Insulator | Broken | None | Company Initiated Outage. Not outage related.
3980 | Company Initiated | Coordination failure | Circuit Breaker | Malfunctioning | None | Company Initiated Outage. Not outage related.
3981 | Company Initiated | Coordination failure | Capacitor | Normal | None | Company Initiated Outage. Not outage related.
3982 | Company Initiated | Coordination failure | Recloser | Malfunctioning | None | Company Initiated Outage. Not outage related.
3983 | Company Initiated | Coordination failure |  | Normal | None | Company Initiated Outage. Not outage related.
3984 | Company Initiated | Coordination failure | Switch (UG) | Normal | None | Company Initiated Outage. Not outage related.
3985 | Company Initiated | Coordination failure | Conductor- Overhead | Burned/flashed | None | Company Initiated Outage. Not outage related.
3986 | Company Initiated | Coordination failure | SCADA | Malfunctioning | None | Company Initiated Outage. Not outage related.
3987 | Company Initiated | Coordination failure | Stepdown | Normal | None | Company Initiated Outage. Not outage related.
3988 | Company Initiated | Coordination failure | Pole-Wood | Broken- wire on ground | None | Company Initiated Outage. Not outage related.
3989 | Company Initiated | Coordination failure | Other | Malfunctioning | None | Company Initiated Outage. Not outage related.
3990 | Company Initiated | Coordination failure | Elbow | Blown/failed | None | Company Initiated Outage. Not outage related.
3991 | Company Initiated | Coordination failure | Pole-Wood | Deteriorated | None | Company Initiated Outage. Not outage related.
3992 | Company Initiated | Coordination failure | Transformer |  | None | Company Initiated Outage. Not outage related.
3993 | Company Initiated | Coordination failure | Crossarm- Wood | Burned/flashed | None | Company Initiated Outage. Not outage related.
3994 | Company Initiated | Dig in- company | Secondary | Broken | None | Company Initiated Outage. Not outage related.
3995 | Company Initiated | Dig in- company | Conductor- Underground | Broken | None | Company Initiated Outage. Not outage related.
3996 | Company Initiated | Dig in- company | Transformer | Normal | None | Company Initiated Outage. Not outage related.
3997 | Company Initiated | Dig in- company | Conductor- Overhead | Normal | None | Company Initiated Outage. Not outage related.
3998 | Company Initiated | Dig in- company | Conductor- Underground | Burned/flashed | None | Company Initiated Outage. Not outage related.
3999 | Company Initiated | Dig in- company | Service conductor | Broken | None | Company Initiated Outage. Not outage related.
4000 | Company Initiated | Dig in- company | Conductor- Underground | Malfunctioning | None | Company Initiated Outage. Not outage related.
4001 | Company Initiated | Dig in- company | Conductor- Underground | Blown/failed | None | Company Initiated Outage. Not outage related.
4002 | Company Initiated | Improper Construction | Conductor- Overhead | Normal | None | Company Initiated Outage. Not outage related.
4003 | Company Initiated | Improper Construction | Secondary | Malfunctioning | None | Company Initiated Outage. Not outage related.
4004 | Company Initiated | Improper Construction | Conductor- Overhead | Together | None | Company Initiated Outage. Not outage related.
4005 | Company Initiated | Improper Construction | Conductor- Overhead | Deteriorated | None | Company Initiated Outage. Not outage related.
4006 | Company Initiated | Improper Construction | Elbow | Normal | None | Company Initiated Outage. Not outage related.
4007 | Company Initiated | Improper Construction | Conductor- Underground | Normal | None | Company Initiated Outage. Not outage related.
4008 | Company Initiated | Improper Construction | Booster | Normal | None | Company Initiated Outage. Not outage related.
4009 | Company Initiated | Improper Construction | Transformer (UG) | Normal | None | Company Initiated Outage. Not outage related.
4010 | Company Initiated | Improper Construction | Conductor- Overhead | Annealed | None | Company Initiated Outage. Not outage related.
4011 | Company Initiated | Improper Construction | Other | Malfunctioning | None | Company Initiated Outage. Not outage related.
4012 | Company Initiated | Improper Construction | Connector or Splice (UG) | Broken | None | Company Initiated Outage. Not outage related.
4013 | Company Initiated | Improper Construction | Cutout- Fused- Distribution | Normal | None | Company Initiated Outage. Not outage related.
4014 | Company Initiated | Improper Construction | Connector or Splice (OH) | Broken | None | Company Initiated Outage. Not outage related.
4015 | Company Initiated | Improper Construction | Cutout- fuse holder | Broken | None | Company Initiated Outage. Not outage related.
4016 | Company Initiated | Improper Construction | Jumper | Arcing | None | Company Initiated Outage. Not outage related.
4017 | Company Initiated | Improper Construction | Switch | Malfunctioning | None | Company Initiated Outage. Not outage related.
4018 | Company Initiated | Improper Construction | Other | Normal | None | Company Initiated Outage. Not outage related.
4019 | Company Initiated | Improper Construction | Cutout- fuse holder | Normal | None | Company Initiated Outage. Not outage related.
4020 | Company Initiated | Improper Construction | Switch (UG) | Normal | None | Company Initiated Outage. Not outage related.
4021 | Company Initiated | Improper Construction | Switch | Normal | None | Company Initiated Outage. Not outage related.
4022 | Company Initiated | Improper Construction | Switch (UG) | Burned/flashed | None | Company Initiated Outage. Not outage related.
4023 | Company Initiated | Improper Construction | Fuse | Blown/failed | None | Company Initiated Outage. Not outage related.
4024 | Company Initiated | Improper Construction | Switch (OH) | Normal | None | Company Initiated Outage. Not outage related.
4025 | Company Initiated | Improper Construction | Switch (OH) | Arcing | None | Company Initiated Outage. Not outage related.
4026 | Company Initiated | Improper Construction | Transformer (OH) | Normal | None | Company Initiated Outage. Not outage related.
4027 | Company Initiated | Improper Construction | Secondary | Broken | None | Company Initiated Outage. Not outage related.
4028 | Company Initiated | Improper Construction | Anchor or Guy | Broken | None | Company Initiated Outage. Not outage related.
4029 | Company Initiated | Improper Construction | Connector or Splice (UG) | Normal | None | Company Initiated Outage. Not outage related.
4030 | Company Initiated | Improper Construction | Transformer | Normal | None | Company Initiated Outage. Not outage related.
4031 | Company Initiated | Improper Construction | Pole-Wood | Normal | None | Company Initiated Outage. Not outage related.
4032 | Company Initiated | Improper Construction | Cutout- fuse holder | Burned/flashed | None | Company Initiated Outage. Not outage related.
4033 | Company Initiated | Improper Construction | Regulator | Burned/flashed | None | Company Initiated Outage. Not outage related.
4034 | Company Initiated | Improper Construction | Secondary | Normal | None | Company Initiated Outage. Not outage related.
4035 | Company Initiated | Improper Construction | Interrupter | Normal | None | Company Initiated Outage. Not outage related.
4036 | Company Initiated | Improper Construction | Transformer | Blown/failed | None | Company Initiated Outage. Not outage related.
4037 | Company Initiated | Improper Construction | Fuse | Normal | None | Company Initiated Outage. Not outage related.
4038 | Company Initiated | Improper Construction | Conductor- Underground | Burned/flashed | None | Company Initiated Outage. Not outage related.
4039 | Company Initiated | Improper Construction | Customer Equipment | Normal | None | Company Initiated Outage. Not outage related.
4040 | Company Initiated | Improper Construction | Other | Arcing | None | Company Initiated Outage. Not outage related.
4041 | Company Initiated | Improper Construction | Switch (OH) | Blown/failed | None | Company Initiated Outage. Not outage related.
4042 | Company Initiated | Improper Construction | Conductor- Overhead | Burned/flashed | None | Company Initiated Outage. Not outage related.
4043 | Company Initiated | Improper Construction | Transformer (UG) | Blown/failed | None | Company Initiated Outage. Not outage related.
4044 | Company Initiated | Improper Construction | Connector or Splice (OH) | Contaminated | None | Company Initiated Outage. Not outage related.
4045 | Company Initiated | Improper Construction | Connector or Splice (UG) | Together | None | Company Initiated Outage. Not outage related.
4046 | Company Initiated | Improper Construction | Jumper | Normal | None | Company Initiated Outage. Not outage related.
4047 | Company Initiated | Improper Construction | Crossarm- Wood | Contaminated | None | Company Initiated Outage. Not outage related.
4048 | Company Initiated | Improper Construction | Crossarm- Wood | Normal | None | Company Initiated Outage. Not outage related.
4049 | Company Initiated | Improper Construction | Recloser | Normal | None | Company Initiated Outage. Not outage related.
4050 | Company Initiated | Improper Construction | Conductor- Overhead | Broken | None | Company Initiated Outage. Not outage related.
4051 | Company Initiated | Improper Construction | Conductor- Overhead | Arcing | None | Company Initiated Outage. Not outage related.
4052 | Company Initiated | Improper Construction | Conductor- Overhead | Broken- wire on ground | None | Company Initiated Outage. Not outage related.
4053 | Company Initiated | Improper Construction | Regulator | Malfunctioning | None | Company Initiated Outage. Not outage related.
4054 | Company Initiated | Improper Construction | Secondary | Together | None | Company Initiated Outage. Not outage related.
4055 | Company Initiated | Improper Construction | Conductor- Underground | Broken | None | Company Initiated Outage. Not outage related.
4056 | Company Initiated | Improper Construction | Conductor- Overhead | Bent or Twisted | None | Company Initiated Outage. Not outage related.
4057 | Company Initiated | Improper Construction | Connector or Splice (OH) | Broken- wire on ground | None | Company Initiated Outage. Not outage related.
4058 | Company Initiated | Improper Construction | Cutout- fuse holder | Blown/failed | None | Company Initiated Outage. Not outage related.
4059 | Company Initiated | Improper Construction | Transformer |  | None | Company Initiated Outage. Not outage related.
4060 | Company Initiated | Improper Construction | Other | Bent or Twisted | None | Company Initiated Outage. Not outage related.
4061 | Company Initiated | Improper Construction | Conductor- Overhead | Malfunctioning | None | Company Initiated Outage. Not outage related.
4062 | Company Initiated | Improper Construction | Crossarm- Wood | Burned/flashed | None | Company Initiated Outage. Not outage related.
4063 | Company Initiated | Improper Construction | Conductor- Underground | Together | None | Company Initiated Outage. Not outage related.
4064 | Company Initiated | Improper Construction | Connector or Splice (OH) | Normal | None | Company Initiated Outage. Not outage related.
4065 | Company Initiated | Improper Construction | Transformer | Malfunctioning | None | Company Initiated Outage. Not outage related.
4066 | Company Initiated | Improper Construction | Conductor- Underground | Malfunctioning | None | Company Initiated Outage. Not outage related.
4067 | Company Initiated | Improper Construction | Other | Together | None | Company Initiated Outage. Not outage related.
4068 | Company Initiated | Improper Construction | Fuse | Arcing | None | Company Initiated Outage. Not outage related.
4069 | Company Initiated | Improper Construction | Insulator | Broken- wire on ground | None | Company Initiated Outage. Not outage related.
4070 | Company Initiated | Improper Construction | Secondary | Bent or Twisted | None | Company Initiated Outage. Not outage related.
4071 | Company Initiated | Improper Construction | Secondary | Burned Open | None | Company Initiated Outage. Not outage related.
4072 | Company Initiated | Improper Construction | Regulator | Normal | None | Company Initiated Outage. Not outage related.
4073 | Company Initiated | Improper Construction | Cable Termination(live front | Normal | None | Company Initiated Outage. Not outage related.
4074 | Company Initiated | Insulator washing | Bushing | Broken | None | Company Initiated Outage. Not outage related.
4075 | Company Initiated | Insulator washing | Circuit Breaker | Burned/flashed | None | Company Initiated Outage. Not outage related.
4076 | Company Initiated | Insulator washing | Conductor- Overhead | Burned/flashed | None | Company Initiated Outage. Not outage related.
4077 | Company Initiated | Operating error | Recloser | Normal | None | Company Initiated Outage. Not outage related.
4078 | Company Initiated | Operating error | Other | Normal | None | Company Initiated Outage. Not outage related.
4079 | Company Initiated | Operating error | Fuse | Normal | None | Company Initiated Outage. Not outage related.
4080 | Company Initiated | Operating error | Switch (UG) | Normal | None | Company Initiated Outage. Not outage related.
4081 | Company Initiated | Operating error | SCADA | Normal | None | Company Initiated Outage. Not outage related.
4082 | Company Initiated | Operating error | Circuit Breaker | Normal | None | Company Initiated Outage. Not outage related.
4083 | Company Initiated | Operating error | Regulator | Normal | None | Company Initiated Outage. Not outage related.
4084 | Company Initiated | Operating error | Conductor- Overhead | Normal | None | Company Initiated Outage. Not outage related.
4085 | Company Initiated | Operating error | Switch (OH) | Normal | None | Company Initiated Outage. Not outage related.
4086 | Company Initiated | Operating error | Jumper | Broken- wire on ground | None | Company Initiated Outage. Not outage related.
4087 | Company Initiated | Operating error | Conductor- Overhead | Together | None | Company Initiated Outage. Not outage related.
4088 | Company Initiated | Operating error | Jumper | Normal | None | Company Initiated Outage. Not outage related.
4089 | Company Initiated | Operating error | Conductor- Underground | Normal | None | Company Initiated Outage. Not outage related.
4090 | Company Initiated | Operating error | Other | Burned/flashed | None | Company Initiated Outage. Not outage related.
4091 | Company Initiated | Operating error |  |  | None | Company Initiated Outage. Not outage related.
4092 | Company Initiated | Operating error | Fuse | Blown/failed | None | Company Initiated Outage. Not outage related.
4093 | Company Initiated | Operating error | Capacitor | Blown/failed | None | Company Initiated Outage. Not outage related.
4094 | Company Initiated | Operating error | Cutout- Fused- Distribution | Normal | None | Company Initiated Outage. Not outage related.
4095 | Company Initiated | Operating error | Sectionalizer | Normal | None | Company Initiated Outage. Not outage related.
4096 | Company Initiated | Operating error | Switch | Contaminated | None | Company Initiated Outage. Not outage related.
4097 | Company Initiated | Operating error |  | Normal | None | Company Initiated Outage. Not outage related.
4098 | Company Initiated | Operating error | Transformer (UG) |  | None | Company Initiated Outage. Not outage related.
4099 | Company Initiated | Operating error | Switch |  | None | Company Initiated Outage. Not outage related.
4100 | Company Initiated | Operating error | Conductor- Overhead | Burned/flashed | None | Company Initiated Outage. Not outage related.
4101 | Company Initiated | Operating error | Switch (OH) | Burned/flashed | None | Company Initiated Outage. Not outage related.
4102 | Company Initiated | Operating error | Relay | Normal | None | Company Initiated Outage. Not outage related.
4103 | Company Initiated | Operating error | Fuse |  | None | Company Initiated Outage. Not outage related.
4104 | Company Initiated | Operating error | Secondary | Arcing | None | Company Initiated Outage. Not outage related.
4105 | Company Initiated | Operating error | Transformer (UG) | Normal | None | Company Initiated Outage. Not outage related.
4106 | Company Initiated | Operating error | Transformer (UG) | Burned/flashed | None | Company Initiated Outage. Not outage related.
4107 | Company Initiated | Operating error | Switch | Normal | None | Company Initiated Outage. Not outage related.
4108 | Company Initiated | Operating error | Regulator | Malfunctioning | None | Company Initiated Outage. Not outage related.
4109 | Company Initiated | Operating error | Conductor- Overhead | Broken- wire on ground | None | Company Initiated Outage. Not outage related.
4110 | Company Initiated | Operating error | Elbow | Burned/flashed | None | Company Initiated Outage. Not outage related.
4111 | Company Initiated | Operating error | Customer Equipment | Malfunctioning | None | Company Initiated Outage. Not outage related.
4112 | Company Initiated | Operating error | Transformer | Normal | None | Company Initiated Outage. Not outage related.
4113 | Company Initiated | Operating error | Elbow | Normal | None | Company Initiated Outage. Not outage related.
4114 | Company Initiated | Operating error | Cutout- fuse holder | Normal | None | Company Initiated Outage. Not outage related.
4115 | Company Initiated | Operating error | Conductor- Underground | Broken | None | Company Initiated Outage. Not outage related.
4116 | Company Initiated | Operating error | Recloser | Blown/failed | None | Company Initiated Outage. Not outage related.
4117 | Company Initiated | Operating error | Jumper | Broken | None | Company Initiated Outage. Not outage related.
4118 | Company Initiated | Other Circuits | Pole-Wood | Together | None | Company Initiated Outage. Not outage related.
4119 | Company Initiated | Other Circuits |  |  | None | Company Initiated Outage. Not outage related.
4120 | Company Initiated | Other Circuits | Recloser | Normal | None | Company Initiated Outage. Not outage related.
4121 | Company Initiated | Other Circuits | Conductor- Overhead | Normal | None | Company Initiated Outage. Not outage related.
4122 | Company Initiated | Other Circuits | Cutout- fuse holder | Broken | None | Company Initiated Outage. Not outage related.
4123 | Company Initiated | Other Circuits | Regulator | Malfunctioning | None | Company Initiated Outage. Not outage related.
4124 | Company Initiated | Other Circuits | Booster | Deteriorated | None | Company Initiated Outage. Not outage related.
4125 | Company Initiated | Other Circuits | Transformer (UG) | Normal | None | Company Initiated Outage. Not outage related.
4126 | Company Initiated | Other Circuits | Transformer | Malfunctioning | None | Company Initiated Outage. Not outage related.
4127 | Company Initiated | Other Circuits | Jumper | Malfunctioning | None | Company Initiated Outage. Not outage related.
4128 | Company Initiated | Other Circuits | Conductor- Underground | Normal | None | Company Initiated Outage. Not outage related.
4129 | Company Initiated | Other Circuits | Switch (OH) | Normal | None | Company Initiated Outage. Not outage related.
4130 | Company Initiated | Other Circuits | Other | Normal | None | Company Initiated Outage. Not outage related.
4131 | Company Initiated | Other Circuits | Capacitor | Normal | None | Company Initiated Outage. Not outage related.
4132 | Company Initiated | Other Circuits | Generator | Malfunctioning | None | Company Initiated Outage. Not outage related.
4133 | Company Initiated | Other Circuits | Jumper | Burned Open | None | Company Initiated Outage. Not outage related.
4134 | Company Initiated | Other Circuits | Jumper | Normal | None | Company Initiated Outage. Not outage related.
4135 | Company Initiated | Other Circuits | Fuse | Normal | None | Company Initiated Outage. Not outage related.
4136 | Company Initiated | Other Circuits | Conductor- Overhead | Broken- wire on object | None | Company Initiated Outage. Not outage related.
4137 | Company Initiated | Other Circuits | Other | Broken | None | Company Initiated Outage. Not outage related.
4138 | Company Initiated | Other Circuits | Regulator | Broken | None | Company Initiated Outage. Not outage related.
4139 | Company Initiated | Other Circuits | Secondary | Burned/flashed | None | Company Initiated Outage. Not outage related.
4140 | Company Initiated | Other Circuits | Conductor- Overhead | Broken- wire on ground | None | Company Initiated Outage. Not outage related.
4141 | Company Initiated | Other Circuits | Conductor- Overhead | Broken | None | Company Initiated Outage. Not outage related.
4142 | Company Initiated | Other Circuits | Conductor- Overhead | Together | None | Company Initiated Outage. Not outage related.
4143 | Company Initiated | Other Circuits | Switch (UG) | Normal | None | Company Initiated Outage. Not outage related.
4144 | Company Initiated | Other Circuits | Circuit Breaker | Normal | None | Company Initiated Outage. Not outage related.
4145 | Company Initiated | Other Circuits | Regulator- LTC substation | Normal | None | Company Initiated Outage. Not outage related.
4146 | Company Initiated | Other Circuits | Fuse | Blown/failed | None | Company Initiated Outage. Not outage related.
4147 | Company Initiated | Other Circuits | Conductor- Underground | Broken | None | Company Initiated Outage. Not outage related.
4148 | Company Initiated | Other Circuits | Generator | Contaminated | None | Company Initiated Outage. Not outage related.
4149 | Company Initiated | Other Circuits | Footings- Tower or Pole | Bent or Twisted | None | Company Initiated Outage. Not outage related.
4150 | Company Initiated | Other Circuits | Lightning Arrestor | Blown/failed | None | Company Initiated Outage. Not outage related.
4151 | Company Initiated | Other Circuits | Pole-Wood | Burned/flashed | None | Company Initiated Outage. Not outage related.
4152 | Company Initiated | Other Circuits | Pole-Wood | Normal | None | Company Initiated Outage. Not outage related.
4153 | Company Initiated | Other Circuits | Pole-Wood | Deteriorated | None | Company Initiated Outage. Not outage related.
4154 | Company Initiated | Other Circuits | Transformer | Deteriorated | None | Company Initiated Outage. Not outage related.
4155 | Company Initiated | Other Circuits | Transformer | Blown/failed | None | Company Initiated Outage. Not outage related.
4156 | Company Initiated | Other Circuits | Conductor- Overhead | Deteriorated | None | Company Initiated Outage. Not outage related.
4157 | Company Initiated | Other Circuits | Secondary | Burned Open | None | Company Initiated Outage. Not outage related.
4158 | Company Initiated | Other Circuits | Conductor- Underground | Burned/flashed | None | Company Initiated Outage. Not outage related.
4159 | Company Initiated | Other Circuits | Elbow | Blown/failed | None | Company Initiated Outage. Not outage related.
4160 | Company Initiated | Other Circuits | Transformer | Broken | None | Company Initiated Outage. Not outage related.
4161 | Company Initiated | Other Circuits | Other |  | None | Company Initiated Outage. Not outage related.
4162 | Company Initiated | Other Circuits | Lightning Arrestor | Malfunctioning | None | Company Initiated Outage. Not outage related.
4163 | Company Initiated | Other Circuits | Transformer | Normal | None | Company Initiated Outage. Not outage related.
4164 | Company Initiated | Other Circuits | Crossarm- Wood | Broken | None | Company Initiated Outage. Not outage related.
4165 | Company Initiated | Other Circuits | Switch | Malfunctioning | None | Company Initiated Outage. Not outage related.
4166 | Company Initiated | Other Circuits | Fuse | Deteriorated | None | Company Initiated Outage. Not outage related.
4167 | Company Initiated | Personnel- company | Conductor- Overhead | Normal | None | Company Initiated Outage. Not outage related.
4168 | Company Initiated | Personnel- company | Elbow | Broken | None | Company Initiated Outage. Not outage related.
4169 | Company Initiated | Personnel- company | Circuit Breaker | Normal | None | Company Initiated Outage. Not outage related.
4170 | Company Initiated | Personnel- company | Cutout- fuse holder | Arcing | None | Company Initiated Outage. Not outage related.
4171 | Company Initiated | Personnel- company | Pole-Wood | Broken | None | Company Initiated Outage. Not outage related.
4172 | Company Initiated | Personnel- company | Elbow | Deteriorated | None | Company Initiated Outage. Not outage related.
4173 | Company Initiated | Personnel- company | Fuse | Normal | None | Company Initiated Outage. Not outage related.
4174 | Company Initiated | Personnel- company | Switch (OH) | Normal | None | Company Initiated Outage. Not outage related.
4175 | Company Initiated | Personnel- company | Conductor- Underground | Normal | None | Company Initiated Outage. Not outage related.
4176 | Company Initiated | Personnel- company | Transformer (UG) | Normal | None | Company Initiated Outage. Not outage related.
4177 | Company Initiated | Personnel- company | Regulator | Broken | None | Company Initiated Outage. Not outage related.
4178 | Company Initiated | Personnel- company | Recloser | Normal | None | Company Initiated Outage. Not outage related.
4179 | Company Initiated | Personnel- company |  |  | None | Company Initiated Outage. Not outage related.
4180 | Company Initiated | Personnel- company | Jumper | Burned/flashed | None | Company Initiated Outage. Not outage related.
4181 | Company Initiated | Personnel- company | Other | Normal | None | Company Initiated Outage. Not outage related.
4182 | Company Initiated | Personnel- company | Service conductor | Together | None | Company Initiated Outage. Not outage related.
4183 | Company Initiated | Personnel- company | Fuse | Blown/failed | None | Company Initiated Outage. Not outage related.
4184 | Company Initiated | Personnel- company | Conductor- Underground | Burned/flashed | None | Company Initiated Outage. Not outage related.
4185 | Company Initiated | Personnel- company | Secondary | Normal | None | Company Initiated Outage. Not outage related.
4186 | Company Initiated | Personnel- company | Switch (UG) | Normal | None | Company Initiated Outage. Not outage related.
4187 | Company Initiated | Personnel- company | Relay | Normal | None | Company Initiated Outage. Not outage related.
4188 | Company Initiated | Personnel- company | Secondary | Together | None | Company Initiated Outage. Not outage related.
4189 | Company Initiated | Personnel- company | Transformer | Normal | None | Company Initiated Outage. Not outage related.
4190 | Company Initiated | Personnel- company | Switch (UG) | Broken | None | Company Initiated Outage. Not outage related.
4191 | Company Initiated | Personnel- company | Transformer (UG) | Leaking | None | Company Initiated Outage. Not outage related.
4192 | Company Initiated | Personnel- company | Transformer (UG) | Arcing | None | Company Initiated Outage. Not outage related.
4193 | Company Initiated | Personnel- company | Transformer (UG) | Deteriorated | None | Company Initiated Outage. Not outage related.
4194 | Company Initiated | Personnel- company | Secondary | Broken | None | Company Initiated Outage. Not outage related.
4195 | Company Initiated | Personnel- company | Switch (OH) | Blown/failed | None | Company Initiated Outage. Not outage related.
4196 | Company Initiated | Personnel- company | Transformer (UG) | Blown/failed | None | Company Initiated Outage. Not outage related.
4197 | Company Initiated | Personnel- company | Interrupter | Malfunctioning | None | Company Initiated Outage. Not outage related.
4198 | Company Initiated | Personnel- company | Conductor- Underground | Blown/failed | None | Company Initiated Outage. Not outage related.
4199 | Company Initiated | Personnel- company | Crossarm- Wood | Broken | None | Company Initiated Outage. Not outage related.
4200 | Company Initiated | Personnel- company | Transformer (UG) |  | None | Company Initiated Outage. Not outage related.
4201 | Company Initiated | Personnel- company | Pothead(Riser Termination) | Normal | None | Company Initiated Outage. Not outage related.
4202 | Company Initiated | Personnel- company | Switch | Normal | None | Company Initiated Outage. Not outage related.
4203 | Company Initiated | Personnel- company | Elbow | Burned/flashed | None | Company Initiated Outage. Not outage related.
4204 | Company Initiated | Personnel- company | Recloser | Malfunctioning | None | Company Initiated Outage. Not outage related.
4205 | Company Initiated | Personnel- company | Transformer (OH) | Normal | None | Company Initiated Outage. Not outage related.
4206 | Company Initiated | Personnel- company | Conductor- Overhead | Arcing | None | Company Initiated Outage. Not outage related.
4207 | Company Initiated | Personnel- company |  | Broken | None | Company Initiated Outage. Not outage related.
4208 | Company Initiated | Personnel- company | Elbow | Normal | None | Company Initiated Outage. Not outage related.
4209 | Company Initiated | Personnel- company | Transformer (OH) | Contaminated | None | Company Initiated Outage. Not outage related.
4210 | Company Initiated | Personnel- company |  | Blown/failed | None | Company Initiated Outage. Not outage related.
4211 | Company Initiated | Personnel- company | Elbow | Blown/failed | None | Company Initiated Outage. Not outage related.
4212 | Company Initiated | Personnel- company | SCADA | Normal | None | Company Initiated Outage. Not outage related.
4213 | Company Initiated | Personnel- company | Connector or Splice (OH) | Broken | None | Company Initiated Outage. Not outage related.
4214 | Company Initiated | Personnel- company | Transformer | Leaking | None | Company Initiated Outage. Not outage related.
4215 | Company Initiated | Personnel- company | Jumper | Normal | None | Company Initiated Outage. Not outage related.
4216 | Company Initiated | Personnel- company | Transformer (OH) | Broken | None | Company Initiated Outage. Not outage related.
4217 | Company Initiated | Personnel- company | Sectionalizer | Normal | None | Company Initiated Outage. Not outage related.
4218 | Company Initiated | Personnel- company | Conductor- Overhead | Broken- wire on ground | None | Company Initiated Outage. Not outage related.
4219 | Company Initiated | Personnel- company | Capacitor | Malfunctioning | None | Company Initiated Outage. Not outage related.
4220 | Company Initiated | Personnel- company | Conductor- Overhead |  | None | Company Initiated Outage. Not outage related.
4221 | Company Initiated | Personnel- company | Conductor- Overhead | Broken | None | Company Initiated Outage. Not outage related.
4222 | Company Initiated | Personnel- company | Secondary | Deteriorated | None | Company Initiated Outage. Not outage related.
4223 | Company Initiated | Personnel- company | Secondary | Burned Open | None | Company Initiated Outage. Not outage related.
4224 | Company Initiated | Personnel- company | Other | Deteriorated | None | Company Initiated Outage. Not outage related.
4225 | Company Initiated | Personnel- company | Interrupter | Normal | None | Company Initiated Outage. Not outage related.
4226 | Company Initiated | Personnel- company | Pole-Wood | Deteriorated | None | Company Initiated Outage. Not outage related.
4227 | Company Initiated | Personnel- company |  | Normal | None | Company Initiated Outage. Not outage related.
4228 | Company Initiated | Personnel- company | Regulator | Blown/failed | None | Company Initiated Outage. Not outage related.
4229 | Company Initiated | Personnel- company | Pole-Wood | Normal | None | Company Initiated Outage. Not outage related.
4230 | Company Initiated | Personnel- company | Connector or Splice (OH) | Normal | None | Company Initiated Outage. Not outage related.
4231 | Company Initiated | Personnel- company | Cutout- Fused- Distribution | Arcing | None | Company Initiated Outage. Not outage related.
4232 | Company Initiated | Personnel- company | Crossarm- Steel | Arcing | None | Company Initiated Outage. Not outage related.
4233 | Company Initiated | Personnel- company | Other | Malfunctioning | None | Company Initiated Outage. Not outage related.
4234 | Company Initiated | Personnel- company | Jumper | Arcing | None | Company Initiated Outage. Not outage related.
4235 | Company Initiated | Personnel- company | Transformer (UG) | Broken | None | Company Initiated Outage. Not outage related.
4236 | Company Initiated | Personnel- company | Metering Equipment |  | None | Company Initiated Outage. Not outage related.
4237 | Company Initiated | Personnel- company | Pole-Wood | Burned/flashed | None | Company Initiated Outage. Not outage related.
4238 | Company Initiated | Personnel- company | Conductor- Underground | Malfunctioning | None | Company Initiated Outage. Not outage related.
4239 | Company Initiated | Personnel- company | Transformer | Malfunctioning | None | Company Initiated Outage. Not outage related.
4240 | Company Initiated | Personnel- company | Switch | Malfunctioning | None | Company Initiated Outage. Not outage related.
4241 | Company Initiated | Personnel- company | Conductor- Overhead | Together | None | Company Initiated Outage. Not outage related.
4242 | Company Initiated | Personnel- company | Cutout- Fused- Distribution | Normal | None | Company Initiated Outage. Not outage related.
4243 | Company Initiated | Personnel- company | Fuse | Arcing | None | Company Initiated Outage. Not outage related.
4244 | Company Initiated | Personnel- company | Bus | Normal | None | Company Initiated Outage. Not outage related.
4245 | Company Initiated | Personnel- company | Transformer (OH) | Leaking | None | Company Initiated Outage. Not outage related.
4246 | Company Initiated | Personnel- company | Conductor- Underground | Deteriorated | None | Company Initiated Outage. Not outage related.
4247 | Company Initiated | Personnel- company | Capacitor | Normal | None | Company Initiated Outage. Not outage related.
4248 | Company Initiated | Return Circuit Normal | Stepdown | Normal | None | Company Initiated Outage. Not outage related.
4249 | Company Initiated | Return Circuit Normal | Pole-Wood | Normal | None | Company Initiated Outage. Not outage related.
4250 | Company Initiated | Return Circuit Normal | Conductor- Underground | Normal | None | Company Initiated Outage. Not outage related.
4251 | Company Initiated | Return Circuit Normal | Elbow | Blown/failed | None | Company Initiated Outage. Not outage related.
4252 | Company Initiated | Return Circuit Normal | Switch (OH) | Normal | None | Company Initiated Outage. Not outage related.
4253 | Company Initiated | Return Circuit Normal | Conductor- Overhead | Normal | None | Company Initiated Outage. Not outage related.
4254 | Company Initiated | Return Circuit Normal | Switch (UG) | Normal | None | Company Initiated Outage. Not outage related.
4255 | Company Initiated | Return Circuit Normal | Other | Normal | None | Company Initiated Outage. Not outage related.
4256 | Company Initiated | Return Circuit Normal | Fuse | Normal | None | Company Initiated Outage. Not outage related.
4257 | Company Initiated | Return Circuit Normal | Jumper | Normal | None | Company Initiated Outage. Not outage related.
4258 | Company Initiated | Return Circuit Normal | Recloser | Normal | None | Company Initiated Outage. Not outage related.
4259 | Company Initiated | Return Circuit Normal | Secondary | Broken | None | Company Initiated Outage. Not outage related.
4260 | Company Initiated | Return Circuit Normal | Switch (OH) | Broken | None | Company Initiated Outage. Not outage related.
4261 | Company Initiated | Return Circuit Normal | Insulator | Burned/flashed | None | Company Initiated Outage. Not outage related.
4262 | Company Initiated | Return Circuit Normal | Elbow | Deteriorated | None | Company Initiated Outage. Not outage related.
4263 | Company Initiated | Return Circuit Normal | Cutout- fuse holder | Broken | None | Company Initiated Outage. Not outage related.
4264 | Company Initiated | Return Circuit Normal | Jumper | Burned Open | None | Company Initiated Outage. Not outage related.
4265 | Company Initiated | Return Circuit Normal | Conductor- Overhead | Broken- wire on object | None | Company Initiated Outage. Not outage related.
4266 | Company Initiated | Return Circuit Normal | Transformer (UG) | Normal | None | Company Initiated Outage. Not outage related.
4267 | Company Initiated | Return Circuit Normal | Crossarm- Wood | Broken | None | Company Initiated Outage. Not outage related.
4268 | Company Initiated | Return Circuit Normal | Cutout- fuse holder | Normal | None | Company Initiated Outage. Not outage related.
4269 | Company Initiated | Return Circuit Normal | Conductor- Underground | Broken | None | Company Initiated Outage. Not outage related.
4270 | Company Initiated | Return Circuit Normal | Conductor- Overhead | Together | None | Company Initiated Outage. Not outage related.
4271 | Company Initiated | Return Circuit Normal | Conductor- Underground | Burned/flashed | None | Company Initiated Outage. Not outage related.
4272 | Company Initiated | Return Circuit Normal | Pole-Wood | Burned/flashed | None | Company Initiated Outage. Not outage related.
4273 | Company Initiated | Return Circuit Normal | Conductor- Underground | Deteriorated | None | Company Initiated Outage. Not outage related.
4274 | Company Initiated | Return Circuit Normal | Recloser | Burned/flashed | None | Company Initiated Outage. Not outage related.
4275 | Company Initiated | Return Circuit Normal | Cutout- fuse holder | Blown/failed | None | Company Initiated Outage. Not outage related.
4276 | Company Initiated | Return Circuit Normal | Transformer (OH) | Normal | None | Company Initiated Outage. Not outage related.
4277 | Company Initiated | Return Circuit Normal | Pothead(Riser Termination) | Normal | None | Company Initiated Outage. Not outage related.
4278 | Company Initiated | Return Circuit Normal | Elbow | Normal | None | Company Initiated Outage. Not outage related.
4279 | Company Initiated | Return Circuit Normal | Connector or Splice (UG) | Normal | None | Company Initiated Outage. Not outage related.
4280 | Company Initiated | Return Circuit Normal | Pole-Wood | Broken- wire on ground | None | Company Initiated Outage. Not outage related.
4281 | Company Initiated | Return Circuit Normal | Fuse | Blown/failed | None | Company Initiated Outage. Not outage related.
4282 | Company Initiated | Return Circuit Normal | Generator | Normal | None | Company Initiated Outage. Not outage related.
4283 | Company Initiated | Return Circuit Normal | Cable Termination(live front | Normal | None | Company Initiated Outage. Not outage related.
4284 | Company Initiated | Return Circuit Normal | Circuit Breaker | Normal | None | Company Initiated Outage. Not outage related.
4285 | Company Initiated | Return Circuit Normal | Transformer (UG) | Broken | None | Company Initiated Outage. Not outage related.
4286 | Company Initiated | Return Circuit Normal | Cable Termination(live front | Blown/failed | None | Company Initiated Outage. Not outage related.
4287 | Company Initiated | Return Circuit Normal | Transformer | Malfunctioning | None | Company Initiated Outage. Not outage related.
4288 | Company Initiated | Return Circuit Normal | Pothead(Riser Termination) | Blown/failed | None | Company Initiated Outage. Not outage related.
4289 | Company Initiated | Return Circuit Normal | Secondary | Normal | None | Company Initiated Outage. Not outage related.
4290 | Company Initiated | Return Circuit Normal | Conductor- Overhead | Broken- wire on ground | None | Company Initiated Outage. Not outage related.
4291 | Company Initiated | Return Circuit Normal | Pole-Wood | Broken | None | Company Initiated Outage. Not outage related.
4292 | Company Initiated | Return Circuit Normal | Other | Deteriorated | None | Company Initiated Outage. Not outage related.
4293 | Company Initiated | Return Circuit Normal | Crossarm- Wood | Burned/flashed | None | Company Initiated Outage. Not outage related.
4294 | Company Initiated | Return Circuit Normal | Connector or Splice (OH) | Normal | None | Company Initiated Outage. Not outage related.
4295 | Company Initiated | Return Circuit Normal | Conductor- Overhead | Broken | None | Company Initiated Outage. Not outage related.
4296 | Company Initiated | Return Circuit Normal | Circuit Breaker | Burned/flashed | None | Company Initiated Outage. Not outage related.
4297 | Company Initiated | Return Circuit Normal | Pole-Wood | Deteriorated | None | Company Initiated Outage. Not outage related.
4298 | Company Initiated | Return Circuit Normal | Recloser | Malfunctioning | None | Company Initiated Outage. Not outage related.
4299 | Company Initiated | Return Circuit Normal | Regulator | Normal | None | Company Initiated Outage. Not outage related.
4300 | Company Initiated | Return Circuit Normal | Cutout- fuse holder | Burned/flashed | None | Company Initiated Outage. Not outage related.
4301 | Company Initiated | Return Circuit Normal | Other | Blown/failed | None | Company Initiated Outage. Not outage related.
4302 | Company Initiated | Return Circuit Normal | Insulator | Normal | None | Company Initiated Outage. Not outage related.
4303 | Company Initiated | Return Circuit Normal | Switch (UG) | Blown/failed | None | Company Initiated Outage. Not outage related.
4304 | Company Initiated | Return Circuit Normal | Cutout- fuse holder | Arcing | None | Company Initiated Outage. Not outage related.
4305 | Company Initiated | Return Circuit Normal | SCADA | Normal | None | Company Initiated Outage. Not outage related.
4306 | Company Initiated | Return Circuit Normal | Connector or Splice (OH) | Broken | None | Company Initiated Outage. Not outage related.
4307 | Company Initiated | Return Circuit Normal | Transformer (UG) | Blown/failed | None | Company Initiated Outage. Not outage related.
4308 | Company Initiated | Return Circuit Normal | Connector or Splice (OH) | Arcing | None | Company Initiated Outage. Not outage related.
4309 | Company Initiated | Return Circuit Normal | Lightning Arrestor | Blown/failed | None | Company Initiated Outage. Not outage related.
4310 | Company Initiated | Return Circuit Normal | Connector or Splice (UG) | Blown/failed | None | Company Initiated Outage. Not outage related.
4311 | Company Initiated | Return Circuit Normal | Conductor- Overhead | Deteriorated | None | Company Initiated Outage. Not outage related.
4312 | Company Initiated | Return Circuit Normal | Customer Equipment | Normal | None | Company Initiated Outage. Not outage related.
4313 | Company Initiated | Return Circuit Normal | Pothead(Riser Termination) | Broken | None | Company Initiated Outage. Not outage related.
4314 | Company Initiated | Return Circuit Normal | Secondary | Burned/flashed | None | Company Initiated Outage. Not outage related.
4315 | Company Initiated | Return Circuit Normal | Jumper | Broken | None | Company Initiated Outage. Not outage related.
4316 | Company Initiated | Return Circuit Normal | PGs- Kearneys | Normal | None | Company Initiated Outage. Not outage related.
4317 | Company Initiated | Return Circuit Normal | Pole-Wood | On Ground | None | Company Initiated Outage. Not outage related.
4318 | Company Initiated | Return Circuit Normal | Connector or Splice (UG) | Burned/flashed | None | Company Initiated Outage. Not outage related.
4319 | Company Initiated | Return Circuit Normal | Transformer (UG) | Leaking | None | Company Initiated Outage. Not outage related.
4320 | Company Initiated | Return Circuit Normal | Elbow | Burned/flashed | None | Company Initiated Outage. Not outage related.
4321 | Company Initiated | Return Circuit Normal | Insulator | Broken | None | Company Initiated Outage. Not outage related.
4322 | Company Initiated | Return Circuit Normal | Other | Broken | None | Company Initiated Outage. Not outage related.
4323 | Company Initiated | Return Circuit Normal | Transformer (OH) | Blown/failed | None | Company Initiated Outage. Not outage related.
4324 | Company Initiated | Return Circuit Normal | Booster | Burned/flashed | None | Company Initiated Outage. Not outage related.
4325 | Company Initiated | Return Circuit Normal | Regulator | Malfunctioning | None | Company Initiated Outage. Not outage related.
4326 | Company Initiated | Return Circuit Normal | Conductor- Overhead | Bent or Twisted | None | Company Initiated Outage. Not outage related.
4327 | Company Initiated | Return Circuit Normal | Insulator | Broken- wire on object | None | Company Initiated Outage. Not outage related.
4328 | Company Initiated | Return Circuit Normal | Crossarm- Wood | Normal | None | Company Initiated Outage. Not outage related.
4329 | Company Initiated | Return Circuit Normal | Bushing | Normal | None | Company Initiated Outage. Not outage related.
4330 | Company Initiated | Return Circuit Normal | Switch (OH) | Arcing | None | Company Initiated Outage. Not outage related.
4331 | Company Initiated | Return Circuit Normal | Woodpin | Broken | None | Company Initiated Outage. Not outage related.
4332 | Company Initiated | Return Circuit Normal | Service conductor | Normal | None | Company Initiated Outage. Not outage related.
4333 | Company Initiated | Return Circuit Normal | Transformer (OH) | Broken | None | Company Initiated Outage. Not outage related.
4334 | Company Initiated | Return Circuit Normal | Sectionalizer | Normal | None | Company Initiated Outage. Not outage related.
4335 | Company Initiated | Return Circuit Normal | Elbow | Broken | None | Company Initiated Outage. Not outage related.
4336 | Company Initiated | Return Circuit Normal | Pothead(Riser Termination) | Burned/flashed | None | Company Initiated Outage. Not outage related.
4337 | Company Initiated | Return Circuit Normal | Recloser | Broken | None | Company Initiated Outage. Not outage related.
4338 | Company Initiated | Return Circuit Normal | Interrupter | Normal | None | Company Initiated Outage. Not outage related.
4339 | Company Initiated | Return Circuit Normal | Conductor- Overhead | Arcing | None | Company Initiated Outage. Not outage related.
4340 | Environmental/External | Earthquake | Other | Deteriorated | Medium | System Hardening will make circuitry more robustand moderately reduce ignition risk.
4341 | Environmental/External | Earthquake | Conductor- Overhead | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4342 | Environmental/External | Earthquake | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4343 | Environmental/External | Earthquake | Conductor- Overhead | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4344 | Environmental/External | Earthquake | Transformer | Burned Open | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4345 | Environmental/External | Earthquake | Crossarm- Wood | Burned Open | Medium | System Hardening will make circuitry more robustand moderately reduce ignition risk.
4346 | Environmental/External | Earthquake | Connector or Splice (OH) | Arcing | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
4347 | Environmental/External | Earthquake | Transformer | Leaking | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4348 | Environmental/External | Earthquake | Conductor- Overhead | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4349 | Environmental/External | Earthquake | Secondary | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4350 | Environmental/External | Earthquake | Conductor- Overhead | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4351 | Environmental/External | Earthquake | Jumper | Broken | High | Larger covered conductor to mostly eliminate cause and risk.
4352 | Environmental/External | Earthquake | Circuit Breaker | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4353 | Environmental/External | Earthquake | Fuse | Broken | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk..
4354 | Environmental/External | Earthquake | Crossarm- Wood | Broken | Medium | System Hardening will make circuitry more robustand moderately reduce ignition risk.
4355 | Environmental/External | Earthquake | Conductor- Overhead | Burned Open | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4356 | Environmental/External | Earthquake | Transformer | Bent or Twisted | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4357 | Environmental/External | Earthquake | Service conductor | On Ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4358 | Environmental/External | Earthquake | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk..
4359 | Environmental/External | Earthquake | Transformer | Malfunctioning | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4360 | Environmental/External | Earthquake | Conductor- Overhead | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4361 | Environmental/External | Earthquake | Fuse | Normal | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk..
4362 | Environmental/External | Earthquake | Transformer | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4363 | Environmental/External | Earthquake | Transformer | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4364 | Environmental/External | Earthquake | Connector or Splice (OH) | Broken | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
4365 | Environmental/External | Earthquake | Jumper | Burned Open | High | Larger covered conductor to mostly eliminate cause and risk.
4366 | Environmental/External | Earthquake | Recloser | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4367 | Environmental/External | Earthquake | Cutout- fuse holder | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
4368 | Environmental/External | Earthquake | Transformer | Burned/flashed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4369 | Environmental/External | Earthquake | Elbow | Blown/failed | All | Underground facilities = no ignition risk
4370 | Environmental/External | Earthquake | Transformer | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4371 | Environmental/External | Earthquake | Conductor- Underground | Malfunctioning | All | Underground facilities = no ignition risk
4372 | Environmental/External | Earthquake | Secondary | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4373 | Environmental/External | Earthquake | Insulator | Broken | Medium | System Hardening will make circuitry more robustand moderately reduce ignition risk.
4374 | Environmental/External | Earthquake | Conductor- Overhead | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4375 | Environmental/External | Earthquake | Fuse | Burned Open | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk..
4376 | Environmental/External | Earthquake | Pole-Wood | Broken | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
4377 | Environmental/External | Earthquake | Transformer |  | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4378 | Environmental/External | Earthquake | Pole-Wood | Burned/flashed | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
4379 | Environmental/External | Earthquake | Insulator | Blown/failed | Medium | System Hardening will make circuitry more robustand moderately reduce ignition risk.
4380 | Environmental/External | Earthquake | Transformer | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4381 | Environmental/External | Earthquake | Recloser | Together | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4382 | Environmental/External | Fire- Forest/Grass | Secondary | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4383 | Environmental/External | Fire- Forest/Grass | Conductor- Overhead | Burned/flashed | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
4384 | Environmental/External | Fire- Forest/Grass | Pole-Wood | Broken- wire on ground | Medium | SECONDARY IGNITION RISK - Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4385 | Environmental/External | Fire- Forest/Grass | Pole-Wood | Burned/flashed | Low | A limited number of Poles have been replaced with composite material. We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
4386 | Environmental/External | Fire- Forest/Grass | Conductor- Overhead | Normal | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
4387 | Environmental/External | Fire- Forest/Grass | Conductor- Overhead | Broken- wire on ground | Medium | SECONDARY IGNITION RISK - Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4388 | Environmental/External | Fire- Forest/Grass | Switch (UG) | Normal | All | Underground facilities = no ignition risk
4389 | Environmental/External | Fire- Forest/Grass | Fuse | Normal | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk..
4390 | Environmental/External | Fire- Forest/Grass | Cutout- fuse holder | Normal | High | SECONDARY IGNITION RISK - Non-exempt fused cutouts are being replaced on System Hardening Projects.
4391 | Environmental/External | Fire- Forest/Grass | Recloser | Normal | All | Covered conductor will eliminate the line slap/smoke arc and risk associated with this outage.
4392 | Environmental/External | Fire- Forest/Grass | Crossarm- Wood | Burned/flashed | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
4393 | Environmental/External | Fire- Forest/Grass | Pole-Wood | Broken | Low | A limited number of Poles have been replaced with composite material. We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
4394 | Environmental/External | Fire- Forest/Grass | Circuit Breaker | Normal | All | Covered conductor will eliminate the line slap and risk/smoke arc associated with this outage.
4395 | Environmental/External | Fire- Forest/Grass | Connector or Splice (UG) | Burned/flashed | All | Underground facilities = no ignition risk
4396 | Environmental/External | Fire- Forest/Grass | Secondary | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4397 | Environmental/External | Fire- Forest/Grass | Other | Normal | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
4398 | Environmental/External | Fire- Forest/Grass | Other | Burned Open | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
4399 | Environmental/External | Fire- Forest/Grass | Other | Burned/flashed | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
4400 | Environmental/External | Fire- Forest/Grass | Pole-Wood | On Ground | Medium | SECONDARY IGNITION RISK - Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4401 | Environmental/External | Fire- Forest/Grass | Service conductor | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4402 | Environmental/External | Fire- Forest/Grass | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk..
4403 | Environmental/External | Fire- Forest/Grass | Transformer (OH) | Blown/failed | High | SECONDARY IGNITION RISK - Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4404 | Environmental/External | Fire- Forest/Grass | Conductor- Overhead | Broken | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
4405 | Environmental/External | Fire- Forest/Grass | Insulator | Broken- wire on object | Medium | SECONDARY IGNITION RISK - Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4406 | Environmental/External | Fire- Forest/Grass | Transformer (UG) | Normal | All | Underground facilities = no ignition risk
4407 | Environmental/External | Fire- Forest/Grass | Metering Equipment | Burned/flashed | None | System Hardening does not address Metering facilities.
4408 | Environmental/External | Fire- Forest/Grass | Fuse | Broken | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk..
4409 | Environmental/External | Fire- Forest/Grass | Transformer | Arcing | High | SECONDARY IGNITION RISK - Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4410 | Environmental/External | Fire- Forest/Grass | Transformer | Malfunctioning | High | SECONDARY IGNITION RISK - Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4411 | Environmental/External | Fire- Forest/Grass | Customer Equipment | Burned/flashed | None | System hardening does not address customer equipment
4412 | Environmental/External | Fire- Forest/Grass | Pothead(Riser Termination) | Burned/flashed | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
4413 | Environmental/External | Fire- Forest/Grass | Pothead(Riser Termination) | Deteriorated | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
4414 | Environmental/External | Fire- Forest/Grass | Conductor- Underground | Burned/flashed | All | Underground facilities = no ignition risk
4415 | Environmental/External | Fire- Forest/Grass | Pole-Wood | Deteriorated | Low | A limited number of Poles have been replaced with composite material. We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
4416 | Environmental/External | Fire- Forest/Grass | Conductor- Overhead | On Ground | Medium | SECONDARY IGNITION RISK - Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4417 | Environmental/External | Fire- Forest/Grass | Conductor- Overhead | Deteriorated | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
4418 | Environmental/External | Fire- Forest/Grass | Secondary | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4419 | Environmental/External | Fire- Forest/Grass | Transformer | Blown/failed | High | SECONDARY IGNITION RISK - Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4420 | Environmental/External | Fire- Forest/Grass |  |  | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
4421 | Environmental/External | Fire- Forest/Grass | Transformer (UG) | Broken | All | Underground facilities = no ignition risk
4422 | Environmental/External | Fire- Forest/Grass | Transformer (OH) | Burned/flashed | High | SECONDARY IGNITION RISK - Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4423 | Environmental/External | Fire- Forest/Grass | Secondary | Burned Open | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4424 | Environmental/External | Fire- Forest/Grass | Transformer (UG) | Burned/flashed | All | Underground facilities = no ignition risk
4425 | Environmental/External | Fire- Forest/Grass | Crossarm- Wood | Broken- wire on ground | Medium | SECONDARY IGNITION RISK - Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4426 | Environmental/External | Fire- Forest/Grass | Service conductor | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4427 | Environmental/External | Fire- Forest/Grass | Pole-Wood | Normal | Low | A limited number of Poles have been replaced with composite material. We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
4428 | Environmental/External | Fire- Forest/Grass | Connector or Splice (OH) | Broken- wire on ground | High | SECONDARY IGNITION RISK - Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
4429 | Environmental/External | Fire- Forest/Grass | Transformer (OH) | Leaking | High | SECONDARY IGNITION RISK - Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4430 | Environmental/External | Fire- Forest/Grass | Secondary | Together | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4431 | Environmental/External | Fire- Forest/Grass | Insulator | Burned/flashed | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
4432 | Environmental/External | Fire- Forest/Grass | Regulator | Burned/flashed | None | Significant external force broke the conductor and brought wire to the ground/object. Ignition risk not mitigated.
4433 | Environmental/External | Fire- Forest/Grass | Crossarm- Wood | Broken | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
4434 | Environmental/External | Fire- Forest/Grass | Insulator | Malfunctioning | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
4435 | Environmental/External | Fire- Forest/Grass | Service conductor | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4436 | Environmental/External | Fire- Forest/Grass | Switch (OH) | Normal | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
4437 | Environmental/External | Fire- Forest/Grass | Cutout- Fused- Distribution | Blown/failed | High | SECONDARY IGNITION RISK - Non-exempt fused cutouts are being replaced on System Hardening Projects.
4438 | Environmental/External | Fire- Forest/Grass | Transformer (OH) | Normal | High | SECONDARY IGNITION RISK - Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4439 | Environmental/External | Fire- Forest/Grass | Conductor- Overhead | Contaminated | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
4440 | Environmental/External | Fire- Forest/Grass | Transformer (UG) | Blown/failed | All | Underground facilities = no ignition risk
4441 | Environmental/External | Fire- Forest/Grass | Transformer (OH) | Broken | High | SECONDARY IGNITION RISK - Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4442 | Environmental/External | Fire- Forest/Grass | Pole-Wood | Broken- wire on object | Medium | SECONDARY IGNITION RISK - Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4443 | Environmental/External | Fire- Forest/Grass | Relay | Normal | All | Covered conductor will eliminate "smoke arcing" and risk associated with this outage.
4444 | Environmental/External | Fire- Forest/Grass | Transformer | Burned/flashed | High | SECONDARY IGNITION RISK - Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4445 | Environmental/External | Fire- Forest/Grass | Elbow | Blown/failed | All | Underground facilities = no ignition risk
4446 | Environmental/External | Fire- Forest/Grass | Conductor- Underground | Broken | All | Underground facilities = no ignition risk
4447 | Environmental/External | Fire- Forest/Grass | Service conductor | Burned Open | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4448 | Environmental/External | Fire- Forest/Grass | Footings- Tower or Pole | Burned/flashed | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
4449 | Environmental/External | Fire- Forest/Grass | Jumper | Broken | High | SECONDARY IGNITION RISK - Larger covered conductor to mostly eliminate cause and risk.
4450 | Environmental/External | Fire- Forest/Grass | Switch | Normal | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
4451 | Environmental/External | Fire- Forest/Grass | Transformer | Broken | High | SECONDARY IGNITION RISK - Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4452 | Environmental/External | Fire- Forest/Grass | Riser | Blown/failed | High | SECONDARY IGNITION RISK - Risers are indirectly addressed on System Hardening - Pole changeouts, the covering of jumpers and leads, along with covering conductor should mitigate outages and risk.
4453 | Environmental/External | Fire- Forest/Grass | Woodpin | Burned Open | All | Composite arms are being installed along with new insulators and bonding. Tracking insulators/pole fires will be limited though not 100% eliminate. Gunshot damage will still be a concern. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
4454 | Environmental/External | Fire- Forest/Grass | Recloser | Burned/flashed | None | System Hardening will not mitigate for Environmental factors for this outage.
4455 | Environmental/External | Fire- Forest/Grass | Service conductor | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4456 | Environmental/External | Fire- Forest/Grass | Cutout- fuse holder | Broken | High | SECONDARY IGNITION RISK - Non-exempt fused cutouts are being replaced on System Hardening Projects.
4457 | Environmental/External | Fire- Forest/Grass | Conductor- Underground | Normal | All | Underground facilities = no ignition risk
4458 | Environmental/External | Fire- Forest/Grass | Customer Equipment | Broken | None | System hardening does not address customer equipment
4459 | Environmental/External | Fire- Forest/Grass | Insulator | Contaminated | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
4460 | Environmental/External | Fire- Forest/Grass | Connector or Splice (OH) | Burned Open | High | SECONDARY IGNITION RISK - Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
4461 | Environmental/External | Fire- Forest/Grass | Cutout- fuse holder | Burned Open | High | SECONDARY IGNITION RISK - Non-exempt fused cutouts are being replaced on System Hardening Projects.
4462 | Environmental/External | Fire- Forest/Grass | Transformer | Normal | High | SECONDARY IGNITION RISK - Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4463 | Environmental/External | Fire- Forest/Grass | Secondary | Blown/failed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4464 | Environmental/External | Fire- Forest/Grass | Pole-Wood | Contaminated | Low | A limited number of Poles have been replaced with composite material. We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
4465 | Environmental/External | Fire- Forest/Grass | Connector or Splice (OH) | On Ground | High | SECONDARY IGNITION RISK - Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
4466 | Environmental/External | Fire- Forest/Grass | Jumper | Normal | High | SECONDARY IGNITION RISK - Larger covered conductor to mostly eliminate cause and risk.
4467 | Environmental/External | Fire- Forest/Grass | Regulator | Blown/failed | None | Significant external force broke the conductor and brought wire to the ground/object. Ignition risk not mitigated.
4468 | Environmental/External | Fire- Forest/Grass | Other | Broken- wire on ground | Medium | SECONDARY IGNITION RISK - Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4469 | Environmental/External | Fire- Forest/Grass | Fuse | Burned Open | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk..
4470 | Environmental/External | Fire- Forest/Grass | Connector or Splice (UG) | Normal | All | Underground facilities = no ignition risk
4471 | Environmental/External | Fire- Forest/Grass | Anchor or Guy | Burned/flashed | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
4472 | Environmental/External | Fire- Forest/Grass | Recloser | Broken | None | System Hardening will not mitigate for Environmental factors for this outage.
4473 | Environmental/External | Fire- Forest/Grass | Conductor- Overhead | Burned Open | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
4474 | Environmental/External | Fire- Forest/Grass | Fuse | Burned/flashed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk..
4475 | Environmental/External | Fire- Forest/Grass | Connector or Splice (OH) | Burned/flashed | High | SECONDARY IGNITION RISK - Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
4476 | Environmental/External | Fire- Forest/Grass | Pole - Tower- steel | Broken- wire on ground | Medium | SECONDARY IGNITION RISK - Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4477 | Environmental/External | Fire- Forest/Grass | Insulator | Normal | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
4478 | Environmental/External | Fire- Forest/Grass | Secondary | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4479 | Environmental/External | Fire- Forest/Grass | Customer Equipment | Malfunctioning | None | System hardening does not address customer equipment
4480 | Environmental/External | Fire- Forest/Grass | Transformer (OH) | Deteriorated | High | SECONDARY IGNITION RISK - Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4481 | Environmental/External | Fire- Forest/Grass | Switch | Burned/flashed | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
4482 | Environmental/External | Fire- Forest/Grass | Connector or Splice (OH) | Broken- wire on object | High | SECONDARY IGNITION RISK - Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
4483 | Environmental/External | Fire- Forest/Grass | Lightning Arrestor | Blown/failed | All | We are replacing lightning arrestors with their exempt equivalent.
4484 | Environmental/External | Fire- Forest/Grass | Conductor- Overhead | Annealed | Low | SECONDARY IGNITION RISK - Covered conductor will eliminate the line slap and risk associated with this outage.
4485 | Environmental/External | Flood/Erosion | Pole-Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4486 | Environmental/External | Flood/Erosion | Pole-Wood | Normal | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
4487 | Environmental/External | Flood/Erosion | Pole-Wood | Broken | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
4488 | Environmental/External | Flood/Erosion | Conductor- Overhead | Together | Low | Water and Moisture limit ignition risk
4489 | Environmental/External | Flood/Erosion | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4490 | Environmental/External | Flood/Erosion | Cutout- fuse holder | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
4491 | Environmental/External | Flood/Erosion | Conductor- Overhead | Normal | Low | Water and Moisture limit ignition risk
4492 | Environmental/External | Flood/Erosion | Conductor- Overhead | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4493 | Environmental/External | Flood/Erosion | Fuse | Normal | High | Moisture and Water should eliminate Ignition Risk. Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk..
4494 | Environmental/External | Flood/Erosion | Conductor- Overhead | Broken | Low | Water and Moisture limit ignition risk
4495 | Environmental/External | Flood/Erosion | Pole-Wood | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4496 | Environmental/External | Flood/Erosion | Conductor- Overhead | Bent or Twisted | Low | Water and Moisture limit ignition risk
4497 | Environmental/External | Flood/Erosion | Transformer (OH) | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4498 | Environmental/External | Flood/Erosion | Conductor- Overhead | Arcing | Low | Water and Moisture limit ignition risk
4499 | Environmental/External | Flood/Erosion | Anchor or Guy | Broken | Low | Water and Moisture limit ignition risk
4500 | Environmental/External | Flood/Erosion | Conductor- Underground | Normal | All | Underground facilities = no ignition risk
4501 | Environmental/External | Flood/Erosion | Conductor- Overhead | Deteriorated | Low | Water and Moisture limit ignition risk
4502 | Environmental/External | Flood/Erosion | Pole-Wood | Deteriorated | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
4503 | Environmental/External | Flood/Erosion | Switch (UG) | Normal | All | Underground facilities = no ignition risk
4504 | Environmental/External | Flood/Erosion | Switch (UG) | Burned/flashed | All | Underground facilities = no ignition risk
4505 | Environmental/External | Flood/Erosion | Insulator | Burned/flashed | Low | Water and Moisture limit ignition risk
4506 | Environmental/External | Flood/Erosion | Transformer (UG) | Normal | All | Underground facilities = no ignition risk
4507 | Environmental/External | Flood/Erosion | Fuse | Blown/failed | High | Moisture and Water should eliminate Ignition Risk. Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk..
4508 | Environmental/External | Flood/Erosion | Transformer | Deteriorated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4509 | Environmental/External | Flood/Erosion | Crossarm- Wood | Broken | Low | Water and Moisture limit ignition risk
4510 | Environmental/External | Flood/Erosion | Pole-Wood | Contaminated | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
4511 | Environmental/External | Flood/Erosion | Customer Equipment | Normal | None | System hardening does not address customer equipment
4512 | Environmental/External | Flood/Erosion | Connector or Splice (UG) | Deteriorated | All | Underground facilities = no ignition risk
4513 | Environmental/External | Flood/Erosion | Other | Normal | Low | Water and Moisture limit ignition risk
4514 | Environmental/External | Flood/Erosion | Conductor- Underground | Contaminated | All | Underground facilities = no ignition risk
4515 | Environmental/External | Flood/Erosion | Customer Equipment | Contaminated | None | System hardening does not address customer equipment
4516 | Environmental/External | Flood/Erosion | Conductor- Underground | Broken | All | Underground facilities = no ignition risk
4517 | Environmental/External | Flood/Erosion | Conductor- Overhead | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4518 | Environmental/External | Flood/Erosion | Switch (OH) | Normal | Low | Water and Moisture limit ignition risk
4519 | Environmental/External | Flood/Erosion | Other | Arcing | Low | Water and Moisture limit ignition risk
4520 | Environmental/External | Flood/Erosion | Other | Deteriorated | Low | Water and Moisture limit ignition risk
4521 | Environmental/External | Flood/Erosion | Conductor- Overhead | Burned/flashed | Low | Water and Moisture limit ignition risk
4522 | Environmental/External | Flood/Erosion | Connector or Splice (UG) | Burned/flashed | All | Underground facilities = no ignition risk
4523 | Environmental/External | Flood/Erosion | Crossarm- Wood | Deteriorated | Low | Water and Moisture limit ignition risk
4524 | Environmental/External | Flood/Erosion | Pole - Tower- steel | Deteriorated | Low | Water and Moisture limit ignition risk
4525 | Environmental/External | Flood/Erosion | Transformer | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4526 | Environmental/External | Flood/Erosion | Metering Equipment | Normal | None | System Hardening does not address Metering facilities.
4527 | Environmental/External | Flood/Erosion | Transformer (OH) | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4528 | Environmental/External | Flood/Erosion | Connector or Splice (OH) | Burned Open | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
4529 | Environmental/External | Flood/Erosion | Service conductor | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4530 | Environmental/External | Flood/Erosion | Transformer (UG) | Contaminated | All | Underground facilities = no ignition risk
4531 | Environmental/External | Flood/Erosion | Transformer (UG) | Broken | All | Underground facilities = no ignition risk
4532 | Environmental/External | Flood/Erosion | Jumper | Burned Open | High | Larger covered conductor to mostly eliminate cause and risk.
4533 | Environmental/External | Flood/Erosion | Transformer | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4534 | Environmental/External | Flood/Erosion | Anchor or Guy | Deteriorated | Low | Water and Moisture limit ignition risk
4535 | Environmental/External | Flood/Erosion | Switch | Broken | Low | Water and Moisture limit ignition risk
4536 | Environmental/External | Flood/Erosion | Secondary | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4537 | Environmental/External | Ice or snow | Conductor- Overhead | Normal | All | Ice and Snow conditions should have no ignition risk.
4538 | Environmental/External | Ice or snow | Service conductor | Broken- wire on ground | All | Ice and Snow conditions should have no ignition risk.
4539 | Environmental/External | Ice or snow | Crossarm- Wood | Broken | All | Ice and Snow conditions should have no ignition risk.
4540 | Environmental/External | Ice or snow | Conductor- Overhead | On Ground | All | Ice and Snow conditions should have no ignition risk.
4541 | Environmental/External | Ice or snow | Conductor- Overhead | Broken- wire on ground | All | Ice and Snow conditions should have no ignition risk.
4542 | Environmental/External | Ice or snow | Conductor- Overhead | Together | All | Ice and Snow conditions should have no ignition risk.
4543 | Environmental/External | Ice or snow | Recloser | Normal | All | Ice and Snow conditions should have no ignition risk.
4544 | Environmental/External | Ice or snow | Insulator | Broken | All | Ice and Snow conditions should have no ignition risk.
4545 | Environmental/External | Ice or snow | Pole-Wood | Broken- wire on ground | All | Ice and Snow conditions should have no ignition risk.
4546 | Environmental/External | Ice or snow | Pole-Wood | Broken- wire on object | All | Ice and Snow conditions should have no ignition risk.
4547 | Environmental/External | Ice or snow | Fuse | Blown/failed | All | Ice and Snow conditions should have no ignition risk.
4548 | Environmental/External | Ice or snow | Transformer (OH) | Blown/failed | All | Ice and Snow conditions should have no ignition risk.
4549 | Environmental/External | Ice or snow | Conductor- Overhead | Bent or Twisted | All | Ice and Snow conditions should have no ignition risk.
4550 | Environmental/External | Ice or snow | Connector or Splice (OH) | Broken- wire on ground | All | Ice and Snow conditions should have no ignition risk.
4551 | Environmental/External | Ice or snow | Insulator | Broken- wire on object | All | Ice and Snow conditions should have no ignition risk.
4552 | Environmental/External | Ice or snow | Conductor- Overhead | Broken | All | Ice and Snow conditions should have no ignition risk.
4553 | Environmental/External | Ice or snow | Crossarm- Wood | Broken- wire on ground | All | Ice and Snow conditions should have no ignition risk.
4554 | Environmental/External | Ice or snow | Fuse | Normal | All | Ice and Snow conditions should have no ignition risk.
4555 | Environmental/External | Ice or snow | Transformer | Broken | All | Ice and Snow conditions should have no ignition risk.
4556 | Environmental/External | Ice or snow | Transformer | Blown/failed | All | Ice and Snow conditions should have no ignition risk.
4557 | Environmental/External | Ice or snow | Connector or Splice (OH) | Broken | All | Ice and Snow conditions should have no ignition risk.
4558 | Environmental/External | Ice or snow | Pole-Wood | Broken | All | Ice and Snow conditions should have no ignition risk.
4559 | Environmental/External | Ice or snow | Conductor- Overhead | Arcing | All | Ice and Snow conditions should have no ignition risk.
4560 | Environmental/External | Ice or snow | Secondary | Deteriorated | All | Ice and Snow conditions should have no ignition risk.
4561 | Environmental/External | Ice or snow | Service conductor | Broken | All | Ice and Snow conditions should have no ignition risk.
4562 | Environmental/External | Ice or snow | Secondary | Broken- wire on ground | All | Ice and Snow conditions should have no ignition risk.
4563 | Environmental/External | Ice or snow | Other | Broken | All | Ice and Snow conditions should have no ignition risk.
4564 | Environmental/External | Ice or snow | Conductor- Overhead | Broken- wire on object | All | Ice and Snow conditions should have no ignition risk.
4565 | Environmental/External | Ice or snow |  |  | All | Ice and Snow conditions should have no ignition risk.
4566 | Environmental/External | Ice or snow | Jumper | Broken | All | Ice and Snow conditions should have no ignition risk.
4567 | Environmental/External | Ice or snow | Conductor- Overhead | Burned/flashed | All | Ice and Snow conditions should have no ignition risk.
4568 | Environmental/External | Ice or snow |  | Blown/failed | All | Ice and Snow conditions should have no ignition risk.
4569 | Environmental/External | Ice or snow | Transformer | Normal | All | Ice and Snow conditions should have no ignition risk.
4570 | Environmental/External | Ice or snow | Transformer (UG) | Broken | All | Underground facilities = no ignition risk
4571 | Environmental/External | Ice or snow | Crossarm- Wood | Broken- wire on object | All | Ice and Snow conditions should have no ignition risk.
4572 | Environmental/External | Ice or snow | Other | Annealed | All | Ice and Snow conditions should have no ignition risk.
4573 | Environmental/External | Ice or snow | Insulator | Broken- wire on ground | All | Ice and Snow conditions should have no ignition risk.
4574 | Environmental/External | Ice or snow | Connector or Splice (OH) | Normal | All | Ice and Snow conditions should have no ignition risk.
4575 | Environmental/External | Ice or snow | Secondary | Broken | All | Ice and Snow conditions should have no ignition risk.
4576 | Environmental/External | Lightning | Recloser | Burned/flashed | None | System Hardening will not mitigate for Environmental factors for this outage.
4577 | Environmental/External | Lightning | Transformer | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4578 | Environmental/External | Lightning | Circuit Breaker | Malfunctioning | None | System Hardening will not mitigate for Environmental factors for this outage.
4579 | Environmental/External | Lightning | Lightning Arrestor | Burned/flashed | All | We are replacing lightning arrestors with their exempt equivalent.
4580 | Environmental/External | Lightning | Transformer (OH) | Burned/flashed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4581 | Environmental/External | Lightning | Transformer (OH) | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4582 | Environmental/External | Lightning | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk..
4583 | Environmental/External | Lightning |  | Blown/failed | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
4584 | Environmental/External | Lightning | Transformer | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4585 | Environmental/External | Lightning | Transformer (OH) | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4586 | Environmental/External | Lightning | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4587 | Environmental/External | Lightning | Switch | Broken | None | System Hardening will not mitigate for Environmental factors for this outage.
4588 | Environmental/External | Lightning | Conductor- Overhead | Normal | None | System Hardening will not mitigate for Environmental factors for this outage.
4589 | Environmental/External | Lightning | Pothead/Riser Termination | Blown/failed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
4590 | Environmental/External | Lightning | Other | Blown/failed | None | System Hardening will not mitigate for Environmental factors for this outage.
4591 | Environmental/External | Lightning | Cutout- fuse holder | Burned/flashed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
4592 | Environmental/External | Lightning | Transformer (UG) | Blown/failed | All | Underground facilities = no ignition risk
4593 | Environmental/External | Lightning |  |  | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
4594 | Environmental/External | Lightning | Transformer (OH) | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4595 | Environmental/External | Lightning | Transformer (UG) | Broken | All | Underground facilities = no ignition risk
4596 | Environmental/External | Lightning | Other | Broken | None | System Hardening will not mitigate for Environmental factors for this outage.
4597 | Environmental/External | Lightning | Transformer (UG) | Burned/flashed | All | Underground facilities = no ignition risk
4598 | Environmental/External | Lightning | Connector or Splice (OH) | Broken- wire on ground | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
4599 | Environmental/External | Lightning | Fuse | Normal | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk..
4600 | Environmental/External | Lightning | Recloser | Normal | None | System Hardening will not mitigate for Environmental factors for this outage.
4601 | Environmental/External | Lightning | Conductor- Overhead | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4602 | Environmental/External | Lightning | Insulator | Broken | None | System Hardening will not mitigate for Environmental factors for this outage.
4603 | Environmental/External | Lightning | Conductor- Overhead | Burned/flashed | None | System Hardening will not mitigate for Environmental factors for this outage.
4604 | Environmental/External | Lightning | Pole-Wood | Burned/flashed | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
4605 | Environmental/External | Lightning | Conductor- Overhead | Blown/failed | None | System Hardening will not mitigate for Environmental factors for this outage.
4606 | Environmental/External | Lightning | Transformer | Burned/flashed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4607 | Environmental/External | Lightning | Pothead(Riser Termination) | Burned/flashed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
4608 | Environmental/External | Lightning | Lightning Arrestor | Blown/failed | All | We are replacing lightning arrestors with their exempt equivalent.
4609 | Environmental/External | Lightning | Conductor- Underground | Burned Open | All | Underground facilities = no ignition risk
4610 | Environmental/External | Lightning | Transformer | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4611 | Environmental/External | Lightning | Transformer | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4612 | Environmental/External | Lightning | Capacitor | Burned/flashed | None | System Hardening will not mitigate for Environmental factors for this outage.
4613 | Environmental/External | Lightning | Transformer (OH) | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4614 | Environmental/External | Lightning | Transformer | Burned Open | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4615 | Environmental/External | Lightning | Transformer | Malfunctioning | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4616 | Environmental/External | Lightning | Conductor- Underground | Burned/flashed | All | Underground facilities = no ignition risk
4617 | Environmental/External | Lightning | Fuse | Burned Open | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk..
4618 | Environmental/External | Lightning | Crossarm- Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4619 | Environmental/External | Lightning | Crossarm- Wood | Broken | None | System Hardening will not mitigate for Environmental factors for this outage.
4620 | Environmental/External | Lightning | Transformer | Deteriorated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4621 | Environmental/External | Lightning | Jumper | Broken | High | Larger covered conductor to mostly eliminate cause and risk.
4622 | Environmental/External | Lightning | Conductor- Overhead | Broken | None | System Hardening will not mitigate for Environmental factors for this outage.
4623 | Environmental/External | Lightning | Crossarm- Wood | Burned/flashed | None | System Hardening will not mitigate for Environmental factors for this outage.
4624 | Environmental/External | Lightning | Transformer | Contaminated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4625 | Environmental/External | Lightning | Pole-Wood | Broken | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
4626 | Environmental/External | Lightning | Jumper | Burned Open | High | Larger covered conductor to mostly eliminate cause and risk.
4627 | Environmental/External | Lightning | Circuit Breaker | Normal | All | Covered conductor will eliminate the line slap and risk/smoke arc associated with this outage.
4628 | Environmental/External | Lightning | Jumper | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4629 | Environmental/External | Lightning | Regulator | Burned/flashed | None | Significant external force broke the conductor and brought wire to the ground/object. Ignition risk not mitigated.
4630 | Environmental/External | Lightning | Insulator | Burned/flashed | None | System Hardening will not mitigate for Environmental factors for this outage.
4631 | Environmental/External | Lightning | Fuse | Burned/flashed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk..
4632 | Environmental/External | Lightning | Pole-Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4633 | Environmental/External | Lightning | Insulator | Blown/failed | None | System Hardening will not mitigate for Environmental factors for this outage.
4634 | Environmental/External | Lightning | Anchor or Guy | Broken | None | System Hardening will not mitigate for Environmental factors for this outage.
4635 | Environmental/External | Lightning | Booster | Blown/failed | None | System Hardening will not mitigate for Environmental factors for this outage.
4636 | Environmental/External | Lightning | Conductor- Overhead | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4637 | Environmental/External | Lightning | Regulator | Blown/failed | None | Significant external force broke the conductor and brought wire to the ground/object. Ignition risk not mitigated.
4638 | Environmental/External | Lightning | Recloser | Blown/failed | None | System Hardening will not mitigate for Environmental factors for this outage.
4639 | Environmental/External | Lightning | Pole-Wood | Normal | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
4640 | Environmental/External | Lightning | Connector or Splice (OH) | Burned Open | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
4641 | Environmental/External | Lightning |  | Normal | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
4642 | Environmental/External | Lightning | Fuse | Broken | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk..
4643 | Environmental/External | Lightning | Pothead(Riser Termination) | Blown/failed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
4644 | Environmental/External | Lightning | Crossarm- Steel | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4645 | Environmental/External | Lightning | Switch (OH) | Blown/failed | None | System Hardening will not mitigate for Environmental factors for this outage.
4646 | Environmental/External | Lightning | Switch | Blown/failed | None | System Hardening will not mitigate for Environmental factors for this outage.
4647 | Environmental/External | Lightning | Cutout- fuse holder | Broken | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
4648 | Environmental/External | Lightning | Bushing | Broken | None | System Hardening will not mitigate for Environmental factors for this outage.
4649 | Environmental/External | Lightning | Transformer | Arcing | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4650 | Environmental/External | Lightning | Capacitor | Blown/failed | None | System Hardening will not mitigate for Environmental factors for this outage.
4651 | Environmental/External | Lightning | Metering Equipment | Burned/flashed | None | System Hardening does not address Metering facilities.
4652 | Environmental/External | Lightning | Transformer |  | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
4653 | Environmental/External | Lightning | Cutout- fuse holder | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
4654 | Environmental/External | Lightning | Customer Equipment | Burned/flashed | None | System hardening does not address customer equipment
4655 | Environmental/External | Lightning | PGs- Kearneys | Broken- wire on ground | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
4656 | Environmental/External | Lightning | Secondary | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4657 | Environmental/External | Lightning | Cutout- fuse holder | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4658 | Environmental/External | Lightning | Secondary | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4659 | Environmental/External | Lightning |  | Burned Open | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
4660 | Environmental/External | Lightning | Other | Normal | None | System Hardening will not mitigate for Environmental factors for this outage.
4661 | Environmental/External | Lightning | Recloser | Malfunctioning | None | System Hardening will not mitigate for Environmental factors for this outage.
4662 | Environmental/External | Lightning | Transformer (OH) | Deteriorated | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4663 | Environmental/External | Lightning |  | Broken | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
4664 | Environmental/External | Lightning | Lightning Arrestor | Broken | All | We are replacing lightning arrestors with their exempt equivalent.
4665 | Environmental/External | Lightning | Customer Equipment | Blown/failed | None | System hardening does not address customer equipment
4666 | Environmental/External | Lightning | Transformer | Leaking | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4667 | Environmental/External | Lightning | Bushing | Blown/failed | None | System Hardening will not mitigate for Environmental factors for this outage.
4668 | Environmental/External | Lightning | Street Light Equipment | Blown/failed | Medium | System Hardening will not address Street Lights but will address their transformers.
4669 | Environmental/External | Lightning | Cutout- Fused- Distribution | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
4670 | Environmental/External | Lightning | Connector or Splice (UG) | Blown/failed | All | Underground facilities = no ignition risk
4671 | Environmental/External | Lightning | Splice box | Burned/flashed | All | Underground facilities = no ignition risk
4672 | Environmental/External | Lightning | Recloser | Broken | None | System Hardening will not mitigate for Environmental factors for this outage.
4673 | Environmental/External | Lightning | Stepdown | Blown/failed | None | System Hardening will not mitigate for Environmental factors for this outage.
4674 | Environmental/External | Lightning | Transformer (UG) | Deteriorated | All | Underground facilities = no ignition risk
4675 | Environmental/External | Lightning | Splice box | Malfunctioning | All | Underground facilities = no ignition risk
4676 | Environmental/External | Lightning | Conductor- Overhead | Together | None | System Hardening will not mitigate for Environmental factors for this outage.
4677 | Environmental/External | Lightning | Switch (OH) | Burned/flashed | None | System Hardening will not mitigate for Environmental factors for this outage.
4678 | Environmental/External | Lightning | Cutout- fuse holder | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
4679 | Environmental/External | Lightning | Transformer (OH) | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4680 | Environmental/External | Lightning | Bushing | Burned/flashed | None | System Hardening will not mitigate for Environmental factors for this outage.
4681 | Environmental/External | Lightning | Transformer (OH) |  | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4682 | Environmental/External | Lightning | Sectionalizer | Broken | None | System Hardening will not mitigate for Environmental factors for this outage.
4683 | Environmental/External | Lightning | Cutout- fuse holder | Arcing | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
4684 | Environmental/External | Lightning | Switch (UG) | Blown/failed | All | Underground facilities = no ignition risk
4685 | Environmental/External | Lightning | Other | Burned/flashed | None | System Hardening will not mitigate for Environmental factors for this outage.
4686 | Environmental/External | Lightning | Fuse | Malfunctioning | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk..
4687 | Environmental/External | Lightning | Capacitor | Arcing | None | System Hardening will not mitigate for Environmental factors for this outage.
4688 | Environmental/External | Lightning | Conductor- Overhead | Malfunctioning | None | System Hardening will not mitigate for Environmental factors for this outage.
4689 | Environmental/External | Lightning | Insulator | Arcing | None | System Hardening will not mitigate for Environmental factors for this outage.
4690 | Environmental/External | Lightning | Conductor- Overhead | Burned Open | None | System Hardening will not mitigate for Environmental factors for this outage.
4691 | Environmental/External | Lightning | Connector or Splice (UG) | Burned/flashed | All | Underground facilities = no ignition risk
4692 | Environmental/External | Lightning | Service conductor | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4693 | Environmental/External | Lightning | Elbow | Blown/failed | All | Underground facilities = no ignition risk
4694 | Environmental/External | Lightning | Pothead(Riser Termination) | Normal | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
4695 | Environmental/External | Lightning | Jumper | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4696 | Environmental/External | Lightning | Fuse | Arcing | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk..
4697 | Environmental/External | Lightning | Crossarm- Steel | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4698 | Environmental/External | Lightning | Conductor- Overhead | Arcing | None | System Hardening will not mitigate for Environmental factors for this outage.
4699 | Environmental/External | Lightning | Jumper | Burned/flashed | High | Larger covered conductor to mostly eliminate cause and risk.
4700 | Environmental/External | Lightning | Other | Malfunctioning | None | System Hardening will not mitigate for Environmental factors for this outage.
4701 | Environmental/External | Lightning | Connector or Splice (OH) | Broken | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
4702 | Environmental/External | Lightning | Other | Bent or Twisted | None | System Hardening will not mitigate for Environmental factors for this outage.
4703 | Environmental/External | Lightning | Regulator | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4704 | Environmental/External | Lightning | Pothead/Riser Termination | Burned Open | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
4705 | Environmental/External | Lightning | Service conductor | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4706 | Environmental/External | Lightning | Secondary | Burned Open | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4707 | Environmental/External | Lightning | Sectionalizer | Normal | None | System Hardening will not mitigate for Environmental factors for this outage.
4708 | Environmental/External | Lightning | Secondary | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4709 | Environmental/External | Lightning | Lightning Arrestor | Arcing | All | We are replacing lightning arrestors with their exempt equivalent.
4710 | Environmental/External | Water | Conductor- Underground | Contaminated | All | Underground facilities = no ignition risk
4711 | Environmental/External | Water | Transformer | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4712 | Environmental/External | Water | Transformer (UG) | Normal | All | Underground facilities = no ignition risk
4713 | Environmental/External | Water | Connector or Splice (UG) | Blown/failed | All | Underground facilities = no ignition risk
4714 | Environmental/External | Water | Conductor- Overhead | Normal | Low | Assume Water Supplemental Cause is a duplicate of Floor/Erosion Supplemental Cause. Water and Moisture limit ignition risk
4715 | Environmental/External | Water | Transformer | Burned Open | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4716 | Environmental/External | Water | Crossarm- Wood | Burned Open | Low | Assume Water Supplemental Cause is a duplicate of Floor/Erosion Supplemental Cause. Water and Moisture limit ignition risk
4717 | Environmental/External | Water | Transformer | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4718 | Environmental/External | Water | Transformer (OH) | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4719 | Environmental/External | Water | Recloser | Normal | Low | Assume Water Supplemental Cause is a duplicate of Floor/Erosion Supplemental Cause. Water and Moisture limit ignition risk
4720 | Environmental/External | Water | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4721 | Environmental/External | Water | Transformer | Blown/failed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4722 | Environmental/External | Water | Crossarm- Wood | Burned/flashed | Low | Assume Water Supplemental Cause is a duplicate of Floor/Erosion Supplemental Cause. Water and Moisture limit ignition risk
4723 | Environmental/External | Water | Elbow | Blown/failed | All | Underground facilities = no ignition risk
4724 | Environmental/External | Water | Transformer | Malfunctioning | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4725 | Environmental/External | Water | Secondary | Burned/flashed | Low | Assume Water Supplemental Cause is a duplicate of Floor/Erosion Supplemental Cause. Water and Moisture limit ignition risk
4726 | Environmental/External | Water | Conductor- Underground | Normal | All | Underground facilities = no ignition risk
4727 | Environmental/External | Water | Fuse | Blown/failed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk..
4728 | Environmental/External | Water | Pole-Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4729 | Environmental/External | Water | Conductor- Underground | Burned/flashed | All | Underground facilities = no ignition risk
4730 | Environmental/External | Water | Connector or Splice (UG) | Contaminated | All | Underground facilities = no ignition risk
4731 | Environmental/External | Water | Conductor- Overhead | Together | Low | Assume Water Supplemental Cause is a duplicate of Floor/Erosion Supplemental Cause. Water and Moisture limit ignition risk
4732 | Environmental/External | Water | Other | Leaking | Low | Assume Water Supplemental Cause is a duplicate of Floor/Erosion Supplemental Cause. Water and Moisture limit ignition risk
4733 | Environmental/External | Water | Jumper | Broken | High | Larger covered conductor to mostly eliminate cause and risk.
4734 | Environmental/External | Water | Cutout- fuse holder | Broken | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
4735 | Environmental/External | Water | Insulator | Blown/failed | Low | Assume Water Supplemental Cause is a duplicate of Floor/Erosion Supplemental Cause. Water and Moisture limit ignition risk
4736 | Environmental/External | Water | Insulator | Broken | Low | Assume Water Supplemental Cause is a duplicate of Floor/Erosion Supplemental Cause. Water and Moisture limit ignition risk
4737 | Environmental/External | Water | Pole-Wood | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4738 | Environmental/External | Water | Elbow | Burned/flashed | All | Underground facilities = no ignition risk
4739 | Environmental/External | Water | Pothead/Riser Termination | Contaminated | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
4740 | Environmental/External | Water | Switch (UG) | Burned/flashed | All | Underground facilities = no ignition risk
4741 | Environmental/External | Water | Pole-Wood | Burned/flashed | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
4742 | Environmental/External | Water | Insulator | Arcing | Low | Assume Water Supplemental Cause is a duplicate of Floor/Erosion Supplemental Cause. Water and Moisture limit ignition risk
4743 | Environmental/External | Water | Connector or Splice (UG) | Burned Open | All | Underground facilities = no ignition risk
4744 | Environmental/External | Water | Secondary | Normal | Low | Assume Water Supplemental Cause is a duplicate of Floor/Erosion Supplemental Cause. Water and Moisture limit ignition risk
4745 | Environmental/External | Water | Switch | Blown/failed | Low | Assume Water Supplemental Cause is a duplicate of Floor/Erosion Supplemental Cause. Water and Moisture limit ignition risk
4746 | Environmental/External | Water | Connector or Splice (OH) | Burned Open | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
4747 | Environmental/External | Water | Pole-Wood | Normal | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
4748 | Environmental/External | Water | Pole-Wood | Broken | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
4749 | Environmental/External | Water | Conductor- Overhead | Contaminated | Low | Assume Water Supplemental Cause is a duplicate of Floor/Erosion Supplemental Cause. Water and Moisture limit ignition risk
4750 | Environmental/External | Water | Transformer (UG) | Blown/failed | All | Underground facilities = no ignition risk
4751 | Environmental/External | Water | Connector or Splice (OH) | Contaminated | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
4752 | Environmental/External | Water | Transformer (UG) | Leaking | All | Underground facilities = no ignition risk
4753 | Environmental/External | Water | Pole-Wood | Deteriorated | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
4754 | Environmental/External | Water | Connector or Splice (OH) | Broken- wire on ground | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
4755 | Environmental/External | Water | Transformer (UG) | Contaminated | All | Underground facilities = no ignition risk
4756 | Environmental/External | Water | Customer Equipment | Normal | None | System hardening does not address customer equipment
4757 | Equipment Failure/Involved | Electrical Overload | Connector or Splice (UG) | Burned Open | All | Underground facilities = no ignition risk
4758 | Equipment Failure/Involved | Electrical Overload | Cutout- fuse holder | Burned Open | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
4759 | Equipment Failure/Involved | Electrical Overload | PGs- Kearneys | Contaminated | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
4760 | Equipment Failure/Involved | Electrical Overload | Conductor- Underground | Burned Open | All | Underground facilities = no ignition risk
4761 | Equipment Failure/Involved | Electrical Overload | Customer Equipment | Broken | None | No work is being completed on customer equipment.
4762 | Equipment Failure/Involved | Electrical Overload | Fuse | Malfunctioning | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
4763 | Equipment Failure/Involved | Electrical Overload | Connector or Splice (OH) | Annealed | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
4764 | Equipment Failure/Involved | Electrical Overload | Cutout- Fused- Distribution | Burned Open | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
4765 | Equipment Failure/Involved | Electrical Overload | Elbow | Normal | All | Underground facilities = no ignition risk
4766 | Equipment Failure/Involved | Electrical Overload | Service conductor | Bent or Twisted | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4767 | Equipment Failure/Involved | Electrical Overload | Connector or Splice (UG) | Burned/flashed | All | Underground facilities = no ignition risk
4768 | Equipment Failure/Involved | Electrical Overload | Connector or Splice (UG) | Blown/failed | All | Underground facilities = no ignition risk
4769 | Equipment Failure/Involved | Electrical Overload | Connector or Splice (OH) | Broken- wire on object | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
4770 | Equipment Failure/Involved | Electrical Overload | Cutout- Fused- Distribution | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
4771 | Equipment Failure/Involved | Electrical Overload | Pothead/Riser Termination | Blown/failed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
4772 | Equipment Failure/Involved | Electrical Overload | Connector or Splice (UG) | Deteriorated | All | Underground facilities = no ignition risk
4773 | Equipment Failure/Involved | Electrical Overload | Secondary | Malfunctioning | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4774 | Equipment Failure/Involved | Electrical Overload | Cutout- Fused- Distribution | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
4775 | Equipment Failure/Involved | Electrical Overload | Elbow | Burned/flashed | All | Underground facilities = no ignition risk
4776 | Equipment Failure/Involved | Electrical Overload | Bus | Burned Open | High | Transformers installed prior to 2014 will be replaced. Work would include covering jumpers and replacing some of the service conductor.
4777 | Equipment Failure/Involved | Electrical Overload | Secondary | Contaminated | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4778 | Equipment Failure/Involved | Electrical Overload | Pothead/Riser Termination | Burned/flashed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
4779 | Equipment Failure/Involved | Electrical Overload | Controls | Broken | None | System hardening project will not typically address controls.
4780 | Equipment Failure/Involved | Electrical Overload | Pole-Wood | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4781 | Equipment Failure/Involved | Fire- pole | Crossarm- Wood | Burned Open | High | Composite arms are being installed along with new insulators and bonding. Tracking insulators/pole fires will be limited though not 100% eliminate. Gunshot damage will still be a concern. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
4782 | Equipment Failure/Involved | Fire- pole | Pothead/Riser Termination | Burned/flashed | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
4783 | Equipment Failure/Involved | Fire- pole | Lightning Arrestor | Arcing | All | We are replacing lightning arrestors with their exempt equivalent. Covered conductor will eliminate the line slap and risk associated with this outage.
4784 | Equipment Failure/Involved | Fire- pole | Fuse | Malfunctioning | All | Composite arms are being installed along with new insulators and bonding. Tracking insulators/pole fires will be limited though not 100% eliminate. Gunshot damage will still be a concern. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
4785 | Equipment Failure/Involved | Fire- pole | Crossarm- Wood | Together | High | Composite arms are being installed along with new insulators and bonding. Tracking insulators/pole fires will be limited though not 100% eliminate. Gunshot damage will still be a concern. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
4786 | Equipment Failure/Involved | Fire- pole | Transformer | Malfunctioning | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
4787 | Equipment Failure/Involved | Fire- pole | Pole - Tower- steel | Burned Open | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
4788 | Equipment Failure/Involved | Fire- pole | Cutout- fuse holder | Burned Open | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
4789 | Equipment Failure/Involved | Fire- pole | Transformer |  | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
4790 | Equipment Failure/Involved | Fire- pole | Cutout- fuse holder | Arcing | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
4791 | Equipment Failure/Involved | Fire- pole | Switch | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4792 | Equipment Failure/Involved | Fire- pole | Conductor- Overhead | Burned Open | None | Circuit Hardening will only mitigate pole fires associated with new composite crossarms.
4793 | Equipment Failure/Involved | Other | Cutout- Fused- Distribution | Burned Open | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
4794 | Equipment Failure/Involved | Other | Secondary | Broken- wire on object | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4795 | Equipment Failure/Involved | Other | Conductor- Overhead | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4796 | Equipment Failure/Involved | Other | Pole-Wood | Together | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
4797 | Equipment Failure/Involved | Other | Cutout- Fused- Distribution | Malfunctioning | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
4798 | Equipment Failure/Involved | Other | Switch | Burned Open | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4799 | Equipment Failure/Involved | Other | Anchor or Guy | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4800 | Equipment Failure/Involved | Other | Conductor- Underground | Arcing | All | Underground facilities = no ignition risk
4801 | Equipment Failure/Involved | Other | Sectionalizer | Malfunctioning | Medium | System Hardening does not address Reclosers/Sectionalizers but coverered conductor will reduce annual recloser operations.
4802 | Equipment Failure/Involved | Other | Anchor or Guy | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4803 | Equipment Failure/Involved | Other | Secondary | Bent or Twisted | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4804 | Equipment Failure/Involved | Other | Riser | Burned Open | High | Risers are indirectly addressed on System Hardening - Pole changeouts, the covering of jumpers and leads, along with covering conductor should mitigate outages and risk.
4805 | Equipment Failure/Involved | Other | Connector or Splice (OH) | Blown/failed | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
4806 | Equipment Failure/Involved | Other | Cutout- Fused- Distribution | Contaminated | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
4807 | Equipment Failure/Involved | Other | Recloser | Normal | Medium | System Hardening does not address Reclosers but coverered conductor will reduce annual recloser operations.
4808 | Equipment Failure/Involved | Other | Jumper | Together | High | Larger covered conductor to mostly eliminate cause and risk.
4809 | Equipment Failure/Involved | Other | Sectionalizer | Burned/flashed | Medium | System Hardening does not address Reclosers/Sectionalizers but coverered conductor will reduce annual recloser operations.
4810 | Equipment Failure/Involved | Other | Pole-Wood | Malfunctioning | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
4811 | Equipment Failure/Involved | Other | Booster | Blown/failed | All | Circuit Hardening replaces boosters with voltage regulators.
4812 | Equipment Failure/Involved | Other | Capacitor | Burned Open | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
4813 | Equipment Failure/Involved | Other | Elbow | Deteriorated | All | Underground facilities = no ignition risk
4814 | Equipment Failure/Involved | Other | Riser | Burned/flashed | High | Risers are indirectly addressed on System Hardening - Pole changeouts, the covering of jumpers and leads, along with covering conductor should mitigate outages and risk.
4815 | Equipment Failure/Involved | Other | Other | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4816 | Equipment Failure/Involved | Other | Customer Equipment | Together | None | No work is being completed on customer equipment.
4817 | Equipment Failure/Involved | Other | Switch | Deteriorated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4818 | Equipment Failure/Involved | Other | Connector or Splice (OH) | Annealed | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
4819 | Equipment Failure/Involved | Other | Anchor or Guy | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4820 | Equipment Failure/Involved | Other | Connector or Splice (OH) | Normal | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
4821 | Equipment Failure/Involved | Other | Bus | Burned Open | High | Transformers installed prior to 2014 will be replaced. Work would include covering jumpers and replacing some of the service conductor.
4822 | Equipment Failure/Involved | Other | Conductor- Underground | Annealed | All | Underground facilities = no ignition risk
4823 | Equipment Failure/Involved | Other | Transformer | Annealed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4824 | Equipment Failure/Involved | Other | Pothead/Riser Termination | Deteriorated | HIgh | Pothead failure by Force/Impact or Fault will be mitigated by System Hardening.
4825 | Equipment Failure/Involved | Other | Crossarm- Wood | Normal | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
4826 | Equipment Failure/Involved | Other | Transformer | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4827 | Equipment Failure/Involved | Other | PGs- Kearneys | Burned Open | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
4828 | Equipment Failure/Involved | Other | Relay | Malfunctioning | None | Circuit Hardening will not affect substation equipment.
4829 | Equipment Failure/Involved | Other | Recloser | Blown/failed | Medium | System Hardening does not address Reclosers but coverered conductor will reduce annual recloser operations.
4830 | Equipment Failure/Involved | Other | Metering Equipment | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4831 | Equipment Failure/Involved | Other | Insulator | Normal | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
4832 | Equipment Failure/Involved | Other | Fuse | Contaminated | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
4833 | Equipment Failure/Involved | Other | Transformer | Together | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4834 | Equipment Failure/Involved | Other | Booster | Deteriorated | All | Circuit Hardening replaces boosters with voltage regulators.
4835 | Equipment Failure/Involved | Other | Elbow | Normal | All | Underground facilities = no ignition risk
4836 | Equipment Failure/Involved | Other | Anchor or Guy | Malfunctioning | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4837 | Equipment Failure/Involved | Other | Recloser | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4838 | Equipment Failure/Involved | Other | Relay | Burned/flashed | None | Circuit Hardening will not affect substation equipment.
4839 | Equipment Failure/Involved | Other | Woodpin | Broken- wire on object | None | Significant external force broke the conductor and brought wire to the ground/object. Ignition risk not mitigated.
4840 | Equipment Failure/Involved | Other |  | Arcing | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
4841 | Equipment Failure/Involved | Other | Manhole- primary box | Blown/failed | All | Underground facilities = no ignition risk
4842 | Equipment Failure/Involved | Other | Jumper | Leaking | High | Larger covered conductor to mostly eliminate cause and risk.
4843 | Equipment Failure/Involved | Other | Recloser | Broken | Medium | System Hardening does not address Reclosers but coverered conductor will reduce annual recloser operations.
4844 | Equipment Failure/Involved | Other | Sectionalizer | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4845 | Equipment Failure/Involved | Other | Capacitor | Contaminated | Low | Capacitors are routinely inspected. Hardening is not addressing the equipment specifically but replaces non exempt fuses.
4846 | Equipment Failure/Involved | Other | Splice box | Blown/failed | All | Underground facilities = no ignition risk
4847 | Equipment Failure/Involved | Other | Cutout- Fused- Distribution | Together | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
4848 | Equipment Failure/Involved | Other | Manhole- primary box | Contaminated | All | Underground facilities = no ignition risk
4849 | Equipment Failure/Involved | Other | Interrupter | Normal | All | Underground facilities = no ignition risk
4850 | Equipment Failure/Involved | Other | Connector or Splice (OH) | Together | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
4851 | Equipment Failure/Involved | Other | Regulator- LTC substation | Normal | None | Circuit Hardening will not affect substation equipment.
4852 | Equipment Failure/Involved | Other | Anchor or Guy | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4853 | Equipment Failure/Involved | Other | Regulator | Deteriorated | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
4854 | Equipment Failure/Involved | Other | Crossarm- Wood | Together | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
4855 | Equipment Failure/Involved | Other | Conductor- Overhead | Contaminated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4856 | Equipment Failure/Involved | Other | Pole - Tower- steel | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4857 | Equipment Failure/Involved | Other | Crossarm- Wood | Arcing | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
4858 | Equipment Failure/Involved | Other | Bushing | Burned Open | None | Significant external force broke the bushing. Ignition risk not mitigated.
4859 | Equipment Failure/Involved | Other | Crossarm- Wood | Bent or Twisted | All | Composite arms are being installed along with new insulators and bonding. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
4860 | Equipment Failure/Involved | Other | Splice box | Burned/flashed | All | Underground facilities = no ignition risk
4861 | Equipment Failure/Involved | Other | Booster | Arcing | All | Circuit Hardening replaces boosters with voltage regulators.
4862 | Equipment Failure/Involved | Other | Switch | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4863 | Equipment Failure/Involved | Other | Metering Equipment | Broken | None | System Hardening does not address Metering facilities.
4864 | Equipment Failure/Involved | Other | Circuit Breaker | Malfunctioning | Medium | System Hardening does not address substation equipment but coverered conductor will reduce annual breaker operations.
4865 | Equipment Failure/Involved | Other | Bushing | Malfunctioning | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks.
4866 | Equipment Failure/Involved | Other | Bus | Malfunctioning | High | Transformers installed prior to 2014 will be replaced. Work would include covering jumpers and replacing some of the service conductor.
4867 | Equipment Failure/Involved | Other | Cutout- fuse holder | Bent or Twisted | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
4868 | Equipment Failure/Involved | Other | Connector or Splice (UG) | Contaminated | All | Underground facilities = no ignition risk
4869 | Equipment Failure/Involved | Other | Cutout- Fused- Distribution | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
4870 | Equipment Failure/Involved | Other | Regulator | Broken | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
4871 | Equipment Failure/Involved | Other | Bushing | Arcing | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks.
4872 | Equipment Failure/Involved | Other | Transformer | Bent or Twisted | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4873 | Equipment Failure/Involved | Other | Street Light Equipment | Malfunctioning | Medium | System Hardening will not address Street Lights but will address their transformers.
4874 | Equipment Failure/Involved | Other | Riser | Arcing | High | Risers are indirectly addressed on System Hardening - Pole changeouts, the covering of jumpers and leads, along with covering conductor should mitigate outages and risk.
4875 | Equipment Failure/Involved | Other | Splice box | Broken | All | Underground facilities = no ignition risk
4876 | Equipment Failure/Involved | Other | Fuse | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4877 | Equipment Failure/Involved | Other | PGs- Kearneys | Contaminated | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
4878 | Equipment Failure/Involved | Other | Bus | Arcing | High | Transformers installed prior to 2014 will be replaced. Work would include covering jumpers and replacing some of the service conductor.
4879 | Equipment Failure/Involved | Other | Woodpin | Burned/flashed | All | Composite arms are being installed along with new insulators and bonding. Tracking insulators/pole fires will be limited though not 100% eliminate. Gunshot damage will still be a concern. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
4880 | Equipment Failure/Involved | Other | Service conductor | Burned/flashed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4881 | Equipment Failure/Involved | Other | Splice box | Malfunctioning | All | Underground facilities = no ignition risk
4882 | Equipment Failure/Involved | Other | Connector or Splice (UG) | Broken- wire on ground | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
4883 | Equipment Failure/Involved | Other | Crossarm- Steel | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4884 | Equipment Failure/Involved | Other | Circuit Breaker | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4885 | Equipment Failure/Involved | Other | Metering Equipment | Deteriorated | None | System Hardening does not address Metering facilities.
4886 | Equipment Failure/Involved | Other | Pole - Tower- steel | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4887 | Equipment Failure/Involved | Other | Other | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4888 | Equipment Failure/Involved | Other | Service conductor | Contaminated | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4889 | Equipment Failure/Involved | Other | Pole-Wood | Contaminated | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
4890 | Equipment Failure/Involved | Other | Woodpin | Burned Open | All | Composite arms are being installed along with new insulators and bonding. Tracking insulators/pole fires will be limited though not 100% eliminate. Gunshot damage will still be a concern. Normal wood related decay/damage will be mitigated through this change and covered conductor will eliminate the line slap and associated risk with this outage
4891 | Equipment Failure/Involved | Other | Elbow | Bent or Twisted | All | Underground facilities = no ignition risk
4892 | Equipment Failure/Involved | Other | Lightning Arrestor | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4893 | Equipment Failure/Involved | Other | Fuse | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4894 | Equipment Failure/Involved | Other | Sectionalizer | Broken | Medium | System Hardening does not address Reclosers/Sectionalizers but coverered conductor will reduce annual recloser operations.
4895 | Equipment Failure/Involved | Other | Fuse | Bent or Twisted | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
4896 | Equipment Failure/Involved | Other | Manhole- primary box | Broken | All | Underground facilities = no ignition risk
4897 | Equipment Failure/Involved | Other | Metering Equipment | Arcing | None | System Hardening does not address Metering facilities.
4898 | Equipment Failure/Involved | Other | Metering Equipment | Normal | None | System Hardening does not address Metering facilities.
4899 | Equipment Failure/Involved | Other | Regulator | Normal | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
4900 | Equipment Failure/Involved | Other | Booster | Broken | All | Circuit Hardening replaces boosters with voltage regulators.
4901 | Equipment Failure/Involved | Other | Booster | Leaking | All | Circuit Hardening replaces boosters with voltage regulators.
4902 | Equipment Failure/Involved | Other | Recloser | Burned Open | Medium | System Hardening does not address Reclosers but coverered conductor will reduce annual recloser operations.
4903 | Equipment Failure/Involved | Other | Bus | Bent or Twisted | High | Transformers installed prior to 2014 will be replaced. Work would include covering jumpers and replacing some of the service conductor.
4904 | Unknown Cause | Patrol - found nothing | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4905 | Unknown Cause | Patrol - found nothing | Fuse | Burned Open | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
4906 | Unknown Cause | Patrol - found nothing | Secondary | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4907 | Unknown Cause | Patrol - found nothing | Sectionalizer | Malfunctioning | Medium | System Hardening does not address Reclosers/Sectionalizers but coverered conductor will reduce annual recloser operations.
4908 | Unknown Cause | Patrol - found nothing | Insulator | Burned/flashed | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
4909 | Unknown Cause | Patrol - found nothing | Connector or Splice (OH) | Deteriorated | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
4910 | Unknown Cause | Patrol - found nothing | Conductor- Overhead | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4911 | Unknown Cause | Patrol - found nothing | Fuse | Normal | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
4912 | Unknown Cause | Patrol - found nothing | Fuse | Broken | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
4913 | Unknown Cause | Patrol - found nothing | Transformer | Arcing | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4914 | Unknown Cause | Patrol - found nothing | Insulator | Arcing | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
4915 | Unknown Cause | Patrol - found nothing | Insulator | Blown/failed | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
4916 | Unknown Cause | Patrol - found nothing | Other | Burned Open | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4917 | Unknown Cause | Patrol - found nothing | Conductor- Overhead | Burned Open | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4918 | Unknown Cause | Patrol - found nothing | Other | Burned/flashed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4919 | Unknown Cause | Patrol - found nothing | Cutout- fuse holder | Burned Open | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
4920 | Unknown Cause | Patrol - found nothing | Transformer | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4921 | Unknown Cause | Patrol - not conducted | Conductor- Underground | Broken | All | Underground facilities = no ignition risk
4922 | Unknown Cause | Patrol - not conducted | Elbow | Blown/failed | All | Underground facilities = no ignition risk
4923 | Unknown Cause | Patrol - not conducted | Fuse | Normal | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
4924 | Unknown Cause | Patrol - not conducted | Fuse | Burned Open | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
4925 | Unknown Cause | Patrol - not conducted | Other | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4926 | Vegetation | Other ground vegetation | Transformer | Malfunctioning | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4927 | Vegetation | Other ground vegetation | Customer Equipment | Arcing | None | No work is being completed on customer equipment.
4928 | Vegetation | Other ground vegetation | Bus | Contaminated | High | Transformers installed prior to 2014 will be replaced. Work would include covering jumpers and replacing some of the service conductor.
4929 | Vegetation | Other ground vegetation | Conductor- Overhead | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4930 | Vegetation | Other ground vegetation | Secondary | Contaminated | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4931 | Vegetation | Tree - bark fell into line | Conductor- Overhead | Malfunctioning | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4932 | Vegetation | Tree - bark fell into line | Cutout- Fused- Distribution | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
4933 | Vegetation | Tree - bark fell into line | Fuse | Burned Open | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
4934 | Vegetation | Tree - bark fell into line | Switch | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4935 | Vegetation | Tree - bark fell into line | Transformer | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4936 | Vegetation | Tree - bark fell into line | Conductor- Overhead | Burned Open | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4937 | Vegetation | Tree - bark fell into line | Bushing | Normal | Medium | System Hardening will indirectly replace some bushings by replacing pre-2014 transformers and Booster banks.
4938 | Vegetation | Tree - bark fell into line | Secondary | Bent or Twisted | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4939 | Vegetation | Tree - bark fell into line | Regulator | Burned/flashed | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
4940 | Vegetation | Tree - branch fell on line | Cutout- Fused- Distribution | Malfunctioning | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
4941 | Vegetation | Tree - branch fell on line | Cutout- Fused- Distribution | Burned/flashed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
4942 | Vegetation | Tree - branch fell on line | Riser | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4943 | Vegetation | Tree - branch fell on line | Crossarm- Steel | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4944 | Vegetation | Tree - branch fell on line | Secondary | Malfunctioning | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4945 | Vegetation | Tree - branch fell on line | Recloser | Blown/failed | Medium | System Hardening does not address Reclosers but coverered conductor will reduce annual recloser operations.
4946 | Vegetation | Tree - branch fell on line | Conductor- Overhead | Burned Open | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4947 | Vegetation | Tree - branch fell on line | Connector or Splice (OH) | Blown/failed | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
4948 | Vegetation | Tree - branch fell on line | Conductor- Underground | Broken- wire on ground | None | Not enough outage information or correct information in ILIS to determine effect of System Hardening
4949 | Vegetation | Tree - branch fell on line | Connector or Splice (OH) | Malfunctioning | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
4950 | Vegetation | Tree - branch fell on line | Conductor- Underground | Burned Open | All | Underground facilities = no ignition risk
4951 | Vegetation | Tree - branch fell on line | Other | Malfunctioning | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4952 | Vegetation | Tree - branch fell on line | Connector or Splice (OH) | Arcing | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
4953 | Vegetation | Tree - branch fell on line | Crossarm- Wood | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4954 | Vegetation | Tree - branch fell on line | Anchor or Guy | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4955 | Vegetation | Tree - branch fell on line | Anchor or Guy | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4956 | Vegetation | Tree - branch fell on line | Cutout- fuse holder | Burned Open | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
4957 | Vegetation | Tree - branch fell on line | Conductor- Underground | Broken | All | Underground facilities = no ignition risk
4958 | Vegetation | Tree - branch fell on line | Elbow | Normal | All | Underground facilities = no ignition risk
4959 | Vegetation | Tree - branch fell on line | Pole-Wood | Burned/flashed | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
4960 | Vegetation | Tree - branch fell on line | Fuse | Burned/flashed | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
4961 | Vegetation | Tree - branch fell on line | Service conductor | Burned Open | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4962 | Vegetation | Tree - cutting- PG&E contractor | Service conductor | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4963 | Vegetation | Tree - cutting- PG&E contractor | Transformer | Broken | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4964 | Vegetation | Tree - cutting- PG&E contractor | Conductor- Overhead | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4965 | Vegetation | Tree - cutting- PG&E contractor | Conductor- Overhead | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4966 | Vegetation | Tree - cutting- PG&E contractor | Fuse | Malfunctioning | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
4967 | Vegetation | Tree - cutting- PG&E contractor | Conductor- Overhead | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4968 | Vegetation | Tree - fell into line | Conductor- Underground | Malfunctioning | All | Underground facilities = no ignition risk
4969 | Vegetation | Tree - fell into line | Secondary | Malfunctioning | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4970 | Vegetation | Tree - fell into line | Anchor or Guy | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4971 | Vegetation | Tree - fell into line | Recloser | Blown/failed | Medium | System Hardening does not address Reclosers but coverered conductor will reduce annual recloser operations.
4972 | Vegetation | Tree - fell into line | Connector or Splice (OH) | Malfunctioning | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
4973 | Vegetation | Tree - fell into line | Service conductor | Arcing | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4974 | Vegetation | Tree - fell into line | Riser | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4975 | Vegetation | Tree - fell into line | Pole-Wood | Bent or Twisted | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
4976 | Vegetation | Tree - fell into line | Other | Malfunctioning | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4977 | Vegetation | Tree - fell into line | Splice box | Malfunctioning | All | Underground facilities = no ignition risk
4978 | Vegetation | Tree - fell into line | Transformer | Annealed | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4979 | Vegetation | Tree - fell into line | Crossarm- Steel | Bent or Twisted | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4980 | Vegetation | Tree - fell into line | Fuse | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4981 | Vegetation | Tree - fell into line | Cutout- Fused- Distribution | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
4982 | Vegetation | Tree - fell into line | Anchor or Guy | Deteriorated | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4983 | Vegetation | Tree - fell into line | Riser | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4984 | Vegetation | Tree - fell into line | Pole-Wood | Malfunctioning | High | We are replacing nearly 100% of the poles, some with alternate materials such as composite. Material failure will be limited though not altogether eliminated. Covered conductor would have eliminated risk line slap and risk.
4985 | Vegetation | Tree - fell into line | Other | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4986 | Vegetation | Tree - grew into line | Conductor- Overhead | Malfunctioning | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4987 | Vegetation | Tree - grew into line | Service conductor | Broken- wire on object | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4988 | Vegetation | Tree - grew into line | Conductor- Overhead | Burned Open | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4989 | Vegetation | Tree - grew into line | Transformer | Malfunctioning | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4990 | Vegetation | Tree - grew into line | Fuse | Broken | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
4991 | Vegetation | Tree - grew into line | Secondary | Malfunctioning | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
4992 | Vegetation | Tree - grew into line | Conductor- Overhead | Annealed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4993 | Vegetation | Tree - grew into line | Connector or Splice (OH) | Arcing | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
4994 | Vegetation | Tree - grew into line | Other | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4995 | Vegetation | Tree - grew into line | Fuse | Burned Open | All | Non-exempt fused cutouts replaced and covering conductor should eliminate outages and risk.
4996 | Vegetation | Tree - grew into line | Other | Arcing | All | Covered conductor will eliminate the line slap and risk associated with this outage.
4997 | Vegetation | Tree - grew into line | Customer Equipment | Broken | None | No work is being completed on customer equipment.
4998 | Vegetation | Tree - grew into line | Transformer | Leaking | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
4999 | Vegetation | Tree - grew into line | Connector or Splice (OH) |  | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
5000 | Vegetation | Tree - grew into line | Transformer | Burned Open | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
5001 | Vegetation | Tree - grew into line | Service conductor | Together | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
5002 | Vegetation | Tree - palm frond fell into line | Cutout- Fused- Distribution | Blown/failed | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
5003 | Vegetation | Tree - palm frond fell into line | Pole-Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
5004 | Vegetation | Tree - palm frond fell into line | Connector or Splice (OH) | On Ground | High | Circuit Hardening will temporarily eliminate splices. Still allowed for emergency repairs. Splices, clamps, and connectors still pose a risk.
5005 | Vegetation | Tree - palm frond fell into line | Secondary | Bent or Twisted | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
5006 | Vegetation | Tree - palm frond fell into line | Transformer | Normal | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
5007 | Vegetation | Tree - palm frond fell into line | Insulator | Blown/failed | All | System hardening replaces with composite cross arms and new insulators. Covered Conductor would have eliminated line slap and risk that caused the outage.
5008 | Vegetation | Tree - palm frond fell into line | Transformer | Arcing | High | Transformers installed prior to 2014 will be replaced with those with FR3 fluid eliminating risk associated with mineral oil. Hardening includes having their leads/jumpers covered.
5009 | Vegetation | Tree - palm frond fell into line | Cutout- fuse holder | Burned Open | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
5010 | Vegetation | Tree - palm frond fell into line | Other | Normal | All | Covered conductor will eliminate the line slap and risk associated with this outage.
5011 | Vegetation | Tree - palm frond fell into line | Cutout- Fused- Distribution | Normal | High | Non-exempt fused cutouts are being replaced on System Hardening Projects.
5012 | Vegetation | Tree - palm frond fell into line | Conductor- Overhead | Burned Open | All | Covered conductor will eliminate the line slap and risk associated with this outage.
5013 | Vegetation | Tree - palm frond fell into line | Conductor- Overhead | Blown/failed | All | Covered conductor will eliminate the line slap and risk associated with this outage.
5014 | Vegetation | Tree - palm frond fell into line | Other | Broken | All | Covered conductor will eliminate the line slap and risk associated with this outage.
5015 | Wildfire Mitigation | CWSP - Vegetation Removal |  |  | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5016 | Wildfire Mitigation | CWSP - Vegetation Removal | Conductor- Overhead | Normal | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5017 | Wildfire Mitigation | CWSP - Vegetation Removal | Transformer (OH) | Normal | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5018 | Wildfire Mitigation | CWSP - Vegetation Removal | Other | Normal | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5019 | Wildfire Mitigation | CWSP - Vegetation Removal | Fuse | Normal | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5020 | Wildfire Mitigation | CWSP - Vegetation Removal | Pole-Wood | Broken | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5021 | Wildfire Mitigation | CWSP - Vegetation Removal | Conductor- Overhead | Annealed | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5022 | Wildfire Mitigation | CWSP - Vegetation Removal | Secondary | Annealed | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
5023 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor- Overhead | Normal | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5024 | Wildfire Mitigation | Public Safety Power Shut-off | Pole-Wood | Broken | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5025 | Wildfire Mitigation | Public Safety Power Shut-off | Crossarm- Wood | Broken | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5026 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor- Overhead | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
5027 | Wildfire Mitigation | Public Safety Power Shut-off |  |  | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5028 | Wildfire Mitigation | Public Safety Power Shut-off | Transformer (UG) | Blown/failed | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5029 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor- Overhead | Broken | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5030 | Wildfire Mitigation | Public Safety Power Shut-off | Cutout- fuse holder | Broken | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5031 | Wildfire Mitigation | Public Safety Power Shut-off | Customer Equipment | Broken | None | No work is being completed on customer equipment.
5032 | Wildfire Mitigation | Public Safety Power Shut-off | Other | Broken | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5033 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor- Overhead | Deteriorated | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5034 | Wildfire Mitigation | Public Safety Power Shut-off | Anchor or Guy | Broken | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5035 | Wildfire Mitigation | Public Safety Power Shut-off | Crossarm- Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
5036 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor- Overhead |  | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5037 | Wildfire Mitigation | Public Safety Power Shut-off | Pole-Wood | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
5038 | Wildfire Mitigation | Public Safety Power Shut-off | Insulator | Broken | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5039 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor- Overhead | Contaminated | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5040 | Wildfire Mitigation | Public Safety Power Shut-off | Circuit Breaker | Normal | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5041 | Wildfire Mitigation | Public Safety Power Shut-off | Fuse | Normal | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5042 | Wildfire Mitigation | Public Safety Power Shut-off | Recloser | Normal | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5043 | Wildfire Mitigation | Public Safety Power Shut-off | Service conductor | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
5044 | Wildfire Mitigation | Public Safety Power Shut-off | Switch (OH) | Normal | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5045 | Wildfire Mitigation | Public Safety Power Shut-off | Sectionalizer | Normal | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5046 | Wildfire Mitigation | Public Safety Power Shut-off | Switch (OH) |  | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5047 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor- Underground | Normal | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5048 | Wildfire Mitigation | Public Safety Power Shut-off | Transformer (OH) | Blown/failed | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5049 | Wildfire Mitigation | Public Safety Power Shut-off | SCADA | Normal | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5050 | Wildfire Mitigation | Public Safety Power Shut-off | Generator | Normal | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5051 | Wildfire Mitigation | Public Safety Power Shut-off | Fuse |  | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5052 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor- Overhead | Together | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5053 | Wildfire Mitigation | Public Safety Power Shut-off | Other | Malfunctioning | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5054 | Wildfire Mitigation | Public Safety Power Shut-off | Crossarm- Wood | Deteriorated | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5055 | Wildfire Mitigation | Public Safety Power Shut-off | Secondary | Broken- wire on ground | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
5056 | Wildfire Mitigation | Public Safety Power Shut-off |  | Broken | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5057 | Wildfire Mitigation | Public Safety Power Shut-off | Switch (UG) | Normal | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5058 | Wildfire Mitigation | Public Safety Power Shut-off |  | Normal | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5059 | Wildfire Mitigation | Public Safety Power Shut-off | Connector or Splice (OH) | Broken | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5060 | Wildfire Mitigation | Public Safety Power Shut-off | Connector or Splice (OH) | Broken- wire on ground | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5061 | Wildfire Mitigation | Public Safety Power Shut-off | Pole-Wood | On Ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
5062 | Wildfire Mitigation | Public Safety Power Shut-off | Jumper | Normal | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5063 | Wildfire Mitigation | Public Safety Power Shut-off | Secondary | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
5064 | Wildfire Mitigation | Public Safety Power Shut-off | Secondary | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
5065 | Wildfire Mitigation | Public Safety Power Shut-off | Secondary | Together | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
5066 | Wildfire Mitigation | Public Safety Power Shut-off | Regulator | Normal | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
5067 | Wildfire Mitigation | Public Safety Power Shut-off | Recloser |  | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5068 | Wildfire Mitigation | Public Safety Power Shut-off | Woodpin | Broken | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5069 | Wildfire Mitigation | Public Safety Power Shut-off | PT/CCVT | Blown/failed | None | Nothing significant to fire mitigation will be done to this equipment as part of hardening.
5070 | Wildfire Mitigation | Public Safety Power Shut-off | Jumper | Broken | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5071 | Wildfire Mitigation | Public Safety Power Shut-off | Conductor- Overhead | Bent or Twisted | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5072 | Wildfire Mitigation | Public Safety Power Shut-off | Transformer | Blown/failed | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5073 | Wildfire Mitigation | Public Safety Power Shut-off | Pole-Wood | Normal | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5074 | Wildfire Mitigation | Public Safety Power Shut-off | Bushing | Broken | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5075 | Wildfire Mitigation | Public Safety Power Shut-off | Jumper | Burned Open | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5076 | Wildfire Mitigation | Public Safety Power Shut-off | Switch (OH) | Broken | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5077 | Wildfire Mitigation | Public Safety Power Shut-off | Crossarm- Wood | Burned/flashed | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5078 | Wildfire Mitigation | Public Safety Power Shut-off | Other | Normal | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5079 | Wildfire Mitigation | Public Safety Power Shut-off | Relay | Normal | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5080 | Wildfire Mitigation | Public Safety Power Shut-off | Transformer | Broken- wire on ground | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
5081 | Wildfire Mitigation | Public Safety Power Shut-off | Transformer (OH) | Broken | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5082 | Wildfire Mitigation | Public Safety Power Shut-off | Service conductor | Broken | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
5083 | Wildfire Mitigation | Public Safety Power Shut-off | Service conductor | Normal | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
5084 | Wildfire Mitigation | Public Safety Power Shut-off | Service conductor | Broken- wire on object | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
5085 | Wildfire Mitigation | Public Safety Power Shut-off | Fuse | Blown/failed | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5086 | Wildfire Mitigation | Public Safety Power Shut-off | Pole-Wood | Burned/flashed | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5087 | Wildfire Mitigation | Public Safety Power Shut-off | Customer Equipment | Deteriorated | None | No work is being completed on customer equipment.
5088 | Wildfire Mitigation | Public Safety Power Shut-off | Transformer (UG) | Burned/flashed | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5089 | Wildfire Mitigation | Public Safety Power Shut-off | Secondary | Deteriorated | Low | System hardening projects will change out pre-2014 transformers and changeout services based on age and condition or not meeting current Standards.
5090 | Wildfire Mitigation | Public Safety Power Shut-off | Pole-Wood | Broken- wire on object | Medium | Significant external force broke the conductor and brought wire to the ground/object. System Hardening will make circuitry more robust. System Hardening moderately reduce ignition risk.
5091 | Wildfire Mitigation | Public Safety Power Shut-off | Cutout- fuse holder | Blown/failed | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5092 | Wildfire Mitigation | Public Safety Power Shut-off | Pole-Wood | Deteriorated | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5093 | Wildfire Mitigation | Public Safety Power Shut-off | Customer Equipment | Normal | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5094 | Wildfire Mitigation | Public Safety Power Shut-off | Lightning Arrestor | Blown/failed | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.
5095 | Wildfire Mitigation | Public Safety Power Shut-off | Transformer | Broken | All | Wildfire/CWSP Vegetation Removal outages - Covered conductor, removal of non-exempt equipment, and more robust circuitry (poles, crossarms, etc) will eliminate ignition risk.